## Contents
System Requirements Form (SRF) – Boundary Transfer Requirement |  |  | Select a Boundary to view
B0
B1
B1a
B2
B3b
B4
B5
B6
B7
B7a
B8
B9
B13
B14
B15
EC5
LE1
NW1
NW2
NW3
SC1
SC1.5
SC2
SC3
How to interprete the Graphs |  |  | Note
Due to the time needed to prepare and conduct the BID3 simulation runs the SRF part A will come in 3 staged parts. First with SQSS boundary required transfers, followed by boundary flow distribution plots and finally with constraint heatmap.
Version | Date Uploaded | Changes
v1 | 2021-05-25 | Initial publication
v2 | 2021-06-10 | 2nd version with boundary flow distributions added
v3 | 2021-07-09 | 3rd version with added constaint heatmap and updated charts
Legal Notice
The information contained within the System Requirements Form (“the Document”) is disclosed voluntarily and without charge. While National Grid Electricity System Operator Limited has not sought to mislead any person as to the contents of this document and whilst such content represent its best view as at the time of publication, readers of this document should not place any reliance on the contents of this document. The contents of this document must be considered as illustrative only and no warranty can be or is made as to the accuracy and completeness of such contents , nor shall anything within this document constitute an offer capable of acceptance or form the basis of any contract. Other than in the event of fraudulent misstatement or fraudulent misrepresentation, National Grid Electricity System Operator Limited does not accept any responsibility for any use which is made of the information contained within this document.
The System Requirements Form (SRF) presents the boundary required transfers for ETYS boundaries calculated in accordance with the planning criteria defined within Chapter 4 of the National Electricity Transmission System Security and Quality of Supply Standard (NETS SQSS). The boundary required transfer calculation uses the latest Future Energy Scenarios (FES) and is the minimum transmission boundary transfer requirement to which we are required to plan the electricity transmission network. In years where the calculated required transfer exceeds the boundary capability, this indicates that the transmission system requires reinforcement or network management solutions in order to satisfy the SQSS.
As part of the annual ETYS process, the ESO produces and circulates the SRF boundary transfer requirements and receives options to satisfy these requirements. It is these options that are assessed within the annual Network Options Assessment (NOA) process.
We are making the SRF publicly available as a first step in our pathway to facilitate options from a broader range of participants. Going forward, we recognise that we need to review our information and processes, including the SRF, in order to make them more accessible to a broader range of participants.
NOTE: This SRF has been prepared by the ESO and can be revised following feedback from the Transmission Owners who undertake their own similar calculations.
If you have any comments or questions on the SRF please email: transmission.etys@nationalgrideso.com
FES Scenarios
SRF: ESO calculates and circulates Boundary Transfer Requirement
ETYS
ESO receives options to meet requirements
NOA

## Interpreting the Graphs
BACK to Contents
Interpreting the boundary graphs
There are two formats of the ETYS boundary transfer graphs provided:
The first graph represents the required tranfers for 2021 (solid lines) and 2020 (dotted). These graphs show the most onerous required transfer considering both the economy and security required transfers for each scenario. The black solid line represents the ETYS published boundary capability for 2020.
The graphs and tables of required transfers can show both positive and negative values. The sign represents direction of power flow. Some boundaries, such as most northern boudnareis mostly experice power flow in one direction but others, such as those in the south, which contain significant demand or European interconnectors can see power flows in both directions. The boundary capability is generally assessed according to the intial direction. It should not be assumed that the boundarycapability is the same in the opposite flow direction.
The second set of four graphs show a distribution of power flow for each scenario, in addition to the boundary power transfer capability (2020) and NETS SQSS requirements to 2041.
Using the B6 boundary charts as an example, it can be seen that a separate chart is provided for each of the four Future Energy Scenarios. Each scenario has different generation and demand so produces different boundary power flow expectations. The NETS SQSS sets the methodology to set the wider boundary planning requirements, i.e., the Economy and Security criteria discussed above. These are shown in the graphs as a solid coloured line for Economy required transfer and a dashed coloured line for Security required transfer.
Boundary capability, in accordance with NETS SQSS requirements, is represented as a solid flat line on the graphs. The line position is calculated to represent the expected boundary capability for 2020/21 winter peak. The boundary capability will change over time as the network, generation and demand change, all of which are uncertain. Therefore, to show system future needs and opportunities for each boundary a single straight capability line based on the present conditions is shown.
Two shaded areas are now shown on each boundary graph which represents the distribution of annual power flow. The darker shaded area shows an area in which 50% of the annual power flows lie. In percentile terms, 75% of annual power flows are lower than the upper edge of the darker shaded area and 75% are higher than the lower edge. The lighter and darker shaded areas together show an area in which 90% of the annual power flows lie. In percentile terms, 95% of annual power flows are lower than the upper edge of the lighter shaded area and 95% are higher than the lower edge.
The calculations of the annual boundary flow are based on unconstrained market operation, meaning network restrictions are not applied. This way, the minimum cost generation output profile can be found. By looking at the free market power flows in comparison with boundary capability, it can be seen where future growing needs can be expected.

## Heatmap
No reinforcements applied
The following heatmaps, the result of simulating future network operational constraints using the Leading the Way scenario, gives indication of which boundaries are potentially constained and to what extent. Green colours are low value constaints, moving towards red which is peak constaint. Th is to indicate which boundaries need reinforced and when. No NOA recommended reinforcements have been included in these constaint calculations. Both 2020 and 2021 FES Leading the Way scenarios have been provided for comparison purposes.

## B0
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B0
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 1000MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 757.3081 | 789.7624 | 890.7718 | 1380.7516 | 1679.3627 | 2171.8638 | 2260.743 | 2801.1391 | 4323.6651 | 5305.4144 | 6493.3596
| Consumer Transformation 2021 | N-D | 758.3792 | 762.3451 | 765.5499 | 889.3803 | 1331.8502 | 1549.3758 | 1707.0717 | 2269.5433 | 2795.4721 | 4869.5396 | 4947.8482
| System Transformation 2021 | N-D | 752.1884 | 760.5634 | 758.8215 | 847.8641 | 1324.9718 | 1474.4051 | 1538.8554 | 1682.149 | 2201.167 | 4142.8518 | 4422.1514
| Steady Progression 2021 | N-D | 683.3225 | 749.194 | 747.0819 | 751.1121 | 748.1737 | 880.7661 | 931.401 | 1509.9822 | 1568.4064 | 2117.4454 | 2158.9317
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 124.2166 | 126.3961 | 134.8834 | 130.0909 | 146.1041 | 217.7773 | 145.2923 | 155.7557 | 240.153 | 192.4694 | 183.5077
| Consumer Transformation 2021 | N-D | 124.1597 | 196.5309 | 202.4815 | 138.1499 | 145.926 | 149.6961 | 153.3363 | 227.7958 | 248.6425 | 265.0058 | 207.4732
| System Transformation 2021 | N-D | 118.1477 | 194.2886 | 191.1683 | 124.235 | 134.1103 | 134.0899 | 134.2029 | 134.2036 | 137.7135 | 217.3516 | 233.4899
| Steady Progression 2021 | N-D | 116.1414 | 187.7645 | 186.0174 | 193.0727 | 186.2452 | 186.666 | 186.5429 | 117.3587 | 186.199 | 185.3942 | 206.8118
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B1
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B1
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 2500MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 2502.7626 | 2610.5632 | 2735.3492 | 3275.5458 | 4175.6008 | 5006.6778 | 5598.8345 | 6294.2108 | 7964.7085 | 8823.9783 | 9906.6196
| Consumer Transformation 2021 | N-D | 2498.65 | 2574.2656 | 2585.4689 | 2706.6825 | 3165.9853 | 3721.2462 | 4424.4235 | 5248.5871 | 6058.4513 | 7775.2265 | 7848.8827
| System Transformation 2021 | N-D | 2482.6842 | 2513.6241 | 2522.912 | 2592.1085 | 3146.4392 | 3538.8938 | 3899.1369 | 4481.8509 | 5067.5583 | 7000.2659 | 7385.0414
| Steady Progression 2021 | N-D | 2419.8532 | 2449.1058 | 2436.043 | 2455.1669 | 2459.6356 | 2620.057 | 2720.2441 | 3513.8129 | 3962.4038 | 4890.0637 | 5124.4845
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 807.3434 | 819.9862 | 837.0805 | 836.902 | 856.2607 | 958.2767 | 855.7322 | 1373.4986 | 2186.3127 | 2175.8741 | 2157.0389
| Consumer Transformation 2021 | N-D | 797.5429 | 920.1467 | 921.0654 | 827.6961 | 839.951 | 845.5884 | 850.3644 | 970.184 | 1038.5548 | 1081.7069 | 1107.6889
| System Transformation 2021 | N-D | 785.2558 | 912.1369 | 894.2434 | 799.6164 | 810.1938 | 806.7726 | 802.4076 | 802.6804 | 798.0578 | 951.3761 | 1007.6908
| Steady Progression 2021 | N-D | 772.2507 | 880.3286 | 869.3298 | 904.1491 | 866.9354 | 866.1018 | 863.6107 | 754.5808 | 859.1532 | 852.0156 | 960.2938
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B1a
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B1a
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 2300MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 3217.0146 | 3324.8152 | 3449.6012 | 4693.2978 | 5479.8052 | 6267.2378 | 6859.3945 | 7596.7708 | 9267.2685 | 10326.5383 | 11456.2196
| Consumer Transformation 2021 | N-D | 3212.902 | 3288.5176 | 3299.7209 | 3420.9345 | 4552.2373 | 5097.365 | 5701.2261 | 6509.1471 | 7319.0113 | 9035.7865 | 9351.4427
| System Transformation 2021 | N-D | 3196.9362 | 3227.8761 | 3237.164 | 3306.3605 | 4532.6912 | 4925.1458 | 5283.7193 | 5780.9292 | 6328.1183 | 8260.8259 | 8645.6014
| Steady Progression 2021 | N-D | 3134.1052 | 3163.3578 | 3150.295 | 3169.4189 | 3173.8876 | 3334.309 | 4106.4961 | 4926.9053 | 5320.9675 | 6150.6237 | 6385.0445
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 807.3434 | 819.9862 | 837.0805 | 836.902 | 856.2607 | 958.2767 | 855.7322 | 1373.4986 | 2186.3127 | 2524.179 | 2502.8764
| Consumer Transformation 2021 | N-D | 797.5429 | 920.1467 | 921.0654 | 827.6961 | 839.951 | 845.5884 | 850.3644 | 970.184 | 1038.5548 | 1081.7069 | 1473.3543
| System Transformation 2021 | N-D | 785.2558 | 912.1369 | 894.2434 | 799.6164 | 810.1938 | 806.7726 | 802.4076 | 802.6804 | 798.0578 | 951.3761 | 1007.6908
| Steady Progression 2021 | N-D | 772.2507 | 880.3286 | 869.3298 | 904.1491 | 866.9354 | 866.1018 | 863.6107 | 754.5808 | 859.1532 | 852.0156 | 960.2938
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B2
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B2
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 2800MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 4698.4719 | 4812.4599 | 4909.7919 | 5916.7409 | 6748.6321 | 6783.7228 | 5964.1723 | 7236.3733 | 8875.5035 | 10677.5329 | 12470.0209
| Consumer Transformation 2021 | N-D | 4686.0104 | 4764.5708 | 4754.6232 | 4841.0775 | 5790.4968 | 6323.296 | 6918.9831 | 5716.0118 | 6433.264 | 8124.484 | 9431.2314
| System Transformation 2021 | N-D | 4665.2222 | 4726.9754 | 4717.9976 | 4734.1759 | 5811.1907 | 6148.0242 | 6524.8646 | 6347.4039 | 5656.1913 | 8143.9058 | 8462.643
| Steady Progression 2021 | N-D | 4614.7595 | 4592.8708 | 4565.2082 | 4600.7667 | 4571.9231 | 4751.5568 | 5395.9258 | 6055.9501 | 6462.8939 | 6342.0595 | 5819.5803
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 1570.8977 | 1590.214 | 1627.1308 | 1630.2285 | 1652.6169 | 771.8823 | 664.4283 | 1176.419 | 1993.6938 | 2355.6209 | 2336.6798
| Consumer Transformation 2021 | N-D | 1558.6247 | 1700.3492 | 1704.7754 | 1608.8934 | 1623.4171 | 1625.1101 | 1626.9684 | 762.7466 | 837.7327 | 907.0839 | 2381.6987
| System Transformation 2021 | N-D | 1540.6305 | 1689.7416 | 1652.8181 | 1570.5482 | 1580.1076 | 1568.7492 | 1557.1563 | 574.1115 | 559.9962 | 1414.0468 | 1496.8062
| Steady Progression 2021 | N-D | 1516.1691 | 1633.0908 | 1610.8697 | 1690.0979 | 1617.5188 | 1611.3231 | 1603.9323 | 1479.6083 | 1589.8011 | 1571.633 | 702.1693
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B3b
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B3b
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 430MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 499.8818 | 554.9833 | 553.6142 | 551.3685 | 643.9646 | 757.4836 | 830.6689 | 910.3818 | 948.2773 | 1004.3695 | 966.7664
| Consumer Transformation 2021 | N-D | 503.3605 | 505.5529 | 530.0513 | 521.1378 | 522.8499 | 584.8902 | 688.625 | 740.4957 | 950.9388 | 968.908 | 995.8323
| System Transformation 2021 | N-D | 498.515 | 503.0681 | 527.0791 | 515.1479 | 517.4528 | 594.4426 | 675.8239 | 649.8279 | 721.9014 | 891.1936 | 989.3245
| Steady Progression 2021 | N-D | 502.8548 | 487.8441 | 481.7391 | 489.5509 | 507.8598 | 509.3853 | 546.1451 | 563.7734 | 642.2002 | 651.3724 | 885.7797
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 246.8559 | 289.0307 | 292.296 | 287.6943 | 334.8271 | 334.5825 | 337.8362 | 339.9382 | 342.3422 | 347.3004 | 348.0682
| Consumer Transformation 2021 | N-D | 245.3017 | 249.2449 | 252.1031 | 254.4618 | 256.3961 | 259.785 | 302.4406 | 303.9211 | 314.497 | 333.9106 | 335.3871
| System Transformation 2021 | N-D | 243.3866 | 247.2381 | 246.6304 | 248.6533 | 248.1361 | 290.5025 | 290.8895 | 289.5366 | 288.7609 | 331.906 | 349.0509
| Steady Progression 2021 | N-D | 242.6323 | 243.0205 | 241.833 | 245.8584 | 242.5484 | 242.2885 | 284.0471 | 282.4926 | 282.7921 | 281.4413 | 300.4436
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.
Not available for B3b

## B4
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B4
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 3200MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 5997.0882 | 6169.4991 | 6271.3874 | 7261.4759 | 8183.7891 | 8304.6407 | 7621.1346 | 8958.8359 | 10585.2633 | 12523.4524 | 14222.3076
| Consumer Transformation 2021 | N-D | 5600.0984 | 6067.1748 | 6065.1619 | 6108.6539 | 7079.7711 | 7690.3379 | 8355.8924 | 7220.114 | 8194.7637 | 9864.269 | 11217.1961
| System Transformation 2021 | N-D | 5549.3665 | 6037.6021 | 6044.8924 | 6020.2377 | 7111.145 | 7505.4128 | 7953.9565 | 7782.3911 | 7149.8312 | 9837.535 | 10323.4556
| Steady Progression 2021 | N-D | 5120.2225 | 5444.5657 | 5782.3575 | 5852.167 | 5824.2805 | 5991.0902 | 6662.0653 | 7338.0661 | 7805.1733 | 7651.0902 | 7333.7787
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 1944.029 | 2041.9553 | 2127.5485 | 2142.8852 | 2204.185 | 1319.0777 | 1203.1026 | 1746.6254 | 2586.7009 | 3304.1288 | 3278.6531
| Consumer Transformation 2021 | N-D | 1927.5761 | 2087.748 | 2089.2819 | 1991.6009 | 2040.9209 | 2078.8077 | 2117.9742 | 1260.9943 | 1639.8153 | 1802.216 | 3336.3716
| System Transformation 2021 | N-D | 1861.3475 | 2068.496 | 2022.9627 | 1941.8327 | 1956.1045 | 1978.9178 | 1960.5561 | 1014.3637 | 1016.629 | 1949.2077 | 2362.7539
| Steady Progression 2021 | N-D | 1826.2481 | 1947.9487 | 1917.8284 | 2067.2452 | 1989.3233 | 1978.3588 | 2007.5824 | 1874.6953 | 1988.8068 | 2257.9455 | 1420.0187
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B5
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B5
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 3700MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 5636.8976 | 5812.1391 | 5885.5142 | 6949.978 | 7882.9025 | 7992.8582 | 7286.4476 | 8570.7286 | 10129.5824 | 12105.1944 | 13716.5957
| Consumer Transformation 2021 | N-D | 5205.5595 | 5678.2141 | 5659.6719 | 5667.0508 | 6639.4668 | 7251.2423 | 7894.755 | 6762.6495 | 7716.9396 | 9391.3064 | 10688.26
| System Transformation 2021 | N-D | 5148.1559 | 5650.8184 | 5653.1825 | 5596.6162 | 6699.8207 | 7084.004 | 7547.7164 | 7358.8285 | 6696.289 | 9317.0965 | 9841.584
| Steady Progression 2021 | N-D | 4722.1223 | 5010.2386 | 5334.9293 | 5400.8354 | 5350.6853 | 5503.7974 | 6165.7185 | 6827.13 | 7280.7798 | 7068.8132 | 6771.3431
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 2249.2871 | 2359.3672 | 2452.3164 | 2656.8864 | 2720.5201 | 1802.1056 | 1714.088 | 2256.7725 | 3155.8473 | 3603.9229 | 3566.0759
| Consumer Transformation 2021 | N-D | 2196.8685 | 2377.7723 | 2372.7448 | 2273.1767 | 2342.2632 | 2377.5325 | 2414.3707 | 1524.8153 | 1713.5888 | 2086.2102 | 3589.3498
| System Transformation 2021 | N-D | 2121.4754 | 2353.0474 | 2294.8283 | 2212.0507 | 2242.1613 | 2255.73 | 2254.0518 | 1261.3087 | 1248.5838 | 2250.1477 | 2435.4438
| Steady Progression 2021 | N-D | 2096.9316 | 2220.897 | 2180.0591 | 2360.4168 | 2251.3499 | 2243.5002 | 2267.3863 | 2113.2376 | 2228.7914 | 2182.1085 | 1460.2594
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B6
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B6
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 5700MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 9077.0892 | 9847.1569 | 10453.3112 | 12572.2529 | 14188.8967 | 15275.477 | 15640.8538 | 18244.6776 | 19920.2709 | 21675.5372 | 25045.2156
| Consumer Transformation 2021 | N-D | 8517.6896 | 8529.73 | 8879.7037 | 9708.5697 | 12113.5585 | 13293.2509 | 15152.417 | 14909.4983 | 17219.9685 | 18660.2675 | 19392.1062
| System Transformation 2021 | N-D | 8332.6971 | 8502.4744 | 8815.1493 | 9977.3288 | 12066.4708 | 13049.6315 | 14574.2998 | 14746.3811 | 15542.4416 | 17812.3801 | 18953.2895
| Steady Progression 2021 | N-D | 7579.8641 | 8242.2479 | 7937.158 | 8090.9946 | 8351.3047 | 9016.98 | 10304.8252 | 12004.1009 | 14335.4362 | 15598.9941 | 15386.3942
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 3007.4083 | 2302.623 | 2458.3659 | 2831.0014 | 2916.9773 | 1996.1055 | 1866.1553 | 2354.8327 | 3468.1812 | 3378.1515 | 2762.9864
| Consumer Transformation 2021 | N-D | 2921.1853 | 2292.1516 | 2322.3581 | 2396.538 | 2467.8167 | 2514.8097 | 2530.21 | 1644.9199 | 1894.4002 | 1936.6294 | 2757.1816
| System Transformation 2021 | N-D | 2813.9001 | 2234.9067 | 2195.8791 | 2288.2321 | 2317.7808 | 2332.2096 | 2303.299 | 1295.2274 | 1233.3795 | 1754.541 | 1970.8382
| Steady Progression 2021 | N-D | 2742.7883 | 2873.8783 | 1977.1967 | 2207.9279 | 2196.3225 | 2150.4361 | 2178.09 | 1970.3151 | 2070.4124 | 1969.2578 | 1403.4049
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B7
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B7
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 6300MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 7606.727 | 8504.0315 | 9096.2758 | 11564.2088 | 13189.1016 | 14458.3025 | 14736.939 | 17337.0037 | 19289.9544 | 21547.8174 | 24675.9373
| Consumer Transformation 2021 | N-D | 7307.4444 | 7444.1319 | 7806.1121 | 8617.2057 | 10584.5545 | 12387.1839 | 14236.3487 | 14048.7483 | 16622.3809 | 17682.436 | 18237.0624
| System Transformation 2021 | N-D | 7477.7426 | 7428.3412 | 7713.1929 | 8864.9611 | 10488.3742 | 11834.2126 | 13584.7877 | 14000.6261 | 14464.4715 | 16825.1469 | 17997.1941
| Steady Progression 2021 | N-D | 6705.5781 | 7994.1313 | 7668.8846 | 7681.2188 | 7754.8715 | 7517.459 | 8616.2704 | 11018.4214 | 13750.7474 | 14486.1122 | 14319.6908
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 3015.7063 | 2430.1416 | 2671.5702 | 3121.7325 | 2246.2081 | 1311.8335 | 1170.538 | 1630.2602 | 3214.9335 | 3664.1954 | 3053.0894
| Consumer Transformation 2021 | N-D | 2849.0544 | 2367.8293 | 2425.0066 | 2502.6526 | 1678.3586 | 1780.6976 | 1811.7914 | 969.8299 | 1290.4442 | 1433.0876 | 2201.8014
| System Transformation 2021 | N-D | 2693.8373 | 2303.9788 | 2265.6255 | 2384.6908 | 1468.6202 | 1475.7864 | 1450.5083 | -871.1741 | -953.3576 | 1046.4273 | 1324.1261
| Steady Progression 2021 | N-D | 2556.8836 | 2750.2115 | 1863.1067 | 2200.9591 | 2148.0965 | 1088.2333 | 1121.2852 | 907.4444 | 1060.2373 | 928.3467 | -994.0887
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B7a
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B7a
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 8700MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 9944.4355 | 10851.6538 | 11462.6967 | 13955.572 | 14666.3626 | 15926.7092 | 16178.5605 | 18737.5158 | 20654.6023 | 21856.6134 | 24933.5018
| Consumer Transformation 2021 | N-D | 9624.2078 | 9770.9547 | 10176.725 | 10974.905 | 12512.1882 | 13842.5195 | 15690.4434 | 15486.7009 | 18033.2061 | 18003.2116 | 18506.5856
| System Transformation 2021 | N-D | 9777.3184 | 9736.926 | 10042.4402 | 11190.2864 | 12359.9558 | 13226.1305 | 14990.3927 | 15393.5448 | 15862.2731 | 17658.6793 | 18323.5506
| Steady Progression 2021 | N-D | 8996.0141 | 10274.1321 | 9952.5499 | 9970.4919 | 10088.6775 | 8875.1558 | 9983.7161 | 12382.6353 | 15128.1579 | 15806.8822 | 15124.6712
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 4354.7248 | 3764.7569 | 4043.1582 | 4545.5713 | 2750.3002 | 1811.3765 | 1655.8483 | 2143.0231 | 3772.6818 | 3145.8983 | 2535.6844
| Consumer Transformation 2021 | N-D | 4180.079 | 3726.0155 | 3839.1343 | 3906.953 | 2683.2853 | 2298.24 | 2329.9885 | 1493.8911 | 1867.4054 | 956.3427 | 1698.0595
| System Transformation 2021 | N-D | 4009.3904 | 3664.1739 | 3615.909 | 3743.0461 | 2372.7464 | 1889.9062 | 1866.7817 | 955.7725 | 928.2378 | 1046.2622 | -800.0589
| Steady Progression 2021 | N-D | 3849.6021 | 4070.462 | 3187.5911 | 3595.6827 | 3546.4251 | 1516.1992 | 1560.5532 | 1366.0424 | 1545.4732 | 1395.1478 | -1089.3257
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B8
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B8
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 10300MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 11396.0224 | 12517.1329 | 13848.0448 | 17268.2284 | 19759.2486 | 20501.8061 | 20648.5377 | 22689.3953 | 23668.5153 | 25220.7248 | 27389.8674
| Consumer Transformation 2021 | N-D | 10789.05 | 11428.4691 | 12733.1265 | 13329.4764 | 16311.668 | 18869.1612 | 20818.5052 | 20061.8494 | 21364.0298 | 22820.6526 | 22763.5398
| System Transformation 2021 | N-D | 10603.2002 | 11083.4914 | 12243.2925 | 13223.5907 | 15872.3787 | 17034.1485 | 19693.1138 | 19137.6019 | 19640.6869 | 22072.0139 | 23757.7989
| Steady Progression 2021 | N-D | 9714.262 | 10971.7342 | 11302.7407 | 11720.5133 | 12135.5448 | 11867.7857 | 13326.2587 | 15804.134 | 19302.8817 | 19719.9727 | 18462.2787
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 9534.4939 | 8468.3677 | 9321.0812 | 9456.348 | 8372.7749 | 6745.1743 | 7222.5648 | 8131.1561 | 8395.7669 | 8126.3231 | 7624.9604
| Consumer Transformation 2021 | N-D | 9223.9506 | 8443.9331 | 9967.9124 | 10008.465 | 9328.2612 | 9221.7315 | 8848.6854 | 7142.9544 | 7224.3393 | 7747.2803 | 8756.2879
| System Transformation 2021 | N-D | 8853.1669 | 8259.2932 | 9421.4737 | 9703.2692 | 8756.3116 | 8303.6067 | 8375.9215 | 7245.5299 | 7681.8718 | 8579.2959 | 8964.7697
| Steady Progression 2021 | N-D | 8620.4537 | 8262.144 | 8566.2941 | 9727.7979 | 10180.1147 | 8999.0176 | 9263.1113 | 8917.4328 | 9562.3105 | 9703.0445 | 7701.8775
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B9
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B9
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 12500MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 9909.7651 | 10593.8384 | 11509.471 | 14175.7672 | 16917.2211 | 17256.464 | 17214.006 | 18516.2675 | 18650.8255 | 20780.9772 | 21961.4649
| Consumer Transformation 2021 | N-D | 9143.4555 | 9068.7865 | 9726.2333 | 10176.0883 | 13150.2943 | 16015.8718 | 17193.9741 | 16495.7305 | 17726.1764 | 18568.2995 | 17363.7063
| System Transformation 2021 | N-D | 8760.9486 | 8520.7834 | 9019.7144 | 9841.4261 | 12530.8838 | 13654.5763 | 15947.3349 | 15313.4452 | 15554.6156 | 17209.3411 | 19396.2697
| Steady Progression 2021 | N-D | 7945.2612 | 8000.8837 | 8270.3117 | 8889.9734 | 9554.1094 | 9263.5716 | 10443.2163 | 12046.9347 | 15601.5953 | 15177.496 | 14354.6695
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 8740.8819 | 8173.3602 | 7747.1759 | 8224.3028 | 7236.485 | 5775.2118 | 6088.9385 | 6857.726 | 7478.1307 | 7336.2191 | 6827.0256
| Consumer Transformation 2021 | N-D | 8974.6672 | 7990.974 | 8382.7321 | 8093.283 | 7815.5063 | 7722.9798 | 7279.498 | 5750.493 | 6269.0394 | 6941.1537 | 6540.6645
| System Transformation 2021 | N-D | 8497.1944 | 7684.7646 | 7600.6508 | 7572.5958 | 7074.0349 | 6641.0117 | 6646.9697 | 5408.1121 | 5717.771 | 7078.847 | 8004.2849
| Steady Progression 2021 | N-D | 8996.189 | 7382.7079 | 7661.6821 | 7723.1164 | 8529.4041 | 7407.8061 | 7566.179 | 6795.8533 | 7761.4114 | 7898.1095 | 6552.3274
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B12a
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B12a
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 4898MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | -3722.5938 | -3492.9937 | -3380.7907 | -3286.2223 | -2656.696 | -2642.5187 | -1549.6364 | -2502.7432 | -2920.4328 | -2799.9774 | -3422.6002
| Consumer Transformation 2021 | N-D | -2959.7121 | -2813.1213 | -3663.782 | -3851.9779 | -3709.072 | -3726.779 | -2526.906 | -1888.0932 | -2144.2426 | -2856.2202 | -3378.0026
| System Transformation 2021 | N-D | -3140.5189 | -2990.0734 | -3392.9321 | -3692.1074 | -3517.3686 | -3284.1788 | -2440.3066 | -1496.49 | -1790.3445 | -2883.3942 | -3459.0533
| Steady Progression 2021 | N-D | -3111.166 | -2911.0292 | -2955.0461 | -3720.9995 | -3793.2683 | -3709.0973 | -3624.75 | -2288.5829 | -1689.8849 | -1886.3461 | -1423.4418
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | -1151.199 | -887.8722 | -674.5176 | -583.9785 | 1030.1034 | 2412.2771 | 3487.7448 | 3533.8042 | 4051.1022 | 4398.1699 | 4440.562
| Consumer Transformation 2021 | N-D | 703.9196 | 912.6051 | -1087.4464 | -735.103 | -671.8891 | 744.673 | 2144.182 | 3240.7585 | 3663.4814 | 4095.0497 | 4034.8137
| System Transformation 2021 | N-D | -643.2404 | 835.1002 | 641.7069 | 675.8159 | 1195.3559 | 1288.3397 | 2141.9486 | 4162.4666 | 4243.7392 | 3966.1863 | 3311.154
| Steady Progression 2021 | N-D | -748.065 | 1325.5881 | 1299.9899 | -664.9314 | -794.0234 | 683.614 | 725.5064 | 2076.2628 | 3518.3701 | 3608.1679 | 4549.5522
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B13
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B13
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 2100MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | -2390.4627 | -2299.313 | -2262.4636 | -2197.7415 | -2062.9871 | -2134.9411 | 1085.6478 | -1221.9968 | -1305.5542 | -1342.6329 | -1532.5814
| Consumer Transformation 2021 | N-D | -1743.4928 | -1680.843 | -2409.4435 | -2509.4801 | -2459.6688 | -3106.1227 | -1943.729 | 1174.8776 | -1015.4308 | -1213.154 | -1405.736
| System Transformation 2021 | N-D | -1810.9139 | -1754.5034 | -2478.0881 | -2557.1355 | -2494.5618 | -2481.5953 | -2158.507 | 1148.4372 | 1065.8302 | -1206.4203 | -1323.7757
| Steady Progression 2021 | N-D | -1829.1474 | -1886.2773 | -1920.4662 | -2654.1505 | -2646.279 | -2678.0089 | -2703.9377 | -1574.2236 | 1031.3086 | 1225.8211 | 1319.8463
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | -1260.4885 | -1177.7764 | -1182.7447 | -1036.6904 | -840.5149 | 1133.9204 | 2422.5899 | 2484.359 | 2460.011 | 2705.3412 | 2740.9174
| Consumer Transformation 2021 | N-D | -490.2858 | -413.2799 | -1262.9994 | -1297.8289 | -1236.8834 | -1191.0081 | 1063.6012 | 2583.6799 | 2711.7862 | 2952.8022 | 2985.1877
| System Transformation 2021 | N-D | -542.0492 | -457.5566 | -1325.5584 | -1340.4676 | -1307.911 | -1328.493 | 622.937 | 2119.6278 | 2291.885 | 2494.4867 | 2800.4372
| Steady Progression 2021 | N-D | -585.2218 | -574.6659 | -595.2125 | -1419.4694 | -1397.3233 | -1420.5417 | -1450.9604 | 530.0329 | 1951.0611 | 1954.2617 | 2317.7565
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B14
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B14
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 11600MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 8792.8839 | 8755.4271 | 8990.5161 | 9092.2079 | 9254.8395 | 9357.3664 | 9682.5502 | 10534.8165 | 11100.3077 | 11259.5628 | 11518.0555
| Consumer Transformation 2021 | N-D | 9011.0869 | 9095.3753 | 9414.3454 | 9584.2207 | 9860.6842 | 9727.9305 | 9919.8703 | 10229.3738 | 10523.1796 | 11226.5401 | 11518.2515
| System Transformation 2021 | N-D | 9154.9324 | 9258.397 | 9552.3405 | 9686.1926 | 9888.4179 | 9816.5371 | 9876.5323 | 10156.2842 | 10310.772 | 10629.0931 | 10605.9758
| Steady Progression 2021 | N-D | 9254.0091 | 9583.6204 | 10012.3866 | 10096.5883 | 10430.8274 | 10460.4494 | 10559.6554 | 10832.3126 | 11250.3167 | 11524.3766 | 11620.5827
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 7690.3679 | 7625.0137 | 7781.884 | 7868.2863 | 8233.8649 | 8220.7682 | 8609.7322 | 9339.1591 | 9973.8004 | 10097.2564 | 10200.5444
| Consumer Transformation 2021 | N-D | 7941.4509 | 7909.3337 | 8230.5516 | 8427.187 | 8750.9543 | 8678.3143 | 8892.3428 | 9114.1283 | 9425.8281 | 9929.2032 | 10109.5948
| System Transformation 2021 | N-D | 8070.816 | 8058.804 | 8354.7843 | 8510.491 | 8770.0562 | 8726.7862 | 8856.7145 | 8966.6361 | 9090.1721 | 9172.1487 | 9251.8886
| Steady Progression 2021 | N-D | 8213.5679 | 8350.4149 | 8776.6908 | 8848.76 | 9232.0337 | 9171.8862 | 9295.4494 | 9623.6654 | 10134.4628 | 10299.448 | 10335.0687
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B15
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B15
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 7405MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 4298.6828 | 3485.7839 | 2552.3656 | -2402.0034 | -5899.8355 | -6400.1441 | -6154.9652 | -6412.539 | -7433.0404 | -7568.4956 | -7318.1933
| Consumer Transformation 2021 | N-D | 4497.8126 | 4408.4976 | 4749.3784 | 4872.3376 | 1771.505 | -3306.2075 | -4876.5516 | -5453.471 | -5919.5413 | -5885.0492 | -4358.5879
| System Transformation 2021 | N-D | 5359.0072 | 5550.5274 | 5662.9749 | 5512.3978 | 2547.9508 | 1305.9098 | -3975.8321 | -4143.9657 | -4992.406 | -5810.7377 | -7334.4269
| Steady Progression 2021 | N-D | 6206.8234 | 6051.6895 | 6567.7614 | 6778.0648 | 6783.1014 | 7098.4211 | 5362.4633 | 3467.4782 | -1346.2652 | -1532.4197 | -1372.3682
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 2549.1225 | 2707.092 | 2776.421 | 2304.5926 | 2854.3859 | 2845.7661 | 2354.36 | 2319.8767 | 2577.6451 | 2624.8372 | 2917.4021
| Consumer Transformation 2021 | N-D | 2137.8368 | 2483.3684 | 3022.3342 | 3063.9613 | 3240.4227 | 3247.9682 | 3265.1916 | 3428.2102 | 2944.6209 | 3058.1747 | 3845.2499
| System Transformation 2021 | N-D | 3067.7605 | 3268.5057 | 3848.8108 | 4001.8482 | 4060.4572 | 4090.4375 | 4062.5304 | 3374.4858 | 2920.2934 | 2673.4262 | 2821.0952
| Steady Progression 2021 | N-D | 3018.2117 | 3131.5068 | 3726.4408 | 4057.0026 | 4007.4861 | 4951.6552 | 4901.1834 | 4852.973 | 4590.2808 | 4627.171 | 4721.3608
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## B17
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | B17
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 7400MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 5721.2352 | 5667.6515 | 5834.2547 | 6456.2327 | 6306.3458 | 6398.2907 | 6628.0053 | 7110.3818 | 7361.8268 | 7407.942 | 7662.5386
| Consumer Transformation 2021 | N-D | 5929.0335 | 6170.9511 | 6923.1109 | 6994.0194 | 6735.7712 | 6665.2043 | 6769.3485 | 7015.4025 | 7205.3175 | 7641.7631 | 7934.9246
| System Transformation 2021 | N-D | 6052.8326 | 6340.1487 | 7114.8375 | 7171.8937 | 6853.9339 | 6805.0492 | 6830.5253 | 7121.0001 | 7271.2543 | 7545.4554 | 7428.2984
| Steady Progression 2021 | N-D | 6058.1089 | 6615.811 | 6639.6332 | 7452.466 | 7150.3703 | 7155.2194 | 7211.6858 | 7440.5102 | 7423.4163 | 7685.1202 | 7670.878
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 4933.9325 | 4471.7759 | 5487.4291 | 5211.6641 | 5161.9085 | 5261.4106 | 5448.6734 | 5658.7813 | 5704.2415 | 5676.8511 | 5673.1275
| Consumer Transformation 2021 | N-D | 4425.3077 | 4724.7645 | 5794.6949 | 5819.1724 | 5470.306 | 5472.5987 | 5556.643 | 5781.1033 | 5847.7105 | 5967.394 | 6152.4509
| System Transformation 2021 | N-D | 4523.4092 | 4887.4796 | 6023.1597 | 6037.2986 | 5623.0185 | 5601.1082 | 5662.1166 | 5816.5162 | 5930.1361 | 5949.3721 | 5850.7493
| Steady Progression 2021 | N-D | 4572.7159 | 5130.5884 | 5137.6861 | 6316.3676 | 5866.9507 | 5817.45 | 5893.9007 | 6056.3152 | 6025.82 | 6105.6071 | 5970.0041
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## SC1
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | SC1
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 4100MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | -1333.1006 | -2237.2106 | -3032.7142 | -5988.3288 | -6536.6409 | -8396.8938 | -10534.2212 | -11126.0721 | -11825.6226 | -13050.7049 | -13427.0513
| Consumer Transformation 2021 | N-D | -1762.2197 | -1831.7879 | -1454.9962 | -1544.9555 | -4730.2173 | -7026.1492 | -8442.2267 | -9458.3314 | -10370.3557 | -12394.7603 | -11370.6527
| System Transformation 2021 | N-D | 1101.9658 | 1212.5227 | 1363.0448 | 1099.9172 | -3965.448 | -5512.4839 | -7617.547 | -7982.1793 | -9314.7444 | -10128.2245 | -10975.3179
| Steady Progression 2021 | N-D | 1644.5355 | 1556.8635 | 2081.2949 | 1909.2751 | 1890.4765 | 1549.9392 | -2450.6838 | -4808.4007 | -7427.2769 | -7277.5771 | -7136.0145
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | -1802.5054 | -1501.0271 | -1410.159 | -1450.6298 | -1114.9432 | -1284.029 | -1549.7822 | -1620.5057 | -2088.6641 | -3105.1221 | -3146.1869
| Consumer Transformation 2021 | N-D | -2857.0822 | -2619.8811 | -2565.693 | -2628.7788 | -2482.9549 | -2513.7912 | -2404.1626 | -2518.622 | -2718.6093 | -2591.0944 | -2244.7416
| System Transformation 2021 | N-D | -2065.6029 | -1888.0975 | -1854.3951 | -1855.1451 | -1716.9772 | -1749.5557 | -1815.8277 | -1866.6984 | -2311.5352 | -2968.3887 | -2827.7861
| Steady Progression 2021 | N-D | -2211.8917 | -2155.9891 | -2117.6215 | -2002.1535 | -2050.9517 | -2075.9194 | -2158.3394 | -2205.8816 | -2758.1542 | -2865.1873 | -3188.2516
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## SC1.5
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | SC1.5
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 4800MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 2156.4346 | 1182.5819 | -1649.9205 | -4711.7083 | -5427.6198 | -6003.4294 | -7951.2317 | -8256.035 | -8886.1591 | -10078.2758 | -10278.5564
| Consumer Transformation 2021 | N-D | 1777.1636 | 1651.6565 | 2038.9242 | 2043.4712 | -3206.7708 | -5009.7777 | -6246.5466 | -6963.2769 | -7694.0439 | -9543.2626 | -8338.1276
| System Transformation 2021 | N-D | 2699.3866 | 2758.327 | 2918.1456 | 2741.7478 | -2383.301 | -3952.2821 | -5200.1865 | -5461.6745 | -6719.5437 | -7276.5538 | -7999.1343
| Steady Progression 2021 | N-D | 3249.1503 | 3220.209 | 3775.3213 | 3600.5246 | 3579.4024 | 3260.9962 | 1277.6477 | -2982.517 | -4784.2843 | -4843.6783 | -4791.3291
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | -812.3025 | -581.1946 | -476.2976 | -670.5397 | -529.6019 | -665.0175 | -777.8012 | -892.3334 | -1237.5087 | -2416.5895 | -2491.7955
| Consumer Transformation 2021 | N-D | -1799.4368 | -1621.57 | -1561.0855 | -1590.3455 | -1502.1548 | -1578.8452 | -1683.2316 | -1804.3203 | -1986.8505 | -1941.0783 | -1626.535
| System Transformation 2021 | N-D | -965.6286 | -844.9281 | -792.3588 | -774.742 | -660.7454 | -669.7197 | -699.3687 | -780.1793 | -1379.9243 | -2085.8102 | -2104.8857
| Steady Progression 2021 | N-D | -1072.6654 | -1011.681 | -950.5614 | -848.3822 | -912.2589 | -910.1221 | -957.6328 | -954.76 | -1461.1047 | -1546.1008 | -1944.8876
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## SC3
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | SC3
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 6200MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 5101.5007 | 4191.6024 | 3201.9502 | -1722.3252 | -4035.4134 | -4442.1487 | -4179.7091 | -4262.7886 | -5240.8945 | -5349.0473 | -5419.5222
| Consumer Transformation 2021 | N-D | 4941.615 | 4738.2112 | 5072.6298 | 5209.2983 | 1769.2329 | -2385.3705 | -3611.4218 | -4055.814 | -3919.2292 | -3823.2471 | -2530.1828
| System Transformation 2021 | N-D | 5844.9416 | 5984.2349 | 6083.6504 | 5894.9278 | 2801.2907 | 1577.5614 | -2726.4153 | -2190.9049 | -3068.2483 | -3711.5329 | -5112.8942
| Steady Progression 2021 | N-D | 6687.3366 | 6584.5334 | 7123.6339 | 7219.8739 | 7176.3321 | 6481.1889 | 4719.8175 | 3114.6266 | 1063.5306 | -1176.7416 | -1205.7662
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 2630.7882 | 2739.2971 | 2769.3062 | 2198.6321 | 2225.0387 | 2242.8757 | 2216.3959 | 2203.1302 | 1891.5436 | 1868.0991 | 1847.3977
| Consumer Transformation 2021 | N-D | 1698.9463 | 1880.4198 | 1880.8031 | 1822.4826 | 1896.7341 | 1905.0883 | 1904.1523 | 1988.6151 | 2088.9705 | 2148.7836 | 2958.8968
| System Transformation 2021 | N-D | 2616.3126 | 2757.5996 | 2801.1243 | 2752.6867 | 2775.0511 | 2815.78 | 2808.2483 | 2823.8993 | 2337.9237 | 2037.7612 | 2137.3526
| Steady Progression 2021 | N-D | 2593.6848 | 2691.2161 | 2776.9094 | 2891.817 | 2816.6419 | 2218.0785 | 2177.7508 | 2164.2355 | 1823.6921 | 1857.5222 | 1629.5874
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## SW1
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | SW1
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 2900MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 922.7477 | 947.6248 | 935.7865 | 951.1469 | 1348.585 | 1276.9136 | 1217.3271 | -1092.2247 | -1272.0527 | -1103.5458 | -1352.3036
| Consumer Transformation 2021 | N-D | 945.6153 | 993.8095 | 1022.055 | -957.3066 | -995.9613 | 1366.0052 | 1357.0639 | 1412.6142 | 1416.0016 | 1072.1308 | -1144.005
| System Transformation 2021 | N-D | -961.9358 | -955.1284 | 1489.1633 | 1303.9581 | 1350.2844 | 1475.7632 | 1728.4242 | 1472.6044 | 1348.5111 | -1266.3167 | -1220.167
| Steady Progression 2021 | N-D | -941.7616 | 1299.8713 | 1299.5898 | 1413.3504 | 1321.4683 | 1363.9309 | 1433.2801 | 1528.5015 | 1521.7232 | 1275.6023 | 1582.1703
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 1320.549 | 1331.7862 | 1409.7168 | 1366.3432 | 1596.7552 | 1620.3308 | 1422.0292 | 1462.5624 | 2015.9565 | 2133.805 | 2167.7654
| Consumer Transformation 2021 | N-D | 1302.7114 | 1381.4159 | 1434.1571 | 1664.7561 | 1623.4397 | 1750.237 | 1520.1101 | 1847.2316 | 2130.8103 | 2339.2926 | 2314.4381
| System Transformation 2021 | N-D | 1269.6302 | 1365.988 | 2121.1592 | 2100.6982 | 2560.6594 | 2598.7697 | 2081.8843 | 2604.337 | 2567.194 | 2009.8719 | 2174.0875
| Steady Progression 2021 | N-D | 1246.7526 | 2016.1286 | 2009.0818 | 2203.4648 | 1990.8361 | 2065.0793 | 2098.1864 | 2094.8223 | 2154.3266 | 2236.076 | 2650.6105
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## LE1
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | LE1
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 7600MW
| Economy | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Economy Background (in MW) | Leading the Way 2021 | N-D | 6119.9246 | 6827.2597 | 7946.1179 | 11015.6922 | 14626.1366 | 15251.2128 | 15279.51 | 16493.5583 | 18153.6511 | 18455.9995 | 18543.8374
| Consumer Transformation 2021 | N-D | 6166.5335 | 6313.3389 | 6247.9162 | 6300.1378 | 9662.936 | 12596.5682 | 14381.427 | 15293.4531 | 16009.2575 | 16761.0605 | 15593.1443
| System Transformation 2021 | N-D | 5471.997 | 5359.3526 | 5537.1348 | 5820.7422 | 8914.6485 | 10078.0237 | 13418.6349 | 13914.0783 | 14956.5487 | 16157.3836 | 17643.0527
| Steady Progression 2021 | N-D | 4735.0649 | 5237.1142 | 5162.7608 | 5040.2747 | 5364.3761 | 5071.6847 | 6913.9659 | 9088.5669 | 12305.9021 | 12831.2017 | 12774.6916
| Security | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak Required Transfers in accordance with NETS SQSS Chapter 4 Security Background (in MW) | Leading the Way 2021 | N-D | 5740.3682 | 5430.4002 | 5416.9207 | 5966.2114 | 5786.3335 | 5799.0927 | 6525.5959 | 7325.9624 | 7738.7339 | 7790.9935 | 7628.3942
| Consumer Transformation 2021 | N-D | 6414.3937 | 6010.4283 | 5728.6444 | 5854.9321 | 5991.227 | 5919.9093 | 6137.7924 | 6214.3853 | 6834.159 | 7204.3906 | 6658.0462
| System Transformation 2021 | N-D | 5663.091 | 5418.2731 | 5142.6281 | 5114.7458 | 5217.3159 | 5149.4959 | 5318.1718 | 6096.3181 | 6687.4243 | 7004.1259 | 6938.6664
| Steady Progression 2021 | N-D | 5872.6985 | 5881.4685 | 5730.6106 | 5478.8672 | 5905.3656 | 4913.0776 | 5093.8504 | 5442.8222 | 6193.0617 | 6346.6422 | 6262.5995
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## NW1
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | NW1
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 1800MW
| Local requirements | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak local boundary requirements (in MW) | Leading the Way 2021 | N-D | -4.967 | -2.094 | 10.934 | 25.25 | 40.978 | 55.871 | 70.683 | 125.539 | 380.22 | 395.731 | 413.889
| Consumer Transformation 2021 | N-D | -6.464 | -4.675 | 0.626 | 7.121 | 15.871 | 24.219 | 32.353 | 41.475 | 331.442 | 344.147 | 378.586
| System Transformation 2021 | N-D | -7.48 | -6.327 | -1.703 | 2.968 | 9.032 | 14.061 | 19.291 | 65.542 | 72.399 | 81.861 | 92.813
| Steady Progression 2021 | N-D | -8.3 | -8.354 | -7.732 | -7.198 | 144.559 | 205.541 | 207.505 | 249.857 | 212.512 | 216.092 | 220.566
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## NW2
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | NW2
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 1400MW
| Local requirements | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak local boundary requirements (in MW) | Leading the Way 2021 | N-D | 2317.037 | 2331.922 | 2641.365 | 2677.781 | 2724.436 | 2762.262 | 2372.0717 | 2564.3643 | 3536.7261 | 3672.8583 | 4146.4064
| Consumer Transformation 2021 | N-D | 2310.509 | 2318.364 | 2606.594 | 2621.076 | 2647.686 | 2666.803 | 2684.52 | 2704.007 | 2692.2787 | 3851.0921 | 3874.1741
| System Transformation 2021 | N-D | 2307.305 | 2313.012 | 2599.547 | 2611.897 | 2629.032 | 2641.746 | 2655.112 | 2711.029 | 2728.039 | 3751.677 | 3779.966
| Steady Progression 2021 | N-D | 2304.066 | 2303.832 | 2579.128 | 2579.883 | 2734.957 | 2797.112 | 2802.083 | 2848.048 | 2814.349 | 2823.077 | 2834.176
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## NW3
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | NW3
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 5500MW
| Local requirements | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak local boundary requirements (in MW) | Leading the Way 2021 | N-D | 2897.608 | 2922.698 | 3243.439 | 3295.4 | 3361.651 | 3418.044 | 3046.7767 | 3258.7813 | 4251.1121 | 4409.6753 | 4909.1984
| Consumer Transformation 2021 | N-D | 2887.573 | 2902.486 | 3199.341 | 3229.6 | 3278.262 | 3319.821 | 3360.208 | 3403.293 | 3415.7537 | 4601.3881 | 4654.5351
| System Transformation 2021 | N-D | 2880.877 | 2891.288 | 3183.557 | 3200.968 | 3225.811 | 3243.791 | 3263.288 | 3325.39 | 3347.699 | 4378.685 | 4415.553
| Steady Progression 2021 | N-D | 2874.741 | 2874.937 | 3150.575 | 3151.813 | 3309.887 | 3373.227 | 3379.878 | 3427.576 | 3394.678 | 3404.254 | 3416.036
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## SC2
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | SC2
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 4800MW
| Local requirements | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak local boundary requirements (in MW) | Leading the Way 2021 | N-D | 5059.3156 | 3655.8608 | 2509.3444 | 1230.024 | 494.1419 | -15.1018 | -749.6321 | 105.5155 | -181.2752 | -401.0046 | 15.915
| Consumer Transformation 2021 | N-D | 4655.1205 | 4082.7612 | 4786.5552 | 5519.8645 | 2440.0725 | 747.2776 | -824.6269 | -525.2829 | -659.0774 | 79.5377 | 868.4531
| System Transformation 2021 | N-D | 5850.0103 | 5411.2395 | 5620.068 | 5937.6924 | 3223.745 | 2416.3303 | 84.4727 | 1380.4878 | 203.6646 | 510.7944 | -195.0132
| Steady Progression 2021 | N-D | 6654.1086 | 6110.9165 | 7339.1431 | 6486.5472 | 6582.0296 | 6412.9831 | 3906.1833 | 2670.8264 | 1271.6954 | 1958.4139 | 2047.6675
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.

## EC5
BACK to Contents
ESO Required Transfer
Boundary under Analysis: | EC5
Winter Peak Boundary Required Transfer Summary:
Year 1 Winter Peak Base Capability from previous year (2020): | 3500MW
| Local requirements | Secured Event | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32
Winter Peak local boundary requirements (in MW) | Leading the Way 2021 | N-D | 3847.061 | 3947.9 | 4179.341 | 5907.759 | 5911.469 | 6718.608 | 8212.875 | 10993.343 | 14837.797 | 13760.4702 | 13709.6193
| Consumer Transformation 2021 | N-D | 3798.922 | 3856.566 | 3898.155 | 4424.962 | 5768.044 | 5834.34 | 5880.652 | 7621.226 | 8050.314 | 13701.838 | 13794.016
| System Transformation 2021 | N-D | 3773.256 | 3817.402 | 3854.195 | 4228.258 | 5625.365 | 5722.291 | 6247.172 | 7254.622 | 9485.896 | 11980.219 | 11618.672
| Steady Progression 2021 | N-D | 3748.868 | 3747.708 | 3746.829 | 3740.242 | 3748.755 | 3787.657 | 4980.648 | 5018.538 | 5661.927 | 8172.41 | 8168.863
Unconstrained Boundary Flows
The section belows details the unconstrained flows across the boundary. The 90th percentile and 50th percentile ranges have been highlighted for each scenario, and this has been shown together with the NETS SQSS required transfers and 2020 base boundary capability.