## Note
NOA Pathfinder Stability Phase 3
Detailed Site Data Tool, including Effectiveness Factors and Sizing Guidance
Technical feasibility study supporting material
Version 2 - January 2022
Version Control
| V1 | Initial version published 20 December 2021
| V2 | Version 2 published 19 January 2022 Update: additional tab "6. Reserved Bay Size Check" added.
This document contains the following: 1. Substation data tool to calculate Short Circuit Level (SCL) MVA contribution 2. System impedance data for each substation within the regions of need 3. Fault impedance data for each substation within the regions of need 4. Effectiveness Factors for each substation within the regions of need 5. Sizing guidance for Tenderers to refer to when sizing their proposed solutions 6. Size check tool for Tenderers to refer to when sizing solutions for reserved bays
This document should be used to help design proposed solutions and to support the required technical feasibility study.
Notes:
1 | Substations are at transmission voltage level (i.e. 275kV and 400kV for Stability Phase 3)
2 | Effectiveness factors show how effective a solution will be based on its location to provide short circuit current contribution to the NGESO regions of need
3 | Short circuit current contribution is based on positive sequence RMS reactive current value at 100ms after fault initiation
4 | The substations included within each of the regions of need have been identified based on their overall effectiveness at contributing to the main reference point of each region, with the view to ensure that each region is defined, with reduced interactivity between regions
Information that is supplied to Tenderers as part of this ITT is supplied in good faith. The information contained in this document or any other document in the ITT Tender Pack and in any related written or oral communication is believed to be correct at the time of issue. NGESO will not accept any liability for its accuracy, adequacy or completeness and no warranty is given as such. Any reliance by a Tenderer or any third party on the information provided by NGESO as part of this document or any other document in the ITT Tender Pack is at the Tenderer’s and/or third party’s risk.

## 1. Phase 3 Site Data
Description:
This interactive worksheet shows how the effectiveness factors, system impedance and fault impedance should be considered in NOA Stability Pathfinder Phase3 Technical Feasibility Study.
This worksheet provides the necessary information required to perform the Technical Feasibility Study for NOA Stability Pathfinder Phase3. The user can choose the solution Grid Entry Point (GEP) in Cell E-F14, and the corresponding system impedance, fault impedance and effectiveness will be updated automatically. After performing the simulations (Test 1 Step 10), the user can plug the solution contribution in corresponding cells in row 28 to get the effective SCL that will be used in the commercial assessment.
Provided by NGESO (Lookup cell)
|  | Bidder to provide based on simulation results |  | How to use:
|  | SCL Contribution to requirement |  | 1- Choose the substation name of your solution here.
NA: Not Applicable
The grid entry point substation where the solution is connected |  | Connection Substation | Offerton 275kV
The voltage of grid entry point substation |  | Connection Substation Voltage (kV) | 275 |  |  | Region | North East of England
|  | System reactance (Xsys: ohm) | 7.501
|  | System resistance (Rsys: ohm) | 0.511
|  | Service region | North East | East England |  | South Coast | South West | South Wales
|  | Reference point in each region | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
|  |  | Hawthorn Pit 400kV | Norwich Main 400kV | Bicker Fen 400kV | Canterbury 400kV | Exeter Main 400kV | Rhigos 400KV | Upper Boat 275kV MC2/3 | Upper Boat 275kV MC1/4
|  | Reference point voltage (kV) | 400 | 400 | 400 | 400 | 400 | 400 | 275 | 275
|  | SCL requirement at the reference point (MVA) | 500 | 1500 | 500 | 2000 | 500 | 1500 | 500 | 500
From Fault Impedance table. Applicable to Test1 (Step 10) |  | Fault reactance for remote fault test(ohm) | 6.363 | NA | NA | NA | NA | NA | NA | NA
|  | Fault resistance for remote fault test (ohm) | 0.433 | NA | NA | NA | NA | NA | NA | NA
Tenderers to provide reactive fault contribution at its GEP based on Test 1 simulation (Step 10a-c), for the given system and fault impedances. |  | Reactive component of fault current in kA from Test 1 Step 10a-c | 1: 1.8
From Effectiveness Factors table |  | Effectiveness factor at Offerton 275kV against Reference point | 59% | NA | NA | NA | NA | NA | NA | NA
Copy this value to the feasibility study report (Table 3) Steps 10a-c |  | Effective SCL at Reference point (MVA) | 505.8454 | NA | NA | NA | NA | NA | NA | NA
How to use: | bar: 1 to 5
*GEP (Grid Entry Point) is defined in the technical specification | 2- Enter fault contribution (in kA) at GEP under the corresponding effectiveness location column (i.e. type figures in gray filled cells) | bar: 1 to 5

## 2. System Impedance
Region | Substation / Nodes | Voltage Level (kV)
|  |  | Sk'' (MVA) | X/R ratio (peak) | Zsys (Ohm) | Rsys (Ohm) | Xsys (Ohm) | Zsys angle (degree)
North East of England | Blyth 275kV | 275 | 12421.311 | 15.381 | 6.088 | 0.395 | 6.075 | 86.28
North East of England | Blyth 400kV | 400 | 12328.743 | 16.173 | 12.978 | 0.801 | 12.953 | 86.462
North East of England | Fourstones 275kV | 275 | 6621.882 | 10.021 | 11.42 | 1.134 | 11.364 | 84.301
North East of England | Greystones A 275kV | 275 | 7535.959 | 23.171 | 10.035 | 0.433 | 10.026 | 87.529
North East of England | Greystones B 275kV | 275 | 7570.893 | 23.328 | 9.989 | 0.428 | 9.98 | 87.545
North East of England | Hartlepool 275kV | 275 | 10315.623 | 16.291 | 7.331 | 0.449 | 7.317 | 86.487
North East of England | Hartmoor 275kV | 275 | 8838.93 | 15.297 | 8.556 | 0.558 | 8.538 | 86.26
North East of England | Hawthorn Pit 275kV | 275 | 11578.276 | 16.595 | 6.532 | 0.393 | 6.52 | 86.552
North East of England | Hawthorn Pit 400kV | 400 | 10531.615 | 17.641 | 15.192 | 0.86 | 15.168 | 86.756
North East of England | Lackenby 275kV | 275 | 8578.416 | 20.094 | 8.816 | 0.438 | 8.805 | 87.151
North East of England | Lackenby 400kV | 400 | 12906.408 | 15.922 | 12.397 | 0.777 | 12.373 | 86.406
North East of England | Norton 275kV | 275 | 11122.18 | 19.603 | 6.799 | 0.346 | 6.791 | 87.08
North East of England | Norton 400kV | 400 | 17374.919 | 16.804 | 9.209 | 0.547 | 9.192 | 86.594
North East of England | Offerton 275kV | 275 | 10058.771 | 14.691 | 7.518 | 0.511 | 7.501 | 86.106
North East of England | Osbaldwick 400kV [MC3/4] | 400 | 12781.163 | 17.213 | 12.518 | 0.726 | 12.497 | 86.675
North East of England | Saltholme 275kV | 275 | 9701.206 | 16.17 | 7.795 | 0.481 | 7.781 | 86.461
North East of England | South Shields 275kV | 275 | 10092.028 | 13.906 | 7.494 | 0.537 | 7.474 | 85.887
North East of England | Spennymoor 400kV | 400 | 13322.455 | 16.488 | 12.01 | 0.727 | 11.988 | 86.529
North East of England | Stella West 275kV | 275 | 12445.903 | 15.439 | 6.076 | 0.393 | 6.064 | 86.294
North East of England | Stella West 400kV | 400 | 15916.717 | 16.81 | 10.052 | 0.597 | 10.035 | 86.596
North East of England | Tod Point 275kV | 275 | 8535.202 | 17.809 | 8.86 | 0.497 | 8.846 | 86.786
North East of England | Tynemouth 275kV | 275 | 9548.597 | 13.484 | 7.92 | 0.586 | 7.898 | 85.758
North East of England | West Boldon 275kV | 275 | 10991.332 | 14.704 | 6.88 | 0.467 | 6.865 | 86.109
East of England | Bicker Fen 400kV | 400 | 20043.473 | 15.705 | 7.983 | 0.507 | 7.967 | 86.357
East of England | Braintree 400kV [B] | 400 | 14784.074 | 15.385 | 10.822 | 0.702 | 10.8 | 86.281
East of England | Braintree 400kV [A] | 400 | 15189.768 | 15.698 | 10.533 | 0.67 | 10.512 | 86.355
East of England | Bramford 400kV [M3] | 400 | 18973.064 | 16.478 | 8.433 | 0.511 | 8.418 | 86.527
East of England | Bramford 400kV [M7] | 400 | 11837.205 | 15.168 | 13.517 | 0.889 | 13.487 | 86.228
East of England | Bulls Lodge 400kV | 400 | 16110.471 | 15.579 | 9.931 | 0.636 | 9.911 | 86.327
East of England | Burwell 400kV | 400 | 20801.087 | 15.477 | 7.692 | 0.496 | 7.676 | 86.303
East of England | Kings Lynn 400kV | 400 | 12709.658 | 16.258 | 12.589 | 0.773 | 12.565 | 86.48
East of England | Leiston 400kV T-Points | 400 | 16327.232 | 18.229 | 9.8 | 0.537 | 9.785 | 86.86
East of England | Necton 400kV | 400 | 15529.426 | 15.444 | 10.303 | 0.666 | 10.281 | 86.295
East of England | Norwich Main 400kV | 400 | 15288.331 | 14.809 | 10.465 | 0.705 | 10.442 | 86.137
East of England | Pelham 400kV | 400 | 28385.919 | 14.78 | 5.637 | 0.381 | 5.624 | 86.129
East of England | Rayleigh 400kV | 400 | 21679.123 | 14.326 | 7.38 | 0.514 | 7.362 | 86.007
East of England | Rye House 400kV | 400 | 16217.688 | 15.506 | 9.866 | 0.635 | 9.845 | 86.31
East of England | Sizewell 400kV | 400 | 16583.066 | 18.316 | 9.648 | 0.526 | 9.634 | 86.875
East of England | Spalding North 400kV | 400 | 18002.805 | 15.665 | 8.888 | 0.566 | 8.869 | 86.347
East of England | Sutton Bridge 400kV | 400 | 18357.648 | 13.836 | 8.716 | 0.628 | 8.693 | 85.866
East of England | Walpole 400kV | 400 | 21291.152 | 14.851 | 7.515 | 0.505 | 7.498 | 86.148
East of England | Yaxley 400kV | 400 | 14671.135 | 14.765 | 10.906 | 0.737 | 10.881 | 86.125
South Coast of England | Bolney 400kV | 400 | 14358.114 | 14.21 | 11.144 | 0.782 | 11.116 | 85.975
South Coast of England | Canterbury 400kV AIS | 400 | 15644.583 | 14.181 | 10.227 | 0.719 | 10.202 | 85.966
South Coast of England | Canterbury 400kV GIS | 400 | 15644.583 | 14.181 | 10.227 | 0.719 | 10.202 | 85.966
South Coast of England | Dungeness 275kV | 275 | 6477.57 | 24.112 | 11.675 | 0.484 | 11.665 | 87.625
South Coast of England | Dungeness 400kV | 400 | 12992.533 | 13.672 | 12.315 | 0.898 | 12.282 | 85.817
South Coast of England | Ninfield 400kV | 400 | 12922.502 | 13.88 | 12.382 | 0.89 | 12.349 | 85.879
South Coast of England | Richborough 400kV | 400 | 11576.437 | 13.459 | 13.821 | 1.024 | 13.783 | 85.751
South Coast of England | Sellindge 400kV Compound A | 400 | 13891.813 | 13.62 | 11.518 | 0.843 | 11.487 | 85.801
South Coast of England | Sellindge 400kV Compound B | 400 | 13872.663 | 13.618 | 11.533 | 0.845 | 11.503 | 85.8
South West of England | Abham 400kV | 400 | 8973.06 | 11.271 | 17.831 | 1.576 | 17.761 | 84.93
South West of England | Alverdiscott 400kV [B] | 400 | 7013.309 | 11.087 | 22.814 | 2.049 | 22.722 | 84.846
South West of England | Alverdiscott 400kV [A] | 400 | 6976.251 | 11.101 | 22.935 | 2.058 | 22.842 | 84.852
South West of England | Axminster 400kV | 400 | 10224.833 | 14.333 | 15.648 | 1.089 | 15.61 | 86.009
South West of England | Botley Wood 400kV | 400 | 16130.854 | 14.459 | 9.919 | 0.684 | 9.895 | 86.044
South West of England | Bridgewater 400kV | 400 | 14721.107 | 14.573 | 10.869 | 0.744 | 10.843 | 86.074
South West of England | Chickerell 400kV | 400 | 9307.678 | 14.574 | 17.19 | 1.177 | 17.15 | 86.075
South West of England | Chilling 400kV | 400 | 16457.799 | 14.337 | 9.722 | 0.676 | 9.698 | 86.01
South West of England | Exeter Main 400kV | 400 | 15079.314 | 13.268 | 10.611 | 0.797 | 10.581 | 85.69
South West of England | Fawley 400kV | 400 | 16362.575 | 14.226 | 9.778 | 0.686 | 9.754 | 85.979
South West of England | Hinkley Point 275kV | 275 | 3586.551 | 46.546 | 21.086 | 0.453 | 21.081 | 88.769
South West of England | Hinkley Point 400kV | 400 | 23427.036 | 17.157 | 6.83 | 0.397 | 6.818 | 86.664
South West of England | Hinkley Point C 400kV | 400 | 23200.291 | 17.12 | 6.896 | 0.402 | 6.885 | 86.657
South West of England | Indian Queens 400kV | 400 | 8865.272 | 10.667 | 18.048 | 1.685 | 17.969 | 84.644
South West of England | Landulph 400kV | 400 | 8171.355 | 10.849 | 19.581 | 1.797 | 19.498 | 84.734
South West of England | Langage 400kV | 400 | 9658.56 | 11.163 | 16.566 | 1.478 | 16.5 | 84.881
South West of England | Lovedean 400kV | 400 | 19701.973 | 13.73 | 8.121 | 0.59 | 8.1 | 85.834
South West of England | Mannington 400kV | 400 | 13453.98 | 14.116 | 11.892 | 0.84 | 11.863 | 85.948
South West of England | Marchwood 400kV | 400 | 13242.815 | 14.293 | 12.082 | 0.843 | 12.053 | 85.998
South West of England | Melksham 400kV | 400 | 23027.27 | 12.907 | 6.948 | 0.537 | 6.928 | 85.57
South West of England | Nursling 400kV [MC1] | 400 | 12949.905 | 14.419 | 12.355 | 0.855 | 12.326 | 86.033
South West of England | Nursling 400kV [A] | 400 | 12350.991 | 14.671 | 12.954 | 0.881 | 12.924 | 86.101
South West of England | Sandford 400kV | 400 | 15085.424 | 16.087 | 10.606 | 0.658 | 10.586 | 86.443
South West of England | Seabank 400kV | 400 | 18124.831 | 15.492 | 8.828 | 0.569 | 8.809 | 86.307
South West of England | Taunton 400kV [M1] | 400 | 14244.901 | 13.457 | 11.232 | 0.832 | 11.201 | 85.75
South West of England | Taunton 400kV [M2] | 400 | 14519.352 | 13.592 | 11.02 | 0.809 | 10.99 | 85.792
South Wales | Aberthaw 275kV | 275 | 8977.018 | 13.413 | 8.424 | 0.626 | 8.401 | 85.736
South Wales | Baglan Bay 275kV | 275 | 6021.698 | 13.335 | 12.559 | 0.939 | 12.524 | 85.711
South Wales | Cardiff East 275kV | 275 | 7218.529 | 12.302 | 10.477 | 0.849 | 10.442 | 85.353
South Wales | Cilfynydd 275kV [B] | 275 | 6987.088 | 16.658 | 10.824 | 0.649 | 10.804 | 86.565
South Wales | Cilfynydd 275kV [A] | 275 | 6946.487 | 16.715 | 10.887 | 0.65 | 10.867 | 86.576
South Wales | Cilfynydd 400kV | 400 | 15750.199 | 13.773 | 10.159 | 0.736 | 10.132 | 85.847
South Wales | Cowbridge 275kV Tee | 275 | 7858.556 | 12.587 | 9.623 | 0.762 | 9.593 | 85.458
South Wales | Imperial Park 400kV | 400 | 12254.428 | 14.591 | 13.057 | 0.893 | 13.026 | 86.079
South Wales | Iron Acton 275kV | 275 | 9950.855 | 13.751 | 7.6 | 0.551 | 7.58 | 85.841
South Wales | Margam 275kV | 275 | 6640.56 | 12.327 | 11.388 | 0.921 | 11.351 | 85.362
South Wales | Pembroke 400kV | 400 | 6312.433 | 13.57 | 25.347 | 1.863 | 25.278 | 85.785
South Wales | Pyle 275kV | 275 | 7143.012 | 11.87 | 10.587 | 0.889 | 10.55 | 85.184
South Wales | Rassau 400kV | 400 | 12082.213 | 14.281 | 13.243 | 0.925 | 13.21 | 85.994
South Wales | Rhigos 400KV | 400 | 10830.212 | 13.878 | 14.773 | 1.062 | 14.735 | 85.879
South Wales | Swansea North 275kV | 275 | 3996.625 | 22.31 | 18.922 | 0.847 | 18.903 | 87.434
South Wales | Swansea North 400kV [M1] | 400 | 7571.047 | 14.141 | 21.133 | 1.491 | 21.08 | 85.955
South Wales | Swansea North 400kV [R3] | 400 | 9139.539 | 13.438 | 17.506 | 1.299 | 17.458 | 85.744
South Wales | Tremorfa 275kV | 275 | 7807.828 | 12.301 | 9.686 | 0.785 | 9.654 | 85.352
South Wales | Upper Boat 275kV [MC1/4] | 275 | 6952.11 | 14.734 | 10.878 | 0.737 | 10.853 | 86.117
South Wales | Upper Boat 275kV [MC2/3] | 275 | 6894.514 | 14.785 | 10.969 | 0.74 | 10.944 | 86.131
South Wales | Uskmouth 275kV | 275 | 10571.546 | 15.045 | 7.154 | 0.474 | 7.138 | 86.197
South Wales | Whitson 275kV [A] | 275 | 8099.226 | 15.059 | 9.337 | 0.619 | 9.317 | 86.201
South Wales | Whitson 275kV [B] | 275 | 8451.712 | 16.51 | 8.948 | 0.541 | 8.932 | 86.534
South Wales | Whitson 275kV [M1] | 275 | 9722.839 | 13.982 | 7.778 | 0.555 | 7.758 | 85.909
South Wales | Whitson 275kV [R2] | 275 | 10488.579 | 15.546 | 7.21 | 0.463 | 7.195 | 86.32
South Wales | Whitson 400kV | 400 | 14629.504 | 15.327 | 10.937 | 0.712 | 10.914 | 86.267

## 3. Fault Impedance
Fault Location
Region | Substation / Nodes | Voltage Level (kV) | Hawthorn Pit 400kV |  | Norwich Main 400kV |  | Bicker Fen 400kV |  | Canterbury 400kV |  | Exeter Main 400kV |  | Rhigos 400KV |  | Upper Boat 275kV MC2/3 |  | Upper Boat 275kV MC1/4
|  |  | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm)
North East of England | Blyth 275kV | 275 | 0.538 | 8.28
North East of England | Blyth 400kV | 400 | 1.127 | 18.23
North East of England | Fourstones 275kV | 275 | 2.338 | 23.429
North East of England | Greystones A 275kV | 275 | 0.404 | 9.351
North East of England | Greystones B 275kV | 275 | 0.399 | 9.308
North East of England | Hartlepool 275kV | 275 | 0.372 | 6.054
North East of England | Hartmoor 275kV | 275 | 0.443 | 6.774
North East of England | Hawthorn Pit 275kV | 275 | 0.292 | 4.843
North East of England | Hawthorn Pit 400kV | 400 | 0 | 0
North East of England | Lackenby 275kV | 275 | 0.448 | 9.011
North East of England | Lackenby 400kV | 400 | 0.734 | 11.694
North East of England | Norton 275kV | 275 | 0.27 | 5.284
North East of England | Norton 400kV | 400 | 0.402 | 6.759
North East of England | Offerton 275kV | 275 | 0.433 | 6.363
North East of England | Osbaldwick 400kV [MC3/4] | 400 | 1.402 | 24.129
North East of England | Saltholme 275kV | 275 | 0.39 | 6.311
North East of England | South Shields 275kV | 275 | 0.539 | 7.494
North East of England | Spennymoor 400kV | 400 | 0.675 | 11.137
North East of England | Stella West 275kV | 275 | 0.634 | 9.787
North East of England | Stella West 400kV | 400 | 0.803 | 13.496
North East of England | Tod Point 275kV | 275 | 0.483 | 8.604
North East of England | Tynemouth 275kV | 275 | 0.642 | 8.662
North East of England | West Boldon 275kV | 275 | 0.442 | 6.504
East of England | Bicker Fen 400kV | 400 |  |  | 0.887 | 13.928 | 0 | 0
East of England | Braintree 400kV [B] | 400 |  |  | 2.582 | 39.72 | 2.512 | 38.655
East of England | Braintree 400kV [A] | 400 |  |  | 1.417 | 22.247 | 2.304 | 36.175
East of England | Bramford 400kV [M3] | 400 |  |  | 0.472 | 7.772 | 1.153 | 18.999
East of England | Bramford 400kV [M7] | 400 |  |  | 0.413 | 6.26 | 1.651 | 25.036
East of England | Bulls Lodge 400kV | 400 |  |  | 1.775 | 27.653 | 2.817 | 43.89
East of England | Burwell 400kV | 400 |  |  | 0.901 | 13.943 | 0.519 | 8.026
East of England | Kings Lynn 400kV | 400 |  |  | 0.385 | 6.264 | 0.485 | 7.878
East of England | Leiston 400kV T-Points | 400 |  |  | 0.478 | 8.722 | 1.245 | 22.689
East of England | Necton 400kV | 400 |  |  | 0.175 | 2.696 | 0.531 | 8.205
East of England | Norwich Main 400kV | 400 |  |  | 0 | 0 | 0.834 | 12.352
East of England | Pelham 400kV | 400 |  |  | 1.03 | 15.216 | 0.802 | 11.856
East of England | Rayleigh 400kV | 400 |  |  | 2.104 | 30.141 | 2.438 | 34.932
East of England | Rye House 400kV | 400 |  |  | 2.021 | 31.343 | 1.601 | 24.819
East of England | Sizewell 400kV | 400 |  |  | 0.474 | 8.689 | 1.225 | 22.438
East of England | Spalding North 400kV | 400 |  |  | 0.834 | 13.06 | 0.071 | 1.107
East of England | Sutton Bridge 400kV | 400 |  |  | 0.707 | 9.778 | 0.259 | 3.589
East of England | Walpole 400kV | 400 |  |  | 0.568 | 8.433 | 0.208 | 3.096
East of England | Yaxley 400kV | 400 |  |  | 0.165 | 2.443 | 1.114 | 16.448
South Coast of England | Bolney 400kV | 400 | [6 empty] | 0.892 | 12.679
South Coast of England | Canterbury 400kV AIS | 400 | [6 empty] | 0 | 0
South Coast of England | Canterbury 400kV GIS | 400 | [6 empty] | 0 | 0
South Coast of England | Dungeness 275kV | 275 | [6 empty] | 0.133 | 3.209
South Coast of England | Dungeness 400kV | 400 | [6 empty] | 0.247 | 3.379
South Coast of England | Ninfield 400kV | 400 | [6 empty] | 0.516 | 7.157
South Coast of England | Richborough 400kV | 400 | [6 empty] | 0 | 0
South Coast of England | Sellindge 400kV Compound A | 400 | [6 empty] | 0.112 | 1.522
South Coast of England | Sellindge 400kV Compound B | 400 | [6 empty] | 0.112 | 1.524
South West of England | Abham 400kV | 400 | [8 empty] | 0.149 | 1.678
South West of England | Alverdiscott 400kV [B] | 400 | [8 empty] | 0.797 | 8.84
South West of England | Alverdiscott 400kV [A] | 400 | [8 empty] | 0.781 | 8.672
South West of England | Axminster 400kV | 400 | [8 empty] | 0.174 | 2.496
South West of England | Botley Wood 400kV | 400 | [8 empty] | 1.404 | 20.3
South West of England | Bridgewater 400kV | 400 | [8 empty] | 0.964 | 14.048
South West of England | Chickerell 400kV | 400 | [8 empty] | 0.441 | 6.431
South West of England | Chilling 400kV | 400 | [8 empty] | 1.326 | 19.013
South West of England | Exeter Main 400kV | 400 | [8 empty] | 0 | 0
South West of England | Fawley 400kV | 400 | [8 empty] | 1.335 | 18.991
South West of England | Hinkley Point 275kV | 275 | [8 empty] | 0.532 | 24.763
South West of England | Hinkley Point 400kV | 400 | [8 empty] | 0.464 | 7.969
South West of England | Hinkley Point C 400kV | 400 | [8 empty] | 0.466 | 7.981
South West of England | Indian Queens 400kV | 400 | [8 empty] | 0.447 | 4.773
South West of England | Landulph 400kV | 400 | [8 empty] | 0.33 | 3.577
South West of England | Langage 400kV | 400 | [8 empty] | 0.21 | 2.349
South West of England | Lovedean 400kV | 400 | [8 empty] | 1.303 | 17.897
South West of England | Mannington 400kV | 400 | [8 empty] | 0.721 | 10.176
South West of England | Marchwood 400kV | 400 | [8 empty] | 1.739 | 24.849
South West of England | Melksham 400kV | 400 | [8 empty] | 1.302 | 16.801
South West of England | Nursling 400kV [MC1] | 400 | [8 empty] | 1.803 | 25.997
South West of England | Nursling 400kV [A] | 400 | [8 empty] | 1.215 | 17.831
South West of England | Sandford 400kV | 400 | [8 empty] | 0.998 | 16.052
South West of England | Seabank 400kV | 400 | [8 empty] | 1.06 | 16.422
South West of England | Taunton 400kV [M1] | 400 | [8 empty] | 0.365 | 4.91
South West of England | Taunton 400kV [M2] | 400 | [8 empty] | 0.369 | 5.021
South Wales | Aberthaw 275kV | 275 | [10 empty] | 0.539 | 7.229 | 0.418 | 5.601 | 0.425 | 5.703
South Wales | Baglan Bay 275kV | 275 | [10 empty] | 0.539 | 7.182 | 0.989 | 13.19 | 1.002 | 13.367
South Wales | Cardiff East 275kV | 275 | [10 empty] | 1.044 | 12.844 | 1.138 | 14.003 | 1.153 | 14.18
South Wales | Cilfynydd 275kV [B] | 275 | [10 empty] | 0.452 | 7.528 | 0.666 | 11.1 | 0.071 | 1.174
South Wales | Cilfynydd 275kV [A] | 275 | [10 empty] | 0.459 | 7.664 | 0.07 | 1.177 | 0.685 | 11.455
South Wales | Cilfynydd 400kV | 400 | [10 empty] | 0.41 | 5.652 | 1.261 | 17.362 | 1.271 | 17.511
South Wales | Cowbridge 275kV Tee | 275 | [10 empty] | 0.677 | 8.519 | 0.636 | 8.005 | 0.646 | 8.133
South Wales | Imperial Park 400kV | 400 | [10 empty] | 0.746 | 10.881 | 1.963 | 28.648 | 1.98 | 28.882
South Wales | Iron Acton 275kV | 275 | [10 empty] | 1.233 | 16.962 | 1.785 | 24.544 | 1.807 | 24.85
South Wales | Margam 275kV | 275 | [10 empty] | 0.64 | 7.888 | 0.871 | 10.742 | 0.884 | 10.898
South Wales | Pembroke 400kV | 400 | [10 empty] | 0.687 | 9.326 | 3.423 | 46.448 | 3.452 | 46.848
South Wales | Pyle 275kV | 275 | [10 empty] | 0.672 | 7.976 | 0.792 | 9.396 | 0.804 | 9.539
South Wales | Rassau 400kV | 400 | [10 empty] | 0.827 | 11.814 | 2.096 | 29.934 | 2.113 | 30.17
South Wales | Rhigos 400KV | 400 | [10 empty] | 0 | 0 | 1.772 | 24.591 | 1.787 | 24.805
South Wales | Swansea North 275kV | 275 | [10 empty] | 0.475 | 10.597 | 1.755 | 39.16 | 1.77 | 39.495
South Wales | Swansea North 400kV [M1] | 400 | [10 empty] | 0.742 | 10.486 | 2.765 | 39.1 | 2.789 | 39.436
South Wales | Swansea North 400kV [R3] | 400 | [10 empty] | 0.247 | 3.316 | 2.188 | 29.399 | 2.208 | 29.667
South Wales | Tremorfa 275kV | 275 | [10 empty] | 1.132 | 13.926 | 1.252 | 15.403 | 1.267 | 15.585
South Wales | Upper Boat 275kV [MC1/4] | 275 | [10 empty] | 0.535 | 7.885 | 0.703 | 10.364 | 0 | 0
South Wales | Upper Boat 275kV [MC2/3] | 275 | [10 empty] | 0.546 | 8.066 | 0 | 0 | 0.728 | 10.759
South Wales | Uskmouth 275kV | 275 | [10 empty] | 0.734 | 11.043 | 0.933 | 14.03 | 0.943 | 14.18
South Wales | Whitson 275kV [A] | 275 | [10 empty] | 1.044 | 15.717 | 1.361 | 20.502 | 1.375 | 20.712
South Wales | Whitson 275kV [B] | 275 | [10 empty] | 0.897 | 14.808 | 1.208 | 19.944 | 1.22 | 20.146
South Wales | Whitson 275kV [M1] | 275 | [10 empty] | 0.878 | 12.27 | 1.118 | 15.629 | 1.13 | 15.795
South Wales | Whitson 275kV [R2] | 275 | [10 empty] | 0.716 | 11.127 | 0.949 | 14.761 | 0.959 | 14.916
South Wales | Whitson 400kV | 400 | [10 empty] | 0.874 | 13.393 | 1.875 | 28.739 | 1.891 | 28.982

## 4. Effectiveness Factors
Effectiveness to:
Region | Substation / Nodes | Voltage Level (kV) | Hawthorn Pit 400kV | Norwich Main 400kV | Bicker Fen 400kV | Canterbury 400kV | Exeter Main 400kV | Rhigos 400KV | Upper Boat 275kV MC3 | Upper Boat 275kV MC4
North East of England | Blyth 275kV | 275 | 48%
North East of England | Blyth 400kV | 400 | 46%
North East of England | Fourstones 275kV | 275 | 39%
North East of England | Greystones A 275kV | 275 | 54%
North East of England | Greystones B 275kV | 275 | 54%
North East of England | Hartlepool 275kV | 275 | 60%
North East of England | Hartmoor 275kV | 275 | 61%
North East of England | Hawthorn Pit 275kV | 275 | 62%
North East of England | Hawthorn Pit 400kV | 400 | 100%
North East of England | Lackenby 275kV | 275 | 54%
North East of England | Lackenby 400kV | 400 | 55%
North East of England | Norton 275kV | 275 | 61%
North East of England | Norton 400kV | 400 | 61%
North East of England | Offerton 275kV | 275 | 59%
North East of England | Osbaldwick 400kV [MC3/4] | 400 | 38%
North East of England | Saltholme 275kV | 275 | 60%
North East of England | South Shields 275kV | 275 | 55%
North East of England | Spennymoor 400kV | 400 | 55%
North East of England | Stella West 275kV | 275 | 44%
North East of England | Stella West 400kV | 400 | 47%
North East of England | Tod Point 275kV | 275 | 55%
North East of England | Tynemouth 275kV | 275 | 53%
North East of England | West Boldon 275kV | 275 | 57%
East of England | Bicker Fen 400kV | 400 |  | 42% | 100%
East of England | Braintree 400kV [B] | 400 |  | 35% | 38%
East of England | Braintree 400kV [A] | 400 |  | 44% | 38%
East of England | Bramford 400kV [M3] | 400 |  | 59% | 42%
East of England | Bramford 400kV [M7] | 400 |  | 73% | 46%
East of England | Bulls Lodge 400kV | 400 |  | 37% | 39%
East of England | Burwell 400kV | 400 |  | 44% | 58%
East of England | Kings Lynn 400kV | 400 |  | 70% | 69%
East of England | Leiston 400kV T-Points | 400 |  | 59% | 41%
East of England | Necton 400kV | 400 |  | 81% | 64%
East of England | Norwich Main 400kV | 400 |  | 100% | 56%
East of England | Pelham 400kV | 400 |  | 37% | 44%
East of England | Rayleigh 400kV | 400 |  | 35% | 35%
East of England | Rye House 400kV | 400 |  | 35% | 42%
East of England | Sizewell 400kV | 400 |  | 59% | 41%
East of England | Spalding North 400kV | 400 |  | 46% | 91%
East of England | Sutton Bridge 400kV | 400 |  | 52% | 76%
East of England | Walpole 400kV | 400 |  | 52% | 76%
East of England | Yaxley 400kV | 400 |  | 84% | 51%
South Coast of England | Bolney 400kV | 400 |  |  |  | 55%
South Coast of England | Canterbury 400kV AIS | 400 |  |  |  | 100%
South Coast of England | Canterbury 400kV GIS | 400 |  |  |  | 100%
South Coast of England | Dungeness 275kV | 275 |  |  |  | 83%
South Coast of England | Dungeness 400kV | 400 |  |  |  | 83%
South Coast of England | Ninfield 400kV | 400 |  |  |  | 70%
South Coast of England | Richborough 400kV | 400 |  |  |  | 100%
South Coast of England | Sellindge 400kV Compound A | 400 |  |  |  | 92%
South Coast of England | Sellindge 400kV Compound B | 400 |  |  |  | 92%
South West of England | Abham 400kV | 400 |  |  |  |  | 93%
South West of England | Alverdiscott 400kV [B] | 400 |  |  |  |  | 76%
South West of England | Alverdiscott 400kV [A] | 400 |  |  |  |  | 77%
South West of England | Axminster 400kV | 400 |  |  |  |  | 88%
South West of England | Botley Wood 400kV | 400 |  |  |  |  | 40%
South West of England | Bridgewater 400kV | 400 |  |  |  |  | 51%
South West of England | Chickerell 400kV | 400 |  |  |  |  | 76%
South West of England | Chilling 400kV | 400 |  |  |  |  | 41%
South West of England | Exeter Main 400kV | 400 |  |  |  |  | 100%
South West of England | Fawley 400kV | 400 |  |  |  |  | 41%
South West of England | Hinkley Point 275kV | 275 |  |  |  |  | 53%
South West of England | Hinkley Point 400kV | 400 |  |  |  |  | 53%
South West of England | Hinkley Point C 400kV | 400 |  |  |  |  | 53%
South West of England | Indian Queens 400kV | 400 |  |  |  |  | 81%
South West of England | Landulph 400kV | 400 |  |  |  |  | 86%
South West of England | Langage 400kV | 400 |  |  |  |  | 89%
South West of England | Lovedean 400kV | 400 |  |  |  |  | 38%
South West of England | Mannington 400kV | 400 |  |  |  |  | 59%
South West of England | Marchwood 400kV | 400 |  |  |  |  | 40%
South West of England | Melksham 400kV | 400 |  |  |  |  | 37%
South West of England | Nursling 400kV [MC1] | 400 |  |  |  |  | 39%
South West of England | Nursling 400kV [A] | 400 |  |  |  |  | 48%
South West of England | Sandford 400kV | 400 |  |  |  |  | 48%
South West of England | Seabank 400kV | 400 |  |  |  |  | 43%
South West of England | Taunton 400kV [M1] | 400 |  |  |  |  | 74%
South West of England | Taunton 400kV [M2] | 400 |  |  |  |  | 73%
South Wales | Aberthaw 275kV | 275 | [5 empty] | 59% | 64% | 64%
South Wales | Baglan Bay 275kV | 275 | [5 empty] | 69% | 53% | 53%
South Wales | Cardiff East 275kV | 275 | [5 empty] | 52% | 49% | 49%
South Wales | Cilfynydd 275kV [B] | 275 | [5 empty] | 62% | 52% | 91%
South Wales | Cilfynydd 275kV [A] | 275 | [5 empty] | 63% | 91% | 52%
South Wales | Cilfynydd 400kV | 400 | [5 empty] | 68% | 40% | 41%
South Wales | Cowbridge 275kV Tee | 275 | [5 empty] | 59% | 59% | 59%
South Wales | Imperial Park 400kV | 400 | [5 empty] | 59% | 36% | 36%
South Wales | Iron Acton 275kV | 275 | [5 empty] | 40% | 31% | 31%
South Wales | Margam 275kV | 275 | [5 empty] | 65% | 56% | 56%
South Wales | Pembroke 400kV | 400 | [5 empty] | 77% | 39% | 39%
South Wales | Pyle 275kV | 275 | [5 empty] | 63% | 57% | 57%
South Wales | Rassau 400kV | 400 | [5 empty] | 57% | 34% | 35%
South Wales | Rhigos 400KV | 400 | [5 empty] | 100% | 40% | 41%
South Wales | Swansea North 275kV | 275 | [5 empty] | 71% | 39% | 39%
South Wales | Swansea North 400kV [M1] | 400 | [5 empty] | 71% | 40% | 40%
South Wales | Swansea North 400kV [R3] | 400 | [5 empty] | 86% | 41% | 41%
South Wales | Tremorfa 275kV | 275 | [5 empty] | 49% | 45% | 45%
South Wales | Upper Boat 275kV [MC1/4] | 275 | [5 empty] | 61% | 53% | 100%
South Wales | Upper Boat 275kV [MC2/3] | 275 | [5 empty] | 62% | 100% | 54%
South Wales | Uskmouth 275kV | 275 | [5 empty] | 47% | 40% | 40%
South Wales | Whitson 275kV [A] | 275 | [5 empty] | 45% | 38% | 38%
South Wales | Whitson 275kV [B] | 275 | [5 empty] | 45% | 37% | 37%
South Wales | Whitson 275kV [M1] | 275 | [5 empty] | 47% | 40% | 40%
South Wales | Whitson 275kV [R2] | 275 | [5 empty] | 47% | 39% | 39%
South Wales | Whitson 400kV | 400 | [5 empty] | 51% | 33% | 33%

## 5. Sizing Guidance
This section provides guidance on the sizing methodology that Tenderers can use when sizing solutions, and provides an example of using this guidance to identify potential solution sizes. | Sizing Methodology and Step-by-Step Guide:
Phase 3 Tenderers are encouraged to use this sizing methodology - combined with other provided information and data tools - to help size the target value of short-circuit level (SCL) injection (refer to Note 3 at Note Tab) at a connection site or Grid Entry Point and choose suitable technology and solution design to deliver the decided SCL injection. | NGESO encourage Tenderers to consider sizing their proposed solutions such that the SCL that is provided at the connection site or (GEP) Grid Entry Point ❷ can, after accounting for the site effectiveness, meet: the full SCL requirement (100%), at least half the SCL requirement (50%), and/or at least one third of the SCL requirement (33.4%) at the main Reference point ➊ in the targetted region of need.
Please note:
This methodology and the example provided is acting as guidance only - Tenderers have full flexibility to tailor their designs in terms of solution size to meet the SCL and inertia service requirements set by Phase 3 tender.
Proposed solutions are required to provide both SCL and inertia. In addition to the SCL sizing methodology provided (see right), NGESO encourage providing an equal ratio of SCL to inertia service when sizing solutions (i.e. providing 1MVA SCL service to 1MW.s inertia service).
Useful information when sizing solutions: | Rationale for 100%/50%/33.4% sizing guidance
Stability Phase 3 requirement across the 5 regions of need:
NGESO expects a low number of solutions per region to be the most cost effective way to meet the need. Due to this, there is a greater risk of NGESO overprocuring to meet the n-1 criteria, particularly when forming a small porfolio of solutions in a region from unconnected Tenderers. The table below shows the optimal size of a solution within differing sizes of regional porfolios.
NGESO encourages Tenderers to provide variations of solutions with different SCL (MVA) capabilties, based on the above percentages for each regional requirement (while remaining within the cap on solutions explained in the Instructions to Tenderers). Please note that these % should be viewed as guidance when used to help size solutions. Note: The cap on the number of solutions per region has been sized to allow for variations of solutions with different sizes at each of the reserved bays within each region.
For additional information on the regions of need, please refer to the Stability Phase 3 Network Diagram Map document.
Example to demonstrate the use of the sizing methodology
For the 5 service regions map, please refer to Stability Phase 3 Network Diagram Map document
Step 1.
Select a region from the 5 regions of need for Stability Phase 3 and note down the SCL requirement:
For example, select North-East England region and note down 500MVA SCL requirement at Reference site (Hawthorn Pit 400kV) for this region.
For regions with multiple reference sites, e.g. East of England or South Wales region, please select the SCL requirement at the Main Reference Site for these regions as these represent the major part of the SCL requirement for these regions. For example, select Norwich Main 400kV and note down 1500MVA for East of England region.
Step 2.
Select a site within the region which the Tenderer is targetting for their solution to connect at to provide both SCL and inertia service.
Please refer to '4. Effectiveness Factors' within this document for the list of substations within each region of need.
For example, select Offerton 275kV site and the site effectiveness factor is 59% againt the reference site (Hawthorn Pit 400kV) in North-East England region:
Please refer to '4. Effectiveness Factors' tab in this document for the list of the transmission substations within each of the regions of need and their effectiveness data.
For regions with multiple reference sites, e.g. if Yaxley 400kV was selected in the East of England region, please use the site effectiveness factor against the Main Reference Site which in this case, would be Norwich Main 400kV site. From the effectivess data, Yaxley 400kV site has an effectiveness factor of 84% against Norwich Main 400kV site:
Step 3:
Work out the SCL injection (MVA) required to contribute the full (100%), half (50%), and/or one third (33.4%) of the SCL requirement at the reference site for the selected region:
In this example, the SCL requirement at Hawthorn Pit 400kV is 500MVA, so to meet full requirement (100%) and considering the site effectiveness factor, the SCL injection at Offerton 275kV connection point would be:
500x100% / 59% = 848MVA (rounded up).
The SCL injection values to meet either the half (50%), one third (33.4%) of the procured SCL volumes 500MVA can also be worked out with same formula and as per table below as example:
Alternative
Another way to workout the required SCL injection at the connection site is via the data table in tab "1. Phase 3 Site Data" of this document:
In this data sheet, first select connection site from drop list 1, e.g. Offerton 275kV. The effectiveness factor can be read from the Cell 2 as indicated in the diagram below.
The Tenderer should then type in the injection SCL current (kA) in the Cell 3, e.g. 0.889kA, in order to check the SCL contribution at the reference site.
In this example, the reference site is Hawthorn Pit 400kV, and the data tool confirms 250MVA SCL contribution in Cell 4. This can be used to identify the % of requirement being met. In this example, 250MVA would meet 50% of the requirement for the North East.
Step 4:
Once the required SCL injection values at the connection site have been worked out, Tenderers are able to use these values to size and design their solutions.
1
2

## 6. Reserved Bay Size check
Provided by NGESO (Lookup cell) |  |  | How to use:
Bidder to provide based on solution size |  |  | 1- Choose the substation name and targeted solution size here.
Calculated cells (formula)
| Site information |  |  | Your solution (at GEP)
| Site: | CANT4 - 50% |  | Ik'(kA) | 1.5 | How to use:
| Reserved capacity (MVA): | 1110 |  | Ik''(kA) | 2.1 | 2- Based on the solution size, fill Ik', Ik'' and X''/R at GEP.
| Site Voltage level (kV): | 400 |  | X''/R | 20
| Reserved Ipeak(kA): | 5.9341 |  | Solution Ipeak(kA): | 5.5343
| Reserved Ibreak(kA): | 1.8317 |  | Solution Ibreak(kA): | 1.6719
| Results: | PASS: The reserved capacity at CANT4 - 50% can accommodate this solution.
This sheet is applicable to solutions planning to be connected at reserved bays only. Question 34 of the Technical Submission Document asks Tenderers to confirm whether their solution is within the sub-transient and transient SCL values assumed for the reserved bays.
This sheet has been developed for Tenderers to use to help identify and understand if the reserved capacity at different sites is sufficient to accommodate your proposed solution by calculating three phase peak current (Ipeak) and break current (Ibreak) of the solution and comparing them to the corresponding reserved Ipeak and Ibreak. Exceeding one or both the reserved currents (Ipeak,Ibreak) means that the reserved site capacity cannot accommodate the solution size.
NGESO encourage Tenderers to use this tool prior to the tender submission deadline to check whether their proposed solution can be accomodated by capacity of the reserved bay.
Ik' refers to the solution's three phase transient current in kA at Grid Entry Point (GEP). Ik'' refers to the solution's three phase sub-transient current in kA at GEP. X''/R is the sub-transient X to R ratio of the solution at GEP.
Please note that the above three values (Ik', Ik'' and X''/R) are calculated at GEP. Planning Code (PC.A.2.5.6) can be used to acquire these values at GEP.

## Reserved Sites(to be hidden) (hidden)
Site | kV | MVA | Ik'(kA) | Ik''(kA) | X''/R | Ip(kA) | Ib(kA)
CANT4 - 50% | 400 | 1110 | 1.6021 | 2.4032 | 10 | 5.9341 | 1.8317
CANT4 - 100% | 400 | 2220 | 3.2043 | 4.8064 | 10 | 11.8682 | 3.6633
RICH4 - 50% | 400 | 1135 | 1.6382 | 2.4573 | 10 | 6.0677 | 1.8729
RICH4 - 100% | 400 | 2220 | 3.2043 | 4.8064 | 10 | 11.8682 | 3.6633
LAGA4 - 50% | 400 | 355 | 0.5124 | 0.7686 | 10 | 1.8978 | 0.5858
LAGA4 - 100% | 400 | 715 | 1.032 | 1.548 | 10 | 3.8224 | 1.1799
LAND4 - 50% | 400 | 380 | 0.54848 | 0.82272 | 10 | 2.0315 | 0.62705
LAND4 - 100% | 400 | 770 | 1.1114 | 1.6671 | 10 | 4.1164 | 1.2706
CILF4 - 33.4% | 400 | 1265 | 1.8259 | 2.7388 | 10 | 6.7627 | 2.0874
CILF4 - 50% | 400 | 1900 | 2.7424 | 4.1136 | 10 | 10.1574 | 3.1353
RASS4 - 33.4% | 400 | 1900 | 2.7424 | 4.1136 | 10 | 10.1574 | 3.1353
RASS4 - 50% | 400 | 2950 | 4.258 | 6.3869 | 10 | 15.7708 | 4.8679
UPPB2 - 33.4% | 275 | 1900 | 3.989 | 5.9834 | 10 | 14.7744 | 4.5604
UPPB2 - 50% | 275 | 2820 | 5.9205 | 8.8807 | 10 | 21.9284 | 6.7686
YAXL4 - 33.4% | 400 | 795 | 1.1475 | 1.7212 | 10 | 4.2501 | 1.3119
YAXL4 - 50% | 400 | 1280 | 1.8475 | 2.7713 | 10 | 6.8429 | 2.1122
YAXL4 - 100% | 400 | 2555 | 3.6878 | 5.5317 | 10 | 13.6591 | 4.2161
NECT4 - 33.4% | 400 | 850 | 1.2269 | 1.8403 | 10 | 4.5441 | 1.4026
NECT4 - 50% | 400 | 1290 | 1.862 | 2.7929 | 10 | 6.8964 | 2.1287
NECT4 - 100% | 400 | 2640 | 3.8105 | 5.7158 | 10 | 14.1135 | 4.3564
WALP4 - 33.4% | 400 | 2135 | 3.0816 | 4.6224 | 10 | 11.4137 | 3.5231
WALP4 - 50% | 400 | 3300 | 4.7631 | 7.1447 | 10 | 17.6419 | 5.4455
WALP4 - 100% | 400 | 7000 | 10.1036 | 15.1554 | 10 | 37.4221 | 11.551
HART2 - 50% | 275 | 855 | 1.795 | 2.6926 | 10 | 6.6485 | 2.0522
HART2 - 100% | 275 | 1650 | 3.4641 | 5.1962 | 10 | 12.8304 | 3.9603
OFFE2 - 50% | 275 | 840 | 1.7635 | 2.6453 | 10 | 6.5319 | 2.0162
OFFE2 - 100% | 275 | 1625 | 3.4116 | 5.1174 | 10 | 12.636 | 3.9003

## 6. All Sites (hidden)
Substation / Nodes
Aberthaw 275kV
Abham 400kV
Alverdiscott 400kV [A]
Alverdiscott 400kV [B]
Axminster 400kV
Baglan Bay 275kV
Bicker Fen 400kV
Blyth 275kV
Blyth 400kV
Bolney 400kV
Botley Wood 400kV
Braintree 400kV [A]
Braintree 400kV [B]
Bramford 400kV [M3]
Bramford 400kV [M7]
Bridgewater 400kV
Bulls Lodge 400kV
Burwell 400kV
Canterbury 400kV AIS
Canterbury 400kV GIS
Cardiff East 275kV
Chickerell 400kV
Chilling 400kV
Cilfynydd 275kV [A]
Cilfynydd 275kV [B]
Cilfynydd 400kV
Cowbridge 275kV Tee
Dungeness 275kV
Dungeness 400kV
Exeter Main 400kV
Fawley 400kV
Fourstones 275kV
Greystones A 275kV
Greystones B 275kV
Hartlepool 275kV
Hartmoor 275kV
Hawthorn Pit 275kV
Hawthorn Pit 400kV
Hinkley Point 275kV
Hinkley Point 400kV
Hinkley Point C 400kV
Imperial Park 400kV
Indian Queens 400kV
Iron Acton 275kV
Kings Lynn 400kV
Lackenby 275kV
Lackenby 400kV
Landulph 400kV
Langage 400kV
Leiston 400kV T-Points
Lovedean 400kV
Mannington 400kV
Marchwood 400kV
Margam 275kV
Melksham 400kV
Necton 400kV
Ninfield 400kV
Norton 275kV
Norton 400kV
Norwich Main 400kV
Nursling 400kV [A]
Nursling 400kV [MC1]
Offerton 275kV
Osbaldwick 400kV [MC3/4]
Pelham 400kV
Pembroke 400kV
Pyle 275kV
Rassau 400kV
Rayleigh 400kV
Rhigos 400KV
Richborough 400kV
Rye House 400kV
Saltholme 275kV
Sandford 400kV
Seabank 400kV
Sellindge 400kV Compound A
Sellindge 400kV Compound B
Sizewell 400kV
South Shields 275kV
Spalding North 400kV
Spennymoor 400kV
Stella West 275kV
Stella West 400kV
Sutton Bridge 400kV
Swansea North 275kV
Swansea North 400kV [M1]
Swansea North 400kV [R3]
Taunton 400kV [M1]
Taunton 400kV [M2]
Tod Point 275kV
Tremorfa 275kV
Tynemouth 275kV
Upper Boat 275kV [MC1/4]
Upper Boat 275kV [MC2/3]
Uskmouth 275kV
Walpole 400kV
West Boldon 275kV
Whitson 275kV [A]
Whitson 275kV [B]
Whitson 275kV [M1]
Whitson 275kV [R2]
Whitson 400kV
Yaxley 400kV