## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.

## Report
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; |  | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) |  | Transmission fault | Voltage Dip | Additional data
20211002-1 | Trip of Eleclink | Eleclink Trip test | 2021-10-02 03:35 | 20211002-1 | 49.864 | 50.187 | 0.15895 | 169 | Eleclink | 1000
20211003-1 | Trip of HEYM-12 |  | 2021-10-03 10:24 | 20211003-1 | 50.07 | 49.84 | -0.033915 | 161 | HEYM-12 | -264
20211004-1 | Trip of TORN-1 |  | 2021-10-04 23:00 | 20211004-1 | 50.099 | 49.998 | -0.040806 | 215 | TORN-1 | -284
20211005-1 | Deload of SPLN-1 |  | 2021-10-05 17:51 | 20211005-1 | 49.971 | 49.87 | -0.045908 | 223 | SPLN-1 | -270
20211007-1 | Trip of CDCL-1 |  | 2021-10-07 09:41 | 20211007-1 | 50.015 | 49.862 | -0.04036 | 243 | CDCL-1 | -340
20211012-1 | Trip of PEMB-41 |  | 2021-10-12 04:27 | 20211012-1 | 49.951 | 49.892 | -0.029027 | 151 | PEMB-41 | -420
20211016-1 | Trip of NSL |  | 2021-10-16 20:27 | 20211016-1 | 49.954 | 49.757 | -0.079748 | 273 | NSL | -700
20211020-1 | Trip of TKNEW-1 |  | 2021-10-20 16:48 | 20211020-1 | 49.976 | 49.861 | -0.029178 | 225 | TKNEW-1 | -280
20211022-1 | Trip of IFA | IFA BP2 trip | 2021-10-22 08:04 | 20211022-1 | 49.983 | 50.283 | 0.094029 | 231 | IFA | 849
20211031-1 | Trip of Whitson - Uskmouth - Tremorfa and Aberthaw - Tremorfa circuits |  | 2021-10-31 18:07 | [8 empty] | Celsa Steel | 85.7

## 20211002-1
In GMT
Date | Time | Freq
2021-10-02 | 2:34 | 49.868
2021-10-02 | 2:34 | 49.868
2021-10-02 | 2:34 | 49.867
2021-10-02 | 2:34 | 49.868
2021-10-02 | 2:34 | 49.869
2021-10-02 | 2:34 | 49.871
2021-10-02 | 2:34 | 49.872
2021-10-02 | 2:34 | 49.873
2021-10-02 | 2:34 | 49.874
2021-10-02 | 2:34 | 49.875
2021-10-02 | 2:34 | 49.873
2021-10-02 | 2:34 | 49.872
2021-10-02 | 2:34 | 49.869
2021-10-02 | 2:34 | 49.869
2021-10-02 | 2:34 | 49.87
2021-10-02 | 2:34 | 49.869
2021-10-02 | 2:34 | 49.87
2021-10-02 | 2:34 | 49.871
2021-10-02 | 2:34 | 49.871
2021-10-02 | 2:34 | 49.872
2021-10-02 | 2:34 | 49.873
2021-10-02 | 2:34 | 49.872
2021-10-02 | 2:34 | 49.872
2021-10-02 | 2:34 | 49.871
2021-10-02 | 2:34 | 49.871
2021-10-02 | 2:34 | 49.873
2021-10-02 | 2:34 | 49.876
2021-10-02 | 2:34 | 49.878
2021-10-02 | 2:34 | 49.878
2021-10-02 | 2:34 | 49.881
2021-10-02 | 2:34 | 49.881
2021-10-02 | 2:35 | 49.88
2021-10-02 | 2:35 | 49.879
2021-10-02 | 2:35 | 49.878
2021-10-02 | 2:35 | 49.877
2021-10-02 | 2:35 | 49.878
2021-10-02 | 2:35 | 49.878
2021-10-02 | 2:35 | 49.877
2021-10-02 | 2:35 | 49.877
2021-10-02 | 2:35 | 49.877
2021-10-02 | 2:35 | 49.875
2021-10-02 | 2:35 | 49.874
2021-10-02 | 2:35 | 49.875
2021-10-02 | 2:35 | 49.874
2021-10-02 | 2:35 | 49.871
2021-10-02 | 2:35 | 49.871
2021-10-02 | 2:35 | 49.869
2021-10-02 | 2:35 | 49.869
2021-10-02 | 2:35 | 49.87
2021-10-02 | 2:35 | 49.87
2021-10-02 | 2:35 | 49.87
2021-10-02 | 2:35 | 49.87
2021-10-02 | 2:35 | 49.87
2021-10-02 | 2:35 | 49.871
2021-10-02 | 2:35 | 49.874
2021-10-02 | 2:35 | 49.877
2021-10-02 | 2:35 | 49.878
2021-10-02 | 2:35 | 49.878
2021-10-02 | 2:35 | 49.876
2021-10-02 | 2:35 | 49.874
2021-10-02 | 2:35 | 49.873
2021-10-02 | 2:35 | 49.871
2021-10-02 | 2:35 | 49.868
2021-10-02 | 2:35 | 49.863
2021-10-02 | 2:35 | 49.861
2021-10-02 | 2:35 | 49.864
2021-10-02 | 2:35 | 49.865
2021-10-02 | 2:35 | 49.93
2021-10-02 | 2:35 | 50.045
2021-10-02 | 2:35 | 50.128
2021-10-02 | 2:35 | 50.173
2021-10-02 | 2:35 | 50.187
2021-10-02 | 2:35 | 50.182
2021-10-02 | 2:35 | 50.162
2021-10-02 | 2:35 | 50.139
2021-10-02 | 2:35 | 50.113
2021-10-02 | 2:35 | 50.089
2021-10-02 | 2:35 | 50.073
2021-10-02 | 2:35 | 50.065
2021-10-02 | 2:35 | 50.063
2021-10-02 | 2:35 | 50.068
2021-10-02 | 2:35 | 50.077
2021-10-02 | 2:35 | 50.082
2021-10-02 | 2:35 | 50.086
2021-10-02 | 2:35 | 50.088
2021-10-02 | 2:35 | 50.089
2021-10-02 | 2:35 | 50.09
2021-10-02 | 2:35 | 50.09
2021-10-02 | 2:35 | 50.089
2021-10-02 | 2:35 | 50.088
2021-10-02 | 2:36 | 50.086
2021-10-02 | 2:36 | 50.086
2021-10-02 | 2:36 | 50.083
2021-10-02 | 2:36 | 50.081
2021-10-02 | 2:36 | 50.079
2021-10-02 | 2:36 | 50.079
2021-10-02 | 2:36 | 50.079
2021-10-02 | 2:36 | 50.081
2021-10-02 | 2:36 | 50.081
2021-10-02 | 2:36 | 50.083
2021-10-02 | 2:36 | 50.083
2021-10-02 | 2:36 | 50.085
2021-10-02 | 2:36 | 50.088
2021-10-02 | 2:36 | 50.093
2021-10-02 | 2:36 | 50.097
2021-10-02 | 2:36 | 50.101
2021-10-02 | 2:36 | 50.104
2021-10-02 | 2:36 | 50.104
2021-10-02 | 2:36 | 50.105
2021-10-02 | 2:36 | 50.105
2021-10-02 | 2:36 | 50.105
2021-10-02 | 2:36 | 50.105
2021-10-02 | 2:36 | 50.105
2021-10-02 | 2:36 | 50.105
2021-10-02 | 2:36 | 50.104
2021-10-02 | 2:36 | 50.106
2021-10-02 | 2:36 | 50.106
2021-10-02 | 2:36 | 50.107
2021-10-02 | 2:36 | 50.111
2021-10-02 | 2:36 | 50.114
2021-10-02 | 2:36 | 50.116
2021-10-02 | 2:36 | 50.117
2021-10-02 | 2:36 | 50.116
2021-10-02 | 2:36 | 50.118
2021-10-02 | 2:36 | 50.118
2021-10-02 | 2:36 | 50.12
2021-10-02 | 2:36 | 50.12
2021-10-02 | 2:36 | 50.122
2021-10-02 | 2:36 | 50.121
2021-10-02 | 2:36 | 50.121
2021-10-02 | 2:36 | 50.122
2021-10-02 | 2:36 | 50.123
2021-10-02 | 2:36 | 50.125
2021-10-02 | 2:36 | 50.125
2021-10-02 | 2:36 | 50.126
2021-10-02 | 2:36 | 50.126
2021-10-02 | 2:36 | 50.126
2021-10-02 | 2:36 | 50.124
2021-10-02 | 2:36 | 50.122
2021-10-02 | 2:36 | 50.122
2021-10-02 | 2:36 | 50.121
2021-10-02 | 2:36 | 50.122
2021-10-02 | 2:36 | 50.124
2021-10-02 | 2:36 | 50.127
2021-10-02 | 2:36 | 50.13
2021-10-02 | 2:36 | 50.132
2021-10-02 | 2:36 | 50.135
2021-10-02 | 2:36 | 50.136
2021-10-02 | 2:36 | 50.137
2021-10-02 | 2:36 | 50.138
2021-10-02 | 2:36 | 50.14
2021-10-02 | 2:37 | 50.141
2021-10-02 | 2:37 | 50.141
2021-10-02 | 2:37 | 50.14
2021-10-02 | 2:37 | 50.139
2021-10-02 | 2:37 | 50.14
2021-10-02 | 2:37 | 50.14
2021-10-02 | 2:37 | 50.142
2021-10-02 | 2:37 | 50.142
2021-10-02 | 2:37 | 50.141
2021-10-02 | 2:37 | 50.139
2021-10-02 | 2:37 | 50.136
2021-10-02 | 2:37 | 50.133
2021-10-02 | 2:37 | 50.119
2021-10-02 | 2:37 | 50.104
2021-10-02 | 2:37 | 50.092
2021-10-02 | 2:37 | 50.085
2021-10-02 | 2:37 | 50.081
2021-10-02 | 2:37 | 50.081
2021-10-02 | 2:37 | 50.081
2021-10-02 | 2:37 | 50.081
2021-10-02 | 2:37 | 50.082
2021-10-02 | 2:37 | 50.081
2021-10-02 | 2:37 | 50.082
2021-10-02 | 2:37 | 50.081
2021-10-02 | 2:37 | 50.083
2021-10-02 | 2:37 | 50.083
2021-10-02 | 2:37 | 50.081
2021-10-02 | 2:37 | 50.078
2021-10-02 | 2:37 | 50.075
2021-10-02 | 2:37 | 50.074
2021-10-02 | 2:37 | 50.071
2021-10-02 | 2:37 | 50.072
2021-10-02 | 2:37 | 50.072
2021-10-02 | 2:37 | 50.076
2021-10-02 | 2:37 | 50.082
2021-10-02 | 2:37 | 50.085
2021-10-02 | 2:37 | 50.088
2021-10-02 | 2:37 | 50.089
2021-10-02 | 2:37 | 50.088
2021-10-02 | 2:37 | 50.091
2021-10-02 | 2:37 | 50.092
2021-10-02 | 2:37 | 50.092
2021-10-02 | 2:37 | 50.092
2021-10-02 | 2:37 | 50.092
2021-10-02 | 2:37 | 50.094
2021-10-02 | 2:37 | 50.092
2021-10-02 | 2:37 | 50.091
2021-10-02 | 2:37 | 50.088
2021-10-02 | 2:37 | 50.087
2021-10-02 | 2:37 | 50.088
2021-10-02 | 2:37 | 50.089
2021-10-02 | 2:37 | 50.089
2021-10-02 | 2:37 | 50.091
2021-10-02 | 2:37 | 50.092
2021-10-02 | 2:37 | 50.094
2021-10-02 | 2:37 | 50.097
2021-10-02 | 2:37 | 50.098
2021-10-02 | 2:37 | 50.099
2021-10-02 | 2:37 | 50.102
2021-10-02 | 2:38 | 50.103
2021-10-02 | 2:38 | 50.103
2021-10-02 | 2:38 | 50.103
2021-10-02 | 2:38 | 50.102
2021-10-02 | 2:38 | 50.102
2021-10-02 | 2:38 | 50.1
2021-10-02 | 2:38 | 50.099
2021-10-02 | 2:38 | 50.1
2021-10-02 | 2:38 | 50.099
2021-10-02 | 2:38 | 50.099
2021-10-02 | 2:38 | 50.099
2021-10-02 | 2:38 | 50.102
2021-10-02 | 2:38 | 50.105
2021-10-02 | 2:38 | 50.105
2021-10-02 | 2:38 | 50.105
2021-10-02 | 2:38 | 50.106
2021-10-02 | 2:38 | 50.105
2021-10-02 | 2:38 | 50.106
2021-10-02 | 2:38 | 50.108
2021-10-02 | 2:38 | 50.111
2021-10-02 | 2:38 | 50.114
2021-10-02 | 2:38 | 50.115
2021-10-02 | 2:38 | 50.115
2021-10-02 | 2:38 | 50.113
2021-10-02 | 2:38 | 50.112
2021-10-02 | 2:38 | 50.11
2021-10-02 | 2:38 | 50.109
2021-10-02 | 2:38 | 50.107
2021-10-02 | 2:38 | 50.106
2021-10-02 | 2:38 | 50.107
2021-10-02 | 2:38 | 50.107
2021-10-02 | 2:38 | 50.107
2021-10-02 | 2:38 | 50.105
2021-10-02 | 2:38 | 50.104
2021-10-02 | 2:38 | 50.102
2021-10-02 | 2:38 | 50.102
2021-10-02 | 2:38 | 50.102
2021-10-02 | 2:38 | 50.1
2021-10-02 | 2:38 | 50.099
2021-10-02 | 2:38 | 50.098
2021-10-02 | 2:38 | 50.099
2021-10-02 | 2:38 | 50.102
2021-10-02 | 2:38 | 50.108
2021-10-02 | 2:38 | 50.114
2021-10-02 | 2:38 | 50.118
2021-10-02 | 2:38 | 50.119
2021-10-02 | 2:38 | 50.119
2021-10-02 | 2:38 | 50.12
2021-10-02 | 2:38 | 50.117
2021-10-02 | 2:38 | 50.116
2021-10-02 | 2:38 | 50.113
2021-10-02 | 2:38 | 50.108
2021-10-02 | 2:38 | 50.104
2021-10-02 | 2:38 | 50.104
2021-10-02 | 2:38 | 50.106
2021-10-02 | 2:38 | 50.108
2021-10-02 | 2:38 | 50.107
2021-10-02 | 2:38 | 50.107
2021-10-02 | 2:38 | 50.107
2021-10-02 | 2:38 | 50.106
2021-10-02 | 2:38 | 50.106
2021-10-02 | 2:39 | 50.105
2021-10-02 | 2:39 | 50.103
2021-10-02 | 2:39 | 50.103
2021-10-02 | 2:39 | 50.1
2021-10-02 | 2:39 | 50.098
2021-10-02 | 2:39 | 50.097
2021-10-02 | 2:39 | 50.098
2021-10-02 | 2:39 | 50.099
2021-10-02 | 2:39 | 50.101
2021-10-02 | 2:39 | 50.104
2021-10-02 | 2:39 | 50.109
2021-10-02 | 2:39 | 50.111
2021-10-02 | 2:39 | 50.112
2021-10-02 | 2:39 | 50.114
2021-10-02 | 2:39 | 50.114
2021-10-02 | 2:39 | 50.115
2021-10-02 | 2:39 | 50.117
2021-10-02 | 2:39 | 50.116
2021-10-02 | 2:39 | 50.117
2021-10-02 | 2:39 | 50.117
2021-10-02 | 2:39 | 50.117
2021-10-02 | 2:39 | 50.119
2021-10-02 | 2:39 | 50.121
2021-10-02 | 2:39 | 50.12
2021-10-02 | 2:39 | 50.12
2021-10-02 | 2:39 | 50.12
2021-10-02 | 2:39 | 50.119
2021-10-02 | 2:39 | 50.117
2021-10-02 | 2:39 | 50.117
2021-10-02 | 2:39 | 50.116
2021-10-02 | 2:39 | 50.114
2021-10-02 | 2:39 | 50.114
2021-10-02 | 2:39 | 50.114
2021-10-02 | 2:39 | 50.112
2021-10-02 | 2:39 | 50.113
2021-10-02 | 2:39 | 50.114
2021-10-02 | 2:39 | 50.114
2021-10-02 | 2:39 | 50.112
2021-10-02 | 2:39 | 50.112
2021-10-02 | 2:39 | 50.111
2021-10-02 | 2:39 | 50.111
2021-10-02 | 2:39 | 50.111
2021-10-02 | 2:39 | 50.111
2021-10-02 | 2:39 | 50.112
2021-10-02 | 2:39 | 50.112
2021-10-02 | 2:39 | 50.111
2021-10-02 | 2:39 | 50.111
2021-10-02 | 2:39 | 50.112
2021-10-02 | 2:39 | 50.112
2021-10-02 | 2:39 | 50.113
2021-10-02 | 2:39 | 50.115
2021-10-02 | 2:39 | 50.115
2021-10-02 | 2:39 | 50.116
2021-10-02 | 2:39 | 50.115
2021-10-02 | 2:39 | 50.116
2021-10-02 | 2:39 | 50.117
2021-10-02 | 2:39 | 50.116
2021-10-02 | 2:39 | 50.115
2021-10-02 | 2:39 | 50.115
2021-10-02 | 2:40 | 50.114
2021-10-02 | 2:40 | 50.113
2021-10-02 | 2:40 | 50.11
2021-10-02 | 2:40 | 50.108
2021-10-02 | 2:40 | 50.108
2021-10-02 | 2:40 | 50.109
2021-10-02 | 2:40 | 50.111
2021-10-02 | 2:40 | 50.111
2021-10-02 | 2:40 | 50.111
2021-10-02 | 2:40 | 50.111
2021-10-02 | 2:40 | 50.113
2021-10-02 | 2:40 | 50.113
2021-10-02 | 2:40 | 50.114
2021-10-02 | 2:40 | 50.113
2021-10-02 | 2:40 | 50.114
2021-10-02 | 2:40 | 50.113
2021-10-02 | 2:40 | 50.112
2021-10-02 | 2:40 | 50.112
2021-10-02 | 2:40 | 50.111
2021-10-02 | 2:40 | 50.111
2021-10-02 | 2:40 | 50.109
2021-10-02 | 2:40 | 50.106
2021-10-02 | 2:40 | 50.103
2021-10-02 | 2:40 | 50.103
2021-10-02 | 2:40 | 50.103
2021-10-02 | 2:40 | 50.104
2021-10-02 | 2:40 | 50.104
2021-10-02 | 2:40 | 50.102
2021-10-02 | 2:40 | 50.102
2021-10-02 | 2:40 | 50.102
2021-10-02 | 2:40 | 50.102
2021-10-02 | 2:40 | 50.099
2021-10-02 | 2:40 | 50.097
2021-10-02 | 2:40 | 50.096
2021-10-02 | 2:40 | 50.096
2021-10-02 | 2:40 | 50.097
2021-10-02 | 2:40 | 50.096
2021-10-02 | 2:40 | 50.093
2021-10-02 | 2:40 | 50.092
2021-10-02 | 2:40 | 50.09
2021-10-02 | 2:40 | 50.091
2021-10-02 | 2:40 | 50.092
2021-10-02 | 2:40 | 50.093
2021-10-02 | 2:40 | 50.094
2021-10-02 | 2:40 | 50.096
2021-10-02 | 2:40 | 50.096
2021-10-02 | 2:40 | 50.097
2021-10-02 | 2:40 | 50.097
2021-10-02 | 2:40 | 50.096
2021-10-02 | 2:40 | 50.095
2021-10-02 | 2:40 | 50.094
2021-10-02 | 2:40 | 50.093
2021-10-02 | 2:40 | 50.092
2021-10-02 | 2:40 | 50.091
2021-10-02 | 2:40 | 50.089
2021-10-02 | 2:40 | 50.091
2021-10-02 | 2:40 | 50.093
2021-10-02 | 2:40 | 50.092
2021-10-02 | 2:40 | 50.093
2021-10-02 | 2:40 | 50.091
2021-10-02 | 2:40 | 50.092
2021-10-02 | 2:41 | 50.089
2021-10-02 | 2:41 | 50.088
2021-10-02 | 2:41 | 50.085
2021-10-02 | 2:41 | 50.084
2021-10-02 | 2:41 | 50.087
2021-10-02 | 2:41 | 50.088
2021-10-02 | 2:41 | 50.088
2021-10-02 | 2:41 | 50.088
2021-10-02 | 2:41 | 50.087
2021-10-02 | 2:41 | 50.085
2021-10-02 | 2:41 | 50.084
2021-10-02 | 2:41 | 50.081
2021-10-02 | 2:41 | 50.081
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.081
2021-10-02 | 2:41 | 50.079
2021-10-02 | 2:41 | 50.079
2021-10-02 | 2:41 | 50.078
2021-10-02 | 2:41 | 50.077
2021-10-02 | 2:41 | 50.078
2021-10-02 | 2:41 | 50.081
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.081
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.081
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.082
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.078
2021-10-02 | 2:41 | 50.078
2021-10-02 | 2:41 | 50.079
2021-10-02 | 2:41 | 50.078
2021-10-02 | 2:41 | 50.079
2021-10-02 | 2:41 | 50.079
2021-10-02 | 2:41 | 50.079
2021-10-02 | 2:41 | 50.079
2021-10-02 | 2:41 | 50.078
2021-10-02 | 2:41 | 50.077
2021-10-02 | 2:41 | 50.077
2021-10-02 | 2:41 | 50.077
2021-10-02 | 2:41 | 50.078
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.082
2021-10-02 | 2:41 | 50.081
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.08
2021-10-02 | 2:41 | 50.078
2021-10-02 | 2:41 | 50.076
2021-10-02 | 2:41 | 50.076
2021-10-02 | 2:41 | 50.074
2021-10-02 | 2:41 | 50.074
2021-10-02 | 2:41 | 50.071
2021-10-02 | 2:41 | 50.066
2021-10-02 | 2:41 | 50.062
2021-10-02 | 2:41 | 50.059
2021-10-02 | 2:42 | 50.056
2021-10-02 | 2:42 | 50.055
2021-10-02 | 2:42 | 50.052
2021-10-02 | 2:42 | 50.052
2021-10-02 | 2:42 | 50.052
2021-10-02 | 2:42 | 50.051
2021-10-02 | 2:42 | 50.052
2021-10-02 | 2:42 | 50.052
2021-10-02 | 2:42 | 50.052
2021-10-02 | 2:42 | 50.054
2021-10-02 | 2:42 | 50.056
2021-10-02 | 2:42 | 50.057
2021-10-02 | 2:42 | 50.059
2021-10-02 | 2:42 | 50.059
2021-10-02 | 2:42 | 50.059
2021-10-02 | 2:42 | 50.059
2021-10-02 | 2:42 | 50.059
2021-10-02 | 2:42 | 50.059
2021-10-02 | 2:42 | 50.059
2021-10-02 | 2:42 | 50.06
2021-10-02 | 2:42 | 50.061
2021-10-02 | 2:42 | 50.062
2021-10-02 | 2:42 | 50.063
2021-10-02 | 2:42 | 50.063
2021-10-02 | 2:42 | 50.063
2021-10-02 | 2:42 | 50.064
2021-10-02 | 2:42 | 50.066
2021-10-02 | 2:42 | 50.065
2021-10-02 | 2:42 | 50.068
2021-10-02 | 2:42 | 50.071
2021-10-02 | 2:42 | 50.071
2021-10-02 | 2:42 | 50.072
2021-10-02 | 2:42 | 50.072
2021-10-02 | 2:42 | 50.073
2021-10-02 | 2:42 | 50.072
2021-10-02 | 2:42 | 50.072
2021-10-02 | 2:42 | 50.071
2021-10-02 | 2:42 | 50.071
2021-10-02 | 2:42 | 50.07
2021-10-02 | 2:42 | 50.069
2021-10-02 | 2:42 | 50.068
2021-10-02 | 2:42 | 50.066
2021-10-02 | 2:42 | 50.065
2021-10-02 | 2:42 | 50.065
2021-10-02 | 2:42 | 50.067
2021-10-02 | 2:42 | 50.068
2021-10-02 | 2:42 | 50.069
2021-10-02 | 2:42 | 50.069
2021-10-02 | 2:42 | 50.07
2021-10-02 | 2:42 | 50.071
2021-10-02 | 2:42 | 50.072
2021-10-02 | 2:42 | 50.071
2021-10-02 | 2:42 | 50.071
2021-10-02 | 2:42 | 50.071
2021-10-02 | 2:42 | 50.071
2021-10-02 | 2:42 | 50.072
2021-10-02 | 2:42 | 50.072
2021-10-02 | 2:42 | 50.073
2021-10-02 | 2:42 | 50.073
2021-10-02 | 2:42 | 50.072
2021-10-02 | 2:42 | 50.073
2021-10-02 | 2:43 | 50.073
2021-10-02 | 2:43 | 50.073
2021-10-02 | 2:43 | 50.075
2021-10-02 | 2:43 | 50.075
2021-10-02 | 2:43 | 50.077
2021-10-02 | 2:43 | 50.077
2021-10-02 | 2:43 | 50.076
2021-10-02 | 2:43 | 50.076
2021-10-02 | 2:43 | 50.076
2021-10-02 | 2:43 | 50.076
2021-10-02 | 2:43 | 50.075
2021-10-02 | 2:43 | 50.074
2021-10-02 | 2:43 | 50.072
2021-10-02 | 2:43 | 50.071
2021-10-02 | 2:43 | 50.069
2021-10-02 | 2:43 | 50.068
2021-10-02 | 2:43 | 50.067
2021-10-02 | 2:43 | 50.067
2021-10-02 | 2:43 | 50.067
2021-10-02 | 2:43 | 50.067
2021-10-02 | 2:43 | 50.067
2021-10-02 | 2:43 | 50.066
2021-10-02 | 2:43 | 50.063
2021-10-02 | 2:43 | 50.063
2021-10-02 | 2:43 | 50.062
2021-10-02 | 2:43 | 50.061
2021-10-02 | 2:43 | 50.062
2021-10-02 | 2:43 | 50.062
2021-10-02 | 2:43 | 50.063
2021-10-02 | 2:43 | 50.063
2021-10-02 | 2:43 | 50.061
2021-10-02 | 2:43 | 50.06
2021-10-02 | 2:43 | 50.058
2021-10-02 | 2:43 | 50.058
2021-10-02 | 2:43 | 50.058
2021-10-02 | 2:43 | 50.057
2021-10-02 | 2:43 | 50.053
2021-10-02 | 2:43 | 50.051
2021-10-02 | 2:43 | 50.049
2021-10-02 | 2:43 | 50.047
2021-10-02 | 2:43 | 50.045
2021-10-02 | 2:43 | 50.043
2021-10-02 | 2:43 | 50.041
2021-10-02 | 2:43 | 50.041
2021-10-02 | 2:43 | 50.041
2021-10-02 | 2:43 | 50.04
2021-10-02 | 2:43 | 50.04
2021-10-02 | 2:43 | 50.039
2021-10-02 | 2:43 | 50.038
2021-10-02 | 2:43 | 50.035
2021-10-02 | 2:43 | 50.034
2021-10-02 | 2:43 | 50.032
2021-10-02 | 2:43 | 50.032
2021-10-02 | 2:43 | 50.032
2021-10-02 | 2:43 | 50.031
2021-10-02 | 2:43 | 50.032
2021-10-02 | 2:43 | 50.033
2021-10-02 | 2:43 | 50.034
2021-10-02 | 2:43 | 50.034
2021-10-02 | 2:44 | 50.035
2021-10-02 | 2:44 | 50.035
2021-10-02 | 2:44 | 50.034
2021-10-02 | 2:44 | 50.036
2021-10-02 | 2:44 | 50.036
2021-10-02 | 2:44 | 50.037
2021-10-02 | 2:44 | 50.036
2021-10-02 | 2:44 | 50.034
2021-10-02 | 2:44 | 50.034
2021-10-02 | 2:44 | 50.034
2021-10-02 | 2:44 | 50.034
2021-10-02 | 2:44 | 50.033
2021-10-02 | 2:44 | 50.035
2021-10-02 | 2:44 | 50.035
2021-10-02 | 2:44 | 50.036
2021-10-02 | 2:44 | 50.035
2021-10-02 | 2:44 | 50.037
2021-10-02 | 2:44 | 50.037
2021-10-02 | 2:44 | 50.037
2021-10-02 | 2:44 | 50.034
2021-10-02 | 2:44 | 50.032
2021-10-02 | 2:44 | 50.031
2021-10-02 | 2:44 | 50.031
2021-10-02 | 2:44 | 50.03
2021-10-02 | 2:44 | 50.031
2021-10-02 | 2:44 | 50.032
2021-10-02 | 2:44 | 50.035
2021-10-02 | 2:44 | 50.04
2021-10-02 | 2:44 | 50.042
2021-10-02 | 2:44 | 50.043
2021-10-02 | 2:44 | 50.043
2021-10-02 | 2:44 | 50.041
2021-10-02 | 2:44 | 50.041
2021-10-02 | 2:44 | 50.042
2021-10-02 | 2:44 | 50.042
2021-10-02 | 2:44 | 50.042
2021-10-02 | 2:44 | 50.043
2021-10-02 | 2:44 | 50.042
2021-10-02 | 2:44 | 50.04
2021-10-02 | 2:44 | 50.039
2021-10-02 | 2:44 | 50.037
2021-10-02 | 2:44 | 50.036
2021-10-02 | 2:44 | 50.035
2021-10-02 | 2:44 | 50.037
2021-10-02 | 2:44 | 50.037
2021-10-02 | 2:44 | 50.038
2021-10-02 | 2:44 | 50.039
2021-10-02 | 2:44 | 50.039
2021-10-02 | 2:44 | 50.041
2021-10-02 | 2:44 | 50.042
2021-10-02 | 2:44 | 50.045
2021-10-02 | 2:44 | 50.046
2021-10-02 | 2:44 | 50.046
2021-10-02 | 2:44 | 50.047
2021-10-02 | 2:44 | 50.047
2021-10-02 | 2:44 | 50.047
2021-10-02 | 2:44 | 50.046
2021-10-02 | 2:44 | 50.046
2021-10-02 | 2:44 | 50.046
2021-10-02 | 2:44 | 50.046
2021-10-02 | 2:44 | 50.046
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.048
2021-10-02 | 2:45 | 50.048
2021-10-02 | 2:45 | 50.048
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.048
2021-10-02 | 2:45 | 50.048
2021-10-02 | 2:45 | 50.046
2021-10-02 | 2:45 | 50.045
2021-10-02 | 2:45 | 50.043
2021-10-02 | 2:45 | 50.043
2021-10-02 | 2:45 | 50.041
2021-10-02 | 2:45 | 50.041
2021-10-02 | 2:45 | 50.042
2021-10-02 | 2:45 | 50.041
2021-10-02 | 2:45 | 50.042
2021-10-02 | 2:45 | 50.043
2021-10-02 | 2:45 | 50.044
2021-10-02 | 2:45 | 50.045
2021-10-02 | 2:45 | 50.045
2021-10-02 | 2:45 | 50.045
2021-10-02 | 2:45 | 50.046
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.046
2021-10-02 | 2:45 | 50.044
2021-10-02 | 2:45 | 50.042
2021-10-02 | 2:45 | 50.042
2021-10-02 | 2:45 | 50.041
2021-10-02 | 2:45 | 50.042
2021-10-02 | 2:45 | 50.043
2021-10-02 | 2:45 | 50.045
2021-10-02 | 2:45 | 50.046
2021-10-02 | 2:45 | 50.047
2021-10-02 | 2:45 | 50.048
2021-10-02 | 2:45 | 50.048
2021-10-02 | 2:45 | 50.049
2021-10-02 | 2:45 | 50.05
2021-10-02 | 2:45 | 50.051
2021-10-02 | 2:45 | 50.054
2021-10-02 | 2:45 | 50.055
2021-10-02 | 2:45 | 50.057
2021-10-02 | 2:45 | 50.057
2021-10-02 | 2:45 | 50.057
2021-10-02 | 2:45 | 50.058
2021-10-02 | 2:45 | 50.058
2021-10-02 | 2:45 | 50.057
2021-10-02 | 2:45 | 50.057
2021-10-02 | 2:45 | 50.057
2021-10-02 | 2:45 | 50.056
2021-10-02 | 2:45 | 50.054
2021-10-02 | 2:45 | 50.052
2021-10-02 | 2:45 | 50.051
2021-10-02 | 2:46 | 50.047
2021-10-02 | 2:46 | 50.044
2021-10-02 | 2:46 | 50.043
2021-10-02 | 2:46 | 50.043
2021-10-02 | 2:46 | 50.043
2021-10-02 | 2:46 | 50.042
2021-10-02 | 2:46 | 50.043
2021-10-02 | 2:46 | 50.043
2021-10-02 | 2:46 | 50.043
2021-10-02 | 2:46 | 50.043
2021-10-02 | 2:46 | 50.047
2021-10-02 | 2:46 | 50.049
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.053
2021-10-02 | 2:46 | 50.053
2021-10-02 | 2:46 | 50.052
2021-10-02 | 2:46 | 50.053
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.052
2021-10-02 | 2:46 | 50.052
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.049
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.048
2021-10-02 | 2:46 | 50.046
2021-10-02 | 2:46 | 50.046
2021-10-02 | 2:46 | 50.046
2021-10-02 | 2:46 | 50.047
2021-10-02 | 2:46 | 50.049
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.052
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.049
2021-10-02 | 2:46 | 50.049
2021-10-02 | 2:46 | 50.049
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.05
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.052
2021-10-02 | 2:46 | 50.052
2021-10-02 | 2:46 | 50.052
2021-10-02 | 2:46 | 50.051
2021-10-02 | 2:46 | 50.047
2021-10-02 | 2:46 | 50.046
2021-10-02 | 2:46 | 50.043
2021-10-02 | 2:46 | 50.044
2021-10-02 | 2:46 | 50.044
2021-10-02 | 2:46 | 50.044
2021-10-02 | 2:47 | 50.042
2021-10-02 | 2:47 | 50.042
2021-10-02 | 2:47 | 50.042
2021-10-02 | 2:47 | 50.042
2021-10-02 | 2:47 | 50.045
2021-10-02 | 2:47 | 50.049
2021-10-02 | 2:47 | 50.053
2021-10-02 | 2:47 | 50.057
2021-10-02 | 2:47 | 50.06
2021-10-02 | 2:47 | 50.061
2021-10-02 | 2:47 | 50.063
2021-10-02 | 2:47 | 50.063
2021-10-02 | 2:47 | 50.062
2021-10-02 | 2:47 | 50.06
2021-10-02 | 2:47 | 50.062
2021-10-02 | 2:47 | 50.063
2021-10-02 | 2:47 | 50.062
2021-10-02 | 2:47 | 50.063
2021-10-02 | 2:47 | 50.063
2021-10-02 | 2:47 | 50.065
2021-10-02 | 2:47 | 50.066
2021-10-02 | 2:47 | 50.065
2021-10-02 | 2:47 | 50.066
2021-10-02 | 2:47 | 50.065
2021-10-02 | 2:47 | 50.061
2021-10-02 | 2:47 | 50.057
2021-10-02 | 2:47 | 50.056
2021-10-02 | 2:47 | 50.055
2021-10-02 | 2:47 | 50.054
2021-10-02 | 2:47 | 50.054
2021-10-02 | 2:47 | 50.055
2021-10-02 | 2:47 | 50.056
2021-10-02 | 2:47 | 50.057
2021-10-02 | 2:47 | 50.057
2021-10-02 | 2:47 | 50.057
2021-10-02 | 2:47 | 50.058
2021-10-02 | 2:47 | 50.06
2021-10-02 | 2:47 | 50.062
2021-10-02 | 2:47 | 50.063
2021-10-02 | 2:47 | 50.064
2021-10-02 | 2:47 | 50.061
2021-10-02 | 2:47 | 50.061
2021-10-02 | 2:47 | 50.057
2021-10-02 | 2:47 | 50.056
2021-10-02 | 2:47 | 50.058
2021-10-02 | 2:47 | 50.059
2021-10-02 | 2:47 | 50.059
2021-10-02 | 2:47 | 50.06
2021-10-02 | 2:47 | 50.06
2021-10-02 | 2:47 | 50.061
2021-10-02 | 2:47 | 50.063
2021-10-02 | 2:47 | 50.062
2021-10-02 | 2:47 | 50.061
2021-10-02 | 2:47 | 50.058
2021-10-02 | 2:47 | 50.056
2021-10-02 | 2:47 | 50.059
2021-10-02 | 2:47 | 50.059
2021-10-02 | 2:47 | 50.06
2021-10-02 | 2:47 | 50.06
2021-10-02 | 2:47 | 50.06
2021-10-02 | 2:48 | 50.061
2021-10-02 | 2:48 | 50.06
2021-10-02 | 2:48 | 50.059
2021-10-02 | 2:48 | 50.058
2021-10-02 | 2:48 | 50.058
2021-10-02 | 2:48 | 50.06
2021-10-02 | 2:48 | 50.059
2021-10-02 | 2:48 | 50.058
2021-10-02 | 2:48 | 50.058
2021-10-02 | 2:48 | 50.056
2021-10-02 | 2:48 | 50.05
2021-10-02 | 2:48 | 50.047
2021-10-02 | 2:48 | 50.044
2021-10-02 | 2:48 | 50.044
2021-10-02 | 2:48 | 50.044
2021-10-02 | 2:48 | 50.046
2021-10-02 | 2:48 | 50.049
2021-10-02 | 2:48 | 50.051
2021-10-02 | 2:48 | 50.054
2021-10-02 | 2:48 | 50.055
2021-10-02 | 2:48 | 50.056
2021-10-02 | 2:48 | 50.055
2021-10-02 | 2:48 | 50.053
2021-10-02 | 2:48 | 50.053
2021-10-02 | 2:48 | 50.054
2021-10-02 | 2:48 | 50.054
2021-10-02 | 2:48 | 50.054
2021-10-02 | 2:48 | 50.054
2021-10-02 | 2:48 | 50.055
2021-10-02 | 2:48 | 50.053
2021-10-02 | 2:48 | 50.053
2021-10-02 | 2:48 | 50.053
2021-10-02 | 2:48 | 50.053
2021-10-02 | 2:48 | 50.052
2021-10-02 | 2:48 | 50.051
2021-10-02 | 2:48 | 50.049
2021-10-02 | 2:48 | 50.041
2021-10-02 | 2:48 | 50.03
2021-10-02 | 2:48 | 50.022
2021-10-02 | 2:48 | 50.016
2021-10-02 | 2:48 | 50.012
2021-10-02 | 2:48 | 50.005
2021-10-02 | 2:48 | 50.002
2021-10-02 | 2:48 | 49.999
2021-10-02 | 2:48 | 49.999
2021-10-02 | 2:48 | 50.001
2021-10-02 | 2:48 | 50.003
2021-10-02 | 2:48 | 50.007
2021-10-02 | 2:48 | 50.011
2021-10-02 | 2:48 | 50.013
2021-10-02 | 2:48 | 50.015
2021-10-02 | 2:48 | 50.016
2021-10-02 | 2:48 | 50.017
2021-10-02 | 2:48 | 50.018
2021-10-02 | 2:48 | 50.018
2021-10-02 | 2:48 | 50.017
2021-10-02 | 2:48 | 50.017
2021-10-02 | 2:48 | 50.015
2021-10-02 | 2:48 | 50.014
2021-10-02 | 2:49 | 50.013
2021-10-02 | 2:49 | 50.014
2021-10-02 | 2:49 | 50.013
2021-10-02 | 2:49 | 50.012
2021-10-02 | 2:49 | 50.013
2021-10-02 | 2:49 | 50.011
2021-10-02 | 2:49 | 50.009
2021-10-02 | 2:49 | 50.006
2021-10-02 | 2:49 | 50.004
2021-10-02 | 2:49 | 50.004
2021-10-02 | 2:49 | 50.004
2021-10-02 | 2:49 | 50.007
2021-10-02 | 2:49 | 50.011
2021-10-02 | 2:49 | 50.016
2021-10-02 | 2:49 | 50.019
2021-10-02 | 2:49 | 50.021
2021-10-02 | 2:49 | 50.021
2021-10-02 | 2:49 | 50.022
2021-10-02 | 2:49 | 50.022
2021-10-02 | 2:49 | 50.022
2021-10-02 | 2:49 | 50.02
2021-10-02 | 2:49 | 50.02
2021-10-02 | 2:49 | 50.019
2021-10-02 | 2:49 | 50.021
2021-10-02 | 2:49 | 50.021
2021-10-02 | 2:49 | 50.021
2021-10-02 | 2:49 | 50.021
2021-10-02 | 2:49 | 50.02
2021-10-02 | 2:49 | 50.019
2021-10-02 | 2:49 | 50.019

## 20211003-1
In GMT
Date | Time | Freq
2021-10-03 | 9:23 | 50.075
2021-10-03 | 9:23 | 50.078
2021-10-03 | 9:23 | 50.078
2021-10-03 | 9:23 | 50.079
2021-10-03 | 9:23 | 50.079
2021-10-03 | 9:23 | 50.078
2021-10-03 | 9:23 | 50.077
2021-10-03 | 9:23 | 50.078
2021-10-03 | 9:23 | 50.079
2021-10-03 | 9:23 | 50.081
2021-10-03 | 9:23 | 50.081
2021-10-03 | 9:23 | 50.08
2021-10-03 | 9:23 | 50.076
2021-10-03 | 9:23 | 50.073
2021-10-03 | 9:23 | 50.067
2021-10-03 | 9:23 | 50.06
2021-10-03 | 9:23 | 50.053
2021-10-03 | 9:23 | 50.052
2021-10-03 | 9:23 | 50.054
2021-10-03 | 9:23 | 50.052
2021-10-03 | 9:23 | 50.052
2021-10-03 | 9:23 | 50.053
2021-10-03 | 9:23 | 50.055
2021-10-03 | 9:23 | 50.055
2021-10-03 | 9:23 | 50.053
2021-10-03 | 9:23 | 50.053
2021-10-03 | 9:23 | 50.053
2021-10-03 | 9:23 | 50.053
2021-10-03 | 9:23 | 50.051
2021-10-03 | 9:23 | 50.05
2021-10-03 | 9:24 | 50.05
2021-10-03 | 9:24 | 50.05
2021-10-03 | 9:24 | 50.05
2021-10-03 | 9:24 | 50.052
2021-10-03 | 9:24 | 50.052
2021-10-03 | 9:24 | 50.053
2021-10-03 | 9:24 | 50.055
2021-10-03 | 9:24 | 50.055
2021-10-03 | 9:24 | 50.056
2021-10-03 | 9:24 | 50.056
2021-10-03 | 9:24 | 50.059
2021-10-03 | 9:24 | 50.062
2021-10-03 | 9:24 | 50.067
2021-10-03 | 9:24 | 50.072
2021-10-03 | 9:24 | 50.076
2021-10-03 | 9:24 | 50.081
2021-10-03 | 9:24 | 50.084
2021-10-03 | 9:24 | 50.085
2021-10-03 | 9:24 | 50.086
2021-10-03 | 9:24 | 50.087
2021-10-03 | 9:24 | 50.087
2021-10-03 | 9:24 | 50.086
2021-10-03 | 9:24 | 50.085
2021-10-03 | 9:24 | 50.085
2021-10-03 | 9:24 | 50.085
2021-10-03 | 9:24 | 50.084
2021-10-03 | 9:24 | 50.082
2021-10-03 | 9:24 | 50.08
2021-10-03 | 9:24 | 50.079
2021-10-03 | 9:24 | 50.074
2021-10-03 | 9:24 | 50.072
2021-10-03 | 9:24 | 50.066
2021-10-03 | 9:24 | 50.063
2021-10-03 | 9:24 | 50.063
2021-10-03 | 9:24 | 50.064
2021-10-03 | 9:24 | 50.066
2021-10-03 | 9:24 | 50.067
2021-10-03 | 9:24 | 50.068
2021-10-03 | 9:24 | 50.069
2021-10-03 | 9:24 | 50.067
2021-10-03 | 9:24 | 50.065
2021-10-03 | 9:24 | 50.063
2021-10-03 | 9:24 | 50.061
2021-10-03 | 9:24 | 50.06
2021-10-03 | 9:24 | 50.058
2021-10-03 | 9:24 | 50.056
2021-10-03 | 9:24 | 50.055
2021-10-03 | 9:24 | 50.055
2021-10-03 | 9:24 | 50.054
2021-10-03 | 9:24 | 50.057
2021-10-03 | 9:24 | 50.06
2021-10-03 | 9:24 | 50.062
2021-10-03 | 9:24 | 50.066
2021-10-03 | 9:24 | 50.07
2021-10-03 | 9:24 | 50.058
2021-10-03 | 9:24 | 50.029
2021-10-03 | 9:24 | 50.003
2021-10-03 | 9:24 | 49.99
2021-10-03 | 9:24 | 49.984
2021-10-03 | 9:24 | 49.984
2021-10-03 | 9:24 | 49.983
2021-10-03 | 9:25 | 49.981
2021-10-03 | 9:25 | 49.979
2021-10-03 | 9:25 | 49.976
2021-10-03 | 9:25 | 49.976
2021-10-03 | 9:25 | 49.974
2021-10-03 | 9:25 | 49.972
2021-10-03 | 9:25 | 49.971
2021-10-03 | 9:25 | 49.973
2021-10-03 | 9:25 | 49.972
2021-10-03 | 9:25 | 49.973
2021-10-03 | 9:25 | 49.977
2021-10-03 | 9:25 | 49.982
2021-10-03 | 9:25 | 49.988
2021-10-03 | 9:25 | 49.993
2021-10-03 | 9:25 | 49.995
2021-10-03 | 9:25 | 49.994
2021-10-03 | 9:25 | 49.992
2021-10-03 | 9:25 | 49.99
2021-10-03 | 9:25 | 49.988
2021-10-03 | 9:25 | 49.984
2021-10-03 | 9:25 | 49.982
2021-10-03 | 9:25 | 49.981
2021-10-03 | 9:25 | 49.981
2021-10-03 | 9:25 | 49.982
2021-10-03 | 9:25 | 49.983
2021-10-03 | 9:25 | 49.985
2021-10-03 | 9:25 | 49.986
2021-10-03 | 9:25 | 49.986
2021-10-03 | 9:25 | 49.985
2021-10-03 | 9:25 | 49.984
2021-10-03 | 9:25 | 49.981
2021-10-03 | 9:25 | 49.981
2021-10-03 | 9:25 | 49.982
2021-10-03 | 9:25 | 49.984
2021-10-03 | 9:25 | 49.986
2021-10-03 | 9:25 | 49.988
2021-10-03 | 9:25 | 49.99
2021-10-03 | 9:25 | 49.994
2021-10-03 | 9:25 | 49.997
2021-10-03 | 9:25 | 50.002
2021-10-03 | 9:25 | 50.006
2021-10-03 | 9:25 | 50.009
2021-10-03 | 9:25 | 50.009
2021-10-03 | 9:25 | 50.008
2021-10-03 | 9:25 | 50.005
2021-10-03 | 9:25 | 50.003
2021-10-03 | 9:25 | 49.999
2021-10-03 | 9:25 | 49.997
2021-10-03 | 9:25 | 49.997
2021-10-03 | 9:25 | 49.996
2021-10-03 | 9:25 | 49.996
2021-10-03 | 9:25 | 49.995
2021-10-03 | 9:25 | 49.994
2021-10-03 | 9:25 | 49.993
2021-10-03 | 9:25 | 49.994
2021-10-03 | 9:25 | 49.998
2021-10-03 | 9:25 | 50
2021-10-03 | 9:25 | 50.004
2021-10-03 | 9:25 | 50.007
2021-10-03 | 9:26 | 50.01
2021-10-03 | 9:26 | 50.015
2021-10-03 | 9:26 | 50.017
2021-10-03 | 9:26 | 50.017
2021-10-03 | 9:26 | 50.016
2021-10-03 | 9:26 | 50.014
2021-10-03 | 9:26 | 50.011
2021-10-03 | 9:26 | 50.007
2021-10-03 | 9:26 | 50.004
2021-10-03 | 9:26 | 50.002
2021-10-03 | 9:26 | 50.001
2021-10-03 | 9:26 | 49.997
2021-10-03 | 9:26 | 49.995
2021-10-03 | 9:26 | 49.997
2021-10-03 | 9:26 | 50
2021-10-03 | 9:26 | 50.004
2021-10-03 | 9:26 | 50.007
2021-10-03 | 9:26 | 50.01
2021-10-03 | 9:26 | 50.012
2021-10-03 | 9:26 | 50.011
2021-10-03 | 9:26 | 50.013
2021-10-03 | 9:26 | 50.014
2021-10-03 | 9:26 | 50.017
2021-10-03 | 9:26 | 50.019
2021-10-03 | 9:26 | 50.019
2021-10-03 | 9:26 | 50.02
2021-10-03 | 9:26 | 50.019
2021-10-03 | 9:26 | 50.016
2021-10-03 | 9:26 | 50.012
2021-10-03 | 9:26 | 50.011

## 20211004-1
In GMT
Date | Time | Freq
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.117
2021-10-04 | 21:59 | 50.117
2021-10-04 | 21:59 | 50.114
2021-10-04 | 21:59 | 50.112
2021-10-04 | 21:59 | 50.109
2021-10-04 | 21:59 | 50.107
2021-10-04 | 21:59 | 50.105
2021-10-04 | 21:59 | 50.104
2021-10-04 | 21:59 | 50.102
2021-10-04 | 21:59 | 50.1
2021-10-04 | 21:59 | 50.101
2021-10-04 | 21:59 | 50.101
2021-10-04 | 21:59 | 50.101
2021-10-04 | 21:59 | 50.103
2021-10-04 | 21:59 | 50.107
2021-10-04 | 21:59 | 50.111
2021-10-04 | 21:59 | 50.114
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.117
2021-10-04 | 21:59 | 50.116
2021-10-04 | 21:59 | 50.117
2021-10-04 | 22:00 | 50.117
2021-10-04 | 22:00 | 50.118
2021-10-04 | 22:00 | 50.119
2021-10-04 | 22:00 | 50.121
2021-10-04 | 22:00 | 50.123
2021-10-04 | 22:00 | 50.126
2021-10-04 | 22:00 | 50.126
2021-10-04 | 22:00 | 50.126
2021-10-04 | 22:00 | 50.126
2021-10-04 | 22:00 | 50.124
2021-10-04 | 22:00 | 50.123
2021-10-04 | 22:00 | 50.119
2021-10-04 | 22:00 | 50.116
2021-10-04 | 22:00 | 50.111
2021-10-04 | 22:00 | 50.107
2021-10-04 | 22:00 | 50.106
2021-10-04 | 22:00 | 50.104
2021-10-04 | 22:00 | 50.102
2021-10-04 | 22:00 | 50.099
2021-10-04 | 22:00 | 50.097
2021-10-04 | 22:00 | 50.097
2021-10-04 | 22:00 | 50.098
2021-10-04 | 22:00 | 50.099
2021-10-04 | 22:00 | 50.099
2021-10-04 | 22:00 | 50.098
2021-10-04 | 22:00 | 50.096
2021-10-04 | 22:00 | 50.095
2021-10-04 | 22:00 | 50.094
2021-10-04 | 22:00 | 50.091
2021-10-04 | 22:00 | 50.084
2021-10-04 | 22:00 | 50.078
2021-10-04 | 22:00 | 50.072
2021-10-04 | 22:00 | 50.068
2021-10-04 | 22:00 | 50.062
2021-10-04 | 22:00 | 50.037
2021-10-04 | 22:00 | 50.017
2021-10-04 | 22:00 | 50.006
2021-10-04 | 22:00 | 49.999
2021-10-04 | 22:00 | 49.998
2021-10-04 | 22:00 | 49.999
2021-10-04 | 22:00 | 50.001
2021-10-04 | 22:00 | 50.002
2021-10-04 | 22:00 | 50.003
2021-10-04 | 22:00 | 50.006
2021-10-04 | 22:00 | 50.005
2021-10-04 | 22:00 | 50.008
2021-10-04 | 22:00 | 50.008
2021-10-04 | 22:00 | 50.008
2021-10-04 | 22:00 | 50.007
2021-10-04 | 22:00 | 50.007
2021-10-04 | 22:00 | 50.005
2021-10-04 | 22:00 | 50.004
2021-10-04 | 22:00 | 50.003
2021-10-04 | 22:00 | 50.001
2021-10-04 | 22:00 | 49.998
2021-10-04 | 22:00 | 49.994
2021-10-04 | 22:00 | 49.991
2021-10-04 | 22:00 | 49.99
2021-10-04 | 22:00 | 49.989
2021-10-04 | 22:00 | 49.988
2021-10-04 | 22:00 | 49.984
2021-10-04 | 22:01 | 49.981
2021-10-04 | 22:01 | 49.978
2021-10-04 | 22:01 | 49.977
2021-10-04 | 22:01 | 49.975
2021-10-04 | 22:01 | 49.972
2021-10-04 | 22:01 | 49.971
2021-10-04 | 22:01 | 49.971
2021-10-04 | 22:01 | 49.97
2021-10-04 | 22:01 | 49.968
2021-10-04 | 22:01 | 49.969
2021-10-04 | 22:01 | 49.969
2021-10-04 | 22:01 | 49.969
2021-10-04 | 22:01 | 49.969
2021-10-04 | 22:01 | 49.969
2021-10-04 | 22:01 | 49.971
2021-10-04 | 22:01 | 49.972
2021-10-04 | 22:01 | 49.971
2021-10-04 | 22:01 | 49.969
2021-10-04 | 22:01 | 49.966
2021-10-04 | 22:01 | 49.965
2021-10-04 | 22:01 | 49.964
2021-10-04 | 22:01 | 49.961
2021-10-04 | 22:01 | 49.958
2021-10-04 | 22:01 | 49.954
2021-10-04 | 22:01 | 49.951
2021-10-04 | 22:01 | 49.947
2021-10-04 | 22:01 | 49.945
2021-10-04 | 22:01 | 49.944
2021-10-04 | 22:01 | 49.943
2021-10-04 | 22:01 | 49.943
2021-10-04 | 22:01 | 49.941
2021-10-04 | 22:01 | 49.94
2021-10-04 | 22:01 | 49.94
2021-10-04 | 22:01 | 49.942
2021-10-04 | 22:01 | 49.946
2021-10-04 | 22:01 | 49.949
2021-10-04 | 22:01 | 49.95
2021-10-04 | 22:01 | 49.95
2021-10-04 | 22:01 | 49.949
2021-10-04 | 22:01 | 49.948
2021-10-04 | 22:01 | 49.947
2021-10-04 | 22:01 | 49.945
2021-10-04 | 22:01 | 49.943
2021-10-04 | 22:01 | 49.939
2021-10-04 | 22:01 | 49.934
2021-10-04 | 22:01 | 49.93
2021-10-04 | 22:01 | 49.925
2021-10-04 | 22:01 | 49.924
2021-10-04 | 22:01 | 49.924
2021-10-04 | 22:01 | 49.923
2021-10-04 | 22:01 | 49.923
2021-10-04 | 22:01 | 49.923
2021-10-04 | 22:01 | 49.924
2021-10-04 | 22:01 | 49.924
2021-10-04 | 22:01 | 49.926
2021-10-04 | 22:01 | 49.929
2021-10-04 | 22:01 | 49.934
2021-10-04 | 22:01 | 49.937
2021-10-04 | 22:01 | 49.94
2021-10-04 | 22:01 | 49.941
2021-10-04 | 22:02 | 49.941
2021-10-04 | 22:02 | 49.941
2021-10-04 | 22:02 | 49.941
2021-10-04 | 22:02 | 49.942
2021-10-04 | 22:02 | 49.939
2021-10-04 | 22:02 | 49.937
2021-10-04 | 22:02 | 49.933
2021-10-04 | 22:02 | 49.929
2021-10-04 | 22:02 | 49.926
2021-10-04 | 22:02 | 49.924
2021-10-04 | 22:02 | 49.922
2021-10-04 | 22:02 | 49.92
2021-10-04 | 22:02 | 49.918
2021-10-04 | 22:02 | 49.916
2021-10-04 | 22:02 | 49.913
2021-10-04 | 22:02 | 49.912
2021-10-04 | 22:02 | 49.91
2021-10-04 | 22:02 | 49.909
2021-10-04 | 22:02 | 49.908
2021-10-04 | 22:02 | 49.907
2021-10-04 | 22:02 | 49.904
2021-10-04 | 22:02 | 49.904
2021-10-04 | 22:02 | 49.906
2021-10-04 | 22:02 | 49.907
2021-10-04 | 22:02 | 49.907
2021-10-04 | 22:02 | 49.907
2021-10-04 | 22:02 | 49.908
2021-10-04 | 22:02 | 49.906
2021-10-04 | 22:02 | 49.905
2021-10-04 | 22:02 | 49.904
2021-10-04 | 22:02 | 49.901
2021-10-04 | 22:02 | 49.898
2021-10-04 | 22:02 | 49.895
2021-10-04 | 22:02 | 49.893
2021-10-04 | 22:02 | 49.89
2021-10-04 | 22:02 | 49.89
2021-10-04 | 22:02 | 49.889
2021-10-04 | 22:02 | 49.888
2021-10-04 | 22:02 | 49.888
2021-10-04 | 22:02 | 49.887
2021-10-04 | 22:02 | 49.886
2021-10-04 | 22:02 | 49.885
2021-10-04 | 22:02 | 49.884
2021-10-04 | 22:02 | 49.884
2021-10-04 | 22:02 | 49.885
2021-10-04 | 22:02 | 49.887
2021-10-04 | 22:02 | 49.89
2021-10-04 | 22:02 | 49.893
2021-10-04 | 22:02 | 49.895
2021-10-04 | 22:02 | 49.896
2021-10-04 | 22:02 | 49.898
2021-10-04 | 22:02 | 49.898
2021-10-04 | 22:02 | 49.901
2021-10-04 | 22:02 | 49.904
2021-10-04 | 22:02 | 49.907
2021-10-04 | 22:02 | 49.909
2021-10-04 | 22:02 | 49.909
2021-10-04 | 22:02 | 49.909
2021-10-04 | 22:02 | 49.91
2021-10-04 | 22:02 | 49.909
2021-10-04 | 22:03 | 49.907
2021-10-04 | 22:03 | 49.906
2021-10-04 | 22:03 | 49.905
2021-10-04 | 22:03 | 49.902
2021-10-04 | 22:03 | 49.898
2021-10-04 | 22:03 | 49.895
2021-10-04 | 22:03 | 49.891
2021-10-04 | 22:03 | 49.888
2021-10-04 | 22:03 | 49.884
2021-10-04 | 22:03 | 49.883
2021-10-04 | 22:03 | 49.882
2021-10-04 | 22:03 | 49.881
2021-10-04 | 22:03 | 49.881
2021-10-04 | 22:03 | 49.881
2021-10-04 | 22:03 | 49.881
2021-10-04 | 22:03 | 49.883
2021-10-04 | 22:03 | 49.887
2021-10-04 | 22:03 | 49.89
2021-10-04 | 22:03 | 49.894
2021-10-04 | 22:03 | 49.899
2021-10-04 | 22:03 | 49.904
2021-10-04 | 22:03 | 49.908
2021-10-04 | 22:03 | 49.911
2021-10-04 | 22:03 | 49.912
2021-10-04 | 22:03 | 49.913
2021-10-04 | 22:03 | 49.916
2021-10-04 | 22:03 | 49.917
2021-10-04 | 22:03 | 49.919
2021-10-04 | 22:03 | 49.919
2021-10-04 | 22:03 | 49.918
2021-10-04 | 22:03 | 49.915
2021-10-04 | 22:03 | 49.913
2021-10-04 | 22:03 | 49.911
2021-10-04 | 22:03 | 49.908
2021-10-04 | 22:03 | 49.906
2021-10-04 | 22:03 | 49.906
2021-10-04 | 22:03 | 49.907
2021-10-04 | 22:03 | 49.907
2021-10-04 | 22:03 | 49.907
2021-10-04 | 22:03 | 49.907
2021-10-04 | 22:03 | 49.906
2021-10-04 | 22:03 | 49.905
2021-10-04 | 22:03 | 49.901
2021-10-04 | 22:03 | 49.9
2021-10-04 | 22:03 | 49.9
2021-10-04 | 22:03 | 49.901
2021-10-04 | 22:03 | 49.904
2021-10-04 | 22:03 | 49.906
2021-10-04 | 22:03 | 49.908
2021-10-04 | 22:03 | 49.909
2021-10-04 | 22:03 | 49.908
2021-10-04 | 22:03 | 49.908
2021-10-04 | 22:03 | 49.906
2021-10-04 | 22:03 | 49.903
2021-10-04 | 22:03 | 49.903
2021-10-04 | 22:03 | 49.903
2021-10-04 | 22:03 | 49.901
2021-10-04 | 22:03 | 49.897
2021-10-04 | 22:03 | 49.893
2021-10-04 | 22:04 | 49.89
2021-10-04 | 22:04 | 49.89
2021-10-04 | 22:04 | 49.888
2021-10-04 | 22:04 | 49.888
2021-10-04 | 22:04 | 49.888
2021-10-04 | 22:04 | 49.886
2021-10-04 | 22:04 | 49.886
2021-10-04 | 22:04 | 49.888
2021-10-04 | 22:04 | 49.891
2021-10-04 | 22:04 | 49.894
2021-10-04 | 22:04 | 49.897
2021-10-04 | 22:04 | 49.897
2021-10-04 | 22:04 | 49.898
2021-10-04 | 22:04 | 49.898
2021-10-04 | 22:04 | 49.899
2021-10-04 | 22:04 | 49.9
2021-10-04 | 22:04 | 49.901
2021-10-04 | 22:04 | 49.902
2021-10-04 | 22:04 | 49.903
2021-10-04 | 22:04 | 49.903
2021-10-04 | 22:04 | 49.903
2021-10-04 | 22:04 | 49.901
2021-10-04 | 22:04 | 49.898
2021-10-04 | 22:04 | 49.893
2021-10-04 | 22:04 | 49.887
2021-10-04 | 22:04 | 49.883
2021-10-04 | 22:04 | 49.881
2021-10-04 | 22:04 | 49.878
2021-10-04 | 22:04 | 49.878
2021-10-04 | 22:04 | 49.877
2021-10-04 | 22:04 | 49.876
2021-10-04 | 22:04 | 49.873
2021-10-04 | 22:04 | 49.867
2021-10-04 | 22:04 | 49.863
2021-10-04 | 22:04 | 49.861
2021-10-04 | 22:04 | 49.861
2021-10-04 | 22:04 | 49.86
2021-10-04 | 22:04 | 49.861
2021-10-04 | 22:04 | 49.861
2021-10-04 | 22:04 | 49.862
2021-10-04 | 22:04 | 49.866
2021-10-04 | 22:04 | 49.866
2021-10-04 | 22:04 | 49.866
2021-10-04 | 22:04 | 49.865
2021-10-04 | 22:04 | 49.865
2021-10-04 | 22:04 | 49.866
2021-10-04 | 22:04 | 49.866
2021-10-04 | 22:04 | 49.867
2021-10-04 | 22:04 | 49.87
2021-10-04 | 22:04 | 49.872
2021-10-04 | 22:04 | 49.875
2021-10-04 | 22:04 | 49.878
2021-10-04 | 22:04 | 49.881
2021-10-04 | 22:04 | 49.883
2021-10-04 | 22:04 | 49.885
2021-10-04 | 22:04 | 49.887
2021-10-04 | 22:04 | 49.887
2021-10-04 | 22:04 | 49.888
2021-10-04 | 22:04 | 49.889
2021-10-04 | 22:04 | 49.89
2021-10-04 | 22:04 | 49.889
2021-10-04 | 22:05 | 49.889
2021-10-04 | 22:05 | 49.888
2021-10-04 | 22:05 | 49.887
2021-10-04 | 22:05 | 49.885
2021-10-04 | 22:05 | 49.882
2021-10-04 | 22:05 | 49.879
2021-10-04 | 22:05 | 49.876
2021-10-04 | 22:05 | 49.874
2021-10-04 | 22:05 | 49.872
2021-10-04 | 22:05 | 49.87
2021-10-04 | 22:05 | 49.869
2021-10-04 | 22:05 | 49.867
2021-10-04 | 22:05 | 49.866
2021-10-04 | 22:05 | 49.866
2021-10-04 | 22:05 | 49.867
2021-10-04 | 22:05 | 49.87
2021-10-04 | 22:05 | 49.874
2021-10-04 | 22:05 | 49.877
2021-10-04 | 22:05 | 49.879
2021-10-04 | 22:05 | 49.881
2021-10-04 | 22:05 | 49.886
2021-10-04 | 22:05 | 49.889
2021-10-04 | 22:05 | 49.891
2021-10-04 | 22:05 | 49.894
2021-10-04 | 22:05 | 49.895
2021-10-04 | 22:05 | 49.896
2021-10-04 | 22:05 | 49.896
2021-10-04 | 22:05 | 49.894
2021-10-04 | 22:05 | 49.893
2021-10-04 | 22:05 | 49.892
2021-10-04 | 22:05 | 49.891
2021-10-04 | 22:05 | 49.889
2021-10-04 | 22:05 | 49.889
2021-10-04 | 22:05 | 49.889
2021-10-04 | 22:05 | 49.889
2021-10-04 | 22:05 | 49.889
2021-10-04 | 22:05 | 49.889
2021-10-04 | 22:05 | 49.892
2021-10-04 | 22:05 | 49.894
2021-10-04 | 22:05 | 49.897
2021-10-04 | 22:05 | 49.898
2021-10-04 | 22:05 | 49.898
2021-10-04 | 22:05 | 49.9
2021-10-04 | 22:05 | 49.9
2021-10-04 | 22:05 | 49.9
2021-10-04 | 22:05 | 49.898
2021-10-04 | 22:05 | 49.897
2021-10-04 | 22:05 | 49.893
2021-10-04 | 22:05 | 49.889
2021-10-04 | 22:05 | 49.884
2021-10-04 | 22:05 | 49.88
2021-10-04 | 22:05 | 49.878
2021-10-04 | 22:05 | 49.878
2021-10-04 | 22:05 | 49.879
2021-10-04 | 22:05 | 49.88
2021-10-04 | 22:05 | 49.881
2021-10-04 | 22:05 | 49.881
2021-10-04 | 22:05 | 49.881
2021-10-04 | 22:05 | 49.881
2021-10-04 | 22:05 | 49.882
2021-10-04 | 22:06 | 49.883
2021-10-04 | 22:06 | 49.883
2021-10-04 | 22:06 | 49.883
2021-10-04 | 22:06 | 49.883
2021-10-04 | 22:06 | 49.883
2021-10-04 | 22:06 | 49.885
2021-10-04 | 22:06 | 49.886
2021-10-04 | 22:06 | 49.887
2021-10-04 | 22:06 | 49.887
2021-10-04 | 22:06 | 49.887
2021-10-04 | 22:06 | 49.887
2021-10-04 | 22:06 | 49.888
2021-10-04 | 22:06 | 49.891
2021-10-04 | 22:06 | 49.896
2021-10-04 | 22:06 | 49.9
2021-10-04 | 22:06 | 49.903
2021-10-04 | 22:06 | 49.903
2021-10-04 | 22:06 | 49.903
2021-10-04 | 22:06 | 49.902
2021-10-04 | 22:06 | 49.902
2021-10-04 | 22:06 | 49.901
2021-10-04 | 22:06 | 49.901
2021-10-04 | 22:06 | 49.899
2021-10-04 | 22:06 | 49.897
2021-10-04 | 22:06 | 49.897
2021-10-04 | 22:06 | 49.895
2021-10-04 | 22:06 | 49.893
2021-10-04 | 22:06 | 49.893
2021-10-04 | 22:06 | 49.894
2021-10-04 | 22:06 | 49.896
2021-10-04 | 22:06 | 49.896
2021-10-04 | 22:06 | 49.897
2021-10-04 | 22:06 | 49.897
2021-10-04 | 22:06 | 49.898
2021-10-04 | 22:06 | 49.897
2021-10-04 | 22:06 | 49.896
2021-10-04 | 22:06 | 49.897
2021-10-04 | 22:06 | 49.897
2021-10-04 | 22:06 | 49.899
2021-10-04 | 22:06 | 49.903
2021-10-04 | 22:06 | 49.906
2021-10-04 | 22:06 | 49.907
2021-10-04 | 22:06 | 49.908
2021-10-04 | 22:06 | 49.907
2021-10-04 | 22:06 | 49.908
2021-10-04 | 22:06 | 49.907
2021-10-04 | 22:06 | 49.908
2021-10-04 | 22:06 | 49.909
2021-10-04 | 22:06 | 49.913
2021-10-04 | 22:06 | 49.917
2021-10-04 | 22:06 | 49.922
2021-10-04 | 22:06 | 49.926
2021-10-04 | 22:06 | 49.926
2021-10-04 | 22:06 | 49.927
2021-10-04 | 22:06 | 49.928
2021-10-04 | 22:06 | 49.927
2021-10-04 | 22:06 | 49.926
2021-10-04 | 22:06 | 49.923
2021-10-04 | 22:06 | 49.921
2021-10-04 | 22:06 | 49.918
2021-10-04 | 22:07 | 49.916
2021-10-04 | 22:07 | 49.913
2021-10-04 | 22:07 | 49.909
2021-10-04 | 22:07 | 49.906
2021-10-04 | 22:07 | 49.906
2021-10-04 | 22:07 | 49.907
2021-10-04 | 22:07 | 49.91
2021-10-04 | 22:07 | 49.912
2021-10-04 | 22:07 | 49.915
2021-10-04 | 22:07 | 49.918
2021-10-04 | 22:07 | 49.921
2021-10-04 | 22:07 | 49.923
2021-10-04 | 22:07 | 49.923
2021-10-04 | 22:07 | 49.923
2021-10-04 | 22:07 | 49.924
2021-10-04 | 22:07 | 49.925
2021-10-04 | 22:07 | 49.927
2021-10-04 | 22:07 | 49.929
2021-10-04 | 22:07 | 49.931
2021-10-04 | 22:07 | 49.931
2021-10-04 | 22:07 | 49.933
2021-10-04 | 22:07 | 49.935
2021-10-04 | 22:07 | 49.935
2021-10-04 | 22:07 | 49.935
2021-10-04 | 22:07 | 49.935
2021-10-04 | 22:07 | 49.936
2021-10-04 | 22:07 | 49.938
2021-10-04 | 22:07 | 49.942
2021-10-04 | 22:07 | 49.946
2021-10-04 | 22:07 | 49.948
2021-10-04 | 22:07 | 49.949
2021-10-04 | 22:07 | 49.948
2021-10-04 | 22:07 | 49.947
2021-10-04 | 22:07 | 49.947
2021-10-04 | 22:07 | 49.945
2021-10-04 | 22:07 | 49.944
2021-10-04 | 22:07 | 49.941
2021-10-04 | 22:07 | 49.939
2021-10-04 | 22:07 | 49.939
2021-10-04 | 22:07 | 49.94
2021-10-04 | 22:07 | 49.939
2021-10-04 | 22:07 | 49.938
2021-10-04 | 22:07 | 49.939
2021-10-04 | 22:07 | 49.939
2021-10-04 | 22:07 | 49.939
2021-10-04 | 22:07 | 49.938
2021-10-04 | 22:07 | 49.938
2021-10-04 | 22:07 | 49.937
2021-10-04 | 22:07 | 49.936
2021-10-04 | 22:07 | 49.935
2021-10-04 | 22:07 | 49.935
2021-10-04 | 22:07 | 49.934
2021-10-04 | 22:07 | 49.936
2021-10-04 | 22:07 | 49.936
2021-10-04 | 22:07 | 49.933
2021-10-04 | 22:07 | 49.932
2021-10-04 | 22:07 | 49.93
2021-10-04 | 22:07 | 49.931
2021-10-04 | 22:07 | 49.931
2021-10-04 | 22:08 | 49.93
2021-10-04 | 22:08 | 49.929
2021-10-04 | 22:08 | 49.926
2021-10-04 | 22:08 | 49.926
2021-10-04 | 22:08 | 49.925
2021-10-04 | 22:08 | 49.925
2021-10-04 | 22:08 | 49.925
2021-10-04 | 22:08 | 49.925
2021-10-04 | 22:08 | 49.924
2021-10-04 | 22:08 | 49.925
2021-10-04 | 22:08 | 49.927
2021-10-04 | 22:08 | 49.928
2021-10-04 | 22:08 | 49.93
2021-10-04 | 22:08 | 49.933
2021-10-04 | 22:08 | 49.936
2021-10-04 | 22:08 | 49.938
2021-10-04 | 22:08 | 49.939
2021-10-04 | 22:08 | 49.939
2021-10-04 | 22:08 | 49.938
2021-10-04 | 22:08 | 49.936
2021-10-04 | 22:08 | 49.934
2021-10-04 | 22:08 | 49.931
2021-10-04 | 22:08 | 49.929
2021-10-04 | 22:08 | 49.927
2021-10-04 | 22:08 | 49.925
2021-10-04 | 22:08 | 49.925
2021-10-04 | 22:08 | 49.924
2021-10-04 | 22:08 | 49.924
2021-10-04 | 22:08 | 49.926
2021-10-04 | 22:08 | 49.928
2021-10-04 | 22:08 | 49.93
2021-10-04 | 22:08 | 49.929
2021-10-04 | 22:08 | 49.931
2021-10-04 | 22:08 | 49.934
2021-10-04 | 22:08 | 49.937
2021-10-04 | 22:08 | 49.94
2021-10-04 | 22:08 | 49.946
2021-10-04 | 22:08 | 49.95
2021-10-04 | 22:08 | 49.951
2021-10-04 | 22:08 | 49.951
2021-10-04 | 22:08 | 49.951
2021-10-04 | 22:08 | 49.951
2021-10-04 | 22:08 | 49.951
2021-10-04 | 22:08 | 49.952
2021-10-04 | 22:08 | 49.953
2021-10-04 | 22:08 | 49.953
2021-10-04 | 22:08 | 49.95
2021-10-04 | 22:08 | 49.946
2021-10-04 | 22:08 | 49.942
2021-10-04 | 22:08 | 49.938
2021-10-04 | 22:08 | 49.933
2021-10-04 | 22:08 | 49.933
2021-10-04 | 22:08 | 49.934
2021-10-04 | 22:08 | 49.936
2021-10-04 | 22:08 | 49.939
2021-10-04 | 22:08 | 49.943
2021-10-04 | 22:08 | 49.946
2021-10-04 | 22:08 | 49.948
2021-10-04 | 22:08 | 49.95
2021-10-04 | 22:08 | 49.953
2021-10-04 | 22:08 | 49.956
2021-10-04 | 22:09 | 49.958
2021-10-04 | 22:09 | 49.96
2021-10-04 | 22:09 | 49.96
2021-10-04 | 22:09 | 49.959
2021-10-04 | 22:09 | 49.958
2021-10-04 | 22:09 | 49.956
2021-10-04 | 22:09 | 49.954
2021-10-04 | 22:09 | 49.952
2021-10-04 | 22:09 | 49.947
2021-10-04 | 22:09 | 49.943
2021-10-04 | 22:09 | 49.94
2021-10-04 | 22:09 | 49.94
2021-10-04 | 22:09 | 49.94
2021-10-04 | 22:09 | 49.94
2021-10-04 | 22:09 | 49.942
2021-10-04 | 22:09 | 49.945
2021-10-04 | 22:09 | 49.948
2021-10-04 | 22:09 | 49.951
2021-10-04 | 22:09 | 49.954
2021-10-04 | 22:09 | 49.955
2021-10-04 | 22:09 | 49.957
2021-10-04 | 22:09 | 49.957
2021-10-04 | 22:09 | 49.956
2021-10-04 | 22:09 | 49.956
2021-10-04 | 22:09 | 49.956
2021-10-04 | 22:09 | 49.957
2021-10-04 | 22:09 | 49.955
2021-10-04 | 22:09 | 49.953
2021-10-04 | 22:09 | 49.953
2021-10-04 | 22:09 | 49.953
2021-10-04 | 22:09 | 49.95
2021-10-04 | 22:09 | 49.947
2021-10-04 | 22:09 | 49.943
2021-10-04 | 22:09 | 49.939
2021-10-04 | 22:09 | 49.935
2021-10-04 | 22:09 | 49.931
2021-10-04 | 22:09 | 49.931
2021-10-04 | 22:09 | 49.931
2021-10-04 | 22:09 | 49.932
2021-10-04 | 22:09 | 49.934
2021-10-04 | 22:09 | 49.934
2021-10-04 | 22:09 | 49.936
2021-10-04 | 22:09 | 49.937
2021-10-04 | 22:09 | 49.938
2021-10-04 | 22:09 | 49.939
2021-10-04 | 22:09 | 49.939
2021-10-04 | 22:09 | 49.941
2021-10-04 | 22:09 | 49.942
2021-10-04 | 22:09 | 49.941
2021-10-04 | 22:09 | 49.94
2021-10-04 | 22:09 | 49.939
2021-10-04 | 22:09 | 49.938
2021-10-04 | 22:09 | 49.936
2021-10-04 | 22:09 | 49.935
2021-10-04 | 22:09 | 49.933
2021-10-04 | 22:09 | 49.931
2021-10-04 | 22:09 | 49.929
2021-10-04 | 22:09 | 49.927
2021-10-04 | 22:09 | 49.926
2021-10-04 | 22:10 | 49.93
2021-10-04 | 22:10 | 49.934
2021-10-04 | 22:10 | 49.936
2021-10-04 | 22:10 | 49.938
2021-10-04 | 22:10 | 49.94
2021-10-04 | 22:10 | 49.942
2021-10-04 | 22:10 | 49.941
2021-10-04 | 22:10 | 49.943
2021-10-04 | 22:10 | 49.943
2021-10-04 | 22:10 | 49.943
2021-10-04 | 22:10 | 49.943
2021-10-04 | 22:10 | 49.944
2021-10-04 | 22:10 | 49.942
2021-10-04 | 22:10 | 49.941
2021-10-04 | 22:10 | 49.942
2021-10-04 | 22:10 | 49.941
2021-10-04 | 22:10 | 49.938
2021-10-04 | 22:10 | 49.936
2021-10-04 | 22:10 | 49.935
2021-10-04 | 22:10 | 49.935
2021-10-04 | 22:10 | 49.936
2021-10-04 | 22:10 | 49.936
2021-10-04 | 22:10 | 49.938
2021-10-04 | 22:10 | 49.938
2021-10-04 | 22:10 | 49.937
2021-10-04 | 22:10 | 49.937
2021-10-04 | 22:10 | 49.935
2021-10-04 | 22:10 | 49.934
2021-10-04 | 22:10 | 49.932
2021-10-04 | 22:10 | 49.932
2021-10-04 | 22:10 | 49.929
2021-10-04 | 22:10 | 49.926
2021-10-04 | 22:10 | 49.922
2021-10-04 | 22:10 | 49.918
2021-10-04 | 22:10 | 49.919
2021-10-04 | 22:10 | 49.919
2021-10-04 | 22:10 | 49.921
2021-10-04 | 22:10 | 49.921
2021-10-04 | 22:10 | 49.922
2021-10-04 | 22:10 | 49.923
2021-10-04 | 22:10 | 49.924
2021-10-04 | 22:10 | 49.923
2021-10-04 | 22:10 | 49.923
2021-10-04 | 22:10 | 49.923
2021-10-04 | 22:10 | 49.921
2021-10-04 | 22:10 | 49.919
2021-10-04 | 22:10 | 49.918
2021-10-04 | 22:10 | 49.917
2021-10-04 | 22:10 | 49.918
2021-10-04 | 22:10 | 49.919
2021-10-04 | 22:10 | 49.923
2021-10-04 | 22:10 | 49.922
2021-10-04 | 22:10 | 49.922
2021-10-04 | 22:10 | 49.921
2021-10-04 | 22:10 | 49.918
2021-10-04 | 22:10 | 49.916
2021-10-04 | 22:10 | 49.912
2021-10-04 | 22:10 | 49.909
2021-10-04 | 22:10 | 49.906
2021-10-04 | 22:10 | 49.904
2021-10-04 | 22:10 | 49.902
2021-10-04 | 22:11 | 49.902
2021-10-04 | 22:11 | 49.902
2021-10-04 | 22:11 | 49.903
2021-10-04 | 22:11 | 49.903
2021-10-04 | 22:11 | 49.901
2021-10-04 | 22:11 | 49.9
2021-10-04 | 22:11 | 49.897
2021-10-04 | 22:11 | 49.897
2021-10-04 | 22:11 | 49.896
2021-10-04 | 22:11 | 49.896
2021-10-04 | 22:11 | 49.897
2021-10-04 | 22:11 | 49.899
2021-10-04 | 22:11 | 49.899
2021-10-04 | 22:11 | 49.9
2021-10-04 | 22:11 | 49.9
2021-10-04 | 22:11 | 49.902
2021-10-04 | 22:11 | 49.903
2021-10-04 | 22:11 | 49.905
2021-10-04 | 22:11 | 49.903
2021-10-04 | 22:11 | 49.901
2021-10-04 | 22:11 | 49.898
2021-10-04 | 22:11 | 49.895
2021-10-04 | 22:11 | 49.892
2021-10-04 | 22:11 | 49.888
2021-10-04 | 22:11 | 49.885
2021-10-04 | 22:11 | 49.882
2021-10-04 | 22:11 | 49.881
2021-10-04 | 22:11 | 49.88
2021-10-04 | 22:11 | 49.88
2021-10-04 | 22:11 | 49.883
2021-10-04 | 22:11 | 49.886
2021-10-04 | 22:11 | 49.887
2021-10-04 | 22:11 | 49.887
2021-10-04 | 22:11 | 49.887
2021-10-04 | 22:11 | 49.885
2021-10-04 | 22:11 | 49.883
2021-10-04 | 22:11 | 49.883
2021-10-04 | 22:11 | 49.882
2021-10-04 | 22:11 | 49.881
2021-10-04 | 22:11 | 49.879
2021-10-04 | 22:11 | 49.879
2021-10-04 | 22:11 | 49.88
2021-10-04 | 22:11 | 49.879
2021-10-04 | 22:11 | 49.877
2021-10-04 | 22:11 | 49.876
2021-10-04 | 22:11 | 49.876
2021-10-04 | 22:11 | 49.876
2021-10-04 | 22:11 | 49.877
2021-10-04 | 22:11 | 49.876
2021-10-04 | 22:11 | 49.875
2021-10-04 | 22:11 | 49.874
2021-10-04 | 22:11 | 49.875
2021-10-04 | 22:11 | 49.877
2021-10-04 | 22:11 | 49.879
2021-10-04 | 22:11 | 49.881
2021-10-04 | 22:11 | 49.885
2021-10-04 | 22:11 | 49.888
2021-10-04 | 22:11 | 49.891
2021-10-04 | 22:11 | 49.892
2021-10-04 | 22:12 | 49.895
2021-10-04 | 22:12 | 49.897
2021-10-04 | 22:12 | 49.9
2021-10-04 | 22:12 | 49.903
2021-10-04 | 22:12 | 49.905
2021-10-04 | 22:12 | 49.906
2021-10-04 | 22:12 | 49.905
2021-10-04 | 22:12 | 49.904
2021-10-04 | 22:12 | 49.901
2021-10-04 | 22:12 | 49.896
2021-10-04 | 22:12 | 49.89
2021-10-04 | 22:12 | 49.882
2021-10-04 | 22:12 | 49.88
2021-10-04 | 22:12 | 49.88
2021-10-04 | 22:12 | 49.879
2021-10-04 | 22:12 | 49.877
2021-10-04 | 22:12 | 49.877
2021-10-04 | 22:12 | 49.879
2021-10-04 | 22:12 | 49.881
2021-10-04 | 22:12 | 49.881
2021-10-04 | 22:12 | 49.882
2021-10-04 | 22:12 | 49.88
2021-10-04 | 22:12 | 49.881
2021-10-04 | 22:12 | 49.88
2021-10-04 | 22:12 | 49.88
2021-10-04 | 22:12 | 49.878
2021-10-04 | 22:12 | 49.874
2021-10-04 | 22:12 | 49.872
2021-10-04 | 22:12 | 49.871
2021-10-04 | 22:12 | 49.87
2021-10-04 | 22:12 | 49.87
2021-10-04 | 22:12 | 49.871
2021-10-04 | 22:12 | 49.872
2021-10-04 | 22:12 | 49.874
2021-10-04 | 22:12 | 49.878
2021-10-04 | 22:12 | 49.881
2021-10-04 | 22:12 | 49.884
2021-10-04 | 22:12 | 49.883
2021-10-04 | 22:12 | 49.881
2021-10-04 | 22:12 | 49.878
2021-10-04 | 22:12 | 49.876
2021-10-04 | 22:12 | 49.873
2021-10-04 | 22:12 | 49.87
2021-10-04 | 22:12 | 49.868
2021-10-04 | 22:12 | 49.865
2021-10-04 | 22:12 | 49.864
2021-10-04 | 22:12 | 49.862
2021-10-04 | 22:12 | 49.86
2021-10-04 | 22:12 | 49.857
2021-10-04 | 22:12 | 49.854
2021-10-04 | 22:12 | 49.853
2021-10-04 | 22:12 | 49.854
2021-10-04 | 22:12 | 49.857
2021-10-04 | 22:12 | 49.857
2021-10-04 | 22:12 | 49.856
2021-10-04 | 22:12 | 49.854
2021-10-04 | 22:12 | 49.851
2021-10-04 | 22:12 | 49.849
2021-10-04 | 22:12 | 49.848
2021-10-04 | 22:12 | 49.851
2021-10-04 | 22:12 | 49.852
2021-10-04 | 22:13 | 49.854
2021-10-04 | 22:13 | 49.855
2021-10-04 | 22:13 | 49.856
2021-10-04 | 22:13 | 49.86
2021-10-04 | 22:13 | 49.862
2021-10-04 | 22:13 | 49.862
2021-10-04 | 22:13 | 49.862
2021-10-04 | 22:13 | 49.862
2021-10-04 | 22:13 | 49.861
2021-10-04 | 22:13 | 49.858
2021-10-04 | 22:13 | 49.857
2021-10-04 | 22:13 | 49.855
2021-10-04 | 22:13 | 49.857
2021-10-04 | 22:13 | 49.857
2021-10-04 | 22:13 | 49.858
2021-10-04 | 22:13 | 49.857
2021-10-04 | 22:13 | 49.857
2021-10-04 | 22:13 | 49.855
2021-10-04 | 22:13 | 49.854
2021-10-04 | 22:13 | 49.853
2021-10-04 | 22:13 | 49.852
2021-10-04 | 22:13 | 49.852
2021-10-04 | 22:13 | 49.851
2021-10-04 | 22:13 | 49.851
2021-10-04 | 22:13 | 49.849
2021-10-04 | 22:13 | 49.85
2021-10-04 | 22:13 | 49.852
2021-10-04 | 22:13 | 49.854
2021-10-04 | 22:13 | 49.856
2021-10-04 | 22:13 | 49.857
2021-10-04 | 22:13 | 49.856
2021-10-04 | 22:13 | 49.855
2021-10-04 | 22:13 | 49.857
2021-10-04 | 22:13 | 49.859
2021-10-04 | 22:13 | 49.863
2021-10-04 | 22:13 | 49.865
2021-10-04 | 22:13 | 49.869
2021-10-04 | 22:13 | 49.873
2021-10-04 | 22:13 | 49.878
2021-10-04 | 22:13 | 49.881
2021-10-04 | 22:13 | 49.882
2021-10-04 | 22:13 | 49.885
2021-10-04 | 22:13 | 49.889
2021-10-04 | 22:13 | 49.893
2021-10-04 | 22:13 | 49.897
2021-10-04 | 22:13 | 49.897
2021-10-04 | 22:13 | 49.896
2021-10-04 | 22:13 | 49.895
2021-10-04 | 22:13 | 49.895
2021-10-04 | 22:13 | 49.894
2021-10-04 | 22:13 | 49.894
2021-10-04 | 22:13 | 49.893
2021-10-04 | 22:13 | 49.894
2021-10-04 | 22:13 | 49.895
2021-10-04 | 22:13 | 49.897
2021-10-04 | 22:13 | 49.898
2021-10-04 | 22:13 | 49.899
2021-10-04 | 22:13 | 49.899
2021-10-04 | 22:13 | 49.898
2021-10-04 | 22:14 | 49.898
2021-10-04 | 22:14 | 49.898
2021-10-04 | 22:14 | 49.897
2021-10-04 | 22:14 | 49.897
2021-10-04 | 22:14 | 49.897
2021-10-04 | 22:14 | 49.897
2021-10-04 | 22:14 | 49.896
2021-10-04 | 22:14 | 49.895
2021-10-04 | 22:14 | 49.894
2021-10-04 | 22:14 | 49.893
2021-10-04 | 22:14 | 49.893
2021-10-04 | 22:14 | 49.894
2021-10-04 | 22:14 | 49.894
2021-10-04 | 22:14 | 49.894
2021-10-04 | 22:14 | 49.894
2021-10-04 | 22:14 | 49.894
2021-10-04 | 22:14 | 49.895
2021-10-04 | 22:14 | 49.896
2021-10-04 | 22:14 | 49.896
2021-10-04 | 22:14 | 49.895
2021-10-04 | 22:14 | 49.894
2021-10-04 | 22:14 | 49.894
2021-10-04 | 22:14 | 49.892
2021-10-04 | 22:14 | 49.89
2021-10-04 | 22:14 | 49.888
2021-10-04 | 22:14 | 49.886
2021-10-04 | 22:14 | 49.884
2021-10-04 | 22:14 | 49.879
2021-10-04 | 22:14 | 49.876
2021-10-04 | 22:14 | 49.874
2021-10-04 | 22:14 | 49.874
2021-10-04 | 22:14 | 49.871
2021-10-04 | 22:14 | 49.869
2021-10-04 | 22:14 | 49.868
2021-10-04 | 22:14 | 49.869
2021-10-04 | 22:14 | 49.87
2021-10-04 | 22:14 | 49.871
2021-10-04 | 22:14 | 49.871
2021-10-04 | 22:14 | 49.872
2021-10-04 | 22:14 | 49.873
2021-10-04 | 22:14 | 49.874
2021-10-04 | 22:14 | 49.876
2021-10-04 | 22:14 | 49.875
2021-10-04 | 22:14 | 49.874
2021-10-04 | 22:14 | 49.873
2021-10-04 | 22:14 | 49.875
2021-10-04 | 22:14 | 49.877
2021-10-04 | 22:14 | 49.879
2021-10-04 | 22:14 | 49.88
2021-10-04 | 22:14 | 49.88
2021-10-04 | 22:14 | 49.881
2021-10-04 | 22:14 | 49.881
2021-10-04 | 22:14 | 49.881
2021-10-04 | 22:14 | 49.881
2021-10-04 | 22:14 | 49.88
2021-10-04 | 22:14 | 49.88
2021-10-04 | 22:14 | 49.881
2021-10-04 | 22:14 | 49.881
2021-10-04 | 22:14 | 49.881
2021-10-04 | 22:14 | 49.881
2021-10-04 | 22:14 | 49.882
2021-10-04 | 22:15 | 49.883
2021-10-04 | 22:15 | 49.884
2021-10-04 | 22:15 | 49.882
2021-10-04 | 22:15 | 49.881
2021-10-04 | 22:15 | 49.881
2021-10-04 | 22:15 | 49.881
2021-10-04 | 22:15 | 49.88
2021-10-04 | 22:15 | 49.881
2021-10-04 | 22:15 | 49.883
2021-10-04 | 22:15 | 49.882
2021-10-04 | 22:15 | 49.882
2021-10-04 | 22:15 | 49.882
2021-10-04 | 22:15 | 49.883
2021-10-04 | 22:15 | 49.882
2021-10-04 | 22:15 | 49.883
2021-10-04 | 22:15 | 49.884
2021-10-04 | 22:15 | 49.884
2021-10-04 | 22:15 | 49.884
2021-10-04 | 22:15 | 49.884
2021-10-04 | 22:15 | 49.883
2021-10-04 | 22:15 | 49.882
2021-10-04 | 22:15 | 49.883
2021-10-04 | 22:15 | 49.885
2021-10-04 | 22:15 | 49.887
2021-10-04 | 22:15 | 49.888
2021-10-04 | 22:15 | 49.889
2021-10-04 | 22:15 | 49.887
2021-10-04 | 22:15 | 49.884
2021-10-04 | 22:15 | 49.879
2021-10-04 | 22:15 | 49.877
2021-10-04 | 22:15 | 49.873
2021-10-04 | 22:15 | 49.869
2021-10-04 | 22:15 | 49.866
2021-10-04 | 22:15 | 49.863
2021-10-04 | 22:15 | 49.86
2021-10-04 | 22:15 | 49.857
2021-10-04 | 22:15 | 49.856
2021-10-04 | 22:15 | 49.854
2021-10-04 | 22:15 | 49.853
2021-10-04 | 22:15 | 49.853
2021-10-04 | 22:15 | 49.854
2021-10-04 | 22:15 | 49.854
2021-10-04 | 22:15 | 49.853
2021-10-04 | 22:15 | 49.856
2021-10-04 | 22:15 | 49.859
2021-10-04 | 22:15 | 49.861
2021-10-04 | 22:15 | 49.861
2021-10-04 | 22:15 | 49.862
2021-10-04 | 22:15 | 49.863
2021-10-04 | 22:15 | 49.863
2021-10-04 | 22:15 | 49.862
2021-10-04 | 22:15 | 49.86
2021-10-04 | 22:15 | 49.861
2021-10-04 | 22:15 | 49.861
2021-10-04 | 22:15 | 49.862
2021-10-04 | 22:15 | 49.86
2021-10-04 | 22:15 | 49.858
2021-10-04 | 22:15 | 49.855
2021-10-04 | 22:15 | 49.853
2021-10-04 | 22:16 | 49.853
2021-10-04 | 22:16 | 49.856
2021-10-04 | 22:16 | 49.86
2021-10-04 | 22:16 | 49.865
2021-10-04 | 22:16 | 49.873
2021-10-04 | 22:16 | 49.879
2021-10-04 | 22:16 | 49.886
2021-10-04 | 22:16 | 49.889
2021-10-04 | 22:16 | 49.887
2021-10-04 | 22:16 | 49.887
2021-10-04 | 22:16 | 49.888
2021-10-04 | 22:16 | 49.889
2021-10-04 | 22:16 | 49.889
2021-10-04 | 22:16 | 49.889
2021-10-04 | 22:16 | 49.886
2021-10-04 | 22:16 | 49.885
2021-10-04 | 22:16 | 49.885
2021-10-04 | 22:16 | 49.883
2021-10-04 | 22:16 | 49.882
2021-10-04 | 22:16 | 49.881
2021-10-04 | 22:16 | 49.881
2021-10-04 | 22:16 | 49.881
2021-10-04 | 22:16 | 49.881
2021-10-04 | 22:16 | 49.881
2021-10-04 | 22:16 | 49.88
2021-10-04 | 22:16 | 49.879
2021-10-04 | 22:16 | 49.877
2021-10-04 | 22:16 | 49.877
2021-10-04 | 22:16 | 49.875
2021-10-04 | 22:16 | 49.876
2021-10-04 | 22:16 | 49.876
2021-10-04 | 22:16 | 49.876
2021-10-04 | 22:16 | 49.878
2021-10-04 | 22:16 | 49.88
2021-10-04 | 22:16 | 49.883
2021-10-04 | 22:16 | 49.885
2021-10-04 | 22:16 | 49.886
2021-10-04 | 22:16 | 49.885
2021-10-04 | 22:16 | 49.884
2021-10-04 | 22:16 | 49.885
2021-10-04 | 22:16 | 49.885
2021-10-04 | 22:16 | 49.885
2021-10-04 | 22:16 | 49.887
2021-10-04 | 22:16 | 49.888
2021-10-04 | 22:16 | 49.89
2021-10-04 | 22:16 | 49.892
2021-10-04 | 22:16 | 49.893
2021-10-04 | 22:16 | 49.896
2021-10-04 | 22:16 | 49.898
2021-10-04 | 22:16 | 49.901
2021-10-04 | 22:16 | 49.903
2021-10-04 | 22:16 | 49.904
2021-10-04 | 22:16 | 49.904
2021-10-04 | 22:16 | 49.907
2021-10-04 | 22:16 | 49.906
2021-10-04 | 22:16 | 49.905
2021-10-04 | 22:16 | 49.904
2021-10-04 | 22:16 | 49.906
2021-10-04 | 22:16 | 49.907
2021-10-04 | 22:16 | 49.906
2021-10-04 | 22:16 | 49.906
2021-10-04 | 22:17 | 49.904
2021-10-04 | 22:17 | 49.903
2021-10-04 | 22:17 | 49.901
2021-10-04 | 22:17 | 49.901
2021-10-04 | 22:17 | 49.902
2021-10-04 | 22:17 | 49.903
2021-10-04 | 22:17 | 49.903
2021-10-04 | 22:17 | 49.904
2021-10-04 | 22:17 | 49.908
2021-10-04 | 22:17 | 49.912
2021-10-04 | 22:17 | 49.914
2021-10-04 | 22:17 | 49.915
2021-10-04 | 22:17 | 49.913
2021-10-04 | 22:17 | 49.912
2021-10-04 | 22:17 | 49.908
2021-10-04 | 22:17 | 49.903
2021-10-04 | 22:17 | 49.901
2021-10-04 | 22:17 | 49.902
2021-10-04 | 22:17 | 49.902
2021-10-04 | 22:17 | 49.904
2021-10-04 | 22:17 | 49.904
2021-10-04 | 22:17 | 49.905
2021-10-04 | 22:17 | 49.901
2021-10-04 | 22:17 | 49.899
2021-10-04 | 22:17 | 49.899
2021-10-04 | 22:17 | 49.902
2021-10-04 | 22:17 | 49.903
2021-10-04 | 22:17 | 49.907
2021-10-04 | 22:17 | 49.911
2021-10-04 | 22:17 | 49.915
2021-10-04 | 22:17 | 49.913
2021-10-04 | 22:17 | 49.913
2021-10-04 | 22:17 | 49.91
2021-10-04 | 22:17 | 49.907
2021-10-04 | 22:17 | 49.904
2021-10-04 | 22:17 | 49.902
2021-10-04 | 22:17 | 49.899
2021-10-04 | 22:17 | 49.898
2021-10-04 | 22:17 | 49.9
2021-10-04 | 22:17 | 49.902
2021-10-04 | 22:17 | 49.903
2021-10-04 | 22:17 | 49.901
2021-10-04 | 22:17 | 49.9
2021-10-04 | 22:17 | 49.902
2021-10-04 | 22:17 | 49.903
2021-10-04 | 22:17 | 49.906
2021-10-04 | 22:17 | 49.908
2021-10-04 | 22:17 | 49.909
2021-10-04 | 22:17 | 49.91
2021-10-04 | 22:17 | 49.91
2021-10-04 | 22:17 | 49.911
2021-10-04 | 22:17 | 49.909
2021-10-04 | 22:17 | 49.907
2021-10-04 | 22:17 | 49.907
2021-10-04 | 22:17 | 49.906
2021-10-04 | 22:17 | 49.904
2021-10-04 | 22:17 | 49.901
2021-10-04 | 22:17 | 49.898
2021-10-04 | 22:17 | 49.898
2021-10-04 | 22:18 | 49.898
2021-10-04 | 22:18 | 49.898
2021-10-04 | 22:18 | 49.899
2021-10-04 | 22:18 | 49.897
2021-10-04 | 22:18 | 49.896
2021-10-04 | 22:18 | 49.897
2021-10-04 | 22:18 | 49.897
2021-10-04 | 22:18 | 49.894
2021-10-04 | 22:18 | 49.893
2021-10-04 | 22:18 | 49.894
2021-10-04 | 22:18 | 49.897
2021-10-04 | 22:18 | 49.899
2021-10-04 | 22:18 | 49.903
2021-10-04 | 22:18 | 49.906
2021-10-04 | 22:18 | 49.909
2021-10-04 | 22:18 | 49.913
2021-10-04 | 22:18 | 49.917
2021-10-04 | 22:18 | 49.92
2021-10-04 | 22:18 | 49.922
2021-10-04 | 22:18 | 49.922
2021-10-04 | 22:18 | 49.922
2021-10-04 | 22:18 | 49.922
2021-10-04 | 22:18 | 49.923
2021-10-04 | 22:18 | 49.923
2021-10-04 | 22:18 | 49.923
2021-10-04 | 22:18 | 49.922
2021-10-04 | 22:18 | 49.923
2021-10-04 | 22:18 | 49.925
2021-10-04 | 22:18 | 49.928
2021-10-04 | 22:18 | 49.93
2021-10-04 | 22:18 | 49.932
2021-10-04 | 22:18 | 49.933
2021-10-04 | 22:18 | 49.931
2021-10-04 | 22:18 | 49.931
2021-10-04 | 22:18 | 49.928
2021-10-04 | 22:18 | 49.927
2021-10-04 | 22:18 | 49.925
2021-10-04 | 22:18 | 49.924
2021-10-04 | 22:18 | 49.922
2021-10-04 | 22:18 | 49.923
2021-10-04 | 22:18 | 49.925
2021-10-04 | 22:18 | 49.928
2021-10-04 | 22:18 | 49.93
2021-10-04 | 22:18 | 49.929
2021-10-04 | 22:18 | 49.929
2021-10-04 | 22:18 | 49.928
2021-10-04 | 22:18 | 49.929
2021-10-04 | 22:18 | 49.93
2021-10-04 | 22:18 | 49.929
2021-10-04 | 22:18 | 49.93
2021-10-04 | 22:18 | 49.931
2021-10-04 | 22:18 | 49.932
2021-10-04 | 22:18 | 49.933
2021-10-04 | 22:18 | 49.936
2021-10-04 | 22:18 | 49.939
2021-10-04 | 22:18 | 49.942
2021-10-04 | 22:18 | 49.946
2021-10-04 | 22:18 | 49.95
2021-10-04 | 22:18 | 49.949
2021-10-04 | 22:18 | 49.947
2021-10-04 | 22:18 | 49.946
2021-10-04 | 22:19 | 49.947
2021-10-04 | 22:19 | 49.946
2021-10-04 | 22:19 | 49.947
2021-10-04 | 22:19 | 49.949
2021-10-04 | 22:19 | 49.949
2021-10-04 | 22:19 | 49.949
2021-10-04 | 22:19 | 49.948
2021-10-04 | 22:19 | 49.95
2021-10-04 | 22:19 | 49.951
2021-10-04 | 22:19 | 49.953
2021-10-04 | 22:19 | 49.954
2021-10-04 | 22:19 | 49.954
2021-10-04 | 22:19 | 49.956
2021-10-04 | 22:19 | 49.958
2021-10-04 | 22:19 | 49.958
2021-10-04 | 22:19 | 49.956
2021-10-04 | 22:19 | 49.954
2021-10-04 | 22:19 | 49.952
2021-10-04 | 22:19 | 49.952
2021-10-04 | 22:19 | 49.954
2021-10-04 | 22:19 | 49.957
2021-10-04 | 22:19 | 49.959
2021-10-04 | 22:19 | 49.96
2021-10-04 | 22:19 | 49.961
2021-10-04 | 22:19 | 49.961
2021-10-04 | 22:19 | 49.963
2021-10-04 | 22:19 | 49.962
2021-10-04 | 22:19 | 49.961
2021-10-04 | 22:19 | 49.962
2021-10-04 | 22:19 | 49.961
2021-10-04 | 22:19 | 49.959
2021-10-04 | 22:19 | 49.958
2021-10-04 | 22:19 | 49.956
2021-10-04 | 22:19 | 49.954
2021-10-04 | 22:19 | 49.953
2021-10-04 | 22:19 | 49.952
2021-10-04 | 22:19 | 49.949
2021-10-04 | 22:19 | 49.947
2021-10-04 | 22:19 | 49.944
2021-10-04 | 22:19 | 49.943
2021-10-04 | 22:19 | 49.942
2021-10-04 | 22:19 | 49.941
2021-10-04 | 22:19 | 49.942
2021-10-04 | 22:19 | 49.943
2021-10-04 | 22:19 | 49.946
2021-10-04 | 22:19 | 49.947
2021-10-04 | 22:19 | 49.947
2021-10-04 | 22:19 | 49.947
2021-10-04 | 22:19 | 49.946
2021-10-04 | 22:19 | 49.945
2021-10-04 | 22:19 | 49.945
2021-10-04 | 22:19 | 49.942
2021-10-04 | 22:19 | 49.938
2021-10-04 | 22:19 | 49.937
2021-10-04 | 22:19 | 49.936
2021-10-04 | 22:19 | 49.934
2021-10-04 | 22:19 | 49.934
2021-10-04 | 22:19 | 49.936
2021-10-04 | 22:19 | 49.937
2021-10-04 | 22:20 | 49.938
2021-10-04 | 22:20 | 49.94
2021-10-04 | 22:20 | 49.943
2021-10-04 | 22:20 | 49.947
2021-10-04 | 22:20 | 49.95
2021-10-04 | 22:20 | 49.951
2021-10-04 | 22:20 | 49.952
2021-10-04 | 22:20 | 49.953
2021-10-04 | 22:20 | 49.954
2021-10-04 | 22:20 | 49.956
2021-10-04 | 22:20 | 49.959
2021-10-04 | 22:20 | 49.96
2021-10-04 | 22:20 | 49.962
2021-10-04 | 22:20 | 49.965
2021-10-04 | 22:20 | 49.965
2021-10-04 | 22:20 | 49.964
2021-10-04 | 22:20 | 49.962
2021-10-04 | 22:20 | 49.959
2021-10-04 | 22:20 | 49.956
2021-10-04 | 22:20 | 49.958
2021-10-04 | 22:20 | 49.958
2021-10-04 | 22:20 | 49.959
2021-10-04 | 22:20 | 49.96
2021-10-04 | 22:20 | 49.962
2021-10-04 | 22:20 | 49.963
2021-10-04 | 22:20 | 49.964
2021-10-04 | 22:20 | 49.962
2021-10-04 | 22:20 | 49.959
2021-10-04 | 22:20 | 49.957
2021-10-04 | 22:20 | 49.957
2021-10-04 | 22:20 | 49.956
2021-10-04 | 22:20 | 49.956
2021-10-04 | 22:20 | 49.957
2021-10-04 | 22:20 | 49.958
2021-10-04 | 22:20 | 49.958
2021-10-04 | 22:20 | 49.959
2021-10-04 | 22:20 | 49.959
2021-10-04 | 22:20 | 49.958
2021-10-04 | 22:20 | 49.959
2021-10-04 | 22:20 | 49.962
2021-10-04 | 22:20 | 49.964
2021-10-04 | 22:20 | 49.964
2021-10-04 | 22:20 | 49.965
2021-10-04 | 22:20 | 49.965
2021-10-04 | 22:20 | 49.965
2021-10-04 | 22:20 | 49.966
2021-10-04 | 22:20 | 49.967
2021-10-04 | 22:20 | 49.967
2021-10-04 | 22:20 | 49.967
2021-10-04 | 22:20 | 49.968
2021-10-04 | 22:20 | 49.97
2021-10-04 | 22:20 | 49.972
2021-10-04 | 22:20 | 49.971
2021-10-04 | 22:20 | 49.971
2021-10-04 | 22:20 | 49.969
2021-10-04 | 22:20 | 49.966
2021-10-04 | 22:20 | 49.96
2021-10-04 | 22:20 | 49.957
2021-10-04 | 22:20 | 49.953
2021-10-04 | 22:20 | 49.95
2021-10-04 | 22:20 | 49.95
2021-10-04 | 22:21 | 49.952
2021-10-04 | 22:21 | 49.953
2021-10-04 | 22:21 | 49.955
2021-10-04 | 22:21 | 49.955
2021-10-04 | 22:21 | 49.957
2021-10-04 | 22:21 | 49.958
2021-10-04 | 22:21 | 49.958
2021-10-04 | 22:21 | 49.958
2021-10-04 | 22:21 | 49.958
2021-10-04 | 22:21 | 49.96
2021-10-04 | 22:21 | 49.96
2021-10-04 | 22:21 | 49.961
2021-10-04 | 22:21 | 49.962
2021-10-04 | 22:21 | 49.963
2021-10-04 | 22:21 | 49.961
2021-10-04 | 22:21 | 49.959
2021-10-04 | 22:21 | 49.955
2021-10-04 | 22:21 | 49.952
2021-10-04 | 22:21 | 49.952
2021-10-04 | 22:21 | 49.953
2021-10-04 | 22:21 | 49.955
2021-10-04 | 22:21 | 49.958
2021-10-04 | 22:21 | 49.96
2021-10-04 | 22:21 | 49.96
2021-10-04 | 22:21 | 49.96
2021-10-04 | 22:21 | 49.961
2021-10-04 | 22:21 | 49.961
2021-10-04 | 22:21 | 49.961
2021-10-04 | 22:21 | 49.96
2021-10-04 | 22:21 | 49.96
2021-10-04 | 22:21 | 49.96
2021-10-04 | 22:21 | 49.959
2021-10-04 | 22:21 | 49.958
2021-10-04 | 22:21 | 49.961
2021-10-04 | 22:21 | 49.96
2021-10-04 | 22:21 | 49.962
2021-10-04 | 22:21 | 49.961
2021-10-04 | 22:21 | 49.964
2021-10-04 | 22:21 | 49.966
2021-10-04 | 22:21 | 49.966
2021-10-04 | 22:21 | 49.964
2021-10-04 | 22:21 | 49.962
2021-10-04 | 22:21 | 49.959
2021-10-04 | 22:21 | 49.958
2021-10-04 | 22:21 | 49.957
2021-10-04 | 22:21 | 49.957
2021-10-04 | 22:21 | 49.958
2021-10-04 | 22:21 | 49.959
2021-10-04 | 22:21 | 49.957
2021-10-04 | 22:21 | 49.954
2021-10-04 | 22:21 | 49.951
2021-10-04 | 22:21 | 49.947
2021-10-04 | 22:21 | 49.944
2021-10-04 | 22:21 | 49.947
2021-10-04 | 22:21 | 49.947
2021-10-04 | 22:21 | 49.95
2021-10-04 | 22:21 | 49.949
2021-10-04 | 22:21 | 49.95
2021-10-04 | 22:21 | 49.949
2021-10-04 | 22:22 | 49.95
2021-10-04 | 22:22 | 49.951
2021-10-04 | 22:22 | 49.954
2021-10-04 | 22:22 | 49.956
2021-10-04 | 22:22 | 49.954
2021-10-04 | 22:22 | 49.954
2021-10-04 | 22:22 | 49.953
2021-10-04 | 22:22 | 49.951
2021-10-04 | 22:22 | 49.951
2021-10-04 | 22:22 | 49.951
2021-10-04 | 22:22 | 49.953
2021-10-04 | 22:22 | 49.955
2021-10-04 | 22:22 | 49.957
2021-10-04 | 22:22 | 49.958
2021-10-04 | 22:22 | 49.96
2021-10-04 | 22:22 | 49.959
2021-10-04 | 22:22 | 49.96
2021-10-04 | 22:22 | 49.961
2021-10-04 | 22:22 | 49.959
2021-10-04 | 22:22 | 49.957
2021-10-04 | 22:22 | 49.952
2021-10-04 | 22:22 | 49.948
2021-10-04 | 22:22 | 49.943
2021-10-04 | 22:22 | 49.94
2021-10-04 | 22:22 | 49.936
2021-10-04 | 22:22 | 49.934
2021-10-04 | 22:22 | 49.936
2021-10-04 | 22:22 | 49.938
2021-10-04 | 22:22 | 49.94
2021-10-04 | 22:22 | 49.941
2021-10-04 | 22:22 | 49.941
2021-10-04 | 22:22 | 49.938
2021-10-04 | 22:22 | 49.933
2021-10-04 | 22:22 | 49.93
2021-10-04 | 22:22 | 49.928
2021-10-04 | 22:22 | 49.929
2021-10-04 | 22:22 | 49.932
2021-10-04 | 22:22 | 49.932
2021-10-04 | 22:22 | 49.93
2021-10-04 | 22:22 | 49.931
2021-10-04 | 22:22 | 49.93
2021-10-04 | 22:22 | 49.932
2021-10-04 | 22:22 | 49.935
2021-10-04 | 22:22 | 49.937
2021-10-04 | 22:22 | 49.939
2021-10-04 | 22:22 | 49.942
2021-10-04 | 22:22 | 49.943
2021-10-04 | 22:22 | 49.946
2021-10-04 | 22:22 | 49.946
2021-10-04 | 22:22 | 49.945
2021-10-04 | 22:22 | 49.948
2021-10-04 | 22:22 | 49.948
2021-10-04 | 22:22 | 49.949
2021-10-04 | 22:22 | 49.951
2021-10-04 | 22:22 | 49.952
2021-10-04 | 22:22 | 49.954
2021-10-04 | 22:22 | 49.952
2021-10-04 | 22:22 | 49.952
2021-10-04 | 22:22 | 49.95
2021-10-04 | 22:22 | 49.948
2021-10-04 | 22:22 | 49.947
2021-10-04 | 22:23 | 49.945
2021-10-04 | 22:23 | 49.945
2021-10-04 | 22:23 | 49.944
2021-10-04 | 22:23 | 49.943
2021-10-04 | 22:23 | 49.941
2021-10-04 | 22:23 | 49.937
2021-10-04 | 22:23 | 49.936
2021-10-04 | 22:23 | 49.933
2021-10-04 | 22:23 | 49.934
2021-10-04 | 22:23 | 49.936
2021-10-04 | 22:23 | 49.937
2021-10-04 | 22:23 | 49.938
2021-10-04 | 22:23 | 49.94
2021-10-04 | 22:23 | 49.942
2021-10-04 | 22:23 | 49.945
2021-10-04 | 22:23 | 49.945
2021-10-04 | 22:23 | 49.946
2021-10-04 | 22:23 | 49.945
2021-10-04 | 22:23 | 49.945
2021-10-04 | 22:23 | 49.945
2021-10-04 | 22:23 | 49.943
2021-10-04 | 22:23 | 49.942
2021-10-04 | 22:23 | 49.939
2021-10-04 | 22:23 | 49.937
2021-10-04 | 22:23 | 49.935
2021-10-04 | 22:23 | 49.934
2021-10-04 | 22:23 | 49.935
2021-10-04 | 22:23 | 49.935
2021-10-04 | 22:23 | 49.935
2021-10-04 | 22:23 | 49.935
2021-10-04 | 22:23 | 49.935
2021-10-04 | 22:23 | 49.934
2021-10-04 | 22:23 | 49.933
2021-10-04 | 22:23 | 49.933
2021-10-04 | 22:23 | 49.933
2021-10-04 | 22:23 | 49.936
2021-10-04 | 22:23 | 49.94
2021-10-04 | 22:23 | 49.942
2021-10-04 | 22:23 | 49.945
2021-10-04 | 22:23 | 49.946
2021-10-04 | 22:23 | 49.946
2021-10-04 | 22:23 | 49.946
2021-10-04 | 22:23 | 49.942
2021-10-04 | 22:23 | 49.941
2021-10-04 | 22:23 | 49.94
2021-10-04 | 22:23 | 49.938
2021-10-04 | 22:23 | 49.938
2021-10-04 | 22:23 | 49.938
2021-10-04 | 22:23 | 49.939
2021-10-04 | 22:23 | 49.938
2021-10-04 | 22:23 | 49.938
2021-10-04 | 22:23 | 49.937
2021-10-04 | 22:23 | 49.939
2021-10-04 | 22:23 | 49.94
2021-10-04 | 22:23 | 49.944
2021-10-04 | 22:23 | 49.945
2021-10-04 | 22:23 | 49.95
2021-10-04 | 22:23 | 49.951
2021-10-04 | 22:23 | 49.953
2021-10-04 | 22:24 | 49.954
2021-10-04 | 22:24 | 49.956
2021-10-04 | 22:24 | 49.957
2021-10-04 | 22:24 | 49.955
2021-10-04 | 22:24 | 49.951
2021-10-04 | 22:24 | 49.946
2021-10-04 | 22:24 | 49.942
2021-10-04 | 22:24 | 49.938
2021-10-04 | 22:24 | 49.935
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.927
2021-10-04 | 22:24 | 49.927
2021-10-04 | 22:24 | 49.928
2021-10-04 | 22:24 | 49.93
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.932
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.929
2021-10-04 | 22:24 | 49.929
2021-10-04 | 22:24 | 49.929
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.932
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.928
2021-10-04 | 22:24 | 49.927
2021-10-04 | 22:24 | 49.927
2021-10-04 | 22:24 | 49.927
2021-10-04 | 22:24 | 49.93
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.93
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.93
2021-10-04 | 22:24 | 49.93
2021-10-04 | 22:24 | 49.93
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.932
2021-10-04 | 22:24 | 49.934
2021-10-04 | 22:24 | 49.934
2021-10-04 | 22:24 | 49.934
2021-10-04 | 22:24 | 49.933
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.93
2021-10-04 | 22:24 | 49.928
2021-10-04 | 22:24 | 49.925
2021-10-04 | 22:24 | 49.923
2021-10-04 | 22:24 | 49.924
2021-10-04 | 22:24 | 49.926
2021-10-04 | 22:24 | 49.928
2021-10-04 | 22:24 | 49.929
2021-10-04 | 22:24 | 49.928
2021-10-04 | 22:24 | 49.927
2021-10-04 | 22:24 | 49.927
2021-10-04 | 22:24 | 49.929
2021-10-04 | 22:24 | 49.931
2021-10-04 | 22:24 | 49.933
2021-10-04 | 22:24 | 49.937
2021-10-04 | 22:24 | 49.943
2021-10-04 | 22:24 | 49.947
2021-10-04 | 22:25 | 49.948
2021-10-04 | 22:25 | 49.944
2021-10-04 | 22:25 | 49.944
2021-10-04 | 22:25 | 49.944
2021-10-04 | 22:25 | 49.946
2021-10-04 | 22:25 | 49.947
2021-10-04 | 22:25 | 49.946
2021-10-04 | 22:25 | 49.944
2021-10-04 | 22:25 | 49.942
2021-10-04 | 22:25 | 49.94
2021-10-04 | 22:25 | 49.938
2021-10-04 | 22:25 | 49.937
2021-10-04 | 22:25 | 49.935
2021-10-04 | 22:25 | 49.932
2021-10-04 | 22:25 | 49.93
2021-10-04 | 22:25 | 49.926
2021-10-04 | 22:25 | 49.924
2021-10-04 | 22:25 | 49.922
2021-10-04 | 22:25 | 49.919
2021-10-04 | 22:25 | 49.919
2021-10-04 | 22:25 | 49.92
2021-10-04 | 22:25 | 49.92
2021-10-04 | 22:25 | 49.92
2021-10-04 | 22:25 | 49.922
2021-10-04 | 22:25 | 49.925
2021-10-04 | 22:25 | 49.927
2021-10-04 | 22:25 | 49.931
2021-10-04 | 22:25 | 49.932
2021-10-04 | 22:25 | 49.934
2021-10-04 | 22:25 | 49.934
2021-10-04 | 22:25 | 49.934
2021-10-04 | 22:25 | 49.932
2021-10-04 | 22:25 | 49.932
2021-10-04 | 22:25 | 49.932
2021-10-04 | 22:25 | 49.931
2021-10-04 | 22:25 | 49.93
2021-10-04 | 22:25 | 49.928
2021-10-04 | 22:25 | 49.927
2021-10-04 | 22:25 | 49.923
2021-10-04 | 22:25 | 49.922
2021-10-04 | 22:25 | 49.921
2021-10-04 | 22:25 | 49.918
2021-10-04 | 22:25 | 49.917
2021-10-04 | 22:25 | 49.916
2021-10-04 | 22:25 | 49.918
2021-10-04 | 22:25 | 49.921
2021-10-04 | 22:25 | 49.923
2021-10-04 | 22:25 | 49.922
2021-10-04 | 22:25 | 49.925
2021-10-04 | 22:25 | 49.926
2021-10-04 | 22:25 | 49.928
2021-10-04 | 22:25 | 49.931
2021-10-04 | 22:25 | 49.934
2021-10-04 | 22:25 | 49.936
2021-10-04 | 22:25 | 49.939
2021-10-04 | 22:25 | 49.941
2021-10-04 | 22:25 | 49.944
2021-10-04 | 22:25 | 49.944
2021-10-04 | 22:25 | 49.946
2021-10-04 | 22:26 | 49.948
2021-10-04 | 22:26 | 49.95
2021-10-04 | 22:26 | 49.951
2021-10-04 | 22:26 | 49.952
2021-10-04 | 22:26 | 49.951
2021-10-04 | 22:26 | 49.946
2021-10-04 | 22:26 | 49.942
2021-10-04 | 22:26 | 49.934
2021-10-04 | 22:26 | 49.929
2021-10-04 | 22:26 | 49.927
2021-10-04 | 22:26 | 49.928
2021-10-04 | 22:26 | 49.929
2021-10-04 | 22:26 | 49.931
2021-10-04 | 22:26 | 49.933
2021-10-04 | 22:26 | 49.937
2021-10-04 | 22:26 | 49.94
2021-10-04 | 22:26 | 49.941
2021-10-04 | 22:26 | 49.941
2021-10-04 | 22:26 | 49.942
2021-10-04 | 22:26 | 49.943
2021-10-04 | 22:26 | 49.943
2021-10-04 | 22:26 | 49.946
2021-10-04 | 22:26 | 49.948
2021-10-04 | 22:26 | 49.947
2021-10-04 | 22:26 | 49.944
2021-10-04 | 22:26 | 49.941
2021-10-04 | 22:26 | 49.937
2021-10-04 | 22:26 | 49.933
2021-10-04 | 22:26 | 49.931
2021-10-04 | 22:26 | 49.931
2021-10-04 | 22:26 | 49.93
2021-10-04 | 22:26 | 49.932
2021-10-04 | 22:26 | 49.935
2021-10-04 | 22:26 | 49.939
2021-10-04 | 22:26 | 49.94
2021-10-04 | 22:26 | 49.943
2021-10-04 | 22:26 | 49.945
2021-10-04 | 22:26 | 49.946
2021-10-04 | 22:26 | 49.947
2021-10-04 | 22:26 | 49.949
2021-10-04 | 22:26 | 49.95
2021-10-04 | 22:26 | 49.949
2021-10-04 | 22:26 | 49.948
2021-10-04 | 22:26 | 49.948
2021-10-04 | 22:26 | 49.949
2021-10-04 | 22:26 | 49.95
2021-10-04 | 22:26 | 49.952
2021-10-04 | 22:26 | 49.953
2021-10-04 | 22:26 | 49.954
2021-10-04 | 22:26 | 49.956
2021-10-04 | 22:26 | 49.956
2021-10-04 | 22:26 | 49.956
2021-10-04 | 22:26 | 49.957
2021-10-04 | 22:26 | 49.958
2021-10-04 | 22:26 | 49.96
2021-10-04 | 22:26 | 49.964
2021-10-04 | 22:26 | 49.969
2021-10-04 | 22:26 | 49.974
2021-10-04 | 22:26 | 49.977
2021-10-04 | 22:26 | 49.975
2021-10-04 | 22:26 | 49.974
2021-10-04 | 22:27 | 49.975
2021-10-04 | 22:27 | 49.976
2021-10-04 | 22:27 | 49.977
2021-10-04 | 22:27 | 49.979
2021-10-04 | 22:27 | 49.984
2021-10-04 | 22:27 | 49.987
2021-10-04 | 22:27 | 49.988
2021-10-04 | 22:27 | 49.989
2021-10-04 | 22:27 | 49.989
2021-10-04 | 22:27 | 49.988
2021-10-04 | 22:27 | 49.986
2021-10-04 | 22:27 | 49.985
2021-10-04 | 22:27 | 49.985
2021-10-04 | 22:27 | 49.985
2021-10-04 | 22:27 | 49.985
2021-10-04 | 22:27 | 49.984
2021-10-04 | 22:27 | 49.981
2021-10-04 | 22:27 | 49.978
2021-10-04 | 22:27 | 49.975
2021-10-04 | 22:27 | 49.973
2021-10-04 | 22:27 | 49.971
2021-10-04 | 22:27 | 49.971
2021-10-04 | 22:27 | 49.971
2021-10-04 | 22:27 | 49.971
2021-10-04 | 22:27 | 49.972
2021-10-04 | 22:27 | 49.973
2021-10-04 | 22:27 | 49.972
2021-10-04 | 22:27 | 49.969
2021-10-04 | 22:27 | 49.967
2021-10-04 | 22:27 | 49.965
2021-10-04 | 22:27 | 49.96
2021-10-04 | 22:27 | 49.957
2021-10-04 | 22:27 | 49.957
2021-10-04 | 22:27 | 49.959
2021-10-04 | 22:27 | 49.961
2021-10-04 | 22:27 | 49.962
2021-10-04 | 22:27 | 49.961
2021-10-04 | 22:27 | 49.96
2021-10-04 | 22:27 | 49.956
2021-10-04 | 22:27 | 49.954
2021-10-04 | 22:27 | 49.953
2021-10-04 | 22:27 | 49.953
2021-10-04 | 22:27 | 49.95
2021-10-04 | 22:27 | 49.948
2021-10-04 | 22:27 | 49.945
2021-10-04 | 22:27 | 49.946
2021-10-04 | 22:27 | 49.949
2021-10-04 | 22:27 | 49.95
2021-10-04 | 22:27 | 49.951
2021-10-04 | 22:27 | 49.952
2021-10-04 | 22:27 | 49.954
2021-10-04 | 22:27 | 49.956
2021-10-04 | 22:27 | 49.957
2021-10-04 | 22:27 | 49.957
2021-10-04 | 22:27 | 49.957
2021-10-04 | 22:27 | 49.96
2021-10-04 | 22:27 | 49.962
2021-10-04 | 22:27 | 49.966
2021-10-04 | 22:27 | 49.97
2021-10-04 | 22:28 | 49.974
2021-10-04 | 22:28 | 49.974
2021-10-04 | 22:28 | 49.974
2021-10-04 | 22:28 | 49.974
2021-10-04 | 22:28 | 49.973
2021-10-04 | 22:28 | 49.97
2021-10-04 | 22:28 | 49.97
2021-10-04 | 22:28 | 49.969
2021-10-04 | 22:28 | 49.968
2021-10-04 | 22:28 | 49.969
2021-10-04 | 22:28 | 49.97
2021-10-04 | 22:28 | 49.967
2021-10-04 | 22:28 | 49.969
2021-10-04 | 22:28 | 49.968
2021-10-04 | 22:28 | 49.97
2021-10-04 | 22:28 | 49.973
2021-10-04 | 22:28 | 49.977
2021-10-04 | 22:28 | 49.98
2021-10-04 | 22:28 | 49.983
2021-10-04 | 22:28 | 49.983
2021-10-04 | 22:28 | 49.988
2021-10-04 | 22:28 | 49.99
2021-10-04 | 22:28 | 49.99
2021-10-04 | 22:28 | 49.99
2021-10-04 | 22:28 | 49.988
2021-10-04 | 22:28 | 49.988
2021-10-04 | 22:28 | 49.985
2021-10-04 | 22:28 | 49.982
2021-10-04 | 22:28 | 49.976
2021-10-04 | 22:28 | 49.971
2021-10-04 | 22:28 | 49.969
2021-10-04 | 22:28 | 49.967
2021-10-04 | 22:28 | 49.965
2021-10-04 | 22:28 | 49.965
2021-10-04 | 22:28 | 49.966
2021-10-04 | 22:28 | 49.969
2021-10-04 | 22:28 | 49.97
2021-10-04 | 22:28 | 49.974
2021-10-04 | 22:28 | 49.977
2021-10-04 | 22:28 | 49.981
2021-10-04 | 22:28 | 49.985
2021-10-04 | 22:28 | 49.987
2021-10-04 | 22:28 | 49.988
2021-10-04 | 22:28 | 49.989
2021-10-04 | 22:28 | 49.989
2021-10-04 | 22:28 | 49.987
2021-10-04 | 22:28 | 49.986
2021-10-04 | 22:28 | 49.984
2021-10-04 | 22:28 | 49.983
2021-10-04 | 22:28 | 49.981
2021-10-04 | 22:28 | 49.982
2021-10-04 | 22:28 | 49.981
2021-10-04 | 22:28 | 49.98
2021-10-04 | 22:28 | 49.981
2021-10-04 | 22:28 | 49.983
2021-10-04 | 22:28 | 49.985
2021-10-04 | 22:28 | 49.986
2021-10-04 | 22:28 | 49.984
2021-10-04 | 22:28 | 49.984
2021-10-04 | 22:28 | 49.982
2021-10-04 | 22:28 | 49.98
2021-10-04 | 22:29 | 49.979
2021-10-04 | 22:29 | 49.977
2021-10-04 | 22:29 | 49.978
2021-10-04 | 22:29 | 49.979
2021-10-04 | 22:29 | 49.98
2021-10-04 | 22:29 | 49.98
2021-10-04 | 22:29 | 49.981
2021-10-04 | 22:29 | 49.983
2021-10-04 | 22:29 | 49.984
2021-10-04 | 22:29 | 49.984
2021-10-04 | 22:29 | 49.985
2021-10-04 | 22:29 | 49.982
2021-10-04 | 22:29 | 49.983
2021-10-04 | 22:29 | 49.986
2021-10-04 | 22:29 | 49.986
2021-10-04 | 22:29 | 49.988
2021-10-04 | 22:29 | 49.991
2021-10-04 | 22:29 | 49.995
2021-10-04 | 22:29 | 50.002
2021-10-04 | 22:29 | 50.008
2021-10-04 | 22:29 | 50.012
2021-10-04 | 22:29 | 50.014
2021-10-04 | 22:29 | 50.013
2021-10-04 | 22:29 | 50.013
2021-10-04 | 22:29 | 50.015
2021-10-04 | 22:29 | 50.017
2021-10-04 | 22:29 | 50.018
2021-10-04 | 22:29 | 50.018
2021-10-04 | 22:29 | 50.019

## 20211005-1
In GMT
Date | Time | Freq
2021-10-05 | 16:50 | 49.963
2021-10-05 | 16:50 | 49.958
2021-10-05 | 16:50 | 49.956
2021-10-05 | 16:50 | 49.951
2021-10-05 | 16:50 | 49.953
2021-10-05 | 16:50 | 49.95
2021-10-05 | 16:50 | 49.952
2021-10-05 | 16:50 | 49.952
2021-10-05 | 16:50 | 49.951
2021-10-05 | 16:50 | 49.954
2021-10-05 | 16:50 | 49.956
2021-10-05 | 16:50 | 49.957
2021-10-05 | 16:50 | 49.962
2021-10-05 | 16:50 | 49.964
2021-10-05 | 16:50 | 49.967
2021-10-05 | 16:50 | 49.969
2021-10-05 | 16:50 | 49.967
2021-10-05 | 16:50 | 49.966
2021-10-05 | 16:50 | 49.967
2021-10-05 | 16:50 | 49.962
2021-10-05 | 16:50 | 49.962
2021-10-05 | 16:50 | 49.959
2021-10-05 | 16:50 | 49.959
2021-10-05 | 16:50 | 49.96
2021-10-05 | 16:50 | 49.963
2021-10-05 | 16:50 | 49.964
2021-10-05 | 16:50 | 49.967
2021-10-05 | 16:50 | 49.972
2021-10-05 | 16:50 | 49.978
2021-10-05 | 16:50 | 49.983
2021-10-05 | 16:50 | 49.989
2021-10-05 | 16:51 | 49.993
2021-10-05 | 16:51 | 49.991
2021-10-05 | 16:51 | 49.993
2021-10-05 | 16:51 | 49.991
2021-10-05 | 16:51 | 49.991
2021-10-05 | 16:51 | 49.99
2021-10-05 | 16:51 | 49.99
2021-10-05 | 16:51 | 49.996
2021-10-05 | 16:51 | 49.999
2021-10-05 | 16:51 | 50.005
2021-10-05 | 16:51 | 50.011
2021-10-05 | 16:51 | 50.014
2021-10-05 | 16:51 | 50.019
2021-10-05 | 16:51 | 50.02
2021-10-05 | 16:51 | 50.022
2021-10-05 | 16:51 | 50.02
2021-10-05 | 16:51 | 50.018
2021-10-05 | 16:51 | 50.018
2021-10-05 | 16:51 | 50.018
2021-10-05 | 16:51 | 50.019
2021-10-05 | 16:51 | 50.02
2021-10-05 | 16:51 | 50.022
2021-10-05 | 16:51 | 50.023
2021-10-05 | 16:51 | 50.023
2021-10-05 | 16:51 | 50.021
2021-10-05 | 16:51 | 50.02
2021-10-05 | 16:51 | 50.017
2021-10-05 | 16:51 | 50.015
2021-10-05 | 16:51 | 50.012
2021-10-05 | 16:51 | 50.01
2021-10-05 | 16:51 | 50.006
2021-10-05 | 16:51 | 50.002
2021-10-05 | 16:51 | 50.002
2021-10-05 | 16:51 | 50.002
2021-10-05 | 16:51 | 50.001
2021-10-05 | 16:51 | 50.002
2021-10-05 | 16:51 | 49.999
2021-10-05 | 16:51 | 49.999
2021-10-05 | 16:51 | 49.994
2021-10-05 | 16:51 | 49.992
2021-10-05 | 16:51 | 49.988
2021-10-05 | 16:51 | 49.984
2021-10-05 | 16:51 | 49.98
2021-10-05 | 16:51 | 49.974
2021-10-05 | 16:51 | 49.972
2021-10-05 | 16:51 | 49.971
2021-10-05 | 16:51 | 49.97
2021-10-05 | 16:51 | 49.971
2021-10-05 | 16:51 | 49.939
2021-10-05 | 16:51 | 49.914
2021-10-05 | 16:51 | 49.893
2021-10-05 | 16:51 | 49.879
2021-10-05 | 16:51 | 49.874
2021-10-05 | 16:51 | 49.87
2021-10-05 | 16:51 | 49.871
2021-10-05 | 16:51 | 49.875
2021-10-05 | 16:51 | 49.875
2021-10-05 | 16:51 | 49.877
2021-10-05 | 16:51 | 49.879
2021-10-05 | 16:52 | 49.885
2021-10-05 | 16:52 | 49.887
2021-10-05 | 16:52 | 49.885
2021-10-05 | 16:52 | 49.888
2021-10-05 | 16:52 | 49.888
2021-10-05 | 16:52 | 49.886
2021-10-05 | 16:52 | 49.887
2021-10-05 | 16:52 | 49.883
2021-10-05 | 16:52 | 49.881
2021-10-05 | 16:52 | 49.876
2021-10-05 | 16:52 | 49.875
2021-10-05 | 16:52 | 49.877
2021-10-05 | 16:52 | 49.88
2021-10-05 | 16:52 | 49.879
2021-10-05 | 16:52 | 49.879
2021-10-05 | 16:52 | 49.882
2021-10-05 | 16:52 | 49.885
2021-10-05 | 16:52 | 49.886
2021-10-05 | 16:52 | 49.889
2021-10-05 | 16:52 | 49.892
2021-10-05 | 16:52 | 49.895
2021-10-05 | 16:52 | 49.9
2021-10-05 | 16:52 | 49.905
2021-10-05 | 16:52 | 49.905
2021-10-05 | 16:52 | 49.903
2021-10-05 | 16:52 | 49.904
2021-10-05 | 16:52 | 49.903
2021-10-05 | 16:52 | 49.9
2021-10-05 | 16:52 | 49.896
2021-10-05 | 16:52 | 49.893
2021-10-05 | 16:52 | 49.89
2021-10-05 | 16:52 | 49.888
2021-10-05 | 16:52 | 49.886
2021-10-05 | 16:52 | 49.887
2021-10-05 | 16:52 | 49.888
2021-10-05 | 16:52 | 49.891
2021-10-05 | 16:52 | 49.891
2021-10-05 | 16:52 | 49.892
2021-10-05 | 16:52 | 49.89
2021-10-05 | 16:52 | 49.892
2021-10-05 | 16:52 | 49.891
2021-10-05 | 16:52 | 49.892
2021-10-05 | 16:52 | 49.891
2021-10-05 | 16:52 | 49.892
2021-10-05 | 16:52 | 49.891
2021-10-05 | 16:52 | 49.891
2021-10-05 | 16:52 | 49.891
2021-10-05 | 16:52 | 49.888
2021-10-05 | 16:52 | 49.888
2021-10-05 | 16:52 | 49.887
2021-10-05 | 16:52 | 49.883
2021-10-05 | 16:52 | 49.882
2021-10-05 | 16:52 | 49.88
2021-10-05 | 16:52 | 49.879
2021-10-05 | 16:52 | 49.88
2021-10-05 | 16:52 | 49.88
2021-10-05 | 16:52 | 49.88
2021-10-05 | 16:52 | 49.88
2021-10-05 | 16:52 | 49.877
2021-10-05 | 16:52 | 49.876
2021-10-05 | 16:52 | 49.875
2021-10-05 | 16:53 | 49.873
2021-10-05 | 16:53 | 49.878
2021-10-05 | 16:53 | 49.877
2021-10-05 | 16:53 | 49.881
2021-10-05 | 16:53 | 49.884
2021-10-05 | 16:53 | 49.887
2021-10-05 | 16:53 | 49.887
2021-10-05 | 16:53 | 49.881
2021-10-05 | 16:53 | 49.877
2021-10-05 | 16:53 | 49.877
2021-10-05 | 16:53 | 49.879
2021-10-05 | 16:53 | 49.88
2021-10-05 | 16:53 | 49.88
2021-10-05 | 16:53 | 49.881
2021-10-05 | 16:53 | 49.88
2021-10-05 | 16:53 | 49.88
2021-10-05 | 16:53 | 49.88
2021-10-05 | 16:53 | 49.883
2021-10-05 | 16:53 | 49.883
2021-10-05 | 16:53 | 49.879
2021-10-05 | 16:53 | 49.879
2021-10-05 | 16:53 | 49.879
2021-10-05 | 16:53 | 49.881
2021-10-05 | 16:53 | 49.883
2021-10-05 | 16:53 | 49.885
2021-10-05 | 16:53 | 49.882
2021-10-05 | 16:53 | 49.877
2021-10-05 | 16:53 | 49.88
2021-10-05 | 16:53 | 49.878
2021-10-05 | 16:53 | 49.88
2021-10-05 | 16:53 | 49.876
2021-10-05 | 16:53 | 49.876
2021-10-05 | 16:53 | 49.876
2021-10-05 | 16:53 | 49.875
2021-10-05 | 16:53 | 49.874
2021-10-05 | 16:53 | 49.875
2021-10-05 | 16:53 | 49.875
2021-10-05 | 16:53 | 49.873
2021-10-05 | 16:53 | 49.869
2021-10-05 | 16:53 | 49.866
2021-10-05 | 16:53 | 49.865
2021-10-05 | 16:53 | 49.865
2021-10-05 | 16:53 | 49.864
2021-10-05 | 16:53 | 49.867
2021-10-05 | 16:53 | 49.868
2021-10-05 | 16:53 | 49.871
2021-10-05 | 16:53 | 49.875
2021-10-05 | 16:53 | 49.878
2021-10-05 | 16:53 | 49.883
2021-10-05 | 16:53 | 49.884
2021-10-05 | 16:53 | 49.886
2021-10-05 | 16:53 | 49.887
2021-10-05 | 16:53 | 49.895
2021-10-05 | 16:53 | 49.894
2021-10-05 | 16:53 | 49.896
2021-10-05 | 16:53 | 49.898
2021-10-05 | 16:53 | 49.898
2021-10-05 | 16:53 | 49.897
2021-10-05 | 16:53 | 49.896
2021-10-05 | 16:54 | 49.894
2021-10-05 | 16:54 | 49.892
2021-10-05 | 16:54 | 49.891
2021-10-05 | 16:54 | 49.892
2021-10-05 | 16:54 | 49.891
2021-10-05 | 16:54 | 49.89
2021-10-05 | 16:54 | 49.886
2021-10-05 | 16:54 | 49.884
2021-10-05 | 16:54 | 49.883
2021-10-05 | 16:54 | 49.881
2021-10-05 | 16:54 | 49.884
2021-10-05 | 16:54 | 49.884
2021-10-05 | 16:54 | 49.881
2021-10-05 | 16:54 | 49.881
2021-10-05 | 16:54 | 49.879
2021-10-05 | 16:54 | 49.876
2021-10-05 | 16:54 | 49.875
2021-10-05 | 16:54 | 49.877
2021-10-05 | 16:54 | 49.881
2021-10-05 | 16:54 | 49.885
2021-10-05 | 16:54 | 49.889
2021-10-05 | 16:54 | 49.888
2021-10-05 | 16:54 | 49.889
2021-10-05 | 16:54 | 49.89
2021-10-05 | 16:54 | 49.887
2021-10-05 | 16:54 | 49.881
2021-10-05 | 16:54 | 49.881
2021-10-05 | 16:54 | 49.879
2021-10-05 | 16:54 | 49.881
2021-10-05 | 16:54 | 49.88
2021-10-05 | 16:54 | 49.879
2021-10-05 | 16:54 | 49.876
2021-10-05 | 16:54 | 49.875
2021-10-05 | 16:54 | 49.874
2021-10-05 | 16:54 | 49.872
2021-10-05 | 16:54 | 49.87
2021-10-05 | 16:54 | 49.872
2021-10-05 | 16:54 | 49.872
2021-10-05 | 16:54 | 49.873
2021-10-05 | 16:54 | 49.872
2021-10-05 | 16:54 | 49.87
2021-10-05 | 16:54 | 49.867
2021-10-05 | 16:54 | 49.864
2021-10-05 | 16:54 | 49.864
2021-10-05 | 16:54 | 49.866
2021-10-05 | 16:54 | 49.869
2021-10-05 | 16:54 | 49.873
2021-10-05 | 16:54 | 49.878
2021-10-05 | 16:54 | 49.881
2021-10-05 | 16:54 | 49.882
2021-10-05 | 16:54 | 49.884
2021-10-05 | 16:54 | 49.886
2021-10-05 | 16:54 | 49.884
2021-10-05 | 16:54 | 49.881
2021-10-05 | 16:54 | 49.88
2021-10-05 | 16:54 | 49.879
2021-10-05 | 16:54 | 49.877
2021-10-05 | 16:54 | 49.876
2021-10-05 | 16:54 | 49.876
2021-10-05 | 16:54 | 49.876
2021-10-05 | 16:55 | 49.88
2021-10-05 | 16:55 | 49.883
2021-10-05 | 16:55 | 49.886
2021-10-05 | 16:55 | 49.89
2021-10-05 | 16:55 | 49.894
2021-10-05 | 16:55 | 49.894
2021-10-05 | 16:55 | 49.897
2021-10-05 | 16:55 | 49.895
2021-10-05 | 16:55 | 49.896
2021-10-05 | 16:55 | 49.895
2021-10-05 | 16:55 | 49.898
2021-10-05 | 16:55 | 49.903
2021-10-05 | 16:55 | 49.908
2021-10-05 | 16:55 | 49.914
2021-10-05 | 16:55 | 49.92
2021-10-05 | 16:55 | 49.925
2021-10-05 | 16:55 | 49.928
2021-10-05 | 16:55 | 49.93
2021-10-05 | 16:55 | 49.931
2021-10-05 | 16:55 | 49.928
2021-10-05 | 16:55 | 49.927
2021-10-05 | 16:55 | 49.926
2021-10-05 | 16:55 | 49.923
2021-10-05 | 16:55 | 49.921
2021-10-05 | 16:55 | 49.917
2021-10-05 | 16:55 | 49.914
2021-10-05 | 16:55 | 49.912
2021-10-05 | 16:55 | 49.911
2021-10-05 | 16:55 | 49.91
2021-10-05 | 16:55 | 49.909
2021-10-05 | 16:55 | 49.91
2021-10-05 | 16:55 | 49.909
2021-10-05 | 16:55 | 49.909
2021-10-05 | 16:55 | 49.909
2021-10-05 | 16:55 | 49.909
2021-10-05 | 16:55 | 49.909
2021-10-05 | 16:55 | 49.91
2021-10-05 | 16:55 | 49.912
2021-10-05 | 16:55 | 49.91
2021-10-05 | 16:55 | 49.909
2021-10-05 | 16:55 | 49.912
2021-10-05 | 16:55 | 49.914
2021-10-05 | 16:55 | 49.916
2021-10-05 | 16:55 | 49.918
2021-10-05 | 16:55 | 49.917
2021-10-05 | 16:55 | 49.917
2021-10-05 | 16:55 | 49.914
2021-10-05 | 16:55 | 49.913
2021-10-05 | 16:55 | 49.914
2021-10-05 | 16:55 | 49.915
2021-10-05 | 16:55 | 49.914
2021-10-05 | 16:55 | 49.913
2021-10-05 | 16:55 | 49.912
2021-10-05 | 16:55 | 49.913
2021-10-05 | 16:55 | 49.914
2021-10-05 | 16:55 | 49.914
2021-10-05 | 16:55 | 49.917
2021-10-05 | 16:55 | 49.921
2021-10-05 | 16:55 | 49.926
2021-10-05 | 16:55 | 49.931
2021-10-05 | 16:56 | 49.934
2021-10-05 | 16:56 | 49.935
2021-10-05 | 16:56 | 49.936
2021-10-05 | 16:56 | 49.938
2021-10-05 | 16:56 | 49.936
2021-10-05 | 16:56 | 49.932
2021-10-05 | 16:56 | 49.929
2021-10-05 | 16:56 | 49.928
2021-10-05 | 16:56 | 49.927
2021-10-05 | 16:56 | 49.928
2021-10-05 | 16:56 | 49.929
2021-10-05 | 16:56 | 49.928
2021-10-05 | 16:56 | 49.928
2021-10-05 | 16:56 | 49.93
2021-10-05 | 16:56 | 49.932
2021-10-05 | 16:56 | 49.932
2021-10-05 | 16:56 | 49.931
2021-10-05 | 16:56 | 49.928
2021-10-05 | 16:56 | 49.927
2021-10-05 | 16:56 | 49.925
2021-10-05 | 16:56 | 49.925
2021-10-05 | 16:56 | 49.927
2021-10-05 | 16:56 | 49.929
2021-10-05 | 16:56 | 49.931
2021-10-05 | 16:56 | 49.935
2021-10-05 | 16:56 | 49.937
2021-10-05 | 16:56 | 49.937
2021-10-05 | 16:56 | 49.936
2021-10-05 | 16:56 | 49.931
2021-10-05 | 16:56 | 49.927
2021-10-05 | 16:56 | 49.924
2021-10-05 | 16:56 | 49.918
2021-10-05 | 16:56 | 49.913
2021-10-05 | 16:56 | 49.912
2021-10-05 | 16:56 | 49.91
2021-10-05 | 16:56 | 49.906
2021-10-05 | 16:56 | 49.906
2021-10-05 | 16:56 | 49.906
2021-10-05 | 16:56 | 49.905
2021-10-05 | 16:56 | 49.901
2021-10-05 | 16:56 | 49.897
2021-10-05 | 16:56 | 49.896
2021-10-05 | 16:56 | 49.896
2021-10-05 | 16:56 | 49.896
2021-10-05 | 16:56 | 49.897
2021-10-05 | 16:56 | 49.897
2021-10-05 | 16:56 | 49.897
2021-10-05 | 16:56 | 49.9
2021-10-05 | 16:56 | 49.901
2021-10-05 | 16:56 | 49.903
2021-10-05 | 16:56 | 49.906
2021-10-05 | 16:56 | 49.904
2021-10-05 | 16:56 | 49.903
2021-10-05 | 16:56 | 49.9
2021-10-05 | 16:56 | 49.903
2021-10-05 | 16:56 | 49.904
2021-10-05 | 16:56 | 49.906
2021-10-05 | 16:56 | 49.908
2021-10-05 | 16:56 | 49.907
2021-10-05 | 16:56 | 49.906
2021-10-05 | 16:56 | 49.903
2021-10-05 | 16:57 | 49.897
2021-10-05 | 16:57 | 49.891
2021-10-05 | 16:57 | 49.886
2021-10-05 | 16:57 | 49.885
2021-10-05 | 16:57 | 49.885
2021-10-05 | 16:57 | 49.888
2021-10-05 | 16:57 | 49.894
2021-10-05 | 16:57 | 49.904
2021-10-05 | 16:57 | 49.914
2021-10-05 | 16:57 | 49.921
2021-10-05 | 16:57 | 49.929
2021-10-05 | 16:57 | 49.936
2021-10-05 | 16:57 | 49.944
2021-10-05 | 16:57 | 49.953
2021-10-05 | 16:57 | 49.962
2021-10-05 | 16:57 | 49.968
2021-10-05 | 16:57 | 49.971
2021-10-05 | 16:57 | 49.973
2021-10-05 | 16:57 | 49.968
2021-10-05 | 16:57 | 49.968
2021-10-05 | 16:57 | 49.966
2021-10-05 | 16:57 | 49.961
2021-10-05 | 16:57 | 49.957
2021-10-05 | 16:57 | 49.95
2021-10-05 | 16:57 | 49.946
2021-10-05 | 16:57 | 49.943
2021-10-05 | 16:57 | 49.939
2021-10-05 | 16:57 | 49.937
2021-10-05 | 16:57 | 49.935
2021-10-05 | 16:57 | 49.936
2021-10-05 | 16:57 | 49.935
2021-10-05 | 16:57 | 49.934
2021-10-05 | 16:57 | 49.935
2021-10-05 | 16:57 | 49.937
2021-10-05 | 16:57 | 49.942
2021-10-05 | 16:57 | 49.946
2021-10-05 | 16:57 | 49.95
2021-10-05 | 16:57 | 49.954
2021-10-05 | 16:57 | 49.956
2021-10-05 | 16:57 | 49.96
2021-10-05 | 16:57 | 49.96
2021-10-05 | 16:57 | 49.959
2021-10-05 | 16:57 | 49.959
2021-10-05 | 16:57 | 49.956
2021-10-05 | 16:57 | 49.956
2021-10-05 | 16:57 | 49.956
2021-10-05 | 16:57 | 49.957
2021-10-05 | 16:57 | 49.953
2021-10-05 | 16:57 | 49.95
2021-10-05 | 16:57 | 49.948
2021-10-05 | 16:57 | 49.947
2021-10-05 | 16:57 | 49.942
2021-10-05 | 16:57 | 49.943
2021-10-05 | 16:57 | 49.947
2021-10-05 | 16:57 | 49.951
2021-10-05 | 16:57 | 49.956
2021-10-05 | 16:57 | 49.959
2021-10-05 | 16:57 | 49.964
2021-10-05 | 16:57 | 49.964
2021-10-05 | 16:58 | 49.964
2021-10-05 | 16:58 | 49.965
2021-10-05 | 16:58 | 49.962
2021-10-05 | 16:58 | 49.963
2021-10-05 | 16:58 | 49.966
2021-10-05 | 16:58 | 49.967
2021-10-05 | 16:58 | 49.973
2021-10-05 | 16:58 | 49.975
2021-10-05 | 16:58 | 49.981
2021-10-05 | 16:58 | 49.981
2021-10-05 | 16:58 | 49.983
2021-10-05 | 16:58 | 49.981
2021-10-05 | 16:58 | 49.982
2021-10-05 | 16:58 | 49.979
2021-10-05 | 16:58 | 49.977
2021-10-05 | 16:58 | 49.975
2021-10-05 | 16:58 | 49.973
2021-10-05 | 16:58 | 49.971
2021-10-05 | 16:58 | 49.969
2021-10-05 | 16:58 | 49.972
2021-10-05 | 16:58 | 49.968
2021-10-05 | 16:58 | 49.969
2021-10-05 | 16:58 | 49.97
2021-10-05 | 16:58 | 49.974
2021-10-05 | 16:58 | 49.978
2021-10-05 | 16:58 | 49.982
2021-10-05 | 16:58 | 49.989
2021-10-05 | 16:58 | 49.991
2021-10-05 | 16:58 | 49.992
2021-10-05 | 16:58 | 49.993
2021-10-05 | 16:58 | 49.993
2021-10-05 | 16:58 | 49.989
2021-10-05 | 16:58 | 49.985
2021-10-05 | 16:58 | 49.979
2021-10-05 | 16:58 | 49.973
2021-10-05 | 16:58 | 49.968
2021-10-05 | 16:58 | 49.965
2021-10-05 | 16:58 | 49.966
2021-10-05 | 16:58 | 49.965
2021-10-05 | 16:58 | 49.965
2021-10-05 | 16:58 | 49.965
2021-10-05 | 16:58 | 49.967
2021-10-05 | 16:58 | 49.966
2021-10-05 | 16:58 | 49.965
2021-10-05 | 16:58 | 49.961
2021-10-05 | 16:58 | 49.961
2021-10-05 | 16:58 | 49.96
2021-10-05 | 16:58 | 49.961
2021-10-05 | 16:58 | 49.959
2021-10-05 | 16:58 | 49.958
2021-10-05 | 16:58 | 49.957
2021-10-05 | 16:58 | 49.959
2021-10-05 | 16:58 | 49.964
2021-10-05 | 16:58 | 49.97
2021-10-05 | 16:58 | 49.977
2021-10-05 | 16:58 | 49.981
2021-10-05 | 16:58 | 49.985
2021-10-05 | 16:58 | 49.986
2021-10-05 | 16:58 | 49.987
2021-10-05 | 16:58 | 49.988
2021-10-05 | 16:59 | 49.986
2021-10-05 | 16:59 | 49.984
2021-10-05 | 16:59 | 49.984
2021-10-05 | 16:59 | 49.984
2021-10-05 | 16:59 | 49.985
2021-10-05 | 16:59 | 49.986
2021-10-05 | 16:59 | 49.988
2021-10-05 | 16:59 | 49.987
2021-10-05 | 16:59 | 49.991
2021-10-05 | 16:59 | 49.996
2021-10-05 | 16:59 | 50.002
2021-10-05 | 16:59 | 50.009
2021-10-05 | 16:59 | 50.012
2021-10-05 | 16:59 | 50.016
2021-10-05 | 16:59 | 50.019
2021-10-05 | 16:59 | 50.021
2021-10-05 | 16:59 | 50.021
2021-10-05 | 16:59 | 50.021
2021-10-05 | 16:59 | 50.016
2021-10-05 | 16:59 | 50.012
2021-10-05 | 16:59 | 50.01
2021-10-05 | 16:59 | 50.01
2021-10-05 | 16:59 | 50.01
2021-10-05 | 16:59 | 50.011
2021-10-05 | 16:59 | 50.01
2021-10-05 | 16:59 | 50.01
2021-10-05 | 16:59 | 50.006
2021-10-05 | 16:59 | 50.008
2021-10-05 | 16:59 | 50.008
2021-10-05 | 16:59 | 50.01

## 20211007-1
In GMT
Date | Time | Freq
2021-10-07 | 8:40 | 50.046
2021-10-07 | 8:40 | 50.045
2021-10-07 | 8:40 | 50.044
2021-10-07 | 8:40 | 50.042
2021-10-07 | 8:40 | 50.04
2021-10-07 | 8:40 | 50.039
2021-10-07 | 8:40 | 50.034
2021-10-07 | 8:40 | 50.031
2021-10-07 | 8:40 | 50.028
2021-10-07 | 8:40 | 50.027
2021-10-07 | 8:40 | 50.025
2021-10-07 | 8:40 | 50.024
2021-10-07 | 8:40 | 50.021
2021-10-07 | 8:40 | 50.019
2021-10-07 | 8:40 | 50.016
2021-10-07 | 8:40 | 50.012
2021-10-07 | 8:40 | 50.01
2021-10-07 | 8:40 | 50.007
2021-10-07 | 8:40 | 50.006
2021-10-07 | 8:40 | 50.008
2021-10-07 | 8:40 | 50.012
2021-10-07 | 8:40 | 50.016
2021-10-07 | 8:40 | 50.02
2021-10-07 | 8:40 | 50.021
2021-10-07 | 8:40 | 50.02
2021-10-07 | 8:40 | 50.019
2021-10-07 | 8:40 | 50.019
2021-10-07 | 8:40 | 50.018
2021-10-07 | 8:40 | 50.019
2021-10-07 | 8:40 | 50.02
2021-10-07 | 8:41 | 50.022
2021-10-07 | 8:41 | 50.024
2021-10-07 | 8:41 | 50.027
2021-10-07 | 8:41 | 50.027
2021-10-07 | 8:41 | 50.03
2021-10-07 | 8:41 | 50.031
2021-10-07 | 8:41 | 50.031
2021-10-07 | 8:41 | 50.027
2021-10-07 | 8:41 | 50.024
2021-10-07 | 8:41 | 50.022
2021-10-07 | 8:41 | 50.021
2021-10-07 | 8:41 | 50.021
2021-10-07 | 8:41 | 50.018
2021-10-07 | 8:41 | 50.022
2021-10-07 | 8:41 | 50.023
2021-10-07 | 8:41 | 50.024
2021-10-07 | 8:41 | 50.025
2021-10-07 | 8:41 | 50.027
2021-10-07 | 8:41 | 50.029
2021-10-07 | 8:41 | 50.028
2021-10-07 | 8:41 | 50.029
2021-10-07 | 8:41 | 50.03
2021-10-07 | 8:41 | 50.03
2021-10-07 | 8:41 | 50.031
2021-10-07 | 8:41 | 50.029
2021-10-07 | 8:41 | 50.027
2021-10-07 | 8:41 | 50.025
2021-10-07 | 8:41 | 50.024
2021-10-07 | 8:41 | 50.021
2021-10-07 | 8:41 | 50.019
2021-10-07 | 8:41 | 50.015
2021-10-07 | 8:41 | 49.992
2021-10-07 | 8:41 | 49.957
2021-10-07 | 8:41 | 49.928
2021-10-07 | 8:41 | 49.904
2021-10-07 | 8:41 | 49.886
2021-10-07 | 8:41 | 49.873
2021-10-07 | 8:41 | 49.867
2021-10-07 | 8:41 | 49.863
2021-10-07 | 8:41 | 49.862
2021-10-07 | 8:41 | 49.864
2021-10-07 | 8:41 | 49.865
2021-10-07 | 8:41 | 49.868
2021-10-07 | 8:41 | 49.873
2021-10-07 | 8:41 | 49.875
2021-10-07 | 8:41 | 49.88
2021-10-07 | 8:41 | 49.881
2021-10-07 | 8:41 | 49.881
2021-10-07 | 8:41 | 49.882
2021-10-07 | 8:41 | 49.879
2021-10-07 | 8:41 | 49.88
2021-10-07 | 8:41 | 49.882
2021-10-07 | 8:41 | 49.884
2021-10-07 | 8:41 | 49.885
2021-10-07 | 8:41 | 49.886
2021-10-07 | 8:41 | 49.883
2021-10-07 | 8:41 | 49.88
2021-10-07 | 8:41 | 49.878
2021-10-07 | 8:41 | 49.876
2021-10-07 | 8:41 | 49.877
2021-10-07 | 8:42 | 49.876
2021-10-07 | 8:42 | 49.878
2021-10-07 | 8:42 | 49.881
2021-10-07 | 8:42 | 49.886
2021-10-07 | 8:42 | 49.888
2021-10-07 | 8:42 | 49.89
2021-10-07 | 8:42 | 49.893
2021-10-07 | 8:42 | 49.894
2021-10-07 | 8:42 | 49.896
2021-10-07 | 8:42 | 49.897
2021-10-07 | 8:42 | 49.897
2021-10-07 | 8:42 | 49.897
2021-10-07 | 8:42 | 49.896
2021-10-07 | 8:42 | 49.894
2021-10-07 | 8:42 | 49.891
2021-10-07 | 8:42 | 49.887
2021-10-07 | 8:42 | 49.884
2021-10-07 | 8:42 | 49.879
2021-10-07 | 8:42 | 49.873
2021-10-07 | 8:42 | 49.873
2021-10-07 | 8:42 | 49.874
2021-10-07 | 8:42 | 49.875
2021-10-07 | 8:42 | 49.875
2021-10-07 | 8:42 | 49.876
2021-10-07 | 8:42 | 49.877
2021-10-07 | 8:42 | 49.874
2021-10-07 | 8:42 | 49.875
2021-10-07 | 8:42 | 49.875
2021-10-07 | 8:42 | 49.875
2021-10-07 | 8:42 | 49.876
2021-10-07 | 8:42 | 49.877
2021-10-07 | 8:42 | 49.876
2021-10-07 | 8:42 | 49.876
2021-10-07 | 8:42 | 49.877
2021-10-07 | 8:42 | 49.877
2021-10-07 | 8:42 | 49.877
2021-10-07 | 8:42 | 49.876
2021-10-07 | 8:42 | 49.874
2021-10-07 | 8:42 | 49.871
2021-10-07 | 8:42 | 49.868
2021-10-07 | 8:42 | 49.862
2021-10-07 | 8:42 | 49.859
2021-10-07 | 8:42 | 49.855
2021-10-07 | 8:42 | 49.853
2021-10-07 | 8:42 | 49.85
2021-10-07 | 8:42 | 49.851
2021-10-07 | 8:42 | 49.851
2021-10-07 | 8:42 | 49.853
2021-10-07 | 8:42 | 49.856
2021-10-07 | 8:42 | 49.863
2021-10-07 | 8:42 | 49.869
2021-10-07 | 8:42 | 49.873
2021-10-07 | 8:42 | 49.874
2021-10-07 | 8:42 | 49.875
2021-10-07 | 8:42 | 49.877
2021-10-07 | 8:42 | 49.879
2021-10-07 | 8:42 | 49.881
2021-10-07 | 8:42 | 49.883
2021-10-07 | 8:42 | 49.884
2021-10-07 | 8:42 | 49.883
2021-10-07 | 8:43 | 49.883
2021-10-07 | 8:43 | 49.885
2021-10-07 | 8:43 | 49.89
2021-10-07 | 8:43 | 49.897
2021-10-07 | 8:43 | 49.903
2021-10-07 | 8:43 | 49.906
2021-10-07 | 8:43 | 49.905
2021-10-07 | 8:43 | 49.905
2021-10-07 | 8:43 | 49.903
2021-10-07 | 8:43 | 49.898
2021-10-07 | 8:43 | 49.895
2021-10-07 | 8:43 | 49.892
2021-10-07 | 8:43 | 49.891
2021-10-07 | 8:43 | 49.892
2021-10-07 | 8:43 | 49.892
2021-10-07 | 8:43 | 49.893
2021-10-07 | 8:43 | 49.893
2021-10-07 | 8:43 | 49.893
2021-10-07 | 8:43 | 49.895
2021-10-07 | 8:43 | 49.896
2021-10-07 | 8:43 | 49.898
2021-10-07 | 8:43 | 49.902
2021-10-07 | 8:43 | 49.906
2021-10-07 | 8:43 | 49.908
2021-10-07 | 8:43 | 49.909
2021-10-07 | 8:43 | 49.911
2021-10-07 | 8:43 | 49.912
2021-10-07 | 8:43 | 49.913
2021-10-07 | 8:43 | 49.913
2021-10-07 | 8:43 | 49.914
2021-10-07 | 8:43 | 49.917
2021-10-07 | 8:43 | 49.918
2021-10-07 | 8:43 | 49.92
2021-10-07 | 8:43 | 49.926
2021-10-07 | 8:43 | 49.932
2021-10-07 | 8:43 | 49.937
2021-10-07 | 8:43 | 49.942
2021-10-07 | 8:43 | 49.945
2021-10-07 | 8:43 | 49.948
2021-10-07 | 8:43 | 49.95
2021-10-07 | 8:43 | 49.954
2021-10-07 | 8:43 | 49.96
2021-10-07 | 8:43 | 49.965
2021-10-07 | 8:43 | 49.972
2021-10-07 | 8:43 | 49.978
2021-10-07 | 8:43 | 49.983
2021-10-07 | 8:43 | 49.984
2021-10-07 | 8:43 | 49.987
2021-10-07 | 8:43 | 49.987
2021-10-07 | 8:43 | 49.989
2021-10-07 | 8:43 | 49.989
2021-10-07 | 8:43 | 49.989
2021-10-07 | 8:43 | 49.989
2021-10-07 | 8:43 | 49.986
2021-10-07 | 8:43 | 49.982
2021-10-07 | 8:43 | 49.978
2021-10-07 | 8:43 | 49.977
2021-10-07 | 8:43 | 49.976
2021-10-07 | 8:43 | 49.978
2021-10-07 | 8:43 | 49.979
2021-10-07 | 8:44 | 49.983
2021-10-07 | 8:44 | 49.986
2021-10-07 | 8:44 | 49.988
2021-10-07 | 8:44 | 49.995
2021-10-07 | 8:44 | 50.001
2021-10-07 | 8:44 | 50.008
2021-10-07 | 8:44 | 50.014
2021-10-07 | 8:44 | 50.021
2021-10-07 | 8:44 | 50.025
2021-10-07 | 8:44 | 50.03
2021-10-07 | 8:44 | 50.033
2021-10-07 | 8:44 | 50.032
2021-10-07 | 8:44 | 50.032
2021-10-07 | 8:44 | 50.029
2021-10-07 | 8:44 | 50.029
2021-10-07 | 8:44 | 50.03
2021-10-07 | 8:44 | 50.033
2021-10-07 | 8:44 | 50.033
2021-10-07 | 8:44 | 50.031
2021-10-07 | 8:44 | 50.028
2021-10-07 | 8:44 | 50.027
2021-10-07 | 8:44 | 50.027
2021-10-07 | 8:44 | 50.024
2021-10-07 | 8:44 | 50.023
2021-10-07 | 8:44 | 50.023
2021-10-07 | 8:44 | 50.023
2021-10-07 | 8:44 | 50.022
2021-10-07 | 8:44 | 50.019
2021-10-07 | 8:44 | 50.017
2021-10-07 | 8:44 | 50.015

## 20211012-1
In GMT
Date | Time | Freq
2021-10-12 | 3:25 | 50.048
2021-10-12 | 3:25 | 50.048
2021-10-12 | 3:25 | 50.049
2021-10-12 | 3:25 | 50.049
2021-10-12 | 3:25 | 50.051
2021-10-12 | 3:25 | 50.051
2021-10-12 | 3:25 | 50.05
2021-10-12 | 3:25 | 50.049
2021-10-12 | 3:25 | 50.048
2021-10-12 | 3:25 | 50.046
2021-10-12 | 3:25 | 50.044
2021-10-12 | 3:25 | 50.044
2021-10-12 | 3:25 | 50.044
2021-10-12 | 3:25 | 50.044
2021-10-12 | 3:25 | 50.043
2021-10-12 | 3:25 | 50.04
2021-10-12 | 3:25 | 50.038
2021-10-12 | 3:25 | 50.034
2021-10-12 | 3:25 | 50.03
2021-10-12 | 3:25 | 50.027
2021-10-12 | 3:25 | 50.025
2021-10-12 | 3:25 | 50.027
2021-10-12 | 3:25 | 50.03
2021-10-12 | 3:25 | 50.032
2021-10-12 | 3:25 | 50.033
2021-10-12 | 3:25 | 50.031
2021-10-12 | 3:25 | 50.03
2021-10-12 | 3:25 | 50.028
2021-10-12 | 3:25 | 50.028
2021-10-12 | 3:25 | 50.027
2021-10-12 | 3:26 | 50.026
2021-10-12 | 3:26 | 50.027
2021-10-12 | 3:26 | 50.029
2021-10-12 | 3:26 | 50.029
2021-10-12 | 3:26 | 50.03
2021-10-12 | 3:26 | 50.03
2021-10-12 | 3:26 | 50.029
2021-10-12 | 3:26 | 50.028
2021-10-12 | 3:26 | 50.025
2021-10-12 | 3:26 | 50.024
2021-10-12 | 3:26 | 50.024
2021-10-12 | 3:26 | 50.025
2021-10-12 | 3:26 | 50.025
2021-10-12 | 3:26 | 50.024
2021-10-12 | 3:26 | 50.023
2021-10-12 | 3:26 | 50.022
2021-10-12 | 3:26 | 50.021
2021-10-12 | 3:26 | 50.019
2021-10-12 | 3:26 | 50.015
2021-10-12 | 3:26 | 50.01
2021-10-12 | 3:26 | 50.007
2021-10-12 | 3:26 | 50.003
2021-10-12 | 3:26 | 49.999
2021-10-12 | 3:26 | 49.998
2021-10-12 | 3:26 | 49.997
2021-10-12 | 3:26 | 49.994
2021-10-12 | 3:26 | 49.992
2021-10-12 | 3:26 | 49.989
2021-10-12 | 3:26 | 49.986
2021-10-12 | 3:26 | 49.982
2021-10-12 | 3:26 | 49.981
2021-10-12 | 3:26 | 49.975
2021-10-12 | 3:26 | 49.972
2021-10-12 | 3:26 | 49.97
2021-10-12 | 3:26 | 49.967
2021-10-12 | 3:26 | 49.966
2021-10-12 | 3:26 | 49.965
2021-10-12 | 3:26 | 49.964
2021-10-12 | 3:26 | 49.963
2021-10-12 | 3:26 | 49.962
2021-10-12 | 3:26 | 49.962
2021-10-12 | 3:26 | 49.963
2021-10-12 | 3:26 | 49.965
2021-10-12 | 3:26 | 49.968
2021-10-12 | 3:26 | 49.972
2021-10-12 | 3:26 | 49.976
2021-10-12 | 3:26 | 49.977
2021-10-12 | 3:26 | 49.978
2021-10-12 | 3:26 | 49.978
2021-10-12 | 3:26 | 49.977
2021-10-12 | 3:26 | 49.977
2021-10-12 | 3:26 | 49.975
2021-10-12 | 3:26 | 49.973
2021-10-12 | 3:26 | 49.97
2021-10-12 | 3:26 | 49.967
2021-10-12 | 3:26 | 49.965
2021-10-12 | 3:26 | 49.963
2021-10-12 | 3:26 | 49.963
2021-10-12 | 3:26 | 49.962
2021-10-12 | 3:26 | 49.961
2021-10-12 | 3:26 | 49.96
2021-10-12 | 3:27 | 49.958
2021-10-12 | 3:27 | 49.956
2021-10-12 | 3:27 | 49.955
2021-10-12 | 3:27 | 49.956
2021-10-12 | 3:27 | 49.956
2021-10-12 | 3:27 | 49.956
2021-10-12 | 3:27 | 49.954
2021-10-12 | 3:27 | 49.952
2021-10-12 | 3:27 | 49.951
2021-10-12 | 3:27 | 49.952
2021-10-12 | 3:27 | 49.952
2021-10-12 | 3:27 | 49.951
2021-10-12 | 3:27 | 49.952
2021-10-12 | 3:27 | 49.951
2021-10-12 | 3:27 | 49.932
2021-10-12 | 3:27 | 49.915
2021-10-12 | 3:27 | 49.902
2021-10-12 | 3:27 | 49.895
2021-10-12 | 3:27 | 49.892
2021-10-12 | 3:27 | 49.892
2021-10-12 | 3:27 | 49.893
2021-10-12 | 3:27 | 49.895
2021-10-12 | 3:27 | 49.896
2021-10-12 | 3:27 | 49.896
2021-10-12 | 3:27 | 49.895
2021-10-12 | 3:27 | 49.896
2021-10-12 | 3:27 | 49.896
2021-10-12 | 3:27 | 49.899
2021-10-12 | 3:27 | 49.901
2021-10-12 | 3:27 | 49.905
2021-10-12 | 3:27 | 49.907
2021-10-12 | 3:27 | 49.909
2021-10-12 | 3:27 | 49.911
2021-10-12 | 3:27 | 49.913
2021-10-12 | 3:27 | 49.915
2021-10-12 | 3:27 | 49.918
2021-10-12 | 3:27 | 49.919
2021-10-12 | 3:27 | 49.92
2021-10-12 | 3:27 | 49.923
2021-10-12 | 3:27 | 49.927
2021-10-12 | 3:27 | 49.928
2021-10-12 | 3:27 | 49.927
2021-10-12 | 3:27 | 49.926
2021-10-12 | 3:27 | 49.926
2021-10-12 | 3:27 | 49.927
2021-10-12 | 3:27 | 49.926
2021-10-12 | 3:27 | 49.926
2021-10-12 | 3:27 | 49.925
2021-10-12 | 3:27 | 49.924
2021-10-12 | 3:27 | 49.925
2021-10-12 | 3:27 | 49.925
2021-10-12 | 3:27 | 49.924
2021-10-12 | 3:27 | 49.923
2021-10-12 | 3:27 | 49.922
2021-10-12 | 3:27 | 49.921
2021-10-12 | 3:27 | 49.919
2021-10-12 | 3:27 | 49.917
2021-10-12 | 3:27 | 49.916
2021-10-12 | 3:27 | 49.916
2021-10-12 | 3:28 | 49.918
2021-10-12 | 3:28 | 49.917
2021-10-12 | 3:28 | 49.916
2021-10-12 | 3:28 | 49.916
2021-10-12 | 3:28 | 49.919
2021-10-12 | 3:28 | 49.919
2021-10-12 | 3:28 | 49.92
2021-10-12 | 3:28 | 49.92
2021-10-12 | 3:28 | 49.921
2021-10-12 | 3:28 | 49.921
2021-10-12 | 3:28 | 49.92
2021-10-12 | 3:28 | 49.92
2021-10-12 | 3:28 | 49.923
2021-10-12 | 3:28 | 49.925
2021-10-12 | 3:28 | 49.927
2021-10-12 | 3:28 | 49.927
2021-10-12 | 3:28 | 49.931
2021-10-12 | 3:28 | 49.932
2021-10-12 | 3:28 | 49.932
2021-10-12 | 3:28 | 49.93
2021-10-12 | 3:28 | 49.928
2021-10-12 | 3:28 | 49.926
2021-10-12 | 3:28 | 49.923
2021-10-12 | 3:28 | 49.921
2021-10-12 | 3:28 | 49.921
2021-10-12 | 3:28 | 49.92
2021-10-12 | 3:28 | 49.918
2021-10-12 | 3:28 | 49.915
2021-10-12 | 3:28 | 49.915
2021-10-12 | 3:28 | 49.913
2021-10-12 | 3:28 | 49.911
2021-10-12 | 3:28 | 49.906
2021-10-12 | 3:28 | 49.902
2021-10-12 | 3:28 | 49.899
2021-10-12 | 3:28 | 49.902
2021-10-12 | 3:28 | 49.903
2021-10-12 | 3:28 | 49.904
2021-10-12 | 3:28 | 49.905
2021-10-12 | 3:28 | 49.905
2021-10-12 | 3:28 | 49.906
2021-10-12 | 3:28 | 49.906
2021-10-12 | 3:28 | 49.904
2021-10-12 | 3:28 | 49.903
2021-10-12 | 3:28 | 49.904
2021-10-12 | 3:28 | 49.906
2021-10-12 | 3:28 | 49.908
2021-10-12 | 3:28 | 49.91
2021-10-12 | 3:28 | 49.911
2021-10-12 | 3:28 | 49.911
2021-10-12 | 3:28 | 49.913
2021-10-12 | 3:28 | 49.913
2021-10-12 | 3:28 | 49.911
2021-10-12 | 3:28 | 49.909
2021-10-12 | 3:28 | 49.905
2021-10-12 | 3:28 | 49.903
2021-10-12 | 3:28 | 49.9
2021-10-12 | 3:28 | 49.897
2021-10-12 | 3:28 | 49.895
2021-10-12 | 3:28 | 49.895
2021-10-12 | 3:28 | 49.895
2021-10-12 | 3:29 | 49.895
2021-10-12 | 3:29 | 49.894
2021-10-12 | 3:29 | 49.893
2021-10-12 | 3:29 | 49.893
2021-10-12 | 3:29 | 49.894
2021-10-12 | 3:29 | 49.894
2021-10-12 | 3:29 | 49.894
2021-10-12 | 3:29 | 49.894
2021-10-12 | 3:29 | 49.893
2021-10-12 | 3:29 | 49.894
2021-10-12 | 3:29 | 49.894
2021-10-12 | 3:29 | 49.892
2021-10-12 | 3:29 | 49.89
2021-10-12 | 3:29 | 49.889
2021-10-12 | 3:29 | 49.887
2021-10-12 | 3:29 | 49.887
2021-10-12 | 3:29 | 49.887
2021-10-12 | 3:29 | 49.886
2021-10-12 | 3:29 | 49.884
2021-10-12 | 3:29 | 49.886
2021-10-12 | 3:29 | 49.887
2021-10-12 | 3:29 | 49.89
2021-10-12 | 3:29 | 49.891
2021-10-12 | 3:29 | 49.893
2021-10-12 | 3:29 | 49.891
2021-10-12 | 3:29 | 49.883
2021-10-12 | 3:29 | 49.882
2021-10-12 | 3:29 | 49.882
2021-10-12 | 3:29 | 49.882
2021-10-12 | 3:29 | 49.884
2021-10-12 | 3:29 | 49.886
2021-10-12 | 3:29 | 49.887
2021-10-12 | 3:29 | 49.887
2021-10-12 | 3:29 | 49.888
2021-10-12 | 3:29 | 49.89
2021-10-12 | 3:29 | 49.891
2021-10-12 | 3:29 | 49.891
2021-10-12 | 3:29 | 49.891
2021-10-12 | 3:29 | 49.891
2021-10-12 | 3:29 | 49.892
2021-10-12 | 3:29 | 49.891
2021-10-12 | 3:29 | 49.889
2021-10-12 | 3:29 | 49.888
2021-10-12 | 3:29 | 49.886
2021-10-12 | 3:29 | 49.886
2021-10-12 | 3:29 | 49.886
2021-10-12 | 3:29 | 49.887
2021-10-12 | 3:29 | 49.887
2021-10-12 | 3:29 | 49.886
2021-10-12 | 3:29 | 49.886
2021-10-12 | 3:29 | 49.886
2021-10-12 | 3:29 | 49.888
2021-10-12 | 3:29 | 49.886
2021-10-12 | 3:29 | 49.887
2021-10-12 | 3:29 | 49.885
2021-10-12 | 3:29 | 49.884
2021-10-12 | 3:29 | 49.882
2021-10-12 | 3:29 | 49.879
2021-10-12 | 3:29 | 49.878
2021-10-12 | 3:29 | 49.875
2021-10-12 | 3:30 | 49.873
2021-10-12 | 3:30 | 49.872
2021-10-12 | 3:30 | 49.873
2021-10-12 | 3:30 | 49.873
2021-10-12 | 3:30 | 49.872
2021-10-12 | 3:30 | 49.873
2021-10-12 | 3:30 | 49.874
2021-10-12 | 3:30 | 49.874
2021-10-12 | 3:30 | 49.876
2021-10-12 | 3:30 | 49.877
2021-10-12 | 3:30 | 49.88
2021-10-12 | 3:30 | 49.883
2021-10-12 | 3:30 | 49.884
2021-10-12 | 3:30 | 49.887
2021-10-12 | 3:30 | 49.888
2021-10-12 | 3:30 | 49.888
2021-10-12 | 3:30 | 49.887
2021-10-12 | 3:30 | 49.887
2021-10-12 | 3:30 | 49.885
2021-10-12 | 3:30 | 49.886
2021-10-12 | 3:30 | 49.884
2021-10-12 | 3:30 | 49.883
2021-10-12 | 3:30 | 49.884
2021-10-12 | 3:30 | 49.883
2021-10-12 | 3:30 | 49.884
2021-10-12 | 3:30 | 49.886
2021-10-12 | 3:30 | 49.886
2021-10-12 | 3:30 | 49.886
2021-10-12 | 3:30 | 49.884
2021-10-12 | 3:30 | 49.885
2021-10-12 | 3:30 | 49.884
2021-10-12 | 3:30 | 49.881
2021-10-12 | 3:30 | 49.878
2021-10-12 | 3:30 | 49.874
2021-10-12 | 3:30 | 49.868
2021-10-12 | 3:30 | 49.867
2021-10-12 | 3:30 | 49.865
2021-10-12 | 3:30 | 49.864
2021-10-12 | 3:30 | 49.862
2021-10-12 | 3:30 | 49.86
2021-10-12 | 3:30 | 49.861
2021-10-12 | 3:30 | 49.861
2021-10-12 | 3:30 | 49.861
2021-10-12 | 3:30 | 49.861
2021-10-12 | 3:30 | 49.86
2021-10-12 | 3:30 | 49.86
2021-10-12 | 3:30 | 49.86
2021-10-12 | 3:30 | 49.861
2021-10-12 | 3:30 | 49.86
2021-10-12 | 3:30 | 49.859
2021-10-12 | 3:30 | 49.858
2021-10-12 | 3:30 | 49.858
2021-10-12 | 3:30 | 49.859
2021-10-12 | 3:30 | 49.857
2021-10-12 | 3:30 | 49.858
2021-10-12 | 3:30 | 49.857
2021-10-12 | 3:30 | 49.857
2021-10-12 | 3:30 | 49.857
2021-10-12 | 3:30 | 49.855
2021-10-12 | 3:30 | 49.855
2021-10-12 | 3:30 | 49.858
2021-10-12 | 3:31 | 49.86
2021-10-12 | 3:31 | 49.863
2021-10-12 | 3:31 | 49.862
2021-10-12 | 3:31 | 49.856
2021-10-12 | 3:31 | 49.855
2021-10-12 | 3:31 | 49.85
2021-10-12 | 3:31 | 49.847
2021-10-12 | 3:31 | 49.842
2021-10-12 | 3:31 | 49.839
2021-10-12 | 3:31 | 49.836
2021-10-12 | 3:31 | 49.837
2021-10-12 | 3:31 | 49.839
2021-10-12 | 3:31 | 49.841
2021-10-12 | 3:31 | 49.843
2021-10-12 | 3:31 | 49.844
2021-10-12 | 3:31 | 49.848
2021-10-12 | 3:31 | 49.85
2021-10-12 | 3:31 | 49.851
2021-10-12 | 3:31 | 49.852
2021-10-12 | 3:31 | 49.854
2021-10-12 | 3:31 | 49.852
2021-10-12 | 3:31 | 49.853
2021-10-12 | 3:31 | 49.853
2021-10-12 | 3:31 | 49.853
2021-10-12 | 3:31 | 49.853
2021-10-12 | 3:31 | 49.855
2021-10-12 | 3:31 | 49.856
2021-10-12 | 3:31 | 49.857
2021-10-12 | 3:31 | 49.857
2021-10-12 | 3:31 | 49.858
2021-10-12 | 3:31 | 49.857
2021-10-12 | 3:31 | 49.857
2021-10-12 | 3:31 | 49.857
2021-10-12 | 3:31 | 49.857
2021-10-12 | 3:31 | 49.859
2021-10-12 | 3:31 | 49.86
2021-10-12 | 3:31 | 49.859
2021-10-12 | 3:31 | 49.861
2021-10-12 | 3:31 | 49.859
2021-10-12 | 3:31 | 49.861
2021-10-12 | 3:31 | 49.859
2021-10-12 | 3:31 | 49.857
2021-10-12 | 3:31 | 49.857
2021-10-12 | 3:31 | 49.855
2021-10-12 | 3:31 | 49.854
2021-10-12 | 3:31 | 49.855
2021-10-12 | 3:31 | 49.855
2021-10-12 | 3:31 | 49.858
2021-10-12 | 3:31 | 49.859
2021-10-12 | 3:31 | 49.861
2021-10-12 | 3:31 | 49.863
2021-10-12 | 3:31 | 49.866
2021-10-12 | 3:31 | 49.867
2021-10-12 | 3:31 | 49.869
2021-10-12 | 3:31 | 49.871
2021-10-12 | 3:31 | 49.874
2021-10-12 | 3:31 | 49.878
2021-10-12 | 3:31 | 49.884
2021-10-12 | 3:31 | 49.889
2021-10-12 | 3:32 | 49.894
2021-10-12 | 3:32 | 49.9
2021-10-12 | 3:32 | 49.91
2021-10-12 | 3:32 | 49.917
2021-10-12 | 3:32 | 49.925
2021-10-12 | 3:32 | 49.929
2021-10-12 | 3:32 | 49.931
2021-10-12 | 3:32 | 49.935
2021-10-12 | 3:32 | 49.938
2021-10-12 | 3:32 | 49.941
2021-10-12 | 3:32 | 49.944
2021-10-12 | 3:32 | 49.948
2021-10-12 | 3:32 | 49.95
2021-10-12 | 3:32 | 49.95
2021-10-12 | 3:32 | 49.949
2021-10-12 | 3:32 | 49.948
2021-10-12 | 3:32 | 49.948
2021-10-12 | 3:32 | 49.949
2021-10-12 | 3:32 | 49.949
2021-10-12 | 3:32 | 49.948
2021-10-12 | 3:32 | 49.946
2021-10-12 | 3:32 | 49.945
2021-10-12 | 3:32 | 49.943
2021-10-12 | 3:32 | 49.941
2021-10-12 | 3:32 | 49.939
2021-10-12 | 3:32 | 49.938
2021-10-12 | 3:32 | 49.94
2021-10-12 | 3:32 | 49.94
2021-10-12 | 3:32 | 49.939
2021-10-12 | 3:32 | 49.937
2021-10-12 | 3:32 | 49.937
2021-10-12 | 3:32 | 49.933
2021-10-12 | 3:32 | 49.929
2021-10-12 | 3:32 | 49.928
2021-10-12 | 3:32 | 49.925
2021-10-12 | 3:32 | 49.926
2021-10-12 | 3:32 | 49.925
2021-10-12 | 3:32 | 49.926
2021-10-12 | 3:32 | 49.924
2021-10-12 | 3:32 | 49.927
2021-10-12 | 3:32 | 49.928
2021-10-12 | 3:32 | 49.931
2021-10-12 | 3:32 | 49.933
2021-10-12 | 3:32 | 49.932
2021-10-12 | 3:32 | 49.934
2021-10-12 | 3:32 | 49.933
2021-10-12 | 3:32 | 49.932
2021-10-12 | 3:32 | 49.93
2021-10-12 | 3:32 | 49.927
2021-10-12 | 3:32 | 49.923
2021-10-12 | 3:32 | 49.92
2021-10-12 | 3:32 | 49.921
2021-10-12 | 3:32 | 49.924
2021-10-12 | 3:32 | 49.927
2021-10-12 | 3:32 | 49.929
2021-10-12 | 3:32 | 49.932
2021-10-12 | 3:32 | 49.936
2021-10-12 | 3:32 | 49.94
2021-10-12 | 3:32 | 49.943
2021-10-12 | 3:32 | 49.946
2021-10-12 | 3:32 | 49.95
2021-10-12 | 3:33 | 49.952
2021-10-12 | 3:33 | 49.953
2021-10-12 | 3:33 | 49.953
2021-10-12 | 3:33 | 49.953
2021-10-12 | 3:33 | 49.953
2021-10-12 | 3:33 | 49.951
2021-10-12 | 3:33 | 49.95
2021-10-12 | 3:33 | 49.948
2021-10-12 | 3:33 | 49.946
2021-10-12 | 3:33 | 49.946
2021-10-12 | 3:33 | 49.947
2021-10-12 | 3:33 | 49.95
2021-10-12 | 3:33 | 49.952
2021-10-12 | 3:33 | 49.954
2021-10-12 | 3:33 | 49.954
2021-10-12 | 3:33 | 49.953
2021-10-12 | 3:33 | 49.95
2021-10-12 | 3:33 | 49.95
2021-10-12 | 3:33 | 49.949
2021-10-12 | 3:33 | 49.95
2021-10-12 | 3:33 | 49.953
2021-10-12 | 3:33 | 49.953
2021-10-12 | 3:33 | 49.953
2021-10-12 | 3:33 | 49.954
2021-10-12 | 3:33 | 49.955
2021-10-12 | 3:33 | 49.957
2021-10-12 | 3:33 | 49.961
2021-10-12 | 3:33 | 49.962
2021-10-12 | 3:33 | 49.962
2021-10-12 | 3:33 | 49.964
2021-10-12 | 3:33 | 49.965
2021-10-12 | 3:33 | 49.968
2021-10-12 | 3:33 | 49.969
2021-10-12 | 3:33 | 49.971
2021-10-12 | 3:33 | 49.971
2021-10-12 | 3:33 | 49.972
2021-10-12 | 3:33 | 49.971
2021-10-12 | 3:33 | 49.97
2021-10-12 | 3:33 | 49.97
2021-10-12 | 3:33 | 49.969
2021-10-12 | 3:33 | 49.969
2021-10-12 | 3:33 | 49.968
2021-10-12 | 3:33 | 49.968
2021-10-12 | 3:33 | 49.967
2021-10-12 | 3:33 | 49.964
2021-10-12 | 3:33 | 49.962
2021-10-12 | 3:33 | 49.958
2021-10-12 | 3:33 | 49.955
2021-10-12 | 3:33 | 49.952
2021-10-12 | 3:33 | 49.952
2021-10-12 | 3:33 | 49.954
2021-10-12 | 3:33 | 49.957
2021-10-12 | 3:33 | 49.96
2021-10-12 | 3:33 | 49.962
2021-10-12 | 3:33 | 49.967
2021-10-12 | 3:33 | 49.967
2021-10-12 | 3:33 | 49.967
2021-10-12 | 3:33 | 49.969
2021-10-12 | 3:33 | 49.968
2021-10-12 | 3:34 | 49.967
2021-10-12 | 3:34 | 49.968
2021-10-12 | 3:34 | 49.97
2021-10-12 | 3:34 | 49.972
2021-10-12 | 3:34 | 49.972
2021-10-12 | 3:34 | 49.972
2021-10-12 | 3:34 | 49.971
2021-10-12 | 3:34 | 49.968
2021-10-12 | 3:34 | 49.966
2021-10-12 | 3:34 | 49.964
2021-10-12 | 3:34 | 49.962
2021-10-12 | 3:34 | 49.961
2021-10-12 | 3:34 | 49.962
2021-10-12 | 3:34 | 49.963
2021-10-12 | 3:34 | 49.966
2021-10-12 | 3:34 | 49.97
2021-10-12 | 3:34 | 49.973
2021-10-12 | 3:34 | 49.975
2021-10-12 | 3:34 | 49.976
2021-10-12 | 3:34 | 49.975
2021-10-12 | 3:34 | 49.974
2021-10-12 | 3:34 | 49.974
2021-10-12 | 3:34 | 49.973
2021-10-12 | 3:34 | 49.973
2021-10-12 | 3:34 | 49.973
2021-10-12 | 3:34 | 49.974
2021-10-12 | 3:34 | 49.974
2021-10-12 | 3:34 | 49.977
2021-10-12 | 3:34 | 49.981
2021-10-12 | 3:34 | 49.985
2021-10-12 | 3:34 | 49.986
2021-10-12 | 3:34 | 49.984
2021-10-12 | 3:34 | 49.985
2021-10-12 | 3:34 | 49.985
2021-10-12 | 3:34 | 49.985
2021-10-12 | 3:34 | 49.985
2021-10-12 | 3:34 | 49.983
2021-10-12 | 3:34 | 49.98
2021-10-12 | 3:34 | 49.978
2021-10-12 | 3:34 | 49.977
2021-10-12 | 3:34 | 49.976
2021-10-12 | 3:34 | 49.973
2021-10-12 | 3:34 | 49.973
2021-10-12 | 3:34 | 49.975
2021-10-12 | 3:34 | 49.979
2021-10-12 | 3:34 | 49.981
2021-10-12 | 3:34 | 49.984
2021-10-12 | 3:34 | 49.987
2021-10-12 | 3:34 | 49.99
2021-10-12 | 3:34 | 49.994
2021-10-12 | 3:34 | 49.996
2021-10-12 | 3:34 | 49.997
2021-10-12 | 3:34 | 49.998
2021-10-12 | 3:34 | 49.997
2021-10-12 | 3:34 | 49.995
2021-10-12 | 3:34 | 49.993
2021-10-12 | 3:34 | 49.994
2021-10-12 | 3:34 | 49.995
2021-10-12 | 3:34 | 49.997
2021-10-12 | 3:34 | 49.999
2021-10-12 | 3:34 | 50.001
2021-10-12 | 3:35 | 50
2021-10-12 | 3:35 | 50.001
2021-10-12 | 3:35 | 50.003
2021-10-12 | 3:35 | 50.005
2021-10-12 | 3:35 | 50.004
2021-10-12 | 3:35 | 50.003
2021-10-12 | 3:35 | 50.004
2021-10-12 | 3:35 | 50.004
2021-10-12 | 3:35 | 50.009
2021-10-12 | 3:35 | 50.01
2021-10-12 | 3:35 | 50.012
2021-10-12 | 3:35 | 50.01
2021-10-12 | 3:35 | 50.011
2021-10-12 | 3:35 | 50.011
2021-10-12 | 3:35 | 50.012
2021-10-12 | 3:35 | 50.011
2021-10-12 | 3:35 | 50.012
2021-10-12 | 3:35 | 50.012
2021-10-12 | 3:35 | 50.014
2021-10-12 | 3:35 | 50.015
2021-10-12 | 3:35 | 50.015
2021-10-12 | 3:35 | 50.017
2021-10-12 | 3:35 | 50.018
2021-10-12 | 3:35 | 50.019
2021-10-12 | 3:35 | 50.019
2021-10-12 | 3:35 | 50.019
2021-10-12 | 3:35 | 50.018
2021-10-12 | 3:35 | 50.018
2021-10-12 | 3:35 | 50.02

## 20211016-1
In GMT
Date | Time | Freq
2021-10-16 | 19:26 | 49.949
2021-10-16 | 19:26 | 49.95
2021-10-16 | 19:26 | 49.95
2021-10-16 | 19:26 | 49.952
2021-10-16 | 19:26 | 49.954
2021-10-16 | 19:26 | 49.957
2021-10-16 | 19:26 | 49.96
2021-10-16 | 19:26 | 49.961
2021-10-16 | 19:26 | 49.963
2021-10-16 | 19:26 | 49.963
2021-10-16 | 19:26 | 49.963
2021-10-16 | 19:26 | 49.961
2021-10-16 | 19:26 | 49.959
2021-10-16 | 19:26 | 49.956
2021-10-16 | 19:26 | 49.952
2021-10-16 | 19:26 | 49.948
2021-10-16 | 19:26 | 49.945
2021-10-16 | 19:26 | 49.943
2021-10-16 | 19:26 | 49.941
2021-10-16 | 19:26 | 49.94
2021-10-16 | 19:26 | 49.938
2021-10-16 | 19:26 | 49.936
2021-10-16 | 19:26 | 49.934
2021-10-16 | 19:26 | 49.933
2021-10-16 | 19:26 | 49.933
2021-10-16 | 19:26 | 49.933
2021-10-16 | 19:26 | 49.936
2021-10-16 | 19:26 | 49.939
2021-10-16 | 19:26 | 49.942
2021-10-16 | 19:26 | 49.942
2021-10-16 | 19:26 | 49.943
2021-10-16 | 19:27 | 49.943
2021-10-16 | 19:27 | 49.944
2021-10-16 | 19:27 | 49.946
2021-10-16 | 19:27 | 49.948
2021-10-16 | 19:27 | 49.949
2021-10-16 | 19:27 | 49.947
2021-10-16 | 19:27 | 49.946
2021-10-16 | 19:27 | 49.943
2021-10-16 | 19:27 | 49.942
2021-10-16 | 19:27 | 49.938
2021-10-16 | 19:27 | 49.935
2021-10-16 | 19:27 | 49.932
2021-10-16 | 19:27 | 49.93
2021-10-16 | 19:27 | 49.929
2021-10-16 | 19:27 | 49.928
2021-10-16 | 19:27 | 49.928
2021-10-16 | 19:27 | 49.928
2021-10-16 | 19:27 | 49.929
2021-10-16 | 19:27 | 49.93
2021-10-16 | 19:27 | 49.932
2021-10-16 | 19:27 | 49.935
2021-10-16 | 19:27 | 49.936
2021-10-16 | 19:27 | 49.94
2021-10-16 | 19:27 | 49.944
2021-10-16 | 19:27 | 49.947
2021-10-16 | 19:27 | 49.952
2021-10-16 | 19:27 | 49.956
2021-10-16 | 19:27 | 49.959
2021-10-16 | 19:27 | 49.959
2021-10-16 | 19:27 | 49.958
2021-10-16 | 19:27 | 49.956
2021-10-16 | 19:27 | 49.954
2021-10-16 | 19:27 | 49.953
2021-10-16 | 19:27 | 49.951
2021-10-16 | 19:27 | 49.948
2021-10-16 | 19:27 | 49.945
2021-10-16 | 19:27 | 49.944
2021-10-16 | 19:27 | 49.943
2021-10-16 | 19:27 | 49.945
2021-10-16 | 19:27 | 49.947
2021-10-16 | 19:27 | 49.948
2021-10-16 | 19:27 | 49.949
2021-10-16 | 19:27 | 49.952
2021-10-16 | 19:27 | 49.954
2021-10-16 | 19:27 | 49.957
2021-10-16 | 19:27 | 49.961
2021-10-16 | 19:27 | 49.964
2021-10-16 | 19:27 | 49.965
2021-10-16 | 19:27 | 49.963
2021-10-16 | 19:27 | 49.962
2021-10-16 | 19:27 | 49.959
2021-10-16 | 19:27 | 49.954
2021-10-16 | 19:27 | 49.891
2021-10-16 | 19:27 | 49.85
2021-10-16 | 19:27 | 49.799
2021-10-16 | 19:27 | 49.776
2021-10-16 | 19:27 | 49.761
2021-10-16 | 19:27 | 49.757
2021-10-16 | 19:27 | 49.76
2021-10-16 | 19:28 | 49.764
2021-10-16 | 19:28 | 49.767
2021-10-16 | 19:28 | 49.77
2021-10-16 | 19:28 | 49.772
2021-10-16 | 19:28 | 49.774
2021-10-16 | 19:28 | 49.775
2021-10-16 | 19:28 | 49.777
2021-10-16 | 19:28 | 49.779
2021-10-16 | 19:28 | 49.78
2021-10-16 | 19:28 | 49.78
2021-10-16 | 19:28 | 49.78
2021-10-16 | 19:28 | 49.78
2021-10-16 | 19:28 | 49.781
2021-10-16 | 19:28 | 49.781
2021-10-16 | 19:28 | 49.777
2021-10-16 | 19:28 | 49.774
2021-10-16 | 19:28 | 49.77
2021-10-16 | 19:28 | 49.768
2021-10-16 | 19:28 | 49.767
2021-10-16 | 19:28 | 49.765
2021-10-16 | 19:28 | 49.763
2021-10-16 | 19:28 | 49.761
2021-10-16 | 19:28 | 49.759
2021-10-16 | 19:28 | 49.758
2021-10-16 | 19:28 | 49.757
2021-10-16 | 19:28 | 49.755
2021-10-16 | 19:28 | 49.752
2021-10-16 | 19:28 | 49.75
2021-10-16 | 19:28 | 49.749
2021-10-16 | 19:28 | 49.75
2021-10-16 | 19:28 | 49.749
2021-10-16 | 19:28 | 49.748
2021-10-16 | 19:28 | 49.746
2021-10-16 | 19:28 | 49.746
2021-10-16 | 19:28 | 49.746
2021-10-16 | 19:28 | 49.747
2021-10-16 | 19:28 | 49.748
2021-10-16 | 19:28 | 49.75
2021-10-16 | 19:28 | 49.75
2021-10-16 | 19:28 | 49.75
2021-10-16 | 19:28 | 49.75
2021-10-16 | 19:28 | 49.75
2021-10-16 | 19:28 | 49.751
2021-10-16 | 19:28 | 49.75
2021-10-16 | 19:28 | 49.75
2021-10-16 | 19:28 | 49.75
2021-10-16 | 19:28 | 49.752
2021-10-16 | 19:28 | 49.753
2021-10-16 | 19:28 | 49.754
2021-10-16 | 19:28 | 49.756
2021-10-16 | 19:28 | 49.755
2021-10-16 | 19:28 | 49.756
2021-10-16 | 19:28 | 49.755
2021-10-16 | 19:28 | 49.755
2021-10-16 | 19:28 | 49.755
2021-10-16 | 19:28 | 49.755
2021-10-16 | 19:28 | 49.756
2021-10-16 | 19:28 | 49.759
2021-10-16 | 19:28 | 49.76
2021-10-16 | 19:28 | 49.76
2021-10-16 | 19:28 | 49.758
2021-10-16 | 19:29 | 49.756
2021-10-16 | 19:29 | 49.755
2021-10-16 | 19:29 | 49.755
2021-10-16 | 19:29 | 49.756
2021-10-16 | 19:29 | 49.757
2021-10-16 | 19:29 | 49.757
2021-10-16 | 19:29 | 49.758
2021-10-16 | 19:29 | 49.757
2021-10-16 | 19:29 | 49.755
2021-10-16 | 19:29 | 49.754
2021-10-16 | 19:29 | 49.753
2021-10-16 | 19:29 | 49.751
2021-10-16 | 19:29 | 49.751
2021-10-16 | 19:29 | 49.751
2021-10-16 | 19:29 | 49.753
2021-10-16 | 19:29 | 49.753
2021-10-16 | 19:29 | 49.753
2021-10-16 | 19:29 | 49.753
2021-10-16 | 19:29 | 49.752
2021-10-16 | 19:29 | 49.75
2021-10-16 | 19:29 | 49.749
2021-10-16 | 19:29 | 49.748
2021-10-16 | 19:29 | 49.747
2021-10-16 | 19:29 | 49.747
2021-10-16 | 19:29 | 49.746
2021-10-16 | 19:29 | 49.744
2021-10-16 | 19:29 | 49.744
2021-10-16 | 19:29 | 49.741
2021-10-16 | 19:29 | 49.74
2021-10-16 | 19:29 | 49.74
2021-10-16 | 19:29 | 49.738
2021-10-16 | 19:29 | 49.738
2021-10-16 | 19:29 | 49.739
2021-10-16 | 19:29 | 49.741
2021-10-16 | 19:29 | 49.746
2021-10-16 | 19:29 | 49.752
2021-10-16 | 19:29 | 49.756
2021-10-16 | 19:29 | 49.761
2021-10-16 | 19:29 | 49.765
2021-10-16 | 19:29 | 49.768
2021-10-16 | 19:29 | 49.769
2021-10-16 | 19:29 | 49.772
2021-10-16 | 19:29 | 49.774
2021-10-16 | 19:29 | 49.778
2021-10-16 | 19:29 | 49.782
2021-10-16 | 19:29 | 49.785
2021-10-16 | 19:29 | 49.788
2021-10-16 | 19:29 | 49.79
2021-10-16 | 19:29 | 49.794
2021-10-16 | 19:29 | 49.795
2021-10-16 | 19:29 | 49.798
2021-10-16 | 19:29 | 49.8
2021-10-16 | 19:29 | 49.804
2021-10-16 | 19:29 | 49.807
2021-10-16 | 19:29 | 49.811
2021-10-16 | 19:29 | 49.815
2021-10-16 | 19:29 | 49.817
2021-10-16 | 19:29 | 49.816
2021-10-16 | 19:29 | 49.817
2021-10-16 | 19:30 | 49.818
2021-10-16 | 19:30 | 49.821
2021-10-16 | 19:30 | 49.826
2021-10-16 | 19:30 | 49.829
2021-10-16 | 19:30 | 49.837
2021-10-16 | 19:30 | 49.841
2021-10-16 | 19:30 | 49.847
2021-10-16 | 19:30 | 49.853
2021-10-16 | 19:30 | 49.859
2021-10-16 | 19:30 | 49.865
2021-10-16 | 19:30 | 49.872
2021-10-16 | 19:30 | 49.879
2021-10-16 | 19:30 | 49.886
2021-10-16 | 19:30 | 49.892
2021-10-16 | 19:30 | 49.896
2021-10-16 | 19:30 | 49.9
2021-10-16 | 19:30 | 49.9
2021-10-16 | 19:30 | 49.902
2021-10-16 | 19:30 | 49.901
2021-10-16 | 19:30 | 49.901
2021-10-16 | 19:30 | 49.9
2021-10-16 | 19:30 | 49.899
2021-10-16 | 19:30 | 49.896
2021-10-16 | 19:30 | 49.895
2021-10-16 | 19:30 | 49.893
2021-10-16 | 19:30 | 49.893
2021-10-16 | 19:30 | 49.893
2021-10-16 | 19:30 | 49.892
2021-10-16 | 19:30 | 49.895
2021-10-16 | 19:30 | 49.896
2021-10-16 | 19:30 | 49.897
2021-10-16 | 19:30 | 49.895
2021-10-16 | 19:30 | 49.893
2021-10-16 | 19:30 | 49.89
2021-10-16 | 19:30 | 49.89
2021-10-16 | 19:30 | 49.887
2021-10-16 | 19:30 | 49.882
2021-10-16 | 19:30 | 49.881
2021-10-16 | 19:30 | 49.879
2021-10-16 | 19:30 | 49.877
2021-10-16 | 19:30 | 49.877
2021-10-16 | 19:30 | 49.877
2021-10-16 | 19:30 | 49.879
2021-10-16 | 19:30 | 49.879
2021-10-16 | 19:30 | 49.881
2021-10-16 | 19:30 | 49.884
2021-10-16 | 19:30 | 49.887
2021-10-16 | 19:30 | 49.889
2021-10-16 | 19:30 | 49.891
2021-10-16 | 19:30 | 49.893
2021-10-16 | 19:30 | 49.895
2021-10-16 | 19:30 | 49.897
2021-10-16 | 19:30 | 49.898
2021-10-16 | 19:30 | 49.899
2021-10-16 | 19:30 | 49.9
2021-10-16 | 19:30 | 49.902
2021-10-16 | 19:30 | 49.906
2021-10-16 | 19:30 | 49.911
2021-10-16 | 19:30 | 49.913
2021-10-16 | 19:30 | 49.916
2021-10-16 | 19:30 | 49.917
2021-10-16 | 19:31 | 49.918
2021-10-16 | 19:31 | 49.92
2021-10-16 | 19:31 | 49.922
2021-10-16 | 19:31 | 49.925
2021-10-16 | 19:31 | 49.927
2021-10-16 | 19:31 | 49.931
2021-10-16 | 19:31 | 49.934
2021-10-16 | 19:31 | 49.936
2021-10-16 | 19:31 | 49.938
2021-10-16 | 19:31 | 49.939
2021-10-16 | 19:31 | 49.938
2021-10-16 | 19:31 | 49.936
2021-10-16 | 19:31 | 49.936
2021-10-16 | 19:31 | 49.933
2021-10-16 | 19:31 | 49.931
2021-10-16 | 19:31 | 49.929
2021-10-16 | 19:31 | 49.928
2021-10-16 | 19:31 | 49.93
2021-10-16 | 19:31 | 49.93
2021-10-16 | 19:31 | 49.932
2021-10-16 | 19:31 | 49.932
2021-10-16 | 19:31 | 49.934
2021-10-16 | 19:31 | 49.938
2021-10-16 | 19:31 | 49.941
2021-10-16 | 19:31 | 49.941
2021-10-16 | 19:31 | 49.94
2021-10-16 | 19:31 | 49.937
2021-10-16 | 19:31 | 49.935
2021-10-16 | 19:31 | 49.935
2021-10-16 | 19:31 | 49.935
2021-10-16 | 19:31 | 49.935
2021-10-16 | 19:31 | 49.936
2021-10-16 | 19:31 | 49.938
2021-10-16 | 19:31 | 49.942
2021-10-16 | 19:31 | 49.946
2021-10-16 | 19:31 | 49.95
2021-10-16 | 19:31 | 49.954
2021-10-16 | 19:31 | 49.957
2021-10-16 | 19:31 | 49.959
2021-10-16 | 19:31 | 49.962
2021-10-16 | 19:31 | 49.965
2021-10-16 | 19:31 | 49.967
2021-10-16 | 19:31 | 49.968
2021-10-16 | 19:31 | 49.965
2021-10-16 | 19:31 | 49.966
2021-10-16 | 19:31 | 49.964
2021-10-16 | 19:31 | 49.965
2021-10-16 | 19:31 | 49.964
2021-10-16 | 19:31 | 49.964
2021-10-16 | 19:31 | 49.965
2021-10-16 | 19:31 | 49.965
2021-10-16 | 19:31 | 49.966
2021-10-16 | 19:31 | 49.966
2021-10-16 | 19:31 | 49.967
2021-10-16 | 19:31 | 49.966
2021-10-16 | 19:31 | 49.966
2021-10-16 | 19:31 | 49.966
2021-10-16 | 19:31 | 49.965
2021-10-16 | 19:31 | 49.965
2021-10-16 | 19:32 | 49.965
2021-10-16 | 19:32 | 49.966
2021-10-16 | 19:32 | 49.968
2021-10-16 | 19:32 | 49.969
2021-10-16 | 19:32 | 49.97
2021-10-16 | 19:32 | 49.972
2021-10-16 | 19:32 | 49.975
2021-10-16 | 19:32 | 49.978
2021-10-16 | 19:32 | 49.984
2021-10-16 | 19:32 | 49.99
2021-10-16 | 19:32 | 49.995
2021-10-16 | 19:32 | 49.997
2021-10-16 | 19:32 | 50.002
2021-10-16 | 19:32 | 50.004
2021-10-16 | 19:32 | 50.007
2021-10-16 | 19:32 | 50.009
2021-10-16 | 19:32 | 50.011
2021-10-16 | 19:32 | 50.012
2021-10-16 | 19:32 | 50.015
2021-10-16 | 19:32 | 50.016
2021-10-16 | 19:32 | 50.017
2021-10-16 | 19:32 | 50.019
2021-10-16 | 19:32 | 50.021
2021-10-16 | 19:32 | 50.023
2021-10-16 | 19:32 | 50.025
2021-10-16 | 19:32 | 50.028
2021-10-16 | 19:32 | 50.031
2021-10-16 | 19:32 | 50.034
2021-10-16 | 19:32 | 50.036
2021-10-16 | 19:32 | 50.038

## 20211020-1
In GMT
Date | Time | Freq
2021-10-20 | 15:47 | 49.97
2021-10-20 | 15:47 | 49.969
2021-10-20 | 15:47 | 49.966
2021-10-20 | 15:47 | 49.963
2021-10-20 | 15:47 | 49.965
2021-10-20 | 15:47 | 49.965
2021-10-20 | 15:47 | 49.965
2021-10-20 | 15:47 | 49.966
2021-10-20 | 15:47 | 49.963
2021-10-20 | 15:47 | 49.959
2021-10-20 | 15:47 | 49.96
2021-10-20 | 15:47 | 49.96
2021-10-20 | 15:47 | 49.962
2021-10-20 | 15:47 | 49.964
2021-10-20 | 15:47 | 49.966
2021-10-20 | 15:47 | 49.967
2021-10-20 | 15:47 | 49.972
2021-10-20 | 15:47 | 49.974
2021-10-20 | 15:47 | 49.977
2021-10-20 | 15:47 | 49.975
2021-10-20 | 15:47 | 49.974
2021-10-20 | 15:47 | 49.972
2021-10-20 | 15:47 | 49.968
2021-10-20 | 15:47 | 49.966
2021-10-20 | 15:47 | 49.964
2021-10-20 | 15:47 | 49.965
2021-10-20 | 15:47 | 49.967
2021-10-20 | 15:47 | 49.966
2021-10-20 | 15:47 | 49.966
2021-10-20 | 15:47 | 49.964
2021-10-20 | 15:47 | 49.965
2021-10-20 | 15:48 | 49.966
2021-10-20 | 15:48 | 49.964
2021-10-20 | 15:48 | 49.962
2021-10-20 | 15:48 | 49.959
2021-10-20 | 15:48 | 49.959
2021-10-20 | 15:48 | 49.96
2021-10-20 | 15:48 | 49.96
2021-10-20 | 15:48 | 49.96
2021-10-20 | 15:48 | 49.961
2021-10-20 | 15:48 | 49.959
2021-10-20 | 15:48 | 49.961
2021-10-20 | 15:48 | 49.961
2021-10-20 | 15:48 | 49.963
2021-10-20 | 15:48 | 49.965
2021-10-20 | 15:48 | 49.967
2021-10-20 | 15:48 | 49.969
2021-10-20 | 15:48 | 49.971
2021-10-20 | 15:48 | 49.974
2021-10-20 | 15:48 | 49.976
2021-10-20 | 15:48 | 49.959
2021-10-20 | 15:48 | 49.934
2021-10-20 | 15:48 | 49.914
2021-10-20 | 15:48 | 49.899
2021-10-20 | 15:48 | 49.891
2021-10-20 | 15:48 | 49.886
2021-10-20 | 15:48 | 49.884
2021-10-20 | 15:48 | 49.883
2021-10-20 | 15:48 | 49.882
2021-10-20 | 15:48 | 49.882
2021-10-20 | 15:48 | 49.879
2021-10-20 | 15:48 | 49.876
2021-10-20 | 15:48 | 49.871
2021-10-20 | 15:48 | 49.866
2021-10-20 | 15:48 | 49.864
2021-10-20 | 15:48 | 49.862
2021-10-20 | 15:48 | 49.861
2021-10-20 | 15:48 | 49.861
2021-10-20 | 15:48 | 49.862
2021-10-20 | 15:48 | 49.865
2021-10-20 | 15:48 | 49.866
2021-10-20 | 15:48 | 49.868
2021-10-20 | 15:48 | 49.867
2021-10-20 | 15:48 | 49.867
2021-10-20 | 15:48 | 49.868
2021-10-20 | 15:48 | 49.869
2021-10-20 | 15:48 | 49.872
2021-10-20 | 15:48 | 49.873
2021-10-20 | 15:48 | 49.875
2021-10-20 | 15:48 | 49.878
2021-10-20 | 15:48 | 49.876
2021-10-20 | 15:48 | 49.877
2021-10-20 | 15:48 | 49.88
2021-10-20 | 15:48 | 49.883
2021-10-20 | 15:48 | 49.884
2021-10-20 | 15:48 | 49.885
2021-10-20 | 15:48 | 49.887
2021-10-20 | 15:48 | 49.885
2021-10-20 | 15:48 | 49.885
2021-10-20 | 15:48 | 49.884
2021-10-20 | 15:49 | 49.881
2021-10-20 | 15:49 | 49.878
2021-10-20 | 15:49 | 49.875
2021-10-20 | 15:49 | 49.875
2021-10-20 | 15:49 | 49.871
2021-10-20 | 15:49 | 49.868
2021-10-20 | 15:49 | 49.871
2021-10-20 | 15:49 | 49.869
2021-10-20 | 15:49 | 49.868
2021-10-20 | 15:49 | 49.868
2021-10-20 | 15:49 | 49.868
2021-10-20 | 15:49 | 49.869
2021-10-20 | 15:49 | 49.872
2021-10-20 | 15:49 | 49.872
2021-10-20 | 15:49 | 49.875
2021-10-20 | 15:49 | 49.881
2021-10-20 | 15:49 | 49.887
2021-10-20 | 15:49 | 49.889
2021-10-20 | 15:49 | 49.889
2021-10-20 | 15:49 | 49.889
2021-10-20 | 15:49 | 49.886
2021-10-20 | 15:49 | 49.888
2021-10-20 | 15:49 | 49.884
2021-10-20 | 15:49 | 49.882
2021-10-20 | 15:49 | 49.878
2021-10-20 | 15:49 | 49.876
2021-10-20 | 15:49 | 49.875
2021-10-20 | 15:49 | 49.877
2021-10-20 | 15:49 | 49.877
2021-10-20 | 15:49 | 49.879
2021-10-20 | 15:49 | 49.881
2021-10-20 | 15:49 | 49.882
2021-10-20 | 15:49 | 49.885
2021-10-20 | 15:49 | 49.886
2021-10-20 | 15:49 | 49.89
2021-10-20 | 15:49 | 49.892
2021-10-20 | 15:49 | 49.889
2021-10-20 | 15:49 | 49.886
2021-10-20 | 15:49 | 49.882
2021-10-20 | 15:49 | 49.88
2021-10-20 | 15:49 | 49.876
2021-10-20 | 15:49 | 49.871
2021-10-20 | 15:49 | 49.866
2021-10-20 | 15:49 | 49.861
2021-10-20 | 15:49 | 49.858
2021-10-20 | 15:49 | 49.858
2021-10-20 | 15:49 | 49.86
2021-10-20 | 15:49 | 49.861
2021-10-20 | 15:49 | 49.865
2021-10-20 | 15:49 | 49.867
2021-10-20 | 15:49 | 49.872
2021-10-20 | 15:49 | 49.873
2021-10-20 | 15:49 | 49.877
2021-10-20 | 15:49 | 49.882
2021-10-20 | 15:49 | 49.888
2021-10-20 | 15:49 | 49.892
2021-10-20 | 15:49 | 49.894
2021-10-20 | 15:49 | 49.898
2021-10-20 | 15:49 | 49.903
2021-10-20 | 15:49 | 49.909
2021-10-20 | 15:49 | 49.912
2021-10-20 | 15:50 | 49.915
2021-10-20 | 15:50 | 49.918
2021-10-20 | 15:50 | 49.92
2021-10-20 | 15:50 | 49.926
2021-10-20 | 15:50 | 49.928
2021-10-20 | 15:50 | 49.93
2021-10-20 | 15:50 | 49.931
2021-10-20 | 15:50 | 49.935
2021-10-20 | 15:50 | 49.938
2021-10-20 | 15:50 | 49.937
2021-10-20 | 15:50 | 49.934
2021-10-20 | 15:50 | 49.934
2021-10-20 | 15:50 | 49.933
2021-10-20 | 15:50 | 49.933
2021-10-20 | 15:50 | 49.931
2021-10-20 | 15:50 | 49.932
2021-10-20 | 15:50 | 49.931
2021-10-20 | 15:50 | 49.934
2021-10-20 | 15:50 | 49.934
2021-10-20 | 15:50 | 49.938
2021-10-20 | 15:50 | 49.94
2021-10-20 | 15:50 | 49.941
2021-10-20 | 15:50 | 49.941
2021-10-20 | 15:50 | 49.94
2021-10-20 | 15:50 | 49.937
2021-10-20 | 15:50 | 49.935
2021-10-20 | 15:50 | 49.933
2021-10-20 | 15:50 | 49.932
2021-10-20 | 15:50 | 49.933
2021-10-20 | 15:50 | 49.933
2021-10-20 | 15:50 | 49.931
2021-10-20 | 15:50 | 49.926
2021-10-20 | 15:50 | 49.923
2021-10-20 | 15:50 | 49.919
2021-10-20 | 15:50 | 49.919
2021-10-20 | 15:50 | 49.918
2021-10-20 | 15:50 | 49.916
2021-10-20 | 15:50 | 49.917
2021-10-20 | 15:50 | 49.914
2021-10-20 | 15:50 | 49.917
2021-10-20 | 15:50 | 49.915
2021-10-20 | 15:50 | 49.92
2021-10-20 | 15:50 | 49.916
2021-10-20 | 15:50 | 49.918
2021-10-20 | 15:50 | 49.916
2021-10-20 | 15:50 | 49.919
2021-10-20 | 15:50 | 49.919
2021-10-20 | 15:50 | 49.922
2021-10-20 | 15:50 | 49.925
2021-10-20 | 15:50 | 49.927
2021-10-20 | 15:50 | 49.928
2021-10-20 | 15:50 | 49.931
2021-10-20 | 15:50 | 49.931
2021-10-20 | 15:50 | 49.934
2021-10-20 | 15:50 | 49.933
2021-10-20 | 15:50 | 49.935
2021-10-20 | 15:50 | 49.935
2021-10-20 | 15:50 | 49.936
2021-10-20 | 15:50 | 49.935
2021-10-20 | 15:51 | 49.931
2021-10-20 | 15:51 | 49.93
2021-10-20 | 15:51 | 49.926
2021-10-20 | 15:51 | 49.925
2021-10-20 | 15:51 | 49.922
2021-10-20 | 15:51 | 49.921
2021-10-20 | 15:51 | 49.92
2021-10-20 | 15:51 | 49.921
2021-10-20 | 15:51 | 49.923
2021-10-20 | 15:51 | 49.923
2021-10-20 | 15:51 | 49.923
2021-10-20 | 15:51 | 49.925
2021-10-20 | 15:51 | 49.927
2021-10-20 | 15:51 | 49.928
2021-10-20 | 15:51 | 49.927
2021-10-20 | 15:51 | 49.926
2021-10-20 | 15:51 | 49.925
2021-10-20 | 15:51 | 49.923
2021-10-20 | 15:51 | 49.92
2021-10-20 | 15:51 | 49.918
2021-10-20 | 15:51 | 49.917
2021-10-20 | 15:51 | 49.917
2021-10-20 | 15:51 | 49.915
2021-10-20 | 15:51 | 49.917
2021-10-20 | 15:51 | 49.919
2021-10-20 | 15:51 | 49.92
2021-10-20 | 15:51 | 49.922
2021-10-20 | 15:51 | 49.921
2021-10-20 | 15:51 | 49.92
2021-10-20 | 15:51 | 49.916
2021-10-20 | 15:51 | 49.913
2021-10-20 | 15:51 | 49.911
2021-10-20 | 15:51 | 49.909
2021-10-20 | 15:51 | 49.906
2021-10-20 | 15:51 | 49.905
2021-10-20 | 15:51 | 49.905
2021-10-20 | 15:51 | 49.905
2021-10-20 | 15:51 | 49.907
2021-10-20 | 15:51 | 49.906
2021-10-20 | 15:51 | 49.904
2021-10-20 | 15:51 | 49.904
2021-10-20 | 15:51 | 49.9
2021-10-20 | 15:51 | 49.898
2021-10-20 | 15:51 | 49.896
2021-10-20 | 15:51 | 49.891
2021-10-20 | 15:51 | 49.885
2021-10-20 | 15:51 | 49.883
2021-10-20 | 15:51 | 49.881
2021-10-20 | 15:51 | 49.882
2021-10-20 | 15:51 | 49.885
2021-10-20 | 15:51 | 49.887
2021-10-20 | 15:51 | 49.89
2021-10-20 | 15:51 | 49.893
2021-10-20 | 15:51 | 49.895
2021-10-20 | 15:51 | 49.894
2021-10-20 | 15:51 | 49.893
2021-10-20 | 15:51 | 49.892
2021-10-20 | 15:51 | 49.892
2021-10-20 | 15:51 | 49.89
2021-10-20 | 15:51 | 49.889
2021-10-20 | 15:51 | 49.889
2021-10-20 | 15:52 | 49.888
2021-10-20 | 15:52 | 49.888
2021-10-20 | 15:52 | 49.888
2021-10-20 | 15:52 | 49.889
2021-10-20 | 15:52 | 49.89
2021-10-20 | 15:52 | 49.894
2021-10-20 | 15:52 | 49.895
2021-10-20 | 15:52 | 49.896
2021-10-20 | 15:52 | 49.9
2021-10-20 | 15:52 | 49.899
2021-10-20 | 15:52 | 49.897
2021-10-20 | 15:52 | 49.894
2021-10-20 | 15:52 | 49.893
2021-10-20 | 15:52 | 49.89
2021-10-20 | 15:52 | 49.89
2021-10-20 | 15:52 | 49.889
2021-10-20 | 15:52 | 49.891
2021-10-20 | 15:52 | 49.893
2021-10-20 | 15:52 | 49.896
2021-10-20 | 15:52 | 49.898
2021-10-20 | 15:52 | 49.904
2021-10-20 | 15:52 | 49.91
2021-10-20 | 15:52 | 49.911
2021-10-20 | 15:52 | 49.913
2021-10-20 | 15:52 | 49.91
2021-10-20 | 15:52 | 49.911
2021-10-20 | 15:52 | 49.91
2021-10-20 | 15:52 | 49.91
2021-10-20 | 15:52 | 49.91
2021-10-20 | 15:52 | 49.91
2021-10-20 | 15:52 | 49.907
2021-10-20 | 15:52 | 49.908
2021-10-20 | 15:52 | 49.91
2021-10-20 | 15:52 | 49.909
2021-10-20 | 15:52 | 49.906
2021-10-20 | 15:52 | 49.9
2021-10-20 | 15:52 | 49.896
2021-10-20 | 15:52 | 49.891
2021-10-20 | 15:52 | 49.887
2021-10-20 | 15:52 | 49.886
2021-10-20 | 15:52 | 49.884
2021-10-20 | 15:52 | 49.881
2021-10-20 | 15:52 | 49.878
2021-10-20 | 15:52 | 49.878
2021-10-20 | 15:52 | 49.88
2021-10-20 | 15:52 | 49.882
2021-10-20 | 15:52 | 49.883
2021-10-20 | 15:52 | 49.884
2021-10-20 | 15:52 | 49.885
2021-10-20 | 15:52 | 49.884
2021-10-20 | 15:52 | 49.884
2021-10-20 | 15:52 | 49.884
2021-10-20 | 15:52 | 49.884
2021-10-20 | 15:52 | 49.882
2021-10-20 | 15:52 | 49.881
2021-10-20 | 15:52 | 49.88
2021-10-20 | 15:52 | 49.877
2021-10-20 | 15:52 | 49.877
2021-10-20 | 15:52 | 49.88
2021-10-20 | 15:52 | 49.881
2021-10-20 | 15:53 | 49.884
2021-10-20 | 15:53 | 49.888
2021-10-20 | 15:53 | 49.891
2021-10-20 | 15:53 | 49.896
2021-10-20 | 15:53 | 49.9
2021-10-20 | 15:53 | 49.904
2021-10-20 | 15:53 | 49.906
2021-10-20 | 15:53 | 49.908
2021-10-20 | 15:53 | 49.909
2021-10-20 | 15:53 | 49.907
2021-10-20 | 15:53 | 49.907
2021-10-20 | 15:53 | 49.906
2021-10-20 | 15:53 | 49.905
2021-10-20 | 15:53 | 49.904
2021-10-20 | 15:53 | 49.901
2021-10-20 | 15:53 | 49.902
2021-10-20 | 15:53 | 49.904
2021-10-20 | 15:53 | 49.905
2021-10-20 | 15:53 | 49.91
2021-10-20 | 15:53 | 49.909
2021-10-20 | 15:53 | 49.91
2021-10-20 | 15:53 | 49.912
2021-10-20 | 15:53 | 49.913
2021-10-20 | 15:53 | 49.916
2021-10-20 | 15:53 | 49.918
2021-10-20 | 15:53 | 49.922
2021-10-20 | 15:53 | 49.926
2021-10-20 | 15:53 | 49.928
2021-10-20 | 15:53 | 49.93
2021-10-20 | 15:53 | 49.931
2021-10-20 | 15:53 | 49.932
2021-10-20 | 15:53 | 49.932
2021-10-20 | 15:53 | 49.929
2021-10-20 | 15:53 | 49.929
2021-10-20 | 15:53 | 49.927
2021-10-20 | 15:53 | 49.926
2021-10-20 | 15:53 | 49.925
2021-10-20 | 15:53 | 49.924
2021-10-20 | 15:53 | 49.922
2021-10-20 | 15:53 | 49.922
2021-10-20 | 15:53 | 49.921
2021-10-20 | 15:53 | 49.92
2021-10-20 | 15:53 | 49.92
2021-10-20 | 15:53 | 49.919
2021-10-20 | 15:53 | 49.914
2021-10-20 | 15:53 | 49.911
2021-10-20 | 15:53 | 49.906
2021-10-20 | 15:53 | 49.901
2021-10-20 | 15:53 | 49.897
2021-10-20 | 15:53 | 49.897
2021-10-20 | 15:53 | 49.898
2021-10-20 | 15:53 | 49.897
2021-10-20 | 15:53 | 49.9
2021-10-20 | 15:53 | 49.902
2021-10-20 | 15:53 | 49.9
2021-10-20 | 15:53 | 49.903
2021-10-20 | 15:53 | 49.905
2021-10-20 | 15:53 | 49.906
2021-10-20 | 15:53 | 49.91
2021-10-20 | 15:54 | 49.914
2021-10-20 | 15:54 | 49.921
2021-10-20 | 15:54 | 49.926
2021-10-20 | 15:54 | 49.929
2021-10-20 | 15:54 | 49.931
2021-10-20 | 15:54 | 49.933
2021-10-20 | 15:54 | 49.934
2021-10-20 | 15:54 | 49.932
2021-10-20 | 15:54 | 49.929
2021-10-20 | 15:54 | 49.929
2021-10-20 | 15:54 | 49.929
2021-10-20 | 15:54 | 49.929
2021-10-20 | 15:54 | 49.929
2021-10-20 | 15:54 | 49.93
2021-10-20 | 15:54 | 49.929
2021-10-20 | 15:54 | 49.925
2021-10-20 | 15:54 | 49.925
2021-10-20 | 15:54 | 49.925
2021-10-20 | 15:54 | 49.925
2021-10-20 | 15:54 | 49.924
2021-10-20 | 15:54 | 49.925
2021-10-20 | 15:54 | 49.925
2021-10-20 | 15:54 | 49.923
2021-10-20 | 15:54 | 49.924
2021-10-20 | 15:54 | 49.923
2021-10-20 | 15:54 | 49.924
2021-10-20 | 15:54 | 49.926
2021-10-20 | 15:54 | 49.927
2021-10-20 | 15:54 | 49.927
2021-10-20 | 15:54 | 49.926
2021-10-20 | 15:54 | 49.925
2021-10-20 | 15:54 | 49.924
2021-10-20 | 15:54 | 49.924
2021-10-20 | 15:54 | 49.923
2021-10-20 | 15:54 | 49.922
2021-10-20 | 15:54 | 49.922
2021-10-20 | 15:54 | 49.92
2021-10-20 | 15:54 | 49.919
2021-10-20 | 15:54 | 49.916
2021-10-20 | 15:54 | 49.914
2021-10-20 | 15:54 | 49.915
2021-10-20 | 15:54 | 49.915
2021-10-20 | 15:54 | 49.914
2021-10-20 | 15:54 | 49.915
2021-10-20 | 15:54 | 49.91
2021-10-20 | 15:54 | 49.909
2021-10-20 | 15:54 | 49.906
2021-10-20 | 15:54 | 49.904
2021-10-20 | 15:54 | 49.903
2021-10-20 | 15:54 | 49.901
2021-10-20 | 15:54 | 49.898
2021-10-20 | 15:54 | 49.897
2021-10-20 | 15:54 | 49.895
2021-10-20 | 15:54 | 49.893
2021-10-20 | 15:54 | 49.893
2021-10-20 | 15:54 | 49.894
2021-10-20 | 15:54 | 49.893
2021-10-20 | 15:54 | 49.894
2021-10-20 | 15:54 | 49.894
2021-10-20 | 15:54 | 49.896
2021-10-20 | 15:54 | 49.897
2021-10-20 | 15:55 | 49.9
2021-10-20 | 15:55 | 49.897
2021-10-20 | 15:55 | 49.898
2021-10-20 | 15:55 | 49.897
2021-10-20 | 15:55 | 49.899
2021-10-20 | 15:55 | 49.9
2021-10-20 | 15:55 | 49.9
2021-10-20 | 15:55 | 49.902
2021-10-20 | 15:55 | 49.902
2021-10-20 | 15:55 | 49.903
2021-10-20 | 15:55 | 49.905
2021-10-20 | 15:55 | 49.908
2021-10-20 | 15:55 | 49.911
2021-10-20 | 15:55 | 49.915
2021-10-20 | 15:55 | 49.918
2021-10-20 | 15:55 | 49.921
2021-10-20 | 15:55 | 49.923
2021-10-20 | 15:55 | 49.924
2021-10-20 | 15:55 | 49.925
2021-10-20 | 15:55 | 49.926
2021-10-20 | 15:55 | 49.925
2021-10-20 | 15:55 | 49.922
2021-10-20 | 15:55 | 49.919
2021-10-20 | 15:55 | 49.916
2021-10-20 | 15:55 | 49.914
2021-10-20 | 15:55 | 49.914
2021-10-20 | 15:55 | 49.913
2021-10-20 | 15:55 | 49.914
2021-10-20 | 15:55 | 49.916
2021-10-20 | 15:55 | 49.917
2021-10-20 | 15:55 | 49.916
2021-10-20 | 15:55 | 49.913
2021-10-20 | 15:55 | 49.909
2021-10-20 | 15:55 | 49.905
2021-10-20 | 15:55 | 49.902
2021-10-20 | 15:55 | 49.902
2021-10-20 | 15:55 | 49.899
2021-10-20 | 15:55 | 49.895
2021-10-20 | 15:55 | 49.891
2021-10-20 | 15:55 | 49.887
2021-10-20 | 15:55 | 49.884
2021-10-20 | 15:55 | 49.884
2021-10-20 | 15:55 | 49.883
2021-10-20 | 15:55 | 49.883
2021-10-20 | 15:55 | 49.881
2021-10-20 | 15:55 | 49.881
2021-10-20 | 15:55 | 49.881
2021-10-20 | 15:55 | 49.88
2021-10-20 | 15:55 | 49.884
2021-10-20 | 15:55 | 49.887
2021-10-20 | 15:55 | 49.89
2021-10-20 | 15:55 | 49.893
2021-10-20 | 15:55 | 49.894
2021-10-20 | 15:55 | 49.896
2021-10-20 | 15:55 | 49.901
2021-10-20 | 15:55 | 49.902
2021-10-20 | 15:55 | 49.902
2021-10-20 | 15:55 | 49.904
2021-10-20 | 15:55 | 49.906
2021-10-20 | 15:56 | 49.909
2021-10-20 | 15:56 | 49.912
2021-10-20 | 15:56 | 49.914
2021-10-20 | 15:56 | 49.915
2021-10-20 | 15:56 | 49.917
2021-10-20 | 15:56 | 49.918
2021-10-20 | 15:56 | 49.919
2021-10-20 | 15:56 | 49.921
2021-10-20 | 15:56 | 49.923
2021-10-20 | 15:56 | 49.927
2021-10-20 | 15:56 | 49.928
2021-10-20 | 15:56 | 49.93
2021-10-20 | 15:56 | 49.931
2021-10-20 | 15:56 | 49.93
2021-10-20 | 15:56 | 49.931
2021-10-20 | 15:56 | 49.931
2021-10-20 | 15:56 | 49.933
2021-10-20 | 15:56 | 49.934
2021-10-20 | 15:56 | 49.934
2021-10-20 | 15:56 | 49.934
2021-10-20 | 15:56 | 49.934
2021-10-20 | 15:56 | 49.936
2021-10-20 | 15:56 | 49.936
2021-10-20 | 15:56 | 49.939
2021-10-20 | 15:56 | 49.939
2021-10-20 | 15:56 | 49.94
2021-10-20 | 15:56 | 49.941
2021-10-20 | 15:56 | 49.94
2021-10-20 | 15:56 | 49.939
2021-10-20 | 15:56 | 49.939
2021-10-20 | 15:56 | 49.941
2021-10-20 | 15:56 | 49.937
2021-10-20 | 15:56 | 49.931
2021-10-20 | 15:56 | 49.929
2021-10-20 | 15:56 | 49.929
2021-10-20 | 15:56 | 49.928
2021-10-20 | 15:56 | 49.926
2021-10-20 | 15:56 | 49.925
2021-10-20 | 15:56 | 49.924
2021-10-20 | 15:56 | 49.918
2021-10-20 | 15:56 | 49.914
2021-10-20 | 15:56 | 49.911
2021-10-20 | 15:56 | 49.908
2021-10-20 | 15:56 | 49.907
2021-10-20 | 15:56 | 49.91
2021-10-20 | 15:56 | 49.912
2021-10-20 | 15:56 | 49.914
2021-10-20 | 15:56 | 49.919
2021-10-20 | 15:56 | 49.923
2021-10-20 | 15:56 | 49.926
2021-10-20 | 15:56 | 49.927
2021-10-20 | 15:56 | 49.93
2021-10-20 | 15:56 | 49.93
2021-10-20 | 15:56 | 49.931
2021-10-20 | 15:56 | 49.934
2021-10-20 | 15:56 | 49.937
2021-10-20 | 15:56 | 49.942
2021-10-20 | 15:56 | 49.945
2021-10-20 | 15:56 | 49.947
2021-10-20 | 15:56 | 49.947
2021-10-20 | 15:56 | 49.947
2021-10-20 | 15:57 | 49.943
2021-10-20 | 15:57 | 49.945
2021-10-20 | 15:57 | 49.945
2021-10-20 | 15:57 | 49.948
2021-10-20 | 15:57 | 49.951
2021-10-20 | 15:57 | 49.952
2021-10-20 | 15:57 | 49.956
2021-10-20 | 15:57 | 49.959
2021-10-20 | 15:57 | 49.958
2021-10-20 | 15:57 | 49.959
2021-10-20 | 15:57 | 49.96
2021-10-20 | 15:57 | 49.959
2021-10-20 | 15:57 | 49.956
2021-10-20 | 15:57 | 49.956
2021-10-20 | 15:57 | 49.953
2021-10-20 | 15:57 | 49.954
2021-10-20 | 15:57 | 49.955
2021-10-20 | 15:57 | 49.956
2021-10-20 | 15:57 | 49.955
2021-10-20 | 15:57 | 49.953
2021-10-20 | 15:57 | 49.95
2021-10-20 | 15:57 | 49.948
2021-10-20 | 15:57 | 49.948
2021-10-20 | 15:57 | 49.947
2021-10-20 | 15:57 | 49.951
2021-10-20 | 15:57 | 49.954
2021-10-20 | 15:57 | 49.958
2021-10-20 | 15:57 | 49.96
2021-10-20 | 15:57 | 49.961
2021-10-20 | 15:57 | 49.964
2021-10-20 | 15:57 | 49.965
2021-10-20 | 15:57 | 49.965
2021-10-20 | 15:57 | 49.964
2021-10-20 | 15:57 | 49.962
2021-10-20 | 15:57 | 49.96
2021-10-20 | 15:57 | 49.955
2021-10-20 | 15:57 | 49.954
2021-10-20 | 15:57 | 49.953
2021-10-20 | 15:57 | 49.953
2021-10-20 | 15:57 | 49.953
2021-10-20 | 15:57 | 49.954
2021-10-20 | 15:57 | 49.954
2021-10-20 | 15:57 | 49.957
2021-10-20 | 15:57 | 49.958
2021-10-20 | 15:57 | 49.96
2021-10-20 | 15:57 | 49.963
2021-10-20 | 15:57 | 49.962
2021-10-20 | 15:57 | 49.963
2021-10-20 | 15:57 | 49.961
2021-10-20 | 15:57 | 49.961
2021-10-20 | 15:57 | 49.957
2021-10-20 | 15:57 | 49.955
2021-10-20 | 15:57 | 49.953
2021-10-20 | 15:57 | 49.95
2021-10-20 | 15:57 | 49.95
2021-10-20 | 15:57 | 49.947
2021-10-20 | 15:57 | 49.947
2021-10-20 | 15:57 | 49.944
2021-10-20 | 15:57 | 49.943
2021-10-20 | 15:58 | 49.942
2021-10-20 | 15:58 | 49.941
2021-10-20 | 15:58 | 49.941
2021-10-20 | 15:58 | 49.941
2021-10-20 | 15:58 | 49.943
2021-10-20 | 15:58 | 49.943
2021-10-20 | 15:58 | 49.946
2021-10-20 | 15:58 | 49.947
2021-10-20 | 15:58 | 49.947
2021-10-20 | 15:58 | 49.948
2021-10-20 | 15:58 | 49.946
2021-10-20 | 15:58 | 49.951
2021-10-20 | 15:58 | 49.95
2021-10-20 | 15:58 | 49.951
2021-10-20 | 15:58 | 49.951
2021-10-20 | 15:58 | 49.953
2021-10-20 | 15:58 | 49.953
2021-10-20 | 15:58 | 49.954
2021-10-20 | 15:58 | 49.956
2021-10-20 | 15:58 | 49.959
2021-10-20 | 15:58 | 49.959
2021-10-20 | 15:58 | 49.959
2021-10-20 | 15:58 | 49.961
2021-10-20 | 15:58 | 49.964
2021-10-20 | 15:58 | 49.966
2021-10-20 | 15:58 | 49.969
2021-10-20 | 15:58 | 49.971
2021-10-20 | 15:58 | 49.971
2021-10-20 | 15:58 | 49.97
2021-10-20 | 15:58 | 49.973
2021-10-20 | 15:58 | 49.972
2021-10-20 | 15:58 | 49.967
2021-10-20 | 15:58 | 49.962
2021-10-20 | 15:58 | 49.958
2021-10-20 | 15:58 | 49.954
2021-10-20 | 15:58 | 49.947
2021-10-20 | 15:58 | 49.947
2021-10-20 | 15:58 | 49.944
2021-10-20 | 15:58 | 49.944
2021-10-20 | 15:58 | 49.942
2021-10-20 | 15:58 | 49.94
2021-10-20 | 15:58 | 49.937
2021-10-20 | 15:58 | 49.934
2021-10-20 | 15:58 | 49.93
2021-10-20 | 15:58 | 49.929
2021-10-20 | 15:58 | 49.927
2021-10-20 | 15:58 | 49.927
2021-10-20 | 15:58 | 49.926
2021-10-20 | 15:58 | 49.923
2021-10-20 | 15:58 | 49.922
2021-10-20 | 15:58 | 49.925
2021-10-20 | 15:58 | 49.925
2021-10-20 | 15:58 | 49.927
2021-10-20 | 15:58 | 49.929
2021-10-20 | 15:58 | 49.93
2021-10-20 | 15:58 | 49.928
2021-10-20 | 15:58 | 49.931
2021-10-20 | 15:58 | 49.932
2021-10-20 | 15:58 | 49.935
2021-10-20 | 15:58 | 49.939
2021-10-20 | 15:58 | 49.944
2021-10-20 | 15:59 | 49.948
2021-10-20 | 15:59 | 49.953
2021-10-20 | 15:59 | 49.955
2021-10-20 | 15:59 | 49.953
2021-10-20 | 15:59 | 49.952
2021-10-20 | 15:59 | 49.952
2021-10-20 | 15:59 | 49.949
2021-10-20 | 15:59 | 49.946
2021-10-20 | 15:59 | 49.943
2021-10-20 | 15:59 | 49.94
2021-10-20 | 15:59 | 49.936
2021-10-20 | 15:59 | 49.935
2021-10-20 | 15:59 | 49.934
2021-10-20 | 15:59 | 49.932
2021-10-20 | 15:59 | 49.932
2021-10-20 | 15:59 | 49.929
2021-10-20 | 15:59 | 49.925
2021-10-20 | 15:59 | 49.924
2021-10-20 | 15:59 | 49.924
2021-10-20 | 15:59 | 49.927
2021-10-20 | 15:59 | 49.929
2021-10-20 | 15:59 | 49.935
2021-10-20 | 15:59 | 49.94
2021-10-20 | 15:59 | 49.945
2021-10-20 | 15:59 | 49.95
2021-10-20 | 15:59 | 49.955
2021-10-20 | 15:59 | 49.959
2021-10-20 | 15:59 | 49.961
2021-10-20 | 15:59 | 49.962
2021-10-20 | 15:59 | 49.964
2021-10-20 | 15:59 | 49.966
2021-10-20 | 15:59 | 49.967
2021-10-20 | 15:59 | 49.969
2021-10-20 | 15:59 | 49.97
2021-10-20 | 15:59 | 49.97
2021-10-20 | 15:59 | 49.97
2021-10-20 | 15:59 | 49.968
2021-10-20 | 15:59 | 49.966
2021-10-20 | 15:59 | 49.963
2021-10-20 | 15:59 | 49.965
2021-10-20 | 15:59 | 49.965
2021-10-20 | 15:59 | 49.965
2021-10-20 | 15:59 | 49.966
2021-10-20 | 15:59 | 49.963
2021-10-20 | 15:59 | 49.963
2021-10-20 | 15:59 | 49.962
2021-10-20 | 15:59 | 49.963
2021-10-20 | 15:59 | 49.962
2021-10-20 | 15:59 | 49.961
2021-10-20 | 15:59 | 49.958
2021-10-20 | 15:59 | 49.956
2021-10-20 | 15:59 | 49.954
2021-10-20 | 15:59 | 49.955
2021-10-20 | 15:59 | 49.957
2021-10-20 | 15:59 | 49.957
2021-10-20 | 15:59 | 49.956
2021-10-20 | 15:59 | 49.954
2021-10-20 | 15:59 | 49.949
2021-10-20 | 15:59 | 49.946
2021-10-20 | 16:00 | 49.943
2021-10-20 | 16:00 | 49.945
2021-10-20 | 16:00 | 49.946
2021-10-20 | 16:00 | 49.95
2021-10-20 | 16:00 | 49.951
2021-10-20 | 16:00 | 49.951
2021-10-20 | 16:00 | 49.954
2021-10-20 | 16:00 | 49.954
2021-10-20 | 16:00 | 49.957
2021-10-20 | 16:00 | 49.958
2021-10-20 | 16:00 | 49.961
2021-10-20 | 16:00 | 49.961
2021-10-20 | 16:00 | 49.965
2021-10-20 | 16:00 | 49.969
2021-10-20 | 16:00 | 49.971
2021-10-20 | 16:00 | 49.974
2021-10-20 | 16:00 | 49.975
2021-10-20 | 16:00 | 49.975
2021-10-20 | 16:00 | 49.972
2021-10-20 | 16:00 | 49.971
2021-10-20 | 16:00 | 49.969
2021-10-20 | 16:00 | 49.967
2021-10-20 | 16:00 | 49.965
2021-10-20 | 16:00 | 49.962
2021-10-20 | 16:00 | 49.963
2021-10-20 | 16:00 | 49.961
2021-10-20 | 16:00 | 49.959
2021-10-20 | 16:00 | 49.96
2021-10-20 | 16:00 | 49.958
2021-10-20 | 16:00 | 49.958
2021-10-20 | 16:00 | 49.955
2021-10-20 | 16:00 | 49.952
2021-10-20 | 16:00 | 49.947
2021-10-20 | 16:00 | 49.947
2021-10-20 | 16:00 | 49.945
2021-10-20 | 16:00 | 49.949
2021-10-20 | 16:00 | 49.952
2021-10-20 | 16:00 | 49.955
2021-10-20 | 16:00 | 49.957
2021-10-20 | 16:00 | 49.962
2021-10-20 | 16:00 | 49.965
2021-10-20 | 16:00 | 49.966
2021-10-20 | 16:00 | 49.97
2021-10-20 | 16:00 | 49.968
2021-10-20 | 16:00 | 49.968
2021-10-20 | 16:00 | 49.97
2021-10-20 | 16:00 | 49.97
2021-10-20 | 16:00 | 49.972
2021-10-20 | 16:00 | 49.974
2021-10-20 | 16:00 | 49.979
2021-10-20 | 16:00 | 49.981
2021-10-20 | 16:00 | 49.985
2021-10-20 | 16:00 | 49.987
2021-10-20 | 16:00 | 49.985
2021-10-20 | 16:00 | 49.977
2021-10-20 | 16:00 | 49.968
2021-10-20 | 16:00 | 49.958
2021-10-20 | 16:00 | 49.947
2021-10-20 | 16:00 | 49.938
2021-10-20 | 16:00 | 49.933
2021-10-20 | 16:00 | 49.93
2021-10-20 | 16:01 | 49.929
2021-10-20 | 16:01 | 49.931
2021-10-20 | 16:01 | 49.932
2021-10-20 | 16:01 | 49.933
2021-10-20 | 16:01 | 49.934
2021-10-20 | 16:01 | 49.935
2021-10-20 | 16:01 | 49.937
2021-10-20 | 16:01 | 49.938
2021-10-20 | 16:01 | 49.941
2021-10-20 | 16:01 | 49.943
2021-10-20 | 16:01 | 49.951
2021-10-20 | 16:01 | 49.958
2021-10-20 | 16:01 | 49.967
2021-10-20 | 16:01 | 49.973
2021-10-20 | 16:01 | 49.981
2021-10-20 | 16:01 | 49.989
2021-10-20 | 16:01 | 49.994
2021-10-20 | 16:01 | 49.999
2021-10-20 | 16:01 | 50.003
2021-10-20 | 16:01 | 50.008
2021-10-20 | 16:01 | 50.011
2021-10-20 | 16:01 | 50.018
2021-10-20 | 16:01 | 50.023
2021-10-20 | 16:01 | 50.029
2021-10-20 | 16:01 | 50.035
2021-10-20 | 16:01 | 50.041
2021-10-20 | 16:01 | 50.045
2021-10-20 | 16:01 | 50.046
2021-10-20 | 16:01 | 50.049

## 20211022-1
In GMT
Date | Time | Freq
2021-10-22 | 7:02 | 50.011
2021-10-22 | 7:02 | 50.012
2021-10-22 | 7:02 | 50.016
2021-10-22 | 7:02 | 50.018
2021-10-22 | 7:02 | 50.017
2021-10-22 | 7:02 | 50.018
2021-10-22 | 7:02 | 50.019
2021-10-22 | 7:02 | 50.02
2021-10-22 | 7:02 | 50.021
2021-10-22 | 7:02 | 50.022
2021-10-22 | 7:02 | 50.019
2021-10-22 | 7:02 | 50.017
2021-10-22 | 7:02 | 50.012
2021-10-22 | 7:02 | 50.01
2021-10-22 | 7:02 | 50.003
2021-10-22 | 7:02 | 49.997
2021-10-22 | 7:02 | 49.994
2021-10-22 | 7:02 | 49.989
2021-10-22 | 7:02 | 49.984
2021-10-22 | 7:02 | 49.98
2021-10-22 | 7:02 | 49.975
2021-10-22 | 7:02 | 49.971
2021-10-22 | 7:02 | 49.968
2021-10-22 | 7:02 | 49.963
2021-10-22 | 7:02 | 49.961
2021-10-22 | 7:02 | 49.961
2021-10-22 | 7:02 | 49.962
2021-10-22 | 7:02 | 49.962
2021-10-22 | 7:02 | 49.962
2021-10-22 | 7:02 | 49.961
2021-10-22 | 7:02 | 49.961
2021-10-22 | 7:03 | 49.96
2021-10-22 | 7:03 | 49.96
2021-10-22 | 7:03 | 49.961
2021-10-22 | 7:03 | 49.963
2021-10-22 | 7:03 | 49.963
2021-10-22 | 7:03 | 49.963
2021-10-22 | 7:03 | 49.961
2021-10-22 | 7:03 | 49.964
2021-10-22 | 7:03 | 49.964
2021-10-22 | 7:03 | 49.966
2021-10-22 | 7:03 | 49.966
2021-10-22 | 7:03 | 49.967
2021-10-22 | 7:03 | 49.969
2021-10-22 | 7:03 | 49.972
2021-10-22 | 7:03 | 49.974
2021-10-22 | 7:03 | 49.976
2021-10-22 | 7:03 | 49.976
2021-10-22 | 7:03 | 49.977
2021-10-22 | 7:03 | 49.976
2021-10-22 | 7:03 | 49.973
2021-10-22 | 7:03 | 49.969
2021-10-22 | 7:03 | 49.967
2021-10-22 | 7:03 | 49.964
2021-10-22 | 7:03 | 49.963
2021-10-22 | 7:03 | 49.96
2021-10-22 | 7:03 | 49.962
2021-10-22 | 7:03 | 49.961
2021-10-22 | 7:03 | 49.959
2021-10-22 | 7:03 | 49.956
2021-10-22 | 7:03 | 49.957
2021-10-22 | 7:03 | 49.953
2021-10-22 | 7:03 | 49.951
2021-10-22 | 7:03 | 49.947
2021-10-22 | 7:03 | 49.946
2021-10-22 | 7:03 | 49.943
2021-10-22 | 7:03 | 49.941
2021-10-22 | 7:03 | 49.936
2021-10-22 | 7:03 | 49.933
2021-10-22 | 7:03 | 49.934
2021-10-22 | 7:03 | 49.934
2021-10-22 | 7:03 | 49.934
2021-10-22 | 7:03 | 49.937
2021-10-22 | 7:03 | 49.938
2021-10-22 | 7:03 | 49.94
2021-10-22 | 7:03 | 49.942
2021-10-22 | 7:03 | 49.942
2021-10-22 | 7:03 | 49.946
2021-10-22 | 7:03 | 49.949
2021-10-22 | 7:03 | 49.953
2021-10-22 | 7:03 | 49.956
2021-10-22 | 7:03 | 49.96
2021-10-22 | 7:03 | 49.962
2021-10-22 | 7:03 | 49.967
2021-10-22 | 7:03 | 49.966
2021-10-22 | 7:03 | 49.964
2021-10-22 | 7:03 | 49.966
2021-10-22 | 7:03 | 49.968
2021-10-22 | 7:03 | 49.971
2021-10-22 | 7:03 | 49.97
2021-10-22 | 7:04 | 49.971
2021-10-22 | 7:04 | 49.972
2021-10-22 | 7:04 | 49.974
2021-10-22 | 7:04 | 49.974
2021-10-22 | 7:04 | 49.975
2021-10-22 | 7:04 | 49.976
2021-10-22 | 7:04 | 49.975
2021-10-22 | 7:04 | 49.975
2021-10-22 | 7:04 | 49.976
2021-10-22 | 7:04 | 49.977
2021-10-22 | 7:04 | 49.978
2021-10-22 | 7:04 | 49.977
2021-10-22 | 7:04 | 49.978
2021-10-22 | 7:04 | 49.975
2021-10-22 | 7:04 | 49.973
2021-10-22 | 7:04 | 49.97
2021-10-22 | 7:04 | 49.969
2021-10-22 | 7:04 | 49.965
2021-10-22 | 7:04 | 49.965
2021-10-22 | 7:04 | 49.965
2021-10-22 | 7:04 | 49.963
2021-10-22 | 7:04 | 49.962
2021-10-22 | 7:04 | 49.964
2021-10-22 | 7:04 | 49.966
2021-10-22 | 7:04 | 49.967
2021-10-22 | 7:04 | 49.966
2021-10-22 | 7:04 | 49.969
2021-10-22 | 7:04 | 49.972
2021-10-22 | 7:04 | 49.976
2021-10-22 | 7:04 | 49.979
2021-10-22 | 7:04 | 49.982
2021-10-22 | 7:04 | 49.981
2021-10-22 | 7:04 | 49.981
2021-10-22 | 7:04 | 49.983
2021-10-22 | 7:04 | 49.984
2021-10-22 | 7:04 | 49.983
2021-10-22 | 7:04 | 49.983
2021-10-22 | 7:04 | 50.01
2021-10-22 | 7:04 | 50.075
2021-10-22 | 7:04 | 50.144
2021-10-22 | 7:04 | 50.198
2021-10-22 | 7:04 | 50.237
2021-10-22 | 7:04 | 50.263
2021-10-22 | 7:04 | 50.278
2021-10-22 | 7:04 | 50.283
2021-10-22 | 7:04 | 50.283
2021-10-22 | 7:04 | 50.279
2021-10-22 | 7:04 | 50.273
2021-10-22 | 7:04 | 50.265
2021-10-22 | 7:04 | 50.257
2021-10-22 | 7:04 | 50.25
2021-10-22 | 7:04 | 50.241
2021-10-22 | 7:04 | 50.234
2021-10-22 | 7:04 | 50.228
2021-10-22 | 7:04 | 50.224
2021-10-22 | 7:04 | 50.222
2021-10-22 | 7:04 | 50.22
2021-10-22 | 7:04 | 50.22
2021-10-22 | 7:04 | 50.22
2021-10-22 | 7:04 | 50.22
2021-10-22 | 7:04 | 50.221
2021-10-22 | 7:05 | 50.222
2021-10-22 | 7:05 | 50.225
2021-10-22 | 7:05 | 50.227
2021-10-22 | 7:05 | 50.228
2021-10-22 | 7:05 | 50.228
2021-10-22 | 7:05 | 50.23
2021-10-22 | 7:05 | 50.226
2021-10-22 | 7:05 | 50.223
2021-10-22 | 7:05 | 50.22
2021-10-22 | 7:05 | 50.215
2021-10-22 | 7:05 | 50.211
2021-10-22 | 7:05 | 50.208
2021-10-22 | 7:05 | 50.208
2021-10-22 | 7:05 | 50.209
2021-10-22 | 7:05 | 50.211
2021-10-22 | 7:05 | 50.211
2021-10-22 | 7:05 | 50.21
2021-10-22 | 7:05 | 50.208
2021-10-22 | 7:05 | 50.206
2021-10-22 | 7:05 | 50.205
2021-10-22 | 7:05 | 50.207
2021-10-22 | 7:05 | 50.21
2021-10-22 | 7:05 | 50.212
2021-10-22 | 7:05 | 50.217
2021-10-22 | 7:05 | 50.221
2021-10-22 | 7:05 | 50.224
2021-10-22 | 7:05 | 50.225
2021-10-22 | 7:05 | 50.225
2021-10-22 | 7:05 | 50.222
2021-10-22 | 7:05 | 50.22
2021-10-22 | 7:05 | 50.215
2021-10-22 | 7:05 | 50.209
2021-10-22 | 7:05 | 50.203
2021-10-22 | 7:05 | 50.195
2021-10-22 | 7:05 | 50.189
2021-10-22 | 7:05 | 50.183
2021-10-22 | 7:05 | 50.176
2021-10-22 | 7:05 | 50.169
2021-10-22 | 7:05 | 50.163
2021-10-22 | 7:05 | 50.162
2021-10-22 | 7:05 | 50.161
2021-10-22 | 7:05 | 50.163
2021-10-22 | 7:05 | 50.161
2021-10-22 | 7:05 | 50.16
2021-10-22 | 7:05 | 50.16
2021-10-22 | 7:05 | 50.16
2021-10-22 | 7:05 | 50.16
2021-10-22 | 7:05 | 50.162
2021-10-22 | 7:05 | 50.163
2021-10-22 | 7:05 | 50.162
2021-10-22 | 7:05 | 50.157
2021-10-22 | 7:05 | 50.155
2021-10-22 | 7:05 | 50.152
2021-10-22 | 7:05 | 50.152
2021-10-22 | 7:05 | 50.152
2021-10-22 | 7:05 | 50.153
2021-10-22 | 7:05 | 50.155
2021-10-22 | 7:05 | 50.156
2021-10-22 | 7:05 | 50.155
2021-10-22 | 7:06 | 50.154
2021-10-22 | 7:06 | 50.156
2021-10-22 | 7:06 | 50.158
2021-10-22 | 7:06 | 50.163
2021-10-22 | 7:06 | 50.164
2021-10-22 | 7:06 | 50.165
2021-10-22 | 7:06 | 50.163
2021-10-22 | 7:06 | 50.161
2021-10-22 | 7:06 | 50.16
2021-10-22 | 7:06 | 50.159
2021-10-22 | 7:06 | 50.156
2021-10-22 | 7:06 | 50.151
2021-10-22 | 7:06 | 50.148
2021-10-22 | 7:06 | 50.143
2021-10-22 | 7:06 | 50.141
2021-10-22 | 7:06 | 50.141
2021-10-22 | 7:06 | 50.141
2021-10-22 | 7:06 | 50.139
2021-10-22 | 7:06 | 50.137
2021-10-22 | 7:06 | 50.136
2021-10-22 | 7:06 | 50.134
2021-10-22 | 7:06 | 50.133
2021-10-22 | 7:06 | 50.134
2021-10-22 | 7:06 | 50.135
2021-10-22 | 7:06 | 50.131
2021-10-22 | 7:06 | 50.131
2021-10-22 | 7:06 | 50.131
2021-10-22 | 7:06 | 50.134
2021-10-22 | 7:06 | 50.136
2021-10-22 | 7:06 | 50.142
2021-10-22 | 7:06 | 50.145
2021-10-22 | 7:06 | 50.145
2021-10-22 | 7:06 | 50.144
2021-10-22 | 7:06 | 50.145
2021-10-22 | 7:06 | 50.145
2021-10-22 | 7:06 | 50.142
2021-10-22 | 7:06 | 50.139
2021-10-22 | 7:06 | 50.135
2021-10-22 | 7:06 | 50.133
2021-10-22 | 7:06 | 50.131
2021-10-22 | 7:06 | 50.128
2021-10-22 | 7:06 | 50.126
2021-10-22 | 7:06 | 50.126
2021-10-22 | 7:06 | 50.125
2021-10-22 | 7:06 | 50.122
2021-10-22 | 7:06 | 50.119
2021-10-22 | 7:06 | 50.119
2021-10-22 | 7:06 | 50.118
2021-10-22 | 7:06 | 50.118
2021-10-22 | 7:06 | 50.114
2021-10-22 | 7:06 | 50.107
2021-10-22 | 7:06 | 50.101
2021-10-22 | 7:06 | 50.097
2021-10-22 | 7:06 | 50.096
2021-10-22 | 7:06 | 50.097
2021-10-22 | 7:06 | 50.097
2021-10-22 | 7:06 | 50.096
2021-10-22 | 7:06 | 50.095
2021-10-22 | 7:06 | 50.091
2021-10-22 | 7:06 | 50.088
2021-10-22 | 7:06 | 50.081
2021-10-22 | 7:07 | 50.074
2021-10-22 | 7:07 | 50.069
2021-10-22 | 7:07 | 50.064
2021-10-22 | 7:07 | 50.057
2021-10-22 | 7:07 | 50.047
2021-10-22 | 7:07 | 50.036
2021-10-22 | 7:07 | 50.028
2021-10-22 | 7:07 | 50.019
2021-10-22 | 7:07 | 50.008
2021-10-22 | 7:07 | 50.006
2021-10-22 | 7:07 | 50.004
2021-10-22 | 7:07 | 50.004
2021-10-22 | 7:07 | 50.001
2021-10-22 | 7:07 | 50.003
2021-10-22 | 7:07 | 50.005
2021-10-22 | 7:07 | 50.005
2021-10-22 | 7:07 | 50.002
2021-10-22 | 7:07 | 50.001
2021-10-22 | 7:07 | 50
2021-10-22 | 7:07 | 49.999
2021-10-22 | 7:07 | 50
2021-10-22 | 7:07 | 50
2021-10-22 | 7:07 | 50
2021-10-22 | 7:07 | 50
2021-10-22 | 7:07 | 50.001
2021-10-22 | 7:07 | 50.004
2021-10-22 | 7:07 | 50.003
2021-10-22 | 7:07 | 50.003
2021-10-22 | 7:07 | 50.002
2021-10-22 | 7:07 | 50.003