## Future Networks
Consultation Questions
What further changes to your network will be needed to enable rapid and accurate restoration of services and ensure robust levels of local power resilience?
Could automation be used to speed up restoration? If so, where and how could automation be used?
No | Responses
1 | Whilst we are not a network operator,our smaller embedded hydro stations are currently involved in the Distributed ReStart project. This experience has highlightedthe following issues to us. Whilst most smaller,embedded generators(with various different fuel types)can probably be upgradedto meet the current Black Startrequirements and pass the current CapabilityAssessmenti.e. starting a unit and making it ready to energise the network, the real problems start during network energisation. Energising lines does not currently appear to be an issue, however energising transformers does appear to create problems as the transient overvoltages frequently trip the generator. Whilst accepting the Distributed ReStart project is still trialling methods of energising transformers using lower voltages and Point on Wave relays, this highlights thatthere needsto be a joint approach between any generator and the network to come up with a combined solution. It is clear that just specifying generator requirements and assuming the generator will then be able to energise the network is unlikely to work and there needs to be a joint plan of works involving both the generator and network operator to get a solution which will work together
2 | We do not consider significant automation is possible. The provisionof Black Start services will always require significant manual input, skill, training and expertise.
3 | We would like to highlight following network requirements that will aid us in supplying through our and the connected network during system restoration Building system resilience for Renewable Generators Renewable generators as restoration service providers will need to build and maintain network, additional plant equipment and restoration service capabilities. Network requirements for renewable generators should be specified as part of the overall technical requirements for the ESRS framework. Such requirements will possibly also require generator substation equipment and convertors to be able to operate and adjust outputs under power islanding and/or weak grid conditions. Renewable generators will need to consider these network requirements as part of their overall cost for new builds and may need to retrofit or upgrade existing sites to meet the defined requirements, which needs to be incentivised through the ESRS framework. Network performance in transient conditions The system resilience under transient network conditions especially in a weak grid needs to be adequately tested and ensured. The performance of transformers and switch gear under transient voltage conditions and presence of inrush currents need to be assessed and adequate solutions need to be in place to avoid these risks in a real restoration scenario. Left unchecked, these could prove to be major barriers to a smooth restoration process. Accurate system asset data, characterisation curves and asset health information, will aid in assessment of viability of restoration process and minimise risk of failure of a planned restoration action. Protection and control philosophy: Current protection and control philosophy for both networks and generators needs to be studied and adapted for system restoration conditions. Adaptive protection will most probably be required, to avoid protection mal-tripping in a restoration scenario. System models, studies and transient simulation studies should include protection relays and automated control systems to accurately predict their behaviour under different system restoration scenarios. A review of current protection and control Electricity System Restoration Standard – Implementation Consultation systems operating in low fault levels conditions is needed to build adaptability where required and avoid maloperation during critical system restoration process. If necessary, provisions should be made for financial incentives to be provided to upgrade protection and control systems to be more flexible and adaptive to increase resilience of the ESRS methodology. TO/DNO-Generator collaboration for strategic placement of system restoration service provider: TO/DNOs should be given an active role and say in strategic requirements for their network restoration service requirements. They should be able to influence based on their knowledge of networks, locational placement of restoration services and participate in selection of the type of technology to be installed. TO/DNOs should also be allowed to actively engage with renewable generator developers to assess technical and communication network requirements to ensure adequacy and resilience of restoration services.
4 | We support use of advanced automation to speed up overall restoration process. We believe that though central co-ordination will be crucial in ensuring system wide restoration, automation can ease the burden on ESO and TO control centre staff, who would need to deal with a huge number of signals, alarms and information during a system restoration process. Increased computational capability and scenario modelling at control centres Automated assessment of the network behaviour and predicted sequence of events both during system restoration planning and actual restoration process will be critical. Control centre staff need to be equipped with tools and computational capacity to automate assessment of large quantity of data and run scenarios to identify fast routes to restoration. Provided, there will be a number of restoration providers participating in the restoration process and the number of signals received by control centres will significantly increase, it will only be prudent to automate part of this assessment to aid the staff to make accurate decisions. Dynamic visibility and Self-healing Grid: Automation and control currently largely rely on low frequency data, which only provides limited visibility of the network conditions. Dynamic visibility of restoration service providers and the network in general using high frequency data (e.g. synchrophasors) will allow better assessment of network parameters and identification of any underlying disturbances, that would otherwise go unnoticed. Dynamic visibility will speed up restoration process by providing detailed picture of the system and allowing operators to safely energise larger parts of the network and synchronise power islands. Dynamic visibility of the network can also be used to run locational or wide-area automated and control schemes, that will automatically identify any network issues and isolate or connect parts of the network depending on wider network conditions within configurable time frames, without manual intervention. Resilience of automation It is largely assumed that system restoration services will be required during a power network failure, which will be a low probability high impact event. However, increasingly it is apparent through few unplanned outage incidents e.g. in August 2019, that such outages due to increased complexity of the network and connected generators will be cascading in nature, where one event triggers a cascading set of events, that potentially results in a large-scale power outage. In addition, cyber-attacks are more prevalent and commonplace now and cyber attackers have a particular interest in power grids. In summary, the next large-scale power outage could be a result of mal-operation and cascading events or a large-scale cyber-attack, crippling the centralised control of the grid. Resilience of the grid and connected generators, should include resilience of automation. This implies, in case of an unusual event the restoration service provider or simply a generator should be able to withstand the event without being disconnected and/or should be able to self-restart its communication interfaces and reset its protection systems in a safe manner. This is analogous to fault-ride-through but for a non-power system related event.
5 | We are not a network operator, however we strongly request that network system design parameters and communication links are in place to enable the interaction with assets and that fail-safe modes are in place to protect both the integrity of the network, as well as active communication links between all ESR participating parties.
6 | Of course - but automation could also be feasibly responsible for increasing the rate of system collapse, should any auto trigger be wrongly activated. Automated systems are inherently open to cyber-attack which must be prevented at all costs. We recommend caution over the level of automation to be considered.
7 | Network Resilience – Ensure transmission, Grid Supply Point (GSP) and primary (33/11kV) substations have resilience (protection and telecoms) for 72hrs (if not already available). • Protection – Carry out assessments to ensure existing protections are adequate with initially weak (low fault level) networks being established. • Generator Secondary availability – Ensure strategic transmission connected generators and DER have resilient comms and an agreed ‘time to connect’ following a blackout, to ensure they are available to supplement generation on the network as required following their connection point being energised. • Strategic Restoration Plans - Develop restoration plans to energise the network to strategic transmission connected generators and DER first e.g. steam generators to keep their boilers warm or wind farm 33kV arrays to keep turbines ‘warm’. • Grid Forming Converters (GFC) – Ensure that strategic converter connected generators (e.g. Battery Energy Storage Systems [BESS} or windfarms) have GFCs that would enable them to connect to a weak network, or initiate energisation of the network as required. • Mvar Neutral Networks – have equipment (e.g. synchronous compensators,BESS) on the network to ensure that it can be energised ‘Mvar neutral’ and thus allow the maximum possible network to be energised. i.e. the Mvars generated by the network are absorbed to eliminate any over voltage issues and exceeding the capability of the anchor generator. • Live Network Testing – Carry out initial and regular live testing to prove as much of the restoration plans as practical. Network simulations, while useful, are no substitute for ensuring a network can be energised in practice. In addition, it is essential for the operational staff to gain experience of operating the network in a non-standard configuration.
8 | Distribution Restoration Zones (DRZs) - Automation could be used to establish distribution power islands at the 33kV GSP level (see the attached for an explanation of the Distribution Restoration Zone Controller [DRZC] which facilitates this). • Adaptive Protections Settings – Ensure any protection setting alteration requirements can be made automatically through the SCADA system (modern protection relays which facilitate ‘Group 2’ settings will be required). • EMS/DMS ‘Scripting’ - To configure the transmission/distribution networks for initial restoration after a black out (e.g. open/close circuit breakers, change protection settings), programme ‘scripts’ within existing EMS/DMS such that only a single control command is required to carry out multiple network operations.
9 | To support low-carbon black-start capability, the deployment of lithium-ion batteries with grid-forming inverters should be incentivised.
10 | We would welcome wider automation to encourage the use of more low-carbon flexible assets, rather than traditional forms of dispatchable generation (e.g. coal / gas plants).

## Regulatory Framework
Consultation Questions
Do you have any early views on which codes and/or licence obligations will need to be changed to allow implementation of the ESRS?
When must code changes be in place to allow you to deliver the potential changes required to implement the ESRS by December 2026?
No | Responses
1 | Depends on the change.
2 | Existing windfarms in GB are protected by Grid Code (CC.6.3.15.3) and Distribution Code requirements, and as such, are prevented from operating in islanded mode when the network is not available. The Grid Code should allow islanding of a power park module (or any grid forming technology) under system restoration conditions. Even under no wind conditions, the grid forming capability of the converter can contribute to the restoration service. We have demonstrated this during our trials where with no wind, the site managed to contribute by absorbing reactive power to the restoration of the system. The Grid Code should also focus on type of protection required specific for restoration services under low fault level conditions. The Grid Code working group GC0137 Minimum Specification Required for Provision of GB Grid Forming Capability modification is currently awaiting Ofgem approval. This modification proposes to add a non-mandatory technical specification to the Grid Code, relating to GB Grid Forming Capability (which was formerly referred to as a Virtual Synchronous Machine (“VSM”) capability). This will be key to providing detailed requirements to renewable generators to provide grid forming and restoration capabilities. We urge NG ESO and Ofgem, to avoid any further delay in approval of this key crucial modification. SPR will also like to highlight that for distribution connected sites, EREC G99 will need also need reviews and modification to enable restoration process through distributed energy resources. This stage is too early to identify the specific areas of CUSC and consequential changes on STC, this needs to be worked through the ESRS working groups. There is a high urgency in requirement for the Grid Codes to change to allow more technologies to participate in the restoration process. When restoration service providers; such as generators, storage, interconnectors etc., know this codified position of the specific technical requirement that they will need to meet, those providers can then prepare to carry out the following activities in time to deliver for December 2026. The longer it takes to reach a conclusion to the codified situation, the more risk will continue to increase in the achievement of the December 2026 deadline.
3 | It concerns us that code changes are described throughout this consultation as necessary and anticipated in number. Whilst we are supportive in ensuring operational requirements are capable of being met, unambiguous and easily discoverable, we are concerned that code changes may act to mandate the permanent adoption by generating companies of upgraded measures and operational capability across their asset base without recompense or foresight of the complexities involved. We are concerned that so-called uncontracted ESR providers may be required to deploy new measures not contained within existing operational plans or maintained technical capability and that any or all (contracted or not) generating plant may face new consequences, cost or fines should parameters relating to any new code change be unobtainable or unreliably available to a prudent and experienced plant operator.
4 | To allow full implementation of the ESRS then changes are likely to be required to the main Technical Codes (Grid Code and Distribution Code). However, work undertaken by the Distributed ReStart project has developed modified legal text for these documents which would allow the learnings from this project to be implemented into these codes. In addition, the System Restoration Plan and associated Test Plan which are required under the Emergency & Restoration Network Code (as retained in UK law) will require to be modified to reflect the change in restoration requirements and strategy needed to achieve the targets established within the ESRS.
5 | To allow for any necessary changes to be implemented into either the Transmission, Distribution or potential service providers networks and systems then changes should be implemented as soon as possible. This would maximise the time available to those affected parties to secure the funding and undertake the necessary investments required ahead of the 2026 deadline for compliance. It should be noted that currently GC0148 is looking to implement measures arising from the Emergency and Restoration Code and these will have to be implemented by December 2022, so coordination to avoid introducing conflicting requirements will be needed to ensure the smooth implementation of new / enhanced requirements by industry.
6 | We think that code changes should be in place by September 2023. Failing this, they should be in place at least two years prior to December 2026.

## Markets & Finding Mechanism
Consultation Questions
Do you see any commercial barriers to entry that may prevent a fair and competitive market for a restoration service across Transmission and Distribution connected technologies? If so, what changes are needed to ensure the ESO provides a level playing field for the provision of restoration services?
We currently use pay-as-bid, do you think that pay-as-bid is an appropriate pricing method for Restoration services? If not, what mechanism do you think better meets the objectives?
Do you think cost pass-through and BSUoS recovery is the correct approach for Restoration Services?
How might we best incentivise providers to design capability as part of their connection?
Do you agree that network costs associated with implementation of ESRS should be recovered through price controls? If not, what funding mechanism do you favour?
No | Responses
1 | It is difficult to operate a competitive market for Black Start services when the service providers technical capabilities vary so much.
2 | Given that Black Start services lack sufficient product homogeneity, a pay as bid approach is likely to be the only feasible approach.
3 | The contracts need also to reflect the range of services being provided by the Black Start plant: the more services, the higher the value of the contract, because other contracts are not needed for those other services, and because other plants do not have to be started in order to provide them. These should be wrapped into a single Black Start contract. Where a single plant cannot provide all the required services (e.g. the full range of grid stability services), other plants that can provide these missing services should be included in a “re-start collective unit” in order to provide the full requirement. Such a unit should lose its contract (after warnings, if appropriate) if any capability is lost, i.e. a service can no longer be provided by the unit.
4 | We believe that competitive tenders are the key method for which to procure restoration services. However, in the initial stage of inclusion of new technology in the ESRS framework, NG ESO need to appreciate the key differences between the conventional power stations and windfarms (particularly offshore installations) which results in higher upfront costs for windfarms to achieve the restoration capability. We strongly believe it will prove difficult to come up with a solution to incentivise/support deliveryfrom renewables plant while also pursuing the ambition to move away from bilateral contracts and secure the capability required through a transparent market. Therefore, we urge NG ESO to review their position in their transitional strategy to ensure technology diversity for implementation of the ESRS by 2026. Within the competitive process itself, also, we believe there needs to be more flexibility over: 1. Earlier service start date (which we have seen in the Stability Pathfinder 2 tender) 2. Later service start date (assets which may miss the first year of a 10-year service should still be considered if they are best placed to provide a service) We believe in order to create a level playing field for renewable generators, including offshore and onshore wind and to incentivise providers to design capability following early indicators are crucial. Provision for early and clear requirements for technology diversification: Current system restoration technical requirements still largely require a bundle of services to be provided from a single plant, which translates to a large CAPEX investment for renewable generators without any clear route to market for return. Early indication by NG ESO is that given the complexity of network and urgency of requirement to diversify technology portfolio for restoration services, renewable generator types and types of services required in different restoration regions need to be clearly identified. Different options should be created on case by case basis for provision of services, and there should not be a one bundle fits all type of approach while assessing any technology that can be valuable to the whole restoration process. Define clear role for 40 GW of Offshore Wind Generation Offshore wind will need to be incentivised in restoration strategy and procurement processes. Plans of having 40GW of Offshore wind to be connected by 2030 require significant degrees of coordination and offshore wind technology must be required to play a part in the restoration strategy, notwithstanding its link to the OTNR project. The capability must be requested by NGESO in the early stages of the design, otherwise it won’t be practical to re-plant equipment offshore to enable the capability. Offshore windfarms are operating in a highly competitive environment, so the capability won’t be built in by default if there’s no certainty around securing a contract to deliver the restoration service. Timescales for the procurement process need to allow for the new pipeline of offshore projects to take decisions in the early stages of their design. Emerging technology and innovation are growing at a pace that NGESO must ensure they have a grasp of in order that procurement can align. Capabilities should not be lost as a result of insufficient engagement to understand the value and opportunities available to support the grid. Furthermore, and given the highly competitive nature of the CfD regime, Electricity System Restoration Standard – Implementation Consultation Offshore windfarm developers must have certainty and lead times of requirements from NG ESO to consider developing restoration capabilities. Retrofitting in large windfarm projects is not desirable and may not be feasible especially in offshore projects due to the potential loss in generation and complexity of adding new systems to systems that are not designed to provide restoration services. We already experienced this challenge on a restoration service trial. Established Route-to-Market: We appreciate the commercial and regulatory difficulties for NG ESO to provide a level of information and transparency that could compromise the realisation of the restoration strategy in GB. However, we would welcome more transparency about the zone requirements and how these are to be covered over time in long term. Without an understanding of the actual needs from the SO and TOs, it is difficult to get a market signal that allows potential providers to invest on new capabilities. Clear Indication of Technology Diversification: Key performance indicators (KPIs) need to be included in the methodology for ensure adaptation to NetZero targets. Ensuring the ESRS assurance framework accounts for technology diversification in alignment with the technology portfolio that’s to become the backbone if the electricity generation in the future could form part of these new Net Zero KPIs. We believe these new KPIs should be included in as part of Procurement Principle 2, related to Competition. Development of Local Joint Restoration Plans with Developers (LJRP) Power Islands are developed in line with LJRPs which are agreed alongside a Restoration service contract and set out the activities and steps that the Restoration Service Providers, relevant TO, DNO and ESO will carry out during a NPO event. Renewable developers who have connection agreements and/or are in the process of obtaining one, should be considered and where possible involved early in the development of LJRPs. This will provide an incentive to the developer to design capability based on the regional restoration requirements.
5 | We have no issues with the pay-as-bid method of procurement.
6 | We believe that BSUoS is the correct approach for cost recovery.
7 | We believe that the network costs of ESRS implementation should be recovered through price controls. Given the unique and vitally important nature of the ESRS, ‘re-openers’ during the price control period should be frequent in order to facilitate additional spend if required. The locational element of ESRS should not be underestimated, with different geographical areas of the network requiring vastly different levels of spend. This should not be overlooked during the price control/re-opener process.
8 | It is good that National Grid and Ofgem are looking to open out the process for new providers. However this initiative will not encourage the construction of appropriate new Black Start capacity unless contracts are awarded for it prior to construction and even (with an enforceable Letter of Intent) prior to planning. This is because of the considerable investment (in 7 or 8 figures) that is needed even in the early stages of developing such plants on the higher-voltage levels of the grid – and plants are indeed needed on these parts of the grid where lower-voltage grid sections cannot, of their very nature, re-start higher-voltage grid sections because they lack the requisite capacity (power and duration) and inertia.
9 | We feel strongly that current standard commercial terms greatly disincentivise any form of participation because it offers no mechanism to limit liabilities or any form of indemnity from plant damage. Current standard terms force participants to accept unquantifiable and uncapped liabilities on behalf of their operating company, thereby providing a valuable service for little net reward. We feel that this situation is unsustainable and becomes more relevant with greater levels of complexity and participants involved in a single restoration event i.e. there is greater likelihood of things going wrong and uncapped liabilities being faced. We strongly recommend that the methodologies for the coverage of testing costs are amended from the current standard form approach to being based on a cost reflective (neutral) position, calculated and agreed at the time of testing. Current standard terms require providers to include for all testing costs against a defined scope of testing at the time the service is tendered for, which can be up to 7 years in advance. Market (risk) volatility is therefore priced into tendered costings resulting in upward pricing pressure and price distortions depending upon the costing approach for testing taken by individual participants at the time of tendering. The implementation measures described in this consultation consider the need for a greater focus on testing all parts of contracted ESR capability, therefore ESO testing resource shall face greater demands as will network bookings to facilitate greater numbers of test requirement. This should be expected to consequently leave available less flexibility in the timing of test activities and therefore decrease the likelihood that low cost test periods would always be available to a provider over the tenure of their ESR agreement. We observe that there is a high cost to participation, an increasing number of competitor solutions and very small number of new services required, particularly once the first new-form procurement events have been run in each restoration zone. We observe that there is high cost, risk and complexity in asset conversions towards ESR capability and therefore sharp downward pressure on liquidity (number of participants) in future procurement rounds. We advise that service providers with funded plant will be frustrated in not being able to utilise that funded plant for the provision of any additional and necessary services in a traded marketplace without loss of revenue from their ESR. These terms will actively sterilise the availability of plant from the network due to the reluctance of any plant operator to swap BSAP revenue for more uncertain revenues facing risk over delivery in other marketplaces.
10 | The ESR tender process requires the participant to set out a detailed breakdown of projected capital and testing costs as a component of the tender pack. If successful, the participant must provide evidence of the spend in order to recover the costs from the ESO. Pay-as-bid seems entirely appropriate with this in mind. Pay-as-clear, for example, is appropriate and widely recommended for standardised products i.e. where MWh is the unit. ESR demands a lot more than simply the energy generated during an NPO. Pay-as-clear would ensure that the cheapest solutions are always accepted, and therefore potentially ignoring the considerable restorative benefits that a large thermal plant brings to the table.
11 | Cost pass-through and BSUoS recovery may be an appropriate mechanism for the procurement of capabilities envisaged within the scope of the document consulted upon, however, these methodologies may be inappropriate when considering the integration of cost associated with new and emergent decarbonisation technologies and industrial partners anticipated within the next 10 year period. We are unsure how implementation measures described in this consultation document consider the near-term need for viable Hydrogen fuel production and transport and the availability of downstream CCS infrastructure during total or partial NPO scenarios once the power sector invests and adapts into emergent decarbonised generation solutions. ESR providers will be reliant upon these new and emergent industries such to be able and capable to operate, therefore we feel funding and cost recovery mechanisms should look ahead and be capable of facilitating requirements once decarbonised modes of power generation are retrofitted across the total UK infrastructure chain.
12 | This may be achieved by designing transparent mechanisms through which investors are rewarded for considering design criteria prior to their Final Investment Decision. Such commercial processes should work in harmony with existing (new) implementation strategies and consider the impact and importance of certainty/likelihood of ESR revenues such that informed investment decisions may be possible (otherwise likely defaulting away from inherent ESR capability to the fullest extent). Please also refer to our response to Q4 above concerning uncapped liabilities and indemnity clauses within standard ESR terms.
13 | The application of the TNUoS methodology should also be considered for the recovery of network costs associated with the implementation of ESRS.
14 | Yes, we would agree that network costs associated with implementation of ESRS should be funded through the RIIO-ET and RIIO-ED price control frameworks. It will therefore be important that the relevant reopener mechanisms within these frameworks, such as the Medium Sized Infrastructure Projects (MSIP) have the necessary scope and flexibility to accommodate such funding. At the moment, we believe this to be the case with the finalised RIIO-T2 framework, however, review of the RIIO-T2 and finalised RIIO-ED2 frameworks may be required, following the necessary code changes to consider whether any further changes are needed to the relevant licences, to reflect any grid code changes.
15 | We think that the current commercial framework does not reflect the changing technical abilities of new assets connecting to the grid. Commercial effectiveness should be determined by technical abilities, such as connection voltage and location. For example, using the Pennines reactive power Pathfinder, certain locations and voltages were given 100% effectiveness, with decreasing weightings depending on 1. connection voltage at national grid, and 2. connection voltage at the distribution network.
16 | We have no issue with pay-as-bid as per the Pathfinder process (stability, reactive, constraint management). This allows for effective price discovery for first-of-a-kind solutions. However, over the long term, as markets for system services needed in low-carbon energy networks become more established, we think that a pay-as-clear approach should be adopted. Price transparency should be a key issue in whatever changes are made to black start services. Black start prices are currently opaque, and this should be remedied to prevent barriers to those wishing to provide black start services.
17 | We agree that cost pass-through and BSUoS recovery is a viable approach.
18 | Information on pricing, locations, and system requirements should be more widely available. Running longer-term contracts should incentivise capacity to deploy in the right places.
19 | We agree that network costs associated with ESRS implementation should be recovered through price controls.

## Modelling & Restoration Tool
Consultation Question
Do you have a view on the adoption of a deterministic model over a probabilistic model?
No | Responses
1 | Difficult to give views on this as there is little transparency of the Black Start models.
2 | We believe with the ever-increasing reliance on the electricity system, NG ESO must ensure it maintains credible and robust restoration plans to achieve a fast recovery. The current power system is changing and evolving, and given the degree of uncertainty it will be prudent to continuously check and improve modelling requirements and consider a greater number of scenarios and possibilities, rather than to focus on more economic scenarios based on a lower probability. The modelling process should account for a range of scenarios and factors, and also to account for processes and methods not working in the way expected during the restoration process. It will be crucial to build extra margins and to account for multiple scenarios in the modelling process. We would like to offer our support if NG ESO feels it can better validate the models through enhanced restoration testing. We believe modelling and validation of models for this system critical process, cannot be the remit of NG ESO alone. NG ESO will need support and engagement from the industry especially from restoration service providers to ensure the models are complete and accurate. This will require a degree of time and financial investment; however, it will help to reduce the uncertainties and the level risks associated. It will also help firm up assumptions made in the modelling process and allow for diverse scenario planning.
3 | The information in the consultation document does not detail the modelling approach taken by the ESO or the specification of the developed modelling tool, therefore it is difficult to provide a coherent response to this question. In principle probabilistic modelling is more suited to representing uncertainty, particularly if the criteria are statistical. If the ESO are needing to understand the probability distribution of various events/parameters it is clear that a deterministic modelling approach would not be appropriate. Whatever the modelling tool used, and however it may be specified, it shall always be fundamentally important to use good quality and appropriately scaled inputs
4 | Deterministic models and probabilistic models for any power outage situation can give very different results based on observations of data, assumptions about the context, and on theoretical probability. The model can then be used to make predictions, test assumptions, and solve problems. A deterministic model does not include elements of randomness. Every time you run the model with the same initial conditions you will get the same results. A probabilistic model includes elements of randomness. Every time you run the model, you are likely to get different results, even with the same initial conditions. A probabilistic model is one which incorporates some aspect of random variation. A deterministic model of the ESRS situation would use the average time (where random variation is relatively small) to start/stabilise generation, energise/grow the DNO and or National Transmission Electricity Network and restore known demand blocks thus giving a linear result. This will continue until the model determines an issue and stops, or restoration is completed. It would also assume on average that all other external influencing factors from manpower availability, raw materials such as fuel, wind, water, sunlight are available which would assist in restoration. The probabilistic model of the same ESRS situation would give a different result as it would assume a greater variation in all the factors mentioned above and therefore restoration following an ESRS event would not be linear. As we move towards a Net Zero future with electrical demand predicted to increase due to customer needs and greater commercial/domestic EV charging, Distribution Network Operators and Renewable Energy Generation resources will play a greater role in the UK and Regional Electricity System recovery as restoration can no longer be only a top down approach (Transmission to Distribution restoration). Therefore, as we move away from a carbon based society we do not believe adopting a deterministic model over a probabilistic model would be wise at this time, as many of the current factors in Demand Restoration modelling during a ESRS event will need to be reconsidered.

## Compliance Activities
Consultation Questions
How could industry provide visibility of its capability to meet the ESRS?
How often would the industry provide visibility of its capability to meet the ESRS?
Are there any additional tests that needs to be considered for assurance of restoration capabilities?
No | Responses
1 | For existing Black Start stations, the testing regime is sufficient. In order to have a more meaningful restoration strategy, tests should be undertaken to connect windfarms (large, transmission connected windfarms) and, even better, some load put on them which might be achievable using pumped storage, interconnectors or batteries. Without proper testing of windfarms we do not have a sufficiently robust restoration strategy.
2 | We requests NG ESO to clearly identify visibility requirements in the ESRS framework and in the procurement procedures to allow for developers to plan for compliance testing requirements and testing requirements during operation and lifecycle of the generator. Visibility of the capability for monitoring can also be achieved through dynamic monitoring of the restorations service providers and through remote access to converter models that can be used realtime modelling and studies, to inform on real-time restoration capability of restoration service provides to meet the ESRS. Compliance qualification Similar to compliance testing and qualification during connection, provided the technical requirements are clearly defined for different technology types, compliance testing and qualification of restoration service providers could be facilitated as part of the service agreement. Any non-compliance can then be addressed by the developer provided they have a service agreement to meet the service requirements. Routine Testing Routine testing is key in order for energy restoration service providers to ensure the plant is resilient and ready to provide services in during a national power outage (NPO). Such testing and associated costs should be included as part of the offer during procurement process. Routine testing should also be carried out at the TO/DNO/ESO interface, with mock simulations of an NPO. This will ensure resource readiness, resilience of service providers and communication infrastructure in the case of an NPO. Modelling, reporting and studies of irregular events that could lead to cascading failures: and Increased data and information transfer: An NPO may result out of an unnoticed network phenomenon, that did not get captured and addressed in real-time. An increase in convertor-based generation on the network, creates interactions across the network with other connected assets, that could potentially lead to maloperation of protection and control equipment and cascading trips of generators. Such incidents are easily avoidable and mitigation measures should be planned and put in place, both for normal operating conditions and under restoration conditions. Traditionally, information and data sharing has been restrictive, with real information available to select few. This could be dangerous going forward and we welcome openness in information sharing to allow developers to proactively act on these issues.
3 | Frequency of visibility to meet ESRS can be contractually enforced and accounted for in the service agreements placed by NG ESO with the service providers. The ESRS should clearly define requirements for compliance and routine testing, include visibility requirements. Service providers should make provisions for these in their offers and provide a clear account for associated costs. NG ESO can assess the costs for such visibility and use to inform the standard. Contracted obligations: The required frequency of routine resilience testing should be outlined in the ESRS, based on the technology type and criticality of its availability during the restoration process. Critical system event conditions and weak grid conditions: Electricity System Restoration Standard – Implementation Consultation Dynamic visibility of the restoration service providers will enable analysis of system behaviour under weak grid conditions and during critical events, which would then allow the data to simulate and accurately plan restoration actions in case of an NPO.
4 | We believe that the ESRS should make provisions for routine testing to ensure resilience of the power network, connected system restoration service providers and critical communication infrastructure, to mitigate risks during the restoration process, in the event of an NPO. Testing restoration capability of service providers to successfully energise power islands Historically, the scope of the restoration testing was limited to the restoration provider facility. The testing procedure only included tests to ensure capability of service providers to self-start without external assistance, but it did not test its capability to energise transmission network (especially large transformers). The ESRS framework should implement a more robust testing regime to prove the restoration of the nearby transmission network and the stable islanded operation of nearby providers. Service provider testing suited to type of technology Restoration service providers should be tested according to their technology type. Testing requirements developed under the ESRS framework should take technology specific aspects into consideration. Communication Network Testing A special emphasis should be placed in ensuring secure, resilient and redundant communication infrastructure availability across the network and to the restoration service providers. This could form a part of the routine testing required to ensure resilience. Resource allocation and adequacy Control centre staff and other resources required to perform critical functions in the event of an NPO, should be provided tools and adequate training to manoeuvre a series of unplanned circumstances to be able to perform their duties in the restoration process. Resource adequacy and competence should be routinely checked, and mock trials could be planned in preparation of an NPO. This is applicable both to networks and restoration of service providers. Quality of models The accuracy and quality of the network models will ensure any simulation and studies performed to plan actions for system restoration are accurate. Accuracy of system models to be used in such scenario should be routinely checked and updated when necessary. Audit of protection systems: Protection and control systems in parts of the network and at the restoration service providers should be audited to ensure that they are resilient to withstand the restoration process without failing to operate or causing maloperation.
5 | We welcome the continuation or strengthening of the existing approach whereby the ESO may undertake proactive and selective audits at any time over a contracted period. We would not welcome the imposition of a new and detailed self-audit burden as such processes so often become detailed paperwork exercise and an administrative burden at best, and fails to provide visibility and certainty over the presence of the capability subject to audit.
6 | This should be done in accordance with the contractual arrangements. The frequency of testing and approach taken under current arrangements are considered appropriate, proportionate and fit-for purpose, while offering flexibility to the ESO should any suspicion of non-capability arise.
7 | Visibility could be provided either through a combination of submission/publication/review of simulation tests and/or from regular testing of capability. The technical codes already require certain capabilities to be demonstrated on a regular basis.
8 | In order to ensure that the ESO can deliver the ESRS requirements (at any time) then regular proving of capability will be required. The existing ‘black start’ providers are obliged via the codes to undertake routine testing and it would be expected that new providers should also be subject to equally rigorous testing to ensure that there is confidence that the strategy will indeed deliver when called upon.
9 | This very much depends on the detail of the actual strategy to be adopted to meet the timescales set out in the ESRS. As this is currently unknown it is quite difficult to provide a definitive view on whether additional or more rigorous tests are required to provide assurance especially if there is adoption of new and unproven technologies within the mix of restoration providers.
10 | Industry already provides visibility through ancillary and capacity market services.
11 | Industry should provide visibility annually.
12 | We agree that there is an increased need for a baseline level of testing and exercising of restoration capabilities across the power sector. There should be a level playing field for assets with similar capabilities across the distribution and transmission networks.

## Tech & Locational Diversity
Consultation Question
Are there any technical barriers that currently prevent you from providing a restoration service? If so, what changes are needed to our technical requirements to ensure the ESO continues to provide a level playing field for the provision of restoration services?
No | Responses
1 | None. We observe the opposite risk in that services are ‘dumbed down’ and superior service attributes are not properly valued e.g. diversified fuel stocks. Even for our embedded asset, the main technical barriers appear to be on the network/communications side.
2 | These consultations lack many essential things such as: ♦ Grid-forming capability; ♦ How much, beyond the unit itself, the ReStart unit can start up within the same grid section; ♦ Ability to re-start neighbouring grid sections; ♦ Ability to re-start neighbouring voltage-levels of the grid, both upwards and downwards in voltage; ♦ Duration of the start-up requirements, which has further echoes (for storage) in how much capacity/duration needs to be reserved so that the storage is not exhausted when called upon – ◊ Durations should not be excessive, or all storage would be excluded, ◊ Nor should they be insufficient to start up neighbouring grid sections and achieve stability; ♦ Inertia / ability to take the electric "jolts" from re-starting neighbouring installations; ♦ Linked re-start cascades, e.g. plant 1 can start from scratch and re-start plants 2 and 3 which can then re-start the rest of the grid section, etc. - these should be tendered and contracted as a single "re-start collective unit" when the "collective unit" can deliver the requirements listed above but individual parts of it cannot.
3 | SPR will like to highlight that, the legacy technical requirements have been developed with consideration of synchronous generator characteristics and system response behaviour that can be called into action during a national power outage (NPO). Under the ESRS framework leading to 2026, these requirements need to be updated to cater for different technologies, especially those associated with renewable generation to remove barriers for such technologies to participate in electricity system restoration. We have identified the following technical barriers and lack of technical requirements, that hinder renewable generation and storage from participating in restoration service: 1. Unclear technical requirements and considerations for small/large scale offshore and onshore wind generation to support system restoration: Wind generators can be equipped with self-starting and grid forming capabilities to provide Phase 1,2,3,4 system restoration services. The technical requirements, therefore, need to be enhanced to account for forecast, modelling and variability of renewable generation into account. Wind generators both onshore and offshore should be identified as anchor generators and provided adequate technical clarification and market signals to participate in procurement of Phase 1,2,3,4 system restoration services. Wind generators demonstrate good capability for providing reactive power support and frequency control. However, despite of being a good supporting asset for network restoration that can provide balancing services, reactive power and frequency control, they are identified as secondary restoration service providers. It is unclear, whether this will then exclude these wind generators from compliance and routine testing, how will these secondary restoration service providers be modelled and how will they be compensated to provide a resilient service. The technical definition of secondary restoration service providers is defined as a noncommercial service, which will not provide adequate incentive to wind generator developers to equip and maintain equipment to be resilient as system restoration service provider. SPR is actively exploring and proposing new approaches to provide zero carbon ancillary services such as phase 1,2,3,4 restoration service and Fast Injection of active power (inertia like response) as demonstrated in Dersalloch’s Innovation Project (https://www.scottishpowerrenewables.com/pages/innovation.aspx). We have also developed and are in the process of developing battery storage projects, co-located and standalone, to enable critical system services during energisation and expansion of power islands. Additional, technical requirements for secondary system restoration service providers need to be developed. 2. High-availability, resilience of supply and sequential start up requirements: High availability requirements need to be reconsidered for renewable generation, due to the nature and variability of generation pattern. The ESRS should consider categorising availability depending on the technology, such as windfarm availability directly depends on wind availability. Large windfarms (especially offshore) can produce up to 50% of its output 90% of the time. Modelling wind generators with consideration to its output variability compared to its capacity, will allow them to meet the high availability requirements required for restoration process. Under no wind conditions, if windfarm generators are equipped with grid forming capacity, support to restoration can be provided which should also be accounted in the ESRS and generators should be incentivised to invest and develop grid forming capability. It needs to be acknowledged that wind turbines will have a higher probability of providing grid services if they are kept warm and the resilience of critical generators in restoration regions are maintained. Additional incentives should be provided to allow wind generators to install additional capability to build resilience and keep turbines connected to increase probability of faster restoration and minimise turbine failure to start. This capability where possible can also be provided through connection to the skeletal power network during development of the power island phase of the restoration process. Maintaining resilience of generators should be made part of the technical requirements. Sequential start-ups are possible for convertor-based generation. Using a hybrid plant (wind +BESS) and grid forming capabilities will aid in meeting this requirement, however this should be commercially viable for the generator developer. 3. Block Loading Requirements: Block loading requirements should be flexible and calculated based on the size and capability of the generator and connected demand in the restoration zone. Block loading does not necessarily need to be mandatory requirement “locally”, if the generator is not in the vicinity of demand or cannot meet the demand in required blocks. The generator should still be allowed to participate in Phase 1,2,3,4 restoration services, as it will enable other generators to connect and provides system services speeding up the overall restoration process. 4. Voltage control, frequency control, short circuit level contribution and inertia response: Wind and renewable generators in combination with or without a BESS, STATCOM, grid forming convertor/inverter can provide some, or all of these services depending on the technology installed and services contracted that provide a return on investment. Rigid technical requirements on these key grid services, will potentially prevent many generators that could otherwise contribute to speeding up the restoration process. ESRS working groups should consider these requirements for generators on a case by case and locational and regional requirement basis, to encourage participation from a wide range of connected technologies in creating a power island. Early indication and a revenue stream will make provision of such services viable for the generator developer. 5. Lack of consideration of combined services and co-ordinated response The combined services approach does open an opportunity for valuating these secondary services but can only be achieved by potential providers teaming up with other partial providers to offer a full package of restoration solutions. This approach is significantly challenging and onerous for new technologies that are looking to enter the market that do not fall into the specific category. Technical requirements could be enhanced to increase opportunities for co-ordinated responses from generators in the same system restoration region, encourage combined services from co-located generators and storage solutions. Electricity System Restoration Standard – Implementation Consultation 6. Lack of dynamic visibility and network models: Power electronics-based converter technology have different response to network events as compared to synchronous generators. In weak-grid conditions connected assets, generators and converters may interact with each other, which can delay the restoration process due to resulting instability caused through these interactions. For system restoration processes to run smoothly with minimal or no negative grid interactions, visibility of the dynamic behaviour of the grid in the early stages of restoration, through accurate modelling and information sharing is required in real-time. This will allow converters to adjust modes and outputs and power oscillation damping mechanism (where present) to be called into action to better support grid restoration. Special considerations for converter-based generators need to be added to the technical requirements for restoration services. 7. Resilience of communication network: System restoration service providers need to demonstrate communication network resilience. Renewable generator communication networks are often developed independent of that of the Transmission Owner (TO) and Distribution Network Owner (DNO). It is therefore unclear whether for critical services such as system restoration, TOs, DNOs and renewable generators should benefit from shared resilient and secure communication network.
4 | We are delighted to learn of the steps you are taking to ensure diversity of provision, including preparing for the use of Distributed Restart as a potential restoration resource.
5 | The tendering of ESR from a non-ESR plant would require a range of studies and ultimately involves the integration of new equipment into existing plant. The technical capability of plant to meet the minimum technical requirements cannot be understood without the commissioning of detailed feasibility studies including the engagement of specialist resource: therefore less experienced operators may not be in a position to fully judge the compatibility of all technical criteria to their specific asset. It should be recognised that minimum threshold parameters will represent a barrier to entry for some asset types and sizes, however we observe a likely scenario where some smarter solutions may be required (and accepted by the ESO) such to preserve access to levels of enhanced capability from otherwise disallowed plant which are of use during a restoration process. For instance, we observe difficulty in enhancing inertia from otherwise low inertia plant and see validity in the continued acceptance of synthetic inertia as an 'inertia top-up' solution towards meeting the minimum inertia specification/threshold. We do not believe that technical requirements should be lowered or adjusted in a way that increases the complexity of the restoration process or places unnecessary strain on 'within event' resourcing and communication protocols. We strongly believe that less reliable technologies (in their technical capability and certainty of continued availability over the course of any total or partial NPO) should not represent any risk to the primary service providers’ ability to establish, support and grow the network from their own sustained generation capabilities.
6 | We would note that the learnings and dissemination of the Distributed ReStart project have yet to completed and formally published so that the wider industry are aware of the technical requirements which are needed to allow distributed energy resources to provide restoration sources. Until these are made fully transparent then it is unlikely that engagement from the full range of potential providers will be possible. It should also be recognised that different geographic areas of Great Britain may require different restoration services due to the network topology or to the availability of a particular type of restoration service provider which may limit the services which can be provided e.g. Distributed ReStart may be better suited to being applied in England and Wales due the larger rated units which are connected to the Distribution 132kV network, whereas the DER connected to the Scottish Distribution network tends to be smaller and would require more significant numbers of plans to be managed by a Control Room to achieve a similar level of restoration.
7 | We are not aware of any barriers preventing lithium-ion batteries from providing black start services. Lithium-ion batteries with grid-forming inverters have black start capability.

## Communication
Consultation Question
How can we continue to deliver a secure and resilient communication infrastructure across the industry?
No | Responses
1 | Need to maintain current capability, extending it to lower voltage connection assets
2 | We recognise the importance of resilient and secure communication infrastructure as a critical necessity for the successful implementation of the ESRS. We believe these requirements should be clearly described and enforced with roll-out of the ESRS. We identify following key factors that will help in development of adequate communication infrastructure across the industry. Investment to ensure resilience and redundancy TOs, SO and ESO need to invest in developing communication infrastructure with adequate bandwidth, redundancy and cybersecurity. Where applicable, we urge that this communication infrastructure is also extended to critical restoration service providers. This will ensure that there is not a mismatch in implementation of communication infrastructure. As a minimum, the requirements should be clearly mentioned in the service agreement and restoration service providers should be allowed to offer resilient communication infrastructure as part of their service offer. The GB communication infrastructure for critical service should also be fast updated to new technologies which allow fast data transfer and allow for cybersecurity protocols to be implemented. It is also prudent to build redundant communication paths over different communication technologies e.g. 5G to ensure not a single type of failure during a critical restoration process. Testing Communication network and infrastructure should be monitored real-time and routinely tested to ensure its resilience and cybersecurity. In case of NPO, there could be an avalanche of events and signals being transported through the communication network. Such scenarios should also be tested, as part of the resilience tests. Early adoption Communication protocols implemented in GB are diverse and there are a lot of legacy systems on the network and also at windfarm sites. Early indication from the ESRS, regarding regional requirements for restoration service and type of technology required will allow wind generators and other service providers to upgrade their communication infrastructure to be able to provide the required service at earliest possible date. Ensuring reliable time synchronisation Power system monitoring, event timestamping and digital applications in power networks and at service provider locations are still largely dependent on satellite-based time synchronisation e.g. GPS. Though, recent industry wide studies prove that satellite signals for time synchronisation are unreliable and are also subject to jamming and spoofing, there is still widespread use of GPS based clocks. During an NPO, GPS availability and accuracy cannot be guaranteed at all sites. This can add to the complexity of the restoration process, where the automated systems and control centre operators may get a false picture of the power system state and this can lead wrong decision making. The ESRS should strive to move away from satellite-based time synchronisation and make provisions for time sharing from atomic clocks or other high precision clocks to different parts of the network and to the critical service providers.
3 | This is a well-studied and debated topic within existing working groups and a recognised challenge to overcome in a reliable way. We advise consideration over how to establish protocols, tools and infrastructures such to maintain communication with interconnected industries during a total or partial NPO event (e.g. Hydrogen production and transport, CCS and ancillary industry, centres of reliable demand etc.).
4 | Security standards for all participants should be as per the Security of Network & Information Systems Regulations (NIS Regulations) 2018 for critical national infrastructure providers applied to the whole system and not just the constituent parts of the participants. Power Resilience should be as defined in ENA Engineering Recommendation G.91 for all participants with the added function of control telephony voice for those participants that are deemed to need such.
5 | We find that the EDT and G99 requirements are robust. We think NGESO should implement the findings from the Distributed Restart project through the communications industry working groups.

## Innovative Solution
Consultation Question
If we were to have a blank sheet of paper and were designing a system that can be restored within 24hours, what would it look like?
No | Responses
1 | We think it is important to determine what role wind farms will play in system restoration. We also think it is inefficient (as well as technically and administratively cumbersome) to focuses resources on small generators
2 | We believe a redesign of the whole system will not be achievable within the timescales of the implementation of the ESRS. That implies we need to collectively think as an industry to make best use of the connected resources, to introduce flexibility and technology diversity in the restoration process. We would like NG ESO to rethink the restoration process along the following lines: 1. Large number of providers geographically spread across GB 2. Healthy mix of providers to avoid reliance on a particular design or feedstock (relying on CCGT technology when NETS becomes unavailable during the shutdown or relying on wind power when it is unavailable) 3. Transmission system re-designed to facilitate operation/restoration with/from large penetration of inverter-based resources (i.e. adequate protection philosophy – transition from the high magnitude current expected when conventional generation was dominant to voltage-based protection). An update of policies and of protection equipment to be more adaptive or an adoption of new philosophy to enable this transition. 4. TOs should be allowed to install additional equipment and allow further flexibility in their designs to ensure a faster restoration. 5. Investment in resilience of automation, communication networks, standardising communication protocols where possible, and ensuring cyber security. This will be challenging but crucial to the successful implementation of the ESRS standard.
3 | It would contrast the system envisaged today via the restoration standard for implementation under consultation. We would describe generator and network reliability and performance standards, resilience, communication structures and coordinated plans across a number of dedicated ESRS network locations (Hubs) encompassing all critical end to end service providers necessary to ensure operation of fuel supply, networks, power generation and key demand centres. We would describe a system whereby each restoration hub is controlled from one purpose built command centre. This would result in the availability of pre-designed and purpose-built subzones within a reliable and resilient interconnected network benefiting from digital control, resilience and fail-safe measures.
4 | From a system planning and design perspective, the implementation of the ESRS must reflect the circumstances prevailing. Particularly in light of the configuration of our systems, it is impractical to consider widespread provision of distribution services without a transmission bridge between Grid Supply Points. We therefore consider a largely (although not exclusively) ‘top down’ restoration strategy will be critical to achieving compliance in some areas. It will be important that this strategy makes best use of soon to be provided facilities from new restoration service providers e.g. battery energy storage systems and synchronous compensators, both of which have the potential to stabilise a weak system and accelerate/ de-risk restoration timescales. The system should be configured to enable the rapid initial re-energisation of a skeleton network followed by the connection of generation sources as and when these become available. This will be particularly important in the period to 2026, and more so beyond, due to the increasing penetration of renewable generation and storage facilities. The skeleton network should enable non grid-forming wind generation to be connected to a system stabilised by grid-forming wind, gridforming batteries and more conventional facilities such as pumped storage. Such an approach will enable rapid network re-energisation and stabilisation, with the key dependency becoming the availability of energy. This approach has the added benefit of allowing grid following renewable generation sources, of which there are significant volumes within Scotland, to be reconnected once the network has been re-energised. The use of grid forming batteries would allow a greater generation output be provided than otherwise would be the case and would facilitate the re-connection of additional demand (as larger demand blocks could be accommodated by appropriate configuration of the batteries to accommodate the larger step changes and demand fluctuations).
5 | We would design a black start system to harness the potential of emerging low-carbon energy storage technologies. Such assets can replace current carbon-intensive black start generation to create black start techniques compatible with net zero.

## General Feedback
Consultation Question
What other issues do you think you will face in implementing the ESRS?
Do you have any general feedback on ESRS implementation?
Do you have any comments about the overall process of this consultation?
No | Responses
1 | I think the issues faced in a real restoration will be far greater than we expect and the reliance on mobile communication may be horribly exposed
2 | We will actively support the ESO, TOs and DNOs in development and implementation of the ESRS. We also want to participate as Phase 1,2,3,4 restorations service provider through our grid forming and self-starting wind generators, a type of which we have already implemented and demonstrated at Dersalloch in Scotland. Aligning timescales to respond to upcoming workgroup requirements: However, we urge the ESO to take onshore and offshore wind grid forming capabilities early on into account and provide right technical and market signals to enable us to invest in these technologies in our upcoming development sites. Delay in doing so, will delay in contribution from wind generators both onshore and offshore and potentially create a gap in technology diversity in various regions. Early indication, technical requirements and clear messaging from the ESO to onshore and offshore wind generators is crucial to the overall success of the ESRS.
3 | We will like to acknowledge the efforts of the ESO to make the development of the ESRS framework a open dialogue and providing us an opportunity to respond and share our views through this consultation.
4 | We believe the consultation has been run in an open and transparent manner, with all required information available to aid in timely response.
5 | Implications arising from the near-term decarbonisation of UK industry - including early decarbonisation of the power generation sector. The opportunity to influence design criteria, ESR-friendly policy and technical capabilities as Hydrogen and CCS industries are created and begin to design solutions of their own, appears to be vitally important to ensure efficient end-to-end ESR solutions and longer-term viability of an enduring and meaningful national ESR capability. For instance: how may a service provider be guaranteed the availability of its necessary Hydrogen fuel throughout any total or partial NPO if that fuel is manufactured/made available or movement via new (national) infrastructure requiring power to facilitate it? For instance: how may a service provider be guaranteed the availability of its necessary post-combustion CCS infrastructure and all associated down-stream capabilities such to facilitate legal/viable operation of the generation plant during a total or partial NPO? For instance: which legal or regulatory dispensations will be necessary to support the viability and efficiency of ESR deployment? We feel that there are likely scenarios within the period that the power generation sector is realising the wholesale switch to decarbonised power generation where the ESO's 'Minimum Service Level' cannot be maintained due to the significance and timing of outages for conversion towards decarbonised operation. We would expect to see some plans and measures in place that consider additional or back-up arrangements over those likely periods of inadequate Minimum Service Level, compared to a 'normal' year for this foreseeable scenario. Timeframes leading from the publication of conclusions and design scenarios from within the ongoing Distributed Re-Start Project are likely to be complex in delivery. This may require network operators to engage differently and require the implementation of a redesign to network management, monitoring and inherent real-time capability. Scenario design will be complex, as will the matching of network performance to the individual performance of connected generators and equipment ancillary to the networks themselves. If the decision is taken such that too much emphasis is placed on DNO network operability, our view is that ESRS delivery is not likely to be achievable within the timeframes and end solutions will be too expensive to endure. We are unsure how the suggestion for a DNO to maintain the standard and ability to reconnect another DER within 4 hours interacts with the requirement for a generator to be capable of restarting within 2 hours. Of course, it is prudent to state the worst reasonable case requirements however we do not understand why a 4 hour window to network operations is contemplated. We are concerned that the implementation standard is likely to result in a much more complex system of restoration than that of today. It may rely upon network systems automation, societal environment as well as any number of service providers supplying services into a fragile and challenging technical. We welcome betterment of systems, development and investment into necessary systems but warn caution over any total solution being too complex to manage and costly to create. We feel that a more complex system may contain a greater number of failure mechanisms capable of causing damage to plant and equipment and deep challenges to any restoration process.
6 | We feel that ESRS planned implementation measures appear consistent with a version of yesterday's changing generation landscape and misses the opportunity to consider today's version of the ever-changing generation landscape, containing the near-term and wholescale decarbonisation of the UK's power generation sector. We advise that it should be anticipated that the power generation sector shall, quite soon, have established direct operational ties with, and have direct reliance upon, new Hydrogen fuel production and transport methodologies, as well as a CCS transport and storage industry which will each be intrinsically connected. We feel that direct engagement with, and specification across, these seedling industries and the regulations that will govern them must be taken now, such that capabilities within them are aligned to necessary performance criteria. This will facilitate self-starting power generation and ESR modes of generator operation during and throughout a total or partial NPO event. We feel that ESR scenarios could be stress-tested against power industry decarbonised operational scenarios and the likely event scenarios causing a total or partial NPO such to determine and gauge the scale of future ESR procurement requirements and suitability of arrangements surrounding ancillary infrastructure and industries to be relied upon. We welcome recognition that uncontracted generators have a role to play in later stages of any restoration process as they generate power to the best of their technical capability and availability in the event of any total or partial NPO. However we are very concerned that the introduction of the new concept of Secondary Restoration Providers that have no contractual framework in place, specifically for restoration, may indicate that new enduring requirements may be placed on this category of plant via Code changes without recompense or consideration of the impact of any additional through-life cost burden. The draft implementation standard states that any (required) upgrades needed to meet the minimum requirements defined under 'Assurance Activities' should be cost neutral suggesting that some unspecified scopes of plant upgrade will be required to be put in place and paid for by others (via ESO). Such arrangements, if we understand them correctly, would raise grave concern over ownership, control and through-life care for those new components and/or capabilities not part of the existing power station and request further detailed engagement over any such plans or assumption. We wonder if any generator may be able to freely decide if they are able to participate as an uncontracted Secondary Restoration Service Provider, particularly where investment of any form is required in order to meet the performance standard(s) i.e. up to 120 hours restart time. We feel that the levels of investment required throughout DNO networks and embedded energy providers to establish ESR capability as envisaged in the implementation plan, may start to exceed alternative investments in the marginal, classical NETS connected asset(s) to enable ESR capability at either 1st investment or via retrofit. Investment in primary NETS connected synchronous generation capabilities to establish ESR performance will lend itself to accessing high performing ESR technical performance and reduced complexity in its deployment at the time of need compared to procurement routes into DNO network operators and power generation providers. It is unclear who would be responsible for the engagement with, design, estimation, tendering of cost and implementation works attributed to necessary DNO network upgrade(s) such to facilitate the participation of a generator in any ESR tendering exercise where such network investment would be required in order to facilitate the operation of the generator for the delivery of a contracted service in any restoration phase. We feel that clarity over responsibilities and processes surrounding network operator, generator and ESO engagement is required and the obligations placed upon each should be evaluated and appropriately set out. We note that standard contract terms place an obligation on the generator/service provider to have an agreed LJRP in place when the restoration service goes live - however there is no mechanism or reliable route for a service provider to mandate the timely engagement of a DNO network operator, or any other required 3rd party, such to guarantee or provide certainty that this obligation can be met. We observe a real-time 'best endeavours approach' relying upon a positive spirit of engagement, however, with contractual penalties around any inability to form and maintain the engagement with any necessary LJRP development working group member(s), the service provider bears unnecessary risk should an unreliable 3rd party be required to participate. We are unclear as to the driver behind the stated expectation to contract a minimum of 3 technology types per restoration phase. We would have expected that the value of any service compared to the next is based only upon technical capability and cost, such to achieve the required standard and reliability of technical delivery. We are concerned that an expectation of a minimum of 3 technology types per restoration phase suggests a level of predetermination, and also arguably renders the process anti-competitive.
7 | We have found this consultation timeline challenging to meet given the range of considerations tied into matters closely linked to it.
8 | • The requirement for 60% of demand restored in 24hrs will be singularly challenging in the SPT/ SPD area given the likely delay to the required transmission network being energised compared to other DNOs, unless a top down approach as noted above is utilised. • More ‘local’ solutions may be required (e.g. DRZs) to ensure a timely restoration of demand.
9 | Implementation of the ESRS needs to be delivered by an economic and efficient restoration plan. Whilst we are fully supportive of market competition, it may not always deliver the most appropriate or cost-effective result to support the system in times of emergency restoration. This must be borne in mind by the ESO as it looks to develop its restoration plan. The ESO’s objective for “competition everywhere by 2025” should not be at the expense of an economic and efficient restoration plan. An appropriate blend of alternative and complimentary technologies will be required to adequately ensure that system restoration can be delivered rapidly and reliably, and achieved under a range of potential scenarios.
10 | We emphasise the need for price transparency.
11 | We think the process is well-designed and efficient.