## Symmetrical Bids - DR
Symmetrical Service Calculations
Export |  | 50 | MW | - the maximum export capacity of the unit
Import |  | 50 | MW | - the maximum import capacity of the unit
Storage capacity |  | 100 | MWh
Starting SoE |  | 50% | % | - the SoE at the beginning of the contracted EFA block
Charge capacity |  | 50 | MWh
Discharge capacity |  | 50 | MWh
Service |  | DR | (L+H)
|  | LF | HF
Contract quantity | MW | 15 | 15
Energy limited? | Y/N | Y | Y | - low Contract Quantity can mean that the Energy Limited rules do not apply
Headroom / footroom | MW | 35 | 35 | - for symmetrical service this assumes the unit baselines at 0MW
Delivery Duration | Min | 60 | 60 | - this is a function of the Service
Response Energy Volume | MWh | 15 | 15 | - this is a function of the Contract Quantity and the Delivery Duration
Energy Recovery | MWh | 3 | 3 | - this is a function of the Contract Quantity, it is how much energy must be recovered in a single SP
Maximum Ramp Rate | MW/min | 0.75 | 0.75 | - this is a function of the Contract Quantity
SoE recovery efficiency | % | 90% | 100% | - charging (for management of LF service) is less than 100% efficient. Discharging is 100% efficienct for SoE management
Energy Recovery per SP | MWh | 3.3333 | 3 | - this is the minimum amount of energy that a unit must be capable of recovering in a single SP
Total ramping mins (max 30) | Min | 15 | 15 | - this is split evenly between the ramp away from the baseline and the ramp returning from the baseline
Remaining mins in SP | Min | 15 | 15
MW Setpoint | MW | 5.625 | 5.625 | - this is the maximum deviation from the baseline, it should not be greater than the headroom/footroom
Ramp 1 | MWh | 0.35156 | 0.35156
Ramp 2 | MWh | 0.35156 | 0.35156
Rectangle | MWh | 1.4062 | 1.4062
Total Energy | MWh | 2.1094 | 2.1094 | - the total energy recovered as a sum of the two ramps plus the rectangle
Shortfall(-) or Surplus(+) | MWh | -1.224 | -0.89062 | - a shortfall would mean that in strict terms the unit can not comply with the SoE rules as it can not recover the required volume of energy
|  | Total Energy 2.109375 MWh | Total Energy 2.109375 MWh
DC | 15
DM | 30
DR | 60
0.35
0.35
1.41
Total Energy 2.109375 MWh
1.41
0.35
0.35
Total Energy 2.109375 MWh
5.63
5.63
35
35

## Symmetrical Bids - DC
Symmetrical Service Calculations
Export |  | 34 | MW | - the maximum export capacity of the unit
Import |  | 34 | MW | - the maximum import capacity of the unit
Storage capacity |  | 68 | MWh
Starting SoE |  | 50% | % | - the SoE at the beginning of the contracted EFA block
Charge capacity |  | 34 | MWh
Discharge capacity |  | 34 | MWh
Service |  | DC | (L+H)
|  | LF | HF
Contract quantity | MW | 32 | 32
Energy limited? | Y/N | Y | Y | - low Contract Quantity can mean that the Energy Limited rules do not apply
Headroom / footroom | MW | 2 | 2 | - for symmetrical service this assumes the unit baselines at 0MW
Delivery Duration | Min | 15 | 15 | - this is a function of the Service
Response Energy Volume | MWh | 8 | 8 | - this is a function of the Contract Quantity and the Delivery Duration
Energy Recovery | MWh | 1.6 | 1.6 | - this is a function of the Contract Quantity, it is how much energy must be recovered in a single SP
Maximum Ramp Rate | MW/min | 1.6 | 1.6 | - this is a function of the Contract Quantity
SoE recovery efficiency | % | 90% | 100% | - charging (for management of LF service) is less than 100% efficient. Discharging is 100% efficienct for SoE management
Energy Recovery per SP | MWh | 1.7778 | 1.6 | - this is the minimum amount of energy that a unit must be capable of recovering in a single SP
Total ramping mins (max 30) | Min | 2 | 2 | - this is split evenly between the ramp away from the baseline and the ramp returning from the baseline
Remaining mins in SP | Min | 28 | 28
MW Setpoint | MW | 1.6 | 1.6 | - this is the maximum deviation from the baseline, it should not be greater than the headroom/footroom
Ramp 1 | MWh | 0.013333 | 0.013333
Ramp 2 | MWh | 0.013333 | 0.013333
Rectangle | MWh | 0.74667 | 0.74667
Total Energy | MWh | 0.77333 | 0.77333 | - the total energy recovered as a sum of the two ramps plus the rectangle
Shortfall(-) or Surplus(+) | MWh | -1.0044 | -0.82667 | - a shortfall would mean that in strict terms the unit can not comply with the SoE rules as it can not recover the required volume of energy
|  | Total Energy 0.773333333333333 MWh | Total Energy 0.773333333333333 MWh
DC | 15
DM | 30
DR | 60
0.01
0.01
0.75
Total Energy 0.773333333333333 MWh
0.75
0.01
0.01
Total Energy 0.773333333333333 MWh
1.60
1.60
2
2

## Symmetrical Bids - DM
Symmetrical Service Calculations
Export |  | 50 | MW | - the maximum export capacity of the unit
Import |  | 50 | MW | - the maximum import capacity of the unit
Storage capacity |  | 100 | MWh
Starting SoE |  | 50% | % | - the SoE at the beginning of the contracted EFA block
Charge capacity |  | 50 | MWh
Discharge capacity |  | 50 | MWh
Service |  | DM | (L+H)
|  | LF | HF
Contract quantity | MW | 39 | 39
Energy limited? | Y/N | Y | Y | - low Contract Quantity can mean that the Energy Limited rules do not apply
Headroom / footroom | MW | 11 | 11 | - for symmetrical service this assumes the unit baselines at 0MW
Delivery Duration | Min | 30 | 30 | - this is a function of the Service
Response Energy Volume | MWh | 19.5 | 19.5 | - this is a function of the Contract Quantity and the Delivery Duration
Energy Recovery | MWh | 3.9 | 3.9 | - this is a function of the Contract Quantity, it is how much energy must be recovered in a single SP
Maximum Ramp Rate | MW/min | 1.95 | 1.95 | - this is a function of the Contract Quantity
SoE recovery efficiency | % | 90% | 100% | - charging (for management of LF service) is less than 100% efficient. Discharging is 100% efficienct for SoE management
Energy Recovery per SP | MWh | 4.3333 | 3.9 | - this is the minimum amount of energy that a unit must be capable of recovering in a single SP
Total ramping mins (max 30) | Min | 10.9 | 9.5 | - this is split evenly between the ramp away from the baseline and the ramp returning from the baseline
Remaining mins in SP | Min | 19.1 | 20.5
MW Setpoint | MW | 10.6275 | 9.2625 | - this is the maximum deviation from the baseline, it should not be greater than the headroom/footroom
Ramp 1 | MWh | 0.48267 | 0.36664
Ramp 2 | MWh | 0.48267 | 0.36664
Rectangle | MWh | 3.3831 | 3.1647
Total Energy | MWh | 4.3484 | 3.898 | - the total energy recovered as a sum of the two ramps plus the rectangle
Shortfall(-) or Surplus(+) | MWh | 0.015085 | -0.0020312 | - a shortfall would mean that in strict terms the unit can not comply with the SoE rules as it can not recover the required volume of energy
|  | Total Energy 4.34841875 MWh | Total Energy 3.89796875 MWh
DC | 15
DM | 30
DR | 60
0.48
0.48
3.38
Total Energy 4.34841875 MWh
3.16
0.37
0.37
Total Energy 3.89796875 MWh
10.63
9.26
11
11