## Slide 1
Regional Development Programmes – MW Dispatch
Matthew Rivett
May 2022

## Slide 2: Regional Development Programme overview
RDPs are examinations of whole areas of the network where more distributed energy resources (DERs) might create operability challenges
By working together, network organisations are finding ways to ‘unlock’ more capacity through non-network solutions
RDPs are considering the use of flexibility services from DERs by developing coordinated markets, systems, processes and ways of working with distribution network operators (DNOs)
RDPs are design by doing projects. They are informed by the ENA Open Networks project and in turn inform the project also.
Notes: National Grid ESO is the electricity system operator for Great Britain. We move electricity around the country second by second to ensure that the right amount of electricity is where it’s needed, when it’s needed –always keeping supply and demand in perfect balance. We achieve this through procurement of balancing services from generators connected to the main transmission network and also increasingly from parties connected to distribution networks, Distributed Energy Resource (DER).
As I’m sure you’re aware, local distribution networks are also becoming more active triggered by the increasing volume of connecting DER. In response local network organisations, DNOs, are developing system operator capabilities, i.e. they are becoming DSOs. My role, and that of my colleagues is to work with these organisations to ensure that DSO is developed in a co-ordinated manner and facilitates service opportunities across transmission and distribution. Regional Development Programmes (RDPs) are at the heart of this work.
RDPs are needed in areas of the system where, increasingly, volumes of DER are putting strain on local distribution and transmission networks. The map above shows the locations and partners in our current RDPs. We’re working with DSOs in each of these regions to facilitate new ways to get DER connected quickly and at low cost, avoiding the need for further network infrastructure. This is primarily through the development of new flexibility services for transmission system needs.
A key aspect of RDPs is co-ordination between ESO and DSO. As we go through this webinar the presenters will explain more about how this co-ordination is being realised.

## Slide 3: RDP Solution Development Steps
Stakeholder engagement
Exploration of issues by GSP
Confirm details of constraint(s)
Identify and assess options
Undertake CBA process
Confirm and implement solution
Undertaking enhanced studies of the region/Grid Supply Point (GSP)
Drivers of, timing, location and volume of constraint
Use identified system need to assess options
Determine most economic solution
Sign off and roll out viable options

## Slide 4: Whole system economic assessment with WPD
Connection application(s)
Whole system studies
Most economic outcome taken forward to implementation
Cost Benefit Analysis of build / no build solutions
The South West of England is expected to play a major part in meeting the future governmental green energy targets because there is lots of renewable solar and wind generation
Sunny days in spring and summer present a challenge to transmission and distribution networks, particularly when windy and / or coincident with low demand
A whole system assessment found that investing in systems to manage generation on the distribution network in the South West is more economic than network investment
It also facilitates quicker connection of new DER to the system than would otherwise be possible
This outcome has been implemented via specific connection terms in distribution connection offers
Notes: But first let me explain a bit more about how we have got to where we are today in the south west with WPD.
The south west of England is expected to play a major part in meeting the future governmental green energy targets. The local climate is suitable for many forms of renewable energy such as solar and wind, and WPD have received many new applications for such DER connections.
At times of minimum demand for electricity this can cause challenges for the local transmission and distribution networks, particularly when the weather is sunny and windy. In the south west, consistent with our approach to other RDPs, we have worked with WPD to asses the potential options to ensure further DER can connect. We have found that the most efficient way forward is to invest in systems to manage periods of high DER output and low demand. Such a system is also quicker to deliver than traditional network investment, meaning DER connections can be accommodated sooner.
As a result, to facilitate this non-network solution, WPD have implemented specific connection terms in distribution connection offers. Ben will now provide more context on these terms and what they mean for you.

## Slide 5: ESO Balancing services and constraint management
We procure a range of services to balance demand and supply and to ensure the security of electricity supply
Thermal constraints are caused when assets reach their physical limitation, creating congestion
This limits how energy can be transmitted across GB – this is what we need to manage in the South West
We are developing a new transmission constraint management service as a new market solution to this need
This service will complement existing routes to ESO markets for DER which are the BM and Wider Access
Frequency Response
Reserve
Reactive Power
Restoration
Balancing Mechanism & Wider Access
Constraint management
Capacity market
Stability

## Slide 6: A new transmission constraint management service
We are developing a new transmission thermal constraint management service to help resolve increasingly regional network constraints
This service is designed to be simple and provide an alternative route for DER to fulfil their ‘visibility & control’ connection terms.
The Balancing Mechanism or Wider Access remain existing options.
Instruction from ESO via DNO system
Instruct to 0MW or “float” for storage
Utilisation payments only
Price can be resubmitted regularly
A continuous service – assumed available (unless declared otherwise)
A separate commercial contract with the ESO
Notes: To ensure there are appropriate routes available for parties to fulfil their V+C conditions, the ESO is working with partner DNOs to create a simplistic transmission constraint management service.
This service is aimed at providers that are not looking to be active in the larger flexibility markets (e.g. the balancing mechanism).
Although simple by design, the service does allow providers to alter their prices as frequently as required.
We are aiming to keep administrative and infrastructure costs as low as possible through utilisation of existing DNO systems, whilst not restricting participation in more complex market offerings, if desired.
Point to key points on slide.

## Slide 7: Final trial service design
The service instruction will instruct DER from their current output to 0MW
Instructions will have a minimum settlement volume calculated over a time period of 5 minutes
Proposed response time to be within 2 minutes
Basis of service payment will be to take a snapshot of output at T1 and assume straight line delivery for duration of instruction
Notes: We have so far worked to develop simple service design that enables participation by a variety of different assets, whilst also ensuring the basic transmission system operability need can be met.
This simplistic approach should also ensure that current systems/infrastructure are able to facilitate the service, enabling a faster roll-out.
In addition, we have also tried to develop a service design that aligns with existing Balancing Mechanism rules to enable a level playing field between the various options.
We are also exploring different options for payment of the service and would welcome views on how these should develop.
Read slides.

## Slide 8: Solution Architecture Overview
ASDP
Platform
(Dispatch)
SCADA System
(Visibility and Metering)
DERMS/
POWER ON
Single Market Platform
(Registration)
Data Validation
(Registration)
DER
Settlement Tool
Web Services
ICCP Links
DERMS Comms
NGESO
DNO
DER
Coordination Activities
Notes: We have so far worked to develop simple service design that enables participation by a variety of different assets, whilst also ensuring the basic transmission system operability need can be met.
This simplistic approach should also ensure that current systems/infrastructure are able to facilitate the service, enabling a faster roll-out.
In addition, we have also tried to develop a service design that aligns with existing Balancing Mechanism rules to enable a level playing field between the various options.
We are also exploring different options for payment of the service and would welcome views on how these should develop.
Read slides.

## Slide 9: Contractual Arrangements
Tri-Party Commercial Agreement
NGESO
DER
DNO
NGESO updates Bilateral Connection Agreement (BCA) with basic Visibility and Control terms and conditions
DNO updates BCA with DER with appropriate V+C terms and conditions
DER sign onto technical conditions as part of their DNO BCA
Connection Agreement
Commercial Services Agreement
Notes: We have so far worked to develop simple service design that enables participation by a variety of different assets, whilst also ensuring the basic transmission system operability need can be met.
This simplistic approach should also ensure that current systems/infrastructure are able to facilitate the service, enabling a faster roll-out.
In addition, we have also tried to develop a service design that aligns with existing Balancing Mechanism rules to enable a level playing field between the various options.
We are also exploring different options for payment of the service and would welcome views on how these should develop.
Read slides.

## Slide 10: Future service enhancements
Possible future ‘upgrades’ to service design following trial period:
1) Alignment of pricing submission window to BM timescales
2) Inclusion of 0.5-1MW DER Units
3) Enable registration by previously connected DER (without V&C terms)
4) Consideration of unique Ramp Rates
5) Configurable Baselining Methodology
Subsequent developments (longer development timeframes)
6) Dispatch of decremental (non-zero) instructions
7) Support for Aggregated DER Units
8) Support for service instruction via alternative routes to DNO dispatch infrastructure
9) DNO access to the service for distribution needs

## Slide 11
Q&A