## Sli.do Questions
Question | Answer
Does the model account for the economic and societal cost of grid failure? | In FRCR 2021 we highlighted that VoLL is not a suitable measure. We think the economic and societal cost of grid failure such as VoLL is more suited to capacity considerations, which are more predictable, and less suited to faults and any resulting transient frequency deviation, which are less predictable. The relatively short-duration of LFDD events and the relatively infrequent rate at which they occur means that the VoLL used for setting Reserve Scarcity Price is likely to be insufficient to provide the right balance between reliability and cost for the FRCR. A new, specific VoLL could be used to set a cost value per avoided occurrence for the FRCR. The output of the model shows the cost and risk of various options, we aim to consult the wider stakeholders (industry / SQSS panel / Ofgem) on whether the incremental cost is worthwhile.
Inertia GVAs is the most important system parameter for frequency & thus system Security but ESO isn't procuring GVA.s like they do Reactive MVARs...why not? | We do procure GVA.s through our stability pathfinder projects and through phases 1 2 and 3 have procured 36GVA.s. We also have the option to procure GVAs from large synchronous machines in the BM, this is through the purchase of energy however rather than specifically for GVAs. On our data portal we highlight the daily costs of our GVAs for inertia procurement. In addition, we are also in the proccess of designing a future stability market to provide a route to market for procuring stability products such as inertia and short circuit level.
does your methodology track not only the risk of frequency deviation but also the consequence of it? | The model and assessment have been developed to ensure we secure credible fault in line with current SQSS and System Operation Guideline (SOGL), meaning frequency deviation will be maintained up to 49.2Hz and return within 49.5Hz within 60 seconds
Does FRCR 2023 consider risks identified in GC0155, including coincident tripping due to high voltage or phase jumps where no ride through is specified in GC? | These were not considered specifically and there impact on the number and severity of frequency excursions were not assessed. However, FRCR 2023 considered some simultaneous events and the BMU+VS events affecting embedded generation fitted with VS protection. These give an idea of the cost implications associated with the management of frequency due to simultaneous tripping of generation. We note that tripping of generation in cases where the voltage profile is above the black line constitutes a non-compliance with the fault ride through requirements under the Grid Code. Where such a risk is identified, the output of the non-compliant plant would be restricted up until the non-compliance has been resolved.
for example if consequence= a less recoverable event or an impact on emergency/ contingency measures- do you plan recommend changes to these in implementation? | We have requirements to manage faults in line with our requirements in the SQSS. There are specific, limited variations to these policies based on technical, probabilistic and economic grounds, applied under paragraphs 5.11.2 and 9.4.2 of the SQSS. This includes additional actions where appropriate during times of increased system risk, such as during severe weather, and exceptions where risks cannot feasibly occur.
Have you examined how closely your model predicts inertia and related factors in frequency dynamics of real events-are these uncertainties increasing over time? i.e. how close to the cliff edge should the analysis methodology take you? and what factors should influence that when considering changes in min inertia? | FRCR is designed to investigate the policy on how to manage frequency risks. The key factor related to reducing the minimum inertia requirement is reliability vs. cost. Given the uncertainty and rapid change in the system, to isolate the reliability vs. cost decisions from the impact of these wider changes, the analysis uses historic scenarios adjusted for known or expected changes in the coming 12 months.
Does the methodology make any allowance for unexpected cause of frequency excursions, so called black swans? https://en.wikipedia.org/wiki/Black_swan_theory | The model considers historical event which triggered and were relevant to freqeuncy events. In 2022 FRCR, we investigated the impacts and costs of simultaneous events on the system. We have also reassessed this modelling within this year's report. Our existing policy already covers at least 75% of simultaneous events and we concluded that the cost vs. risk of securing the remaining events would not represent good value for consumers (at a cost of c.£370m in 2022 and £321m in 2023).
I also struggle to understand where the event risk statistics come from. FRCR 2022 included some arbitrary assumptions (eg 1 in 30 years for a worst-case simultaneous event) but also stated that "...simultaneous events occur more frequently than mathematical probability suggests." | System failure stats are based on historical events on the system. We revise this input data on an annual basis as part of the FRCR process. For simultaneous events, due to limited cases in history and the complexity involved, we assumed simultaneous events occur 1-in-10 years and the peak event occur 1-in-30 year. But for the past 30 years, there was no peak events occurred, so FRCR 2023 resultant 48.8 Hz event risk of 1-in-30 years means only the loss level at peak events will end up with demand control.
How is the ability to form a sine wave being assessed? DC will maintain energy balance, however don't we need a quality waveform produced by spinning mass? | Dynamic Containment providers (such as batteries), are connected through converters to the grid. They provides ancillary service for us to manage post fault frequency. The quality of the sine wave sits within the connection agreement/industry standards, hence outside of the FRCR scope.
Re 1 in 17/30 years event probability - what is it based upon? | Based on FRCR policy, we secure up to the largest BMU-only event (including the consequential RoCoF losses). So any potential events that have a loss size greater than this threshold will have the possibility to trigger 49.2/48.8 frequency deviations. 1 in 17 years of 49.2Hz risks and 1 in 30 years of 48.8Hz risks are the accumulated possibility considering 1) the likelihood of each event based on historical occurrence and 2) the percentage of time that event is at risk.
Where do the event risk statistics come from? | Please find the following link for the published fault data including transmission fault and any generator trips that caused more than 250 MW power loss. https://www.nationalgrideso.com/industry-information/industry-data-and-reports/system-performance-reports. The requirement of publishing system incidents is in line with OC3 - System Incidents Report.
How are you measuring inertia? | Currently we measure inertia through a stable component of inertia calculated from demand as well as the known inertia contributions from all large scale generation on the system. This model is regularly reviewed when system events occur. In addition, we have new innovation projects ongoing to monitor system inertia in real time.
it would be really helpful to do an FRCR "look ahead" to the 2030 system as part of the operability strategy for this and future years of converter penetration | This is in scope of our BP2 and our ambition is that future versions of FRCR look further ahead than just 1 year (as is currently the case)
in previous FRCR 2021/22 your ambition was to operate @96GVAs to allow more RES to run (that don't produce GVAs!) but failed so are you too ambitious/ risky? | Our ambition to operate at lower inertia is driven by our zero carbon ambition by 2025. This is defined within the Operability Strategy Report and not something we committed to achieving in the 2021/22 report. Therefore we wouldn't suggest we have failed and are too ambitious/risky. We consider a move to 120GVAs a prudent first step to operating in future, at lower inertia levels.
r.e. look ahead- the solutions are being designed and specified now- so really theres not alot of time available to influence. | We acnkowledge this and have multiple workstreams that are ongoing to ensure we are looking at these ever-changing system conditions.
What's the VoLL or equivalent used in the analysis? and why is the cost of 110GVAs not higher than 120GVAs, presumably the risk of events is higher? | In FRCR 2021 we highlighted that VoLL is not a suitable measure, and we proposed to use cost per avoided event as the matrix. In terms of the cost to manage frequency risks, it includes all the controls that are available but two major cost categories are 1) do we need additional inertia to meet the minimum inertia requirement and 2) how much response service do we need. The level of 110GVAs and 120GVAs are for the minimum inertia requirement which mainly affects the cost of increasing inertia, and an appropriate level of response will be procured to achieve the same level of system security. The cost saving in holding less inertia trumps the cost increase in holding more response.
How’s ESO cost assessment impact by the commodity prices? With lower gas prices currently do you expect the 2023 cost could be much lower than 2022? | To cope with the uncertainties in commodity prices, renewable generations availabilities and other system aspects, the FRCR analysis uses historic data for the past year with the adjustment for known or expected changes in the coming 12 months. We review the cost assumptions annually to provide the best view to the policy recommendations.
How much of the savings will be realised. Will the inertia problem just become a voltage or a SCL problem? | Agreed with this point that the actual saving could be eroded by solving voltage or SCL issues. However, our inertia dataset considered the actions made for voltage support or SCL purpose and the annual saving potential is quantified to be £65m. If only considering the market inertia, the annual saving potential could rise to more than £100m.
How does the assessment take account of changes in likelihood of tail events ie low probability / high cost. Considering the probability assessment is estimate | The probability of large BMU+VS intact events is based on historical data and we review it annually. The probability of simultaneous events is based on the estimate because it is complex and difficult to quantify the true probability. However, this still allows us to perform a combined qualitative and quantitative analysis for managing the frequency risks.
You mentioned that 120GVA.s would give the industry opportunity to adapt to lower system strength, what adaptations are you hoping for and over what timeframe? | As a prudent system operator we want to make sure that we are not taking a leap to a future state without an inerim period first. This gives both the ESO and industry time to ensure that all processes and systems are sufficent to deal with lower inertia on the system. As suggested in the report, this reduction would be to 130GVA.s in the first instance, for a 1-2 month period, and then a further reduction to the proposed 120GAVA.s.
Is there sufficient accuracy and precision in the associated empirical measurements to be sure the model and reality are in agreement? | We ran a separate consultation on the methodology when producing FRCR 2020 - the first version. ESO has internal assurance to ensure the data and model are reviewed on annual basis.
Renwbles don't produce Inertia but are displacing generation with inertia plant & yet you pay RES on & then off to buy back on Inertia plant-how costly is this? | All inertia actions are published on our data portal (https://data.nationalgrideso.com/). All actions taken in the control room are to ensure system security and are based on the most economic solution at a given time, as per our licence conditions. We have ongoing projects to review our future stability strategy (such as the Stability Market Innovation project) and identify optimal solutions for managing stability as the system dynamics continue to change.
So in an actuarial basis a £65m savings may hazard losses in the billions plus excess deaths etc? | The assessment in FRCR determines the appropriate balance between system security and cost. As a result of continuing developments with the Loss of Mains programme, combined with the growing DC pipeline we have available, the risk profile presented within the report actually represents an improvement in the risk profile of the system (when compared with last year). Largely this is due to the combined loss size reduction due to these mentioned changes. Our role is to conduct this analysis and present a recommendation. This enables the Authority to make an informed decision on the right balance between the reliability of electricity supplies and the cost to end consumers. Any feedback to the consultation to highlight any new/novel risks is strongly encouraged.
Does this increase the demand for DC? | The proposed changes regarding the minimum inertia requirement will only affect the Dynamic Containment (DC) demand for the low inertia periods (when the minimum inertia requirement is binding), and more DC is needed to offset the reduction in inertia. In the meantime, we aim to further develop DC to cope with the future largest loss, more information can be found in the Frequency Response Product Market Information Report and Operability Strategy Report. We expect to see further growth in DC market and in other new service market development. Together we are stepping further to Net Zero operation and cope operability challenges.
My worry isn't the freq dev but how fast it is, what catches it/responds to it, & RoCoF measured in power electronic controller. Low inertia= >risk | How fast frequency moves can be determined by the swing equations and the key parameters are the loss size, inertia in the system, and the volume and speed of the response products. Dynamic Containment (DC) is designed to be a very effective tool for managing frequency deviations, with reduced inertia holdings frequency will move faster but still within the acceptable window for DC to operate and contain the frequency drop/raise. Additionally, due to the developments in ALoMCP, we see a much smaller amount of RoCoF losses at both 0.125 and 0.25hz/s tranches, result in a reduced total loss size.
The terminology choice of DC (Dynamic Containment) is likely to cause confusion with DC (direct current). Six sigma would suggest coming up something else. | Thanks for the feedback on this. It is unlikely that we will change the naming convention of our frequency products at this stage to avoid further uncertainty. We aim to define all acronyms within the report where necessary.
Thank you for answering but it did not really clarify the statistical basis. As a professor might say. Show your work. | Thank you for your feedback. If you require further information please get in touch with us directly at box.sqss@nationalgrideso.com
Can you publish the historic event data that you mentioned, covering the last 10 years? | You can find the historical transmission fault and generation losses back to 2020 from our website. https://www.nationalgrideso.com/industry-information/industry-data-and-reports/system-performance-reports If you need further assistant for data before 2020, please get in touch directly at box.sqss@nationalgrideso.com
“An idea” of inertia level is terribly vague | https://www.nationalgrideso.com/industry-information/industry-data-and-reports/system-performance-reports
Do you expect Ofgem to approve? | Yes we do expect Ofgem to approve. We believe the assessment and report present significant cost benefits for GB consumers whilst improvement in system security. Running at lower inertia presents a firm step forward to GB net zero operation in near future. We have briefed Ofgem on the recommendation and will submit the report by 31 March.
No that did not answer the question re measurements sufficiency | Thank you for your feedback. If you require further information please get in touch with us directly at box.sqss@nationalgrideso.com
Slido appears to have too much inertia | Thank you for your feedback. If you require further information please get in touch with us directly at box.sqss@nationalgrideso.com
With the success of reducing the inertia by increased DC service, do you expect more demand requirement? | Please see response to Q25.
How do you account for the massive changes in the grid’s composition vs rear view statistical basis? | Agreed that the grid is in a period of rapid change which affects many of the key inputs to the analysis. To cope with this, the analysis uses historic datasets adjusted for known or expected changes in the coming 12 months. This includes the impact of new transmission connections, plant retirements, growth of embedded generations, tools and controls that are available to us, etc. to be factored into the dataset used for the assessment to provide the best view for the policy recommendations.
Are you considering the ability of grid-forming technologies to provide responses much faster than 0.5s and how this could reduce the minimum inertia level? | We are certainly aware of the capabilities that grid forming technologies could provide for system inertia. At present, as the technology is still maturing, we don't see a high penetration of this capability, meaning we can't rely on this for system inertia at present. We are in the process of designing future stability markets and we envisage grid forming technologies to be a key player within these markets in future. We would still maintain a minimum level of system inertia so grid forming wouldn't reduce the minimum directly, rather the technology would improve how we manage any future shortfalls in inertia.
Lower inertia is likely to lead to larger phase jumps during faults. Has the potential impact of inverter based resources been considered? | We have considered this in our system stability studies and can determine that there is no system operability impacts for 2023 and 2024 when considering reduced inertia levels as far as 120GVA.s. There is an expectation that IBRs will be able to ride through faults, however we do not envisage there to be any issues during the 2023/2024 period that this recommendation will cover. We will review our assumptions annually within each FRCR process.
Inertia levels critically related to wind levels so should u have a STm market buying the right level of inertia which might be cheaper than buying wind on/off? | Yes, through the work we have prepared on Grid Forming (Grid Code Modification GC0137) and our stability pathfinder work, a natural progression of this are our plans to develop a short term market for stability which is currently in progress. More information on this will be shared in the Market Roadmap which will be published in March 2023.
Is there risk associated w local hotspot frequency events? | We are aware of the phenomena of the difference in regional frequencies during the transient stage. With the current system conditions, this issue is not affecting our decision-making, but we will keep reviewing this issue in future projects regarding the necessity of regional inertia and response constraints.
Didn’t the NGESO Chief Engineer identify frequency management as a top challenge? Doesn’t this change aggravate that challenge? | The introduction of FRCR provides a transparent model for assessing two key objectives - reliability and cost. The report and assessment helps us to focus on the right balance between these two competing objectives of reliability and cost, focusing on the risks, impacts and controls for managing the frequency. This change doesn't aggravate the challenge, but represents a prudent decision when balancing a cost vs risk assessment.
To clarify qstion- converter protection, PE control response RoCoF (i mean df/dt measured grid follow control)-sampled over 50-300us;checks to cap assmptns | Thank you for your clarification. If you require further information please get in touch with us directly at box.sqss@nationalgrideso.com