## Tender Query Log
ESO response to Tender Queries
TQ No. | Technical or Commercial Query? | Tender Query | Evaluator Response
1 | Technical | Is the tender only for Transmission connected generators or can Distribution connected generators join the service? | We are currently tendering for the EC5 CMIS ‘interim’, which is a precursor to the full EC5 service tender later this year. The main requirement for the ‘interim’ tender that the unit already has or will have its own connection to the East Anglia Operational Tripping Scheme (EAOTS) before April 2025 (i.e. the ‘interim’ tender will not create new EAOTS connections). This is because new connections will take at least 2 years to build and the aim of the ‘interim’ tender is to have a temporary service in place that runs while the new connections are being built for the full EC5 service.
2 | Commercial | Contract Terms: In the new version you have introduced a new term; De-load and De-loading Payment. How is this supposed to be implemented? Will the final contract refer to either De-load or Trip? Or will both be included in the contract? In which situations will the De-load Payment be paid and when will we receive a Tripping Payment. | The EC5 CMIS ‘interim’ will be using a units current connection to the East Anglia Operational Tripping Scheme (EAOTS). As units may be set up to either de-load and/or fast trip, we are enabling both types to bid into the service and will adjust the final ‘interim’ contract to reflect this. The payment is a one off ‘intertrip fee’ that the ESO will pay if a network fault occurs and the ‘armed’ EAOTS unit is de-loaded or tripped.
3 | Technical | If the OFTO asset becomes offline as a result of a trip, is this classed as unavailable or is it exempt? | The interim service is designed to utilise the EAOTS connections that are already in place. As a result, the same conditions that are already agreed would be utilised for the service. It should be noted too that if an asset is only set up to de-load, the EC5 CMIS ‘interim’ the ESO would issue instructions to de-load the asset. Therefore a trip would only occur as part of the generator’s own safety measures, or when the generator fails to de-load wind turbines. For information though, we are in discussion around these points with Ofgem for the enduring service, as the design is different.
4 | technical | Will the ESO require any testing of the 10 second de-load capability ahead of delivery? | The TO may check the comms link by sending a signal to the relevant circuit breaker. This will not affect the asset as it only checks whether the signal is received.
5 | technical | What is the expected start date of the EC5 CMIS Interim? | The interim will begin once providers sign their contracts, which is expected to be towards the end of this year. The interim will run until the enduring EC5 CMIS begins (the planned starting date is April 2025). If the enduring service is delayed the ESO plan to continue to utilise the interim.
6 | technical | How will instruction to arm, deload and trip be communicated? | The ESO control room will instruct NGET to arm generators to the tripping schemes as the tripping/deload signal is sent by the TO using the East Anglia Operational Tripping Scheme. The ENCC will then use EDL Reason Codes to communicate to providers that their generator is armed (with email as a backup option). The codes are ITA and ITD for when the units are armed and disarmed respectively. We may carry out a test to check you are able to receive the reason codes. The interim service is designed to utilise the EAOTS connections that are already in place. As a result, the same conditions that are already agreed would be utilised for the service.
7 | technical | Will any action need to be taken by the asset's Control Centre upon receipt of an arming instruction? | The generator will need to send an acknowledgement back to the ESO once that arming/disarming reason codes are received (similar to how BOAs are acknowledged), though no change in output/operation of the generator is required.
8 | Commercial | Definitions: The Commercial intertrip Scheme definition does not refer to de-loading and therefore does not come under the ABSVD payments. How is this paid? | A new umbrella term called ‘Service’ will be added and refer to both the Constraint Management Intertrip Service and Fast De-load Service to align with the terms used in ABSVD. The rules of ABSVD shall apply to the applicable services.
9 | Commercial | 3.5.3. This sentence needs to be changed: 'In the event of a [De-load/Trip] not caused by the Commercial Intertrip Scheme, continue to submit MEL to zero until the Company agrees otherwise.' | Sentence is being amended and will now refer the generator to the BC1 of the Grid Code in the event of a de-load or trip that is not caused by the CMIS.
10 | Technical | How does a back-up trip work in real time? Would the assets own control room arm the back-up when the ESO notifies them of a de-load or is it an automatic system? | The technology is specific to each generator so will need to be investigated on a case-by-case basis.
11 | Commercial | Some of the Commercial Proforma cells are locked in the complaince tab. | An unlocked version has now been uploaded.
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
Yes
No

## ProcInspection (hidden)
Procurement Excel Wookbook Inspection
Date: | 2023-07-06 10:13
UserName: | Alex.Palmer
Workbook Secure: | FALSE
HyperLinks List
| Worksheet Name | No of Embedded Documents | Is Worksheet Hidden | HyperLinks | Protected | External Excel Links | Worksheet Name | Cell Reference | HyperLink
| Tender Query Log | 0 | No | 0 | No