## Sheet1
PRIMARY RESTORATION SERVICE PROVIDERS
| ESR Tender - Wind 2023 |  | PROVIDER NAME
SUBMISSION / SCORING
| Requirement |  |  | Score
| Time to Connect (h) | Phase 1, 2 or 3 |  | Pass/Fail | Other Info
| Service Availability (%) |  |  |  | Installed Capacity (MW)
| Voltage Regulation (Leading) (%) |  |  |  | Contracted Units for ESR (Number and Ref)
| Voltage Regulation (Lagging) (%) |  |  |  | Time Between Blocks of Load (min)
| Frequency Regulation (Lower) (Hz) |  |  |  | Point of Connection (kV & Substation)
| Frequency Regulation (Upper) (Hz) |  |  |  | Local DNO
Resilience of supply, Black Start Service (h)
Resilience of Supply, BS Auxiliary Unit(s) (h)
Block loading size (MW)
Reactive Capability (MVAr)
Sequential Black Starts (number)
Connection Voltage (kV)
Short-circuit level, t ≤ 80ms (kA)
Short-circuit level, t > 80ms (kA)
Inertia (MVA.s)
| Connection to Network / Transmission - Distribution Connected |  | T | 2%
| Connection to Network / Multiple - Single connections to the Network |  | 2 | 3%
| Other BS Service Provider(s) in the same Substation |  | N | 3%
| Time to Connect (h) |  | 0.5 | 5%
| Service Availability (%) |  | 500 | 10%
| Power Output / Reactive Capability at 0MW (MVAr) |  | 500 | 10%
| Power Output / Active Capability (MW) |  | 500 | 15%
| Block Loading Size (MW) |  | 500 | 10%
| Resilience of Supply / BS service at contracted Power Output (h) |  | 500 | 15%
| Resilience of Supply / BS Auxiliary Units (h) |  | 500 | 5%
| Contribution to System Stability / Short Circuit Level, t ≤ 80ms (kA) |  | 500 | 4%
| Contribution to System Stability / Short circuit Level, t > 80ms (kA) |  | 500 | 3%
| Contribution to System Stability / Inertia (MVA.s) |  | 1500 | 5%
| Contribution to Restoration Time (h) |  |  | 0%
PROVIDER SCORE - TECHNICAL |  |  |  | 90%
Note on D7: Format - Number (Example: "1.7")
Note on E7: For ESO to populate: "Pass" or "Fail"
Note on D8: Format - Number (Example: "100") Expected to be ≥ 80
Note on D9: Format - number Expected: "+10"
Note on D10: Format - number Expected: "-10"
Note on D11: Format - number Expected: "47.5"
Note on D12: Format - number Expected: "52"
Note on D13: Format - number Expected to be ≥10
Note on D14: Format - number Expected to be ≥72
Note on D15: Format - number Expected to be ≥10
Note on D16: Format - number Expected to be ≥50
Note on D17: Format - integer Expected to be ≥3
Note on D18: Format - number Expected to be: 11, 33, 132, 275 or 400.
Note on D19: Format - number (Example: "1.32")
Note on D20: Format - number (Example: "1.32")
Note on D21: Format - number Expected to be ≥400
Note on D22: Format - letter Expected to be a "T" or a "D"
Note on D23: Format - number (integer) Expected to be ≥1 Note: Number of physical connections onto the Network that will enable the delivery of the full contracted service.
Note on D24: To be populated by the ESO: "Y" or "N"
Note on D25: Format - number (Example: "1.7") Note: should match the same requirement listed previously/above
Note on D26: Format - Number (Example: "100") Expected to be ≥ 80 Note: should match the same requirement listed previously/above
Note on D27: Format - number Expected to be ≥50 Note: should match the same requirement listed previously/above
Note on D28: Format - number Note: contracted MW for the provision of the ESR Service
Note on D29: Format - number Expected to be ≥10 Note: should match the same requirement listed previously/above
Note on D30: Format - number(integer) Expected to be ≥10 Notes: - Should match the same requirement listed previously/above - If "Indefinite", please include "121"
Note on D31: Format - number Expected to be ≥72 Note: should match the same requirement listed previously/above
Note on D32: Format - number Note: should match the same requirement listed previously/above
Note on D33: Format - number Note: should match the same requirement listed previously/above
Note on D34: Format - number Expected to be ≥400 Note: should match the same requirement listed previously/above
Note on D35: For ESO to populate