## Sheet1
Distributed Restart - Anchor Generators
| ESR Tender - Northern Region 2023 | PROVIDER NAME
| ITT5 SUBMISSION / SCORING | "Provider Name"
| Requirement |  | Score
| Time to Connect (h) |  | Pass/Fail
Service Availability (%)
Voltage Regulation (Leading) (%)
Voltage Regulation (Lagging) (%)
Frequency Regulation (Lower) (Hz)
Frequency Regulation (Upper) (Hz)
Resilience of supply, Black Start Service (h)
Resilience of Supply, BS Auxiliary Unit(s) (h)
Block loading size (MW)
Reactive Capability (MVAr)
Sequential Black Starts (number)
Connection Voltage (kV)
Short-circuit level (kA)
Inertia (MVA.s)
| Earthing | Y
| Connection to Network / Multiple - Single connections to the Network | 2 | 5%
| Time to Connect | 0.5 | 10%
| Service Availability | 100 | 15%
| Power Output / Active Capability (MW) | 151 | 20%
| Block Loading Size | 20 | 10%
| Resilience of Supply / BS service at contracted Power Output (h) | 120 | 15%
| Resilience of Supply / BS Auxiliary Units (h) | 180 | 10%
| Contribution to Restoration Time (h) |  | 15%
100%
Note on D7: Format - Number (Example: "1.7") Expected to be ≤8
Note on D8: Format - Number (Example: "100") Expected to be ≥ 80
Note on D9: Format - number Expected: "+10"
Note on D10: Format - number Expected: "-10"
Note on D11: Format - number Expected: "47.5"
Note on D12: Format - number Expected: "52"
Note on D13: Format - number Expected to be ≥72
Note on D14: Format - number Expected to be ≥120
Note on D15: Format - number Expected to be ≥2
Note on D16: Power factor of 0.95 lead/lag at Point of Connection
Note on D17: Format - integer Expected to be ≥3
Note on D18: Format - number Expected to be: 11, 33, 132, 275 or 400.
Note on D19: Format - number (Example: "1.32") ≥ 1x Anchor’s MVA Rating
Note on D20: Format - number Linked to the Block Loading Capability. Expected to be: - 2MW, ≥ 80 MVA.s - 3MW, ≥ 120 MVA.s - 4MW, ≥ 160 MVA.s - 5MW, ≥ 200 MVA.s - 6MW, ≥ 240 MVA.s - 7MW, ≥ 280 MVA.s - 8MW, ≥ 320 MVA.s - 9MW, ≥ 360 MVA.s - 10MW, ≥ 400 MVA.s - etc.
Note on D21: Format - letter Expected to be a "Y"
Note on D22: Format - number (integer) Expected to be ≥1 Note: Number of physical connections onto the Network that will enable the delivery of the full contracted service.
Note on D23: Format - number (Example: "1.7") Note: should match the same requirement listed previously/above
Note on D24: Format - Number (Example: "100") Expected to be ≥ 80
Note on D25: Format - number Note: contracted MW for the provision of the ESR Service
Note on D26: Format - number Expected to be ≥2 Note: should match the same requirement listed previously/above
Note on D27: Format - number(integer) Expected to be ≥72 Notes: - Should match the same requirement listed previously/above - If "Indefinite", please include "121"
Note on D28: Format - number Expected to be ≥120 Note: should match the same requirement listed previously/above