## Version
Date | Version | Details
2023-08-15 | 1 | This file only contains the indicative reporting associated with draft data for GC0151 for August 2023. This file will be updated in September to reflect the full data set.
2023-09-15 | 2 | This file only contains the indicative reporting associated with data for GC0151 for August 2023. This file is updated in September to reflect the full data set.
2023-10-05 | 3 | This file only contains the reporting associated with data for GC0105 & GC151 for August 2023.

## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.
MW trip/loss of all generation/ interconnection related to the incident | Positive sign: indicates a loss of infeed, generator or importing interconnector. Negative sign: indicates a loss of outfeed, exporting interconnector.

## Transmission Faults (GC0151)
Location | Network Operator | Date Time | Voltage Trace (Refer to sheet) | Notes
Blackhillock - Keith 2 (HKU2) 275kV circuit | SHETL | 2023-08-01 15:25
Elvanfoot - Moffat 400kV circuit | SPT | 2023-08-02 15:53
Elvanfoot - Moffat 400kV circuit | SPT | 2023-08-02 15:55
Elvanfoot - Moffat 400kV circuit | SPT | 2023-08-02 16:11
Elvanfoot - Moffat 400kV circuit | SPT | 2023-08-02 17:01
Denny North - Melgarve 400kV circuit | SHETL | 2023-08-11 04:36
Blackhillock - Keith 2 (HKU2) 275kV circuit | SHETL | 2023-08-11 07:08
Braintree 400/132kV SGT2 | NGET | 2023-08-13 19:15
Dunoon - Sloy - Whistlefield - Windyhill 1 (SWE1/GL1) 132 kV circuit | SHETL | 2023-08-15 04:44
DUNG - NINF 1 400kV circuit | NGET | 2023-08-19 00:15
Knocknagael 2 - Tomatin 1 275kV (CMA1) and Boat of Garten - Tomatin 2 (MAG2) 132/33kV circuit | SHETL | 2023-08-28 05:43
Burbo Bank Extension SVC | OFTO | 2023-08-28 21:58
Bramford - Burstall SGT2 and East Anglia GT2 | OFTO | 2023-08-29 19:49

## System Incidents (GC0105)
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) | Transmission fault | Voltage Dip | Additional data
20230802-1 | Trip of HOWBO-3 |  | 2023-08-02 11:49 | 20230802-1 | 49.991 | 49.771 | -0.16083 | 141 | HOWBO-3 | 422.906
20230803-1 | Trip of DRAXX-2 |  | 2023-08-03 11:57 | 20230803-1 | 49.93 | 49.783 | -0.16083 | 135 | DRAXX-2 | 594.75
20230803-2 | Trip of DRAXX-2 |  | 2023-08-03 15:02 | 20230803-2 | 49.798 | 49.751 | -0.024681 | 154 | DRAXX-2 | 344.153
20230823-1 | Trip of IFA Bipole 1 | IFA Bipole 1 tripped while importing 571MW from France to GB | 2023-08-23 09:56 | 20230823-1 | 50.108 | 49.869 | -0.052133 | 239 | IFA Bipole 1 | 571.05
20230826-1 | Trip of IFA Bipole 1 | IFA Bipole 1 tripped while importing 996MW from France to GB | 2023-08-26 12:30 | 20230826-1 | 50.027 | 49.697 | -0.052133 | 166 | IFA Bipole 1 | 996.75

## 20230802-1
In GMT
Date | Time | Freq
2023-08-02 | 10:48 | 50.015
2023-08-02 | 10:48 | 50.015
2023-08-02 | 10:48 | 50.012
2023-08-02 | 10:48 | 50.014
2023-08-02 | 10:48 | 50.014
2023-08-02 | 10:48 | 50.015
2023-08-02 | 10:48 | 50.014
2023-08-02 | 10:48 | 50.015
2023-08-02 | 10:48 | 50.013
2023-08-02 | 10:48 | 50.009
2023-08-02 | 10:48 | 50.009
2023-08-02 | 10:48 | 50.008
2023-08-02 | 10:48 | 50.005
2023-08-02 | 10:48 | 50.003
2023-08-02 | 10:48 | 50.001
2023-08-02 | 10:48 | 49.999
2023-08-02 | 10:48 | 49.998
2023-08-02 | 10:48 | 49.998
2023-08-02 | 10:48 | 49.999
2023-08-02 | 10:48 | 50.005
2023-08-02 | 10:48 | 50.005
2023-08-02 | 10:48 | 50.009
2023-08-02 | 10:48 | 50.008
2023-08-02 | 10:48 | 50.007
2023-08-02 | 10:48 | 50.008
2023-08-02 | 10:48 | 50.008
2023-08-02 | 10:48 | 50.006
2023-08-02 | 10:48 | 50.004
2023-08-02 | 10:48 | 49.996
2023-08-02 | 10:48 | 49.99
2023-08-02 | 10:48 | 49.986
2023-08-02 | 10:49 | 49.984
2023-08-02 | 10:49 | 49.983
2023-08-02 | 10:49 | 49.985
2023-08-02 | 10:49 | 49.987
2023-08-02 | 10:49 | 49.991
2023-08-02 | 10:49 | 49.996
2023-08-02 | 10:49 | 50.002
2023-08-02 | 10:49 | 50.004
2023-08-02 | 10:49 | 50.007
2023-08-02 | 10:49 | 50.011
2023-08-02 | 10:49 | 50.013
2023-08-02 | 10:49 | 50.012
2023-08-02 | 10:49 | 50.011
2023-08-02 | 10:49 | 50.012
2023-08-02 | 10:49 | 50.014
2023-08-02 | 10:49 | 50.013
2023-08-02 | 10:49 | 50.013
2023-08-02 | 10:49 | 50.012
2023-08-02 | 10:49 | 50.008
2023-08-02 | 10:49 | 50.007
2023-08-02 | 10:49 | 50.005
2023-08-02 | 10:49 | 50.002
2023-08-02 | 10:49 | 49.998
2023-08-02 | 10:49 | 49.994
2023-08-02 | 10:49 | 49.992
2023-08-02 | 10:49 | 49.989
2023-08-02 | 10:49 | 49.984
2023-08-02 | 10:49 | 49.98
2023-08-02 | 10:49 | 49.981
2023-08-02 | 10:49 | 49.98
2023-08-02 | 10:49 | 49.978
2023-08-02 | 10:49 | 49.977
2023-08-02 | 10:49 | 49.98
2023-08-02 | 10:49 | 49.98
2023-08-02 | 10:49 | 49.983
2023-08-02 | 10:49 | 49.984
2023-08-02 | 10:49 | 49.985
2023-08-02 | 10:49 | 49.986
2023-08-02 | 10:49 | 49.985
2023-08-02 | 10:49 | 49.99
2023-08-02 | 10:49 | 49.992
2023-08-02 | 10:49 | 49.993
2023-08-02 | 10:49 | 49.991
2023-08-02 | 10:49 | 49.992
2023-08-02 | 10:49 | 49.994
2023-08-02 | 10:49 | 49.994
2023-08-02 | 10:49 | 49.995
2023-08-02 | 10:49 | 49.994
2023-08-02 | 10:49 | 49.996
2023-08-02 | 10:49 | 49.996
2023-08-02 | 10:49 | 49.996
2023-08-02 | 10:49 | 49.995
2023-08-02 | 10:49 | 49.996
2023-08-02 | 10:49 | 49.996
2023-08-02 | 10:49 | 49.994
2023-08-02 | 10:49 | 49.993
2023-08-02 | 10:49 | 49.992
2023-08-02 | 10:49 | 49.993
2023-08-02 | 10:49 | 49.994
2023-08-02 | 10:49 | 49.991
2023-08-02 | 10:50 | 49.984
2023-08-02 | 10:50 | 49.975
2023-08-02 | 10:50 | 49.97
2023-08-02 | 10:50 | 49.914
2023-08-02 | 10:50 | 49.839
2023-08-02 | 10:50 | 49.796
2023-08-02 | 10:50 | 49.777
2023-08-02 | 10:50 | 49.771
2023-08-02 | 10:50 | 49.771
2023-08-02 | 10:50 | 49.777
2023-08-02 | 10:50 | 49.799
2023-08-02 | 10:50 | 49.816
2023-08-02 | 10:50 | 49.822
2023-08-02 | 10:50 | 49.828
2023-08-02 | 10:50 | 49.833
2023-08-02 | 10:50 | 49.836
2023-08-02 | 10:50 | 49.842
2023-08-02 | 10:50 | 49.843
2023-08-02 | 10:50 | 49.845
2023-08-02 | 10:50 | 49.849
2023-08-02 | 10:50 | 49.854
2023-08-02 | 10:50 | 49.852
2023-08-02 | 10:50 | 49.85
2023-08-02 | 10:50 | 49.85
2023-08-02 | 10:50 | 49.851
2023-08-02 | 10:50 | 49.849
2023-08-02 | 10:50 | 49.846
2023-08-02 | 10:50 | 49.845
2023-08-02 | 10:50 | 49.846
2023-08-02 | 10:50 | 49.844
2023-08-02 | 10:50 | 49.837
2023-08-02 | 10:50 | 49.837
2023-08-02 | 10:50 | 49.837
2023-08-02 | 10:50 | 49.84
2023-08-02 | 10:50 | 49.841
2023-08-02 | 10:50 | 49.841
2023-08-02 | 10:50 | 49.839
2023-08-02 | 10:50 | 49.834
2023-08-02 | 10:50 | 49.833
2023-08-02 | 10:50 | 49.833
2023-08-02 | 10:50 | 49.835
2023-08-02 | 10:50 | 49.833
2023-08-02 | 10:50 | 49.833
2023-08-02 | 10:50 | 49.833
2023-08-02 | 10:50 | 49.835
2023-08-02 | 10:50 | 49.839
2023-08-02 | 10:50 | 49.835
2023-08-02 | 10:50 | 49.834
2023-08-02 | 10:50 | 49.836
2023-08-02 | 10:50 | 49.831
2023-08-02 | 10:50 | 49.834
2023-08-02 | 10:50 | 49.836
2023-08-02 | 10:50 | 49.834
2023-08-02 | 10:50 | 49.838
2023-08-02 | 10:50 | 49.839
2023-08-02 | 10:50 | 49.838
2023-08-02 | 10:50 | 49.842
2023-08-02 | 10:50 | 49.841
2023-08-02 | 10:50 | 49.84
2023-08-02 | 10:50 | 49.844
2023-08-02 | 10:51 | 49.847
2023-08-02 | 10:51 | 49.847
2023-08-02 | 10:51 | 49.844
2023-08-02 | 10:51 | 49.847
2023-08-02 | 10:51 | 49.849
2023-08-02 | 10:51 | 49.848
2023-08-02 | 10:51 | 49.851
2023-08-02 | 10:51 | 49.85
2023-08-02 | 10:51 | 49.852
2023-08-02 | 10:51 | 49.853
2023-08-02 | 10:51 | 49.852
2023-08-02 | 10:51 | 49.85
2023-08-02 | 10:51 | 49.844
2023-08-02 | 10:51 | 49.842
2023-08-02 | 10:51 | 49.838
2023-08-02 | 10:51 | 49.837
2023-08-02 | 10:51 | 49.835
2023-08-02 | 10:51 | 49.833
2023-08-02 | 10:51 | 49.833
2023-08-02 | 10:51 | 49.836
2023-08-02 | 10:51 | 49.837
2023-08-02 | 10:51 | 49.839
2023-08-02 | 10:51 | 49.838
2023-08-02 | 10:51 | 49.838
2023-08-02 | 10:51 | 49.839
2023-08-02 | 10:51 | 49.836
2023-08-02 | 10:51 | 49.837
2023-08-02 | 10:51 | 49.839
2023-08-02 | 10:51 | 49.841
2023-08-02 | 10:51 | 49.84
2023-08-02 | 10:51 | 49.837
2023-08-02 | 10:51 | 49.84
2023-08-02 | 10:51 | 49.839
2023-08-02 | 10:51 | 49.837
2023-08-02 | 10:51 | 49.839
2023-08-02 | 10:51 | 49.837
2023-08-02 | 10:51 | 49.836
2023-08-02 | 10:51 | 49.836
2023-08-02 | 10:51 | 49.836
2023-08-02 | 10:51 | 49.833
2023-08-02 | 10:51 | 49.834
2023-08-02 | 10:51 | 49.835
2023-08-02 | 10:51 | 49.833
2023-08-02 | 10:51 | 49.834
2023-08-02 | 10:51 | 49.836
2023-08-02 | 10:51 | 49.833
2023-08-02 | 10:51 | 49.831
2023-08-02 | 10:51 | 49.83
2023-08-02 | 10:51 | 49.831
2023-08-02 | 10:51 | 49.837
2023-08-02 | 10:51 | 49.844
2023-08-02 | 10:51 | 49.849
2023-08-02 | 10:51 | 49.848
2023-08-02 | 10:51 | 49.848
2023-08-02 | 10:51 | 49.843
2023-08-02 | 10:51 | 49.843
2023-08-02 | 10:51 | 49.845
2023-08-02 | 10:51 | 49.846
2023-08-02 | 10:51 | 49.845
2023-08-02 | 10:51 | 49.849
2023-08-02 | 10:52 | 49.852
2023-08-02 | 10:52 | 49.852
2023-08-02 | 10:52 | 49.852
2023-08-02 | 10:52 | 49.849
2023-08-02 | 10:52 | 49.846
2023-08-02 | 10:52 | 49.844
2023-08-02 | 10:52 | 49.842
2023-08-02 | 10:52 | 49.846
2023-08-02 | 10:52 | 49.851
2023-08-02 | 10:52 | 49.847
2023-08-02 | 10:52 | 49.848
2023-08-02 | 10:52 | 49.848
2023-08-02 | 10:52 | 49.844
2023-08-02 | 10:52 | 49.843
2023-08-02 | 10:52 | 49.837
2023-08-02 | 10:52 | 49.836
2023-08-02 | 10:52 | 49.838
2023-08-02 | 10:52 | 49.832
2023-08-02 | 10:52 | 49.833
2023-08-02 | 10:52 | 49.834
2023-08-02 | 10:52 | 49.836
2023-08-02 | 10:52 | 49.839
2023-08-02 | 10:52 | 49.835
2023-08-02 | 10:52 | 49.837
2023-08-02 | 10:52 | 49.838
2023-08-02 | 10:52 | 49.832
2023-08-02 | 10:52 | 49.835
2023-08-02 | 10:52 | 49.835
2023-08-02 | 10:52 | 49.838
2023-08-02 | 10:52 | 49.841
2023-08-02 | 10:52 | 49.839
2023-08-02 | 10:52 | 49.838
2023-08-02 | 10:52 | 49.841
2023-08-02 | 10:52 | 49.843
2023-08-02 | 10:52 | 49.842
2023-08-02 | 10:52 | 49.84
2023-08-02 | 10:52 | 49.842
2023-08-02 | 10:52 | 49.847
2023-08-02 | 10:52 | 49.85
2023-08-02 | 10:52 | 49.849
2023-08-02 | 10:52 | 49.851
2023-08-02 | 10:52 | 49.851
2023-08-02 | 10:52 | 49.852
2023-08-02 | 10:52 | 49.851
2023-08-02 | 10:52 | 49.853
2023-08-02 | 10:52 | 49.853
2023-08-02 | 10:52 | 49.856
2023-08-02 | 10:52 | 49.856
2023-08-02 | 10:52 | 49.856
2023-08-02 | 10:52 | 49.859
2023-08-02 | 10:52 | 49.856
2023-08-02 | 10:52 | 49.855
2023-08-02 | 10:52 | 49.849
2023-08-02 | 10:52 | 49.849
2023-08-02 | 10:52 | 49.849
2023-08-02 | 10:52 | 49.852
2023-08-02 | 10:52 | 49.863
2023-08-02 | 10:52 | 49.867
2023-08-02 | 10:52 | 49.874
2023-08-02 | 10:52 | 49.877
2023-08-02 | 10:53 | 49.877
2023-08-02 | 10:53 | 49.876
2023-08-02 | 10:53 | 49.878
2023-08-02 | 10:53 | 49.878
2023-08-02 | 10:53 | 49.88
2023-08-02 | 10:53 | 49.885
2023-08-02 | 10:53 | 49.89
2023-08-02 | 10:53 | 49.886
2023-08-02 | 10:53 | 49.883
2023-08-02 | 10:53 | 49.88
2023-08-02 | 10:53 | 49.885
2023-08-02 | 10:53 | 49.891
2023-08-02 | 10:53 | 49.897
2023-08-02 | 10:53 | 49.896
2023-08-02 | 10:53 | 49.894
2023-08-02 | 10:53 | 49.895
2023-08-02 | 10:53 | 49.896
2023-08-02 | 10:53 | 49.899
2023-08-02 | 10:53 | 49.897
2023-08-02 | 10:53 | 49.894
2023-08-02 | 10:53 | 49.892
2023-08-02 | 10:53 | 49.89
2023-08-02 | 10:53 | 49.891
2023-08-02 | 10:53 | 49.888
2023-08-02 | 10:53 | 49.883
2023-08-02 | 10:53 | 49.881
2023-08-02 | 10:53 | 49.88
2023-08-02 | 10:53 | 49.881
2023-08-02 | 10:53 | 49.88
2023-08-02 | 10:53 | 49.877
2023-08-02 | 10:53 | 49.874
2023-08-02 | 10:53 | 49.874
2023-08-02 | 10:53 | 49.881
2023-08-02 | 10:53 | 49.886
2023-08-02 | 10:53 | 49.892
2023-08-02 | 10:53 | 49.892
2023-08-02 | 10:53 | 49.892
2023-08-02 | 10:53 | 49.889
2023-08-02 | 10:53 | 49.89
2023-08-02 | 10:53 | 49.891
2023-08-02 | 10:53 | 49.892
2023-08-02 | 10:53 | 49.894
2023-08-02 | 10:53 | 49.891
2023-08-02 | 10:53 | 49.889
2023-08-02 | 10:53 | 49.887
2023-08-02 | 10:53 | 49.888
2023-08-02 | 10:53 | 49.889
2023-08-02 | 10:53 | 49.891
2023-08-02 | 10:53 | 49.893
2023-08-02 | 10:53 | 49.895
2023-08-02 | 10:53 | 49.896
2023-08-02 | 10:53 | 49.894
2023-08-02 | 10:53 | 49.893
2023-08-02 | 10:53 | 49.89
2023-08-02 | 10:53 | 49.889
2023-08-02 | 10:53 | 49.889
2023-08-02 | 10:53 | 49.891
2023-08-02 | 10:53 | 49.893
2023-08-02 | 10:53 | 49.893
2023-08-02 | 10:54 | 49.892
2023-08-02 | 10:54 | 49.893
2023-08-02 | 10:54 | 49.891
2023-08-02 | 10:54 | 49.888
2023-08-02 | 10:54 | 49.888
2023-08-02 | 10:54 | 49.888
2023-08-02 | 10:54 | 49.888
2023-08-02 | 10:54 | 49.885
2023-08-02 | 10:54 | 49.883
2023-08-02 | 10:54 | 49.883
2023-08-02 | 10:54 | 49.885
2023-08-02 | 10:54 | 49.89
2023-08-02 | 10:54 | 49.892
2023-08-02 | 10:54 | 49.893
2023-08-02 | 10:54 | 49.891
2023-08-02 | 10:54 | 49.891
2023-08-02 | 10:54 | 49.894
2023-08-02 | 10:54 | 49.893
2023-08-02 | 10:54 | 49.895
2023-08-02 | 10:54 | 49.892
2023-08-02 | 10:54 | 49.889
2023-08-02 | 10:54 | 49.886
2023-08-02 | 10:54 | 49.885
2023-08-02 | 10:54 | 49.885
2023-08-02 | 10:54 | 49.886
2023-08-02 | 10:54 | 49.884
2023-08-02 | 10:54 | 49.882
2023-08-02 | 10:54 | 49.879
2023-08-02 | 10:54 | 49.882
2023-08-02 | 10:54 | 49.886
2023-08-02 | 10:54 | 49.886
2023-08-02 | 10:54 | 49.885
2023-08-02 | 10:54 | 49.883
2023-08-02 | 10:54 | 49.881
2023-08-02 | 10:54 | 49.882
2023-08-02 | 10:54 | 49.885
2023-08-02 | 10:54 | 49.89
2023-08-02 | 10:54 | 49.896
2023-08-02 | 10:54 | 49.901
2023-08-02 | 10:54 | 49.904
2023-08-02 | 10:54 | 49.91
2023-08-02 | 10:54 | 49.913
2023-08-02 | 10:54 | 49.914
2023-08-02 | 10:54 | 49.918
2023-08-02 | 10:54 | 49.92
2023-08-02 | 10:54 | 49.923
2023-08-02 | 10:54 | 49.92
2023-08-02 | 10:54 | 49.918
2023-08-02 | 10:54 | 49.914
2023-08-02 | 10:54 | 49.915
2023-08-02 | 10:54 | 49.918
2023-08-02 | 10:54 | 49.921
2023-08-02 | 10:54 | 49.923
2023-08-02 | 10:54 | 49.925
2023-08-02 | 10:54 | 49.924
2023-08-02 | 10:54 | 49.922
2023-08-02 | 10:54 | 49.923
2023-08-02 | 10:54 | 49.921
2023-08-02 | 10:54 | 49.925
2023-08-02 | 10:54 | 49.931
2023-08-02 | 10:54 | 49.932
2023-08-02 | 10:55 | 49.932
2023-08-02 | 10:55 | 49.935
2023-08-02 | 10:55 | 49.941
2023-08-02 | 10:55 | 49.943
2023-08-02 | 10:55 | 49.945
2023-08-02 | 10:55 | 49.941
2023-08-02 | 10:55 | 49.941
2023-08-02 | 10:55 | 49.943
2023-08-02 | 10:55 | 49.946
2023-08-02 | 10:55 | 49.948
2023-08-02 | 10:55 | 49.949
2023-08-02 | 10:55 | 49.952
2023-08-02 | 10:55 | 49.948
2023-08-02 | 10:55 | 49.949
2023-08-02 | 10:55 | 49.944
2023-08-02 | 10:55 | 49.938
2023-08-02 | 10:55 | 49.933
2023-08-02 | 10:55 | 49.93
2023-08-02 | 10:55 | 49.924
2023-08-02 | 10:55 | 49.923
2023-08-02 | 10:55 | 49.926
2023-08-02 | 10:55 | 49.928
2023-08-02 | 10:55 | 49.926
2023-08-02 | 10:55 | 49.925
2023-08-02 | 10:55 | 49.927
2023-08-02 | 10:55 | 49.929
2023-08-02 | 10:55 | 49.925
2023-08-02 | 10:55 | 49.928
2023-08-02 | 10:55 | 49.931
2023-08-02 | 10:55 | 49.932
2023-08-02 | 10:55 | 49.931
2023-08-02 | 10:55 | 49.927
2023-08-02 | 10:55 | 49.931
2023-08-02 | 10:55 | 49.934
2023-08-02 | 10:55 | 49.933
2023-08-02 | 10:55 | 49.936
2023-08-02 | 10:55 | 49.937
2023-08-02 | 10:55 | 49.936
2023-08-02 | 10:55 | 49.936
2023-08-02 | 10:55 | 49.936
2023-08-02 | 10:55 | 49.936
2023-08-02 | 10:55 | 49.938
2023-08-02 | 10:55 | 49.941
2023-08-02 | 10:55 | 49.942
2023-08-02 | 10:55 | 49.945
2023-08-02 | 10:55 | 49.946
2023-08-02 | 10:55 | 49.939
2023-08-02 | 10:55 | 49.93
2023-08-02 | 10:55 | 49.924
2023-08-02 | 10:55 | 49.922
2023-08-02 | 10:55 | 49.918
2023-08-02 | 10:55 | 49.919
2023-08-02 | 10:55 | 49.917
2023-08-02 | 10:55 | 49.915
2023-08-02 | 10:55 | 49.912
2023-08-02 | 10:55 | 49.911
2023-08-02 | 10:55 | 49.91
2023-08-02 | 10:55 | 49.912
2023-08-02 | 10:55 | 49.912
2023-08-02 | 10:56 | 49.91
2023-08-02 | 10:56 | 49.906
2023-08-02 | 10:56 | 49.901
2023-08-02 | 10:56 | 49.898
2023-08-02 | 10:56 | 49.904
2023-08-02 | 10:56 | 49.907
2023-08-02 | 10:56 | 49.912
2023-08-02 | 10:56 | 49.916
2023-08-02 | 10:56 | 49.922
2023-08-02 | 10:56 | 49.925
2023-08-02 | 10:56 | 49.928
2023-08-02 | 10:56 | 49.927
2023-08-02 | 10:56 | 49.93
2023-08-02 | 10:56 | 49.929
2023-08-02 | 10:56 | 49.928
2023-08-02 | 10:56 | 49.929
2023-08-02 | 10:56 | 49.929
2023-08-02 | 10:56 | 49.93
2023-08-02 | 10:56 | 49.928
2023-08-02 | 10:56 | 49.927
2023-08-02 | 10:56 | 49.926
2023-08-02 | 10:56 | 49.924
2023-08-02 | 10:56 | 49.925
2023-08-02 | 10:56 | 49.924
2023-08-02 | 10:56 | 49.927
2023-08-02 | 10:56 | 49.932
2023-08-02 | 10:56 | 49.935
2023-08-02 | 10:56 | 49.932
2023-08-02 | 10:56 | 49.928
2023-08-02 | 10:56 | 49.927
2023-08-02 | 10:56 | 49.926
2023-08-02 | 10:56 | 49.922
2023-08-02 | 10:56 | 49.919
2023-08-02 | 10:56 | 49.921
2023-08-02 | 10:56 | 49.923
2023-08-02 | 10:56 | 49.929
2023-08-02 | 10:56 | 49.933
2023-08-02 | 10:56 | 49.932
2023-08-02 | 10:56 | 49.929
2023-08-02 | 10:56 | 49.926
2023-08-02 | 10:56 | 49.93
2023-08-02 | 10:56 | 49.935
2023-08-02 | 10:56 | 49.939
2023-08-02 | 10:56 | 49.943
2023-08-02 | 10:56 | 49.949
2023-08-02 | 10:56 | 49.953
2023-08-02 | 10:56 | 49.953
2023-08-02 | 10:56 | 49.953
2023-08-02 | 10:56 | 49.951
2023-08-02 | 10:56 | 49.954
2023-08-02 | 10:56 | 49.956
2023-08-02 | 10:56 | 49.954
2023-08-02 | 10:56 | 49.953
2023-08-02 | 10:56 | 49.951
2023-08-02 | 10:56 | 49.951
2023-08-02 | 10:56 | 49.946
2023-08-02 | 10:56 | 49.944
2023-08-02 | 10:56 | 49.942
2023-08-02 | 10:56 | 49.941
2023-08-02 | 10:56 | 49.938
2023-08-02 | 10:56 | 49.937
2023-08-02 | 10:57 | 49.939
2023-08-02 | 10:57 | 49.942
2023-08-02 | 10:57 | 49.941
2023-08-02 | 10:57 | 49.937
2023-08-02 | 10:57 | 49.933
2023-08-02 | 10:57 | 49.932
2023-08-02 | 10:57 | 49.931
2023-08-02 | 10:57 | 49.929
2023-08-02 | 10:57 | 49.927
2023-08-02 | 10:57 | 49.925
2023-08-02 | 10:57 | 49.924
2023-08-02 | 10:57 | 49.925
2023-08-02 | 10:57 | 49.926
2023-08-02 | 10:57 | 49.926
2023-08-02 | 10:57 | 49.927
2023-08-02 | 10:57 | 49.933
2023-08-02 | 10:57 | 49.936
2023-08-02 | 10:57 | 49.938
2023-08-02 | 10:57 | 49.932
2023-08-02 | 10:57 | 49.927
2023-08-02 | 10:57 | 49.928
2023-08-02 | 10:57 | 49.931
2023-08-02 | 10:57 | 49.932
2023-08-02 | 10:57 | 49.932
2023-08-02 | 10:57 | 49.932
2023-08-02 | 10:57 | 49.932
2023-08-02 | 10:57 | 49.926
2023-08-02 | 10:57 | 49.916
2023-08-02 | 10:57 | 49.904
2023-08-02 | 10:57 | 49.892
2023-08-02 | 10:57 | 49.879
2023-08-02 | 10:57 | 49.872
2023-08-02 | 10:57 | 49.87
2023-08-02 | 10:57 | 49.868
2023-08-02 | 10:57 | 49.869
2023-08-02 | 10:57 | 49.868
2023-08-02 | 10:57 | 49.866
2023-08-02 | 10:57 | 49.861
2023-08-02 | 10:57 | 49.859
2023-08-02 | 10:57 | 49.867
2023-08-02 | 10:57 | 49.871
2023-08-02 | 10:57 | 49.881
2023-08-02 | 10:57 | 49.905
2023-08-02 | 10:57 | 49.924
2023-08-02 | 10:57 | 49.934
2023-08-02 | 10:57 | 49.94
2023-08-02 | 10:57 | 49.944
2023-08-02 | 10:57 | 49.946
2023-08-02 | 10:57 | 49.944
2023-08-02 | 10:57 | 49.943
2023-08-02 | 10:57 | 49.943
2023-08-02 | 10:57 | 49.943
2023-08-02 | 10:57 | 49.944
2023-08-02 | 10:57 | 49.948
2023-08-02 | 10:57 | 49.953
2023-08-02 | 10:57 | 49.959
2023-08-02 | 10:57 | 49.966
2023-08-02 | 10:57 | 49.965
2023-08-02 | 10:57 | 49.963
2023-08-02 | 10:58 | 49.956
2023-08-02 | 10:58 | 49.95
2023-08-02 | 10:58 | 49.945
2023-08-02 | 10:58 | 49.94
2023-08-02 | 10:58 | 49.937
2023-08-02 | 10:58 | 49.934
2023-08-02 | 10:58 | 49.934
2023-08-02 | 10:58 | 49.936
2023-08-02 | 10:58 | 49.94
2023-08-02 | 10:58 | 49.94
2023-08-02 | 10:58 | 49.941
2023-08-02 | 10:58 | 49.94
2023-08-02 | 10:58 | 49.941
2023-08-02 | 10:58 | 49.943
2023-08-02 | 10:58 | 49.946
2023-08-02 | 10:58 | 49.947
2023-08-02 | 10:58 | 49.946
2023-08-02 | 10:58 | 49.946
2023-08-02 | 10:58 | 49.95
2023-08-02 | 10:58 | 49.954
2023-08-02 | 10:58 | 49.954
2023-08-02 | 10:58 | 49.951
2023-08-02 | 10:58 | 49.946
2023-08-02 | 10:58 | 49.945
2023-08-02 | 10:58 | 49.94
2023-08-02 | 10:58 | 49.939
2023-08-02 | 10:58 | 49.939
2023-08-02 | 10:58 | 49.937
2023-08-02 | 10:58 | 49.935
2023-08-02 | 10:58 | 49.932
2023-08-02 | 10:58 | 49.928
2023-08-02 | 10:58 | 49.924
2023-08-02 | 10:58 | 49.919
2023-08-02 | 10:58 | 49.919
2023-08-02 | 10:58 | 49.918
2023-08-02 | 10:58 | 49.919
2023-08-02 | 10:58 | 49.917
2023-08-02 | 10:58 | 49.919
2023-08-02 | 10:58 | 49.92
2023-08-02 | 10:58 | 49.924
2023-08-02 | 10:58 | 49.929
2023-08-02 | 10:58 | 49.935
2023-08-02 | 10:58 | 49.938
2023-08-02 | 10:58 | 49.937
2023-08-02 | 10:58 | 49.936
2023-08-02 | 10:58 | 49.935
2023-08-02 | 10:58 | 49.932
2023-08-02 | 10:58 | 49.932
2023-08-02 | 10:58 | 49.933
2023-08-02 | 10:58 | 49.935
2023-08-02 | 10:58 | 49.937
2023-08-02 | 10:58 | 49.937
2023-08-02 | 10:58 | 49.938
2023-08-02 | 10:58 | 49.936
2023-08-02 | 10:58 | 49.936
2023-08-02 | 10:58 | 49.937
2023-08-02 | 10:58 | 49.942
2023-08-02 | 10:58 | 49.946
2023-08-02 | 10:58 | 49.952
2023-08-02 | 10:58 | 49.956
2023-08-02 | 10:58 | 49.961
2023-08-02 | 10:59 | 49.965
2023-08-02 | 10:59 | 49.97
2023-08-02 | 10:59 | 49.971
2023-08-02 | 10:59 | 49.974
2023-08-02 | 10:59 | 49.975
2023-08-02 | 10:59 | 49.974
2023-08-02 | 10:59 | 49.976
2023-08-02 | 10:59 | 49.975
2023-08-02 | 10:59 | 49.977
2023-08-02 | 10:59 | 49.978
2023-08-02 | 10:59 | 49.977
2023-08-02 | 10:59 | 49.975
2023-08-02 | 10:59 | 49.972
2023-08-02 | 10:59 | 49.97
2023-08-02 | 10:59 | 49.969
2023-08-02 | 10:59 | 49.972
2023-08-02 | 10:59 | 49.973
2023-08-02 | 10:59 | 49.973
2023-08-02 | 10:59 | 49.972
2023-08-02 | 10:59 | 49.97
2023-08-02 | 10:59 | 49.966
2023-08-02 | 10:59 | 49.962
2023-08-02 | 10:59 | 49.96
2023-08-02 | 10:59 | 49.96
2023-08-02 | 10:59 | 49.964
2023-08-02 | 10:59 | 49.966
2023-08-02 | 10:59 | 49.967
2023-08-02 | 10:59 | 49.969
2023-08-02 | 10:59 | 49.971
2023-08-02 | 10:59 | 49.97
2023-08-02 | 10:59 | 49.966
2023-08-02 | 10:59 | 49.963
2023-08-02 | 10:59 | 49.96
2023-08-02 | 10:59 | 49.959
2023-08-02 | 10:59 | 49.961
2023-08-02 | 10:59 | 49.961
2023-08-02 | 10:59 | 49.962
2023-08-02 | 10:59 | 49.963
2023-08-02 | 10:59 | 49.963
2023-08-02 | 10:59 | 49.962
2023-08-02 | 10:59 | 49.96
2023-08-02 | 10:59 | 49.957
2023-08-02 | 10:59 | 49.955
2023-08-02 | 10:59 | 49.956
2023-08-02 | 10:59 | 49.956
2023-08-02 | 10:59 | 49.96
2023-08-02 | 10:59 | 49.963
2023-08-02 | 10:59 | 49.965
2023-08-02 | 10:59 | 49.968
2023-08-02 | 10:59 | 49.97
2023-08-02 | 10:59 | 49.971
2023-08-02 | 10:59 | 49.973
2023-08-02 | 10:59 | 49.971
2023-08-02 | 10:59 | 49.972
2023-08-02 | 10:59 | 49.975
2023-08-02 | 10:59 | 49.98
2023-08-02 | 10:59 | 49.982
2023-08-02 | 10:59 | 49.985
2023-08-02 | 10:59 | 49.986
2023-08-02 | 11:00 | 49.988
2023-08-02 | 11:00 | 49.989
2023-08-02 | 11:00 | 49.989
2023-08-02 | 11:00 | 49.992
2023-08-02 | 11:00 | 49.996
2023-08-02 | 11:00 | 50.003
2023-08-02 | 11:00 | 50.011
2023-08-02 | 11:00 | 50.018
2023-08-02 | 11:00 | 50.019
2023-08-02 | 11:00 | 50.016
2023-08-02 | 11:00 | 50.015
2023-08-02 | 11:00 | 50.014
2023-08-02 | 11:00 | 50.015
2023-08-02 | 11:00 | 50.017
2023-08-02 | 11:00 | 50.02
2023-08-02 | 11:00 | 50.021
2023-08-02 | 11:00 | 50.016
2023-08-02 | 11:00 | 50.012
2023-08-02 | 11:00 | 50.009
2023-08-02 | 11:00 | 50.008
2023-08-02 | 11:00 | 50.009
2023-08-02 | 11:00 | 50.008
2023-08-02 | 11:00 | 50.01
2023-08-02 | 11:00 | 50.014
2023-08-02 | 11:00 | 50.018
2023-08-02 | 11:00 | 50.023
2023-08-02 | 11:00 | 50.029
2023-08-02 | 11:00 | 50.031
2023-08-02 | 11:00 | 50.029
2023-08-02 | 11:00 | 50.028
2023-08-02 | 11:00 | 50.027
2023-08-02 | 11:00 | 50.026
2023-08-02 | 11:00 | 50.028
2023-08-02 | 11:00 | 50.029
2023-08-02 | 11:00 | 50.029
2023-08-02 | 11:00 | 50.029
2023-08-02 | 11:00 | 50.029
2023-08-02 | 11:00 | 50.031
2023-08-02 | 11:00 | 50.03
2023-08-02 | 11:00 | 50.028
2023-08-02 | 11:00 | 50.026
2023-08-02 | 11:00 | 50.024
2023-08-02 | 11:00 | 50.027
2023-08-02 | 11:00 | 50.032
2023-08-02 | 11:00 | 50.034
2023-08-02 | 11:00 | 50.033
2023-08-02 | 11:00 | 50.033
2023-08-02 | 11:00 | 50.034
2023-08-02 | 11:00 | 50.032
2023-08-02 | 11:00 | 50.028
2023-08-02 | 11:00 | 50.025
2023-08-02 | 11:00 | 50.021
2023-08-02 | 11:00 | 50.019
2023-08-02 | 11:00 | 50.017
2023-08-02 | 11:00 | 50.015
2023-08-02 | 11:00 | 50.013
2023-08-02 | 11:00 | 50.013
2023-08-02 | 11:00 | 50.014
2023-08-02 | 11:00 | 50.015
2023-08-02 | 11:00 | 50.016
2023-08-02 | 11:00 | 50.017
2023-08-02 | 11:01 | 50.019
2023-08-02 | 11:01 | 50.021
2023-08-02 | 11:01 | 50.019
2023-08-02 | 11:01 | 50.016
2023-08-02 | 11:01 | 50.014
2023-08-02 | 11:01 | 50.014
2023-08-02 | 11:01 | 50.013
2023-08-02 | 11:01 | 50.012
2023-08-02 | 11:01 | 50.013
2023-08-02 | 11:01 | 50.015
2023-08-02 | 11:01 | 50.011
2023-08-02 | 11:01 | 50.006
2023-08-02 | 11:01 | 50.001
2023-08-02 | 11:01 | 50.001
2023-08-02 | 11:01 | 50.002
2023-08-02 | 11:01 | 50.004
2023-08-02 | 11:01 | 50.009
2023-08-02 | 11:01 | 50.013
2023-08-02 | 11:01 | 50.019
2023-08-02 | 11:01 | 50.024
2023-08-02 | 11:01 | 50.027
2023-08-02 | 11:01 | 50.028
2023-08-02 | 11:01 | 50.027
2023-08-02 | 11:01 | 50.028
2023-08-02 | 11:01 | 50.029
2023-08-02 | 11:01 | 50.028
2023-08-02 | 11:01 | 50.027
2023-08-02 | 11:01 | 50.024
2023-08-02 | 11:01 | 50.022

## 20230803-1
In GMT
Date | Time | Freq
2023-08-03 | 10:56 | 50.021
2023-08-03 | 10:56 | 50.019
2023-08-03 | 10:56 | 50.018
2023-08-03 | 10:56 | 50.014
2023-08-03 | 10:56 | 50.009
2023-08-03 | 10:56 | 50.005
2023-08-03 | 10:56 | 50.002
2023-08-03 | 10:56 | 49.995
2023-08-03 | 10:56 | 49.989
2023-08-03 | 10:56 | 49.983
2023-08-03 | 10:56 | 49.976
2023-08-03 | 10:56 | 49.974
2023-08-03 | 10:56 | 49.976
2023-08-03 | 10:56 | 49.977
2023-08-03 | 10:56 | 49.977
2023-08-03 | 10:56 | 49.977
2023-08-03 | 10:56 | 49.975
2023-08-03 | 10:56 | 49.972
2023-08-03 | 10:56 | 49.971
2023-08-03 | 10:56 | 49.971
2023-08-03 | 10:56 | 49.972
2023-08-03 | 10:56 | 49.973
2023-08-03 | 10:56 | 49.973
2023-08-03 | 10:56 | 49.972
2023-08-03 | 10:56 | 49.969
2023-08-03 | 10:56 | 49.967
2023-08-03 | 10:56 | 49.966
2023-08-03 | 10:56 | 49.964
2023-08-03 | 10:56 | 49.957
2023-08-03 | 10:56 | 49.95
2023-08-03 | 10:56 | 49.948
2023-08-03 | 10:57 | 49.946
2023-08-03 | 10:57 | 49.943
2023-08-03 | 10:57 | 49.939
2023-08-03 | 10:57 | 49.936
2023-08-03 | 10:57 | 49.939
2023-08-03 | 10:57 | 49.942
2023-08-03 | 10:57 | 49.945
2023-08-03 | 10:57 | 49.943
2023-08-03 | 10:57 | 49.941
2023-08-03 | 10:57 | 49.937
2023-08-03 | 10:57 | 49.938
2023-08-03 | 10:57 | 49.936
2023-08-03 | 10:57 | 49.934
2023-08-03 | 10:57 | 49.934
2023-08-03 | 10:57 | 49.93
2023-08-03 | 10:57 | 49.93
2023-08-03 | 10:57 | 49.925
2023-08-03 | 10:57 | 49.881
2023-08-03 | 10:57 | 49.821
2023-08-03 | 10:57 | 49.791
2023-08-03 | 10:57 | 49.783
2023-08-03 | 10:57 | 49.788
2023-08-03 | 10:57 | 49.794
2023-08-03 | 10:57 | 49.8
2023-08-03 | 10:57 | 49.803
2023-08-03 | 10:57 | 49.803
2023-08-03 | 10:57 | 49.803
2023-08-03 | 10:57 | 49.803
2023-08-03 | 10:57 | 49.806
2023-08-03 | 10:57 | 49.807
2023-08-03 | 10:57 | 49.806
2023-08-03 | 10:57 | 49.806
2023-08-03 | 10:57 | 49.807
2023-08-03 | 10:57 | 49.806
2023-08-03 | 10:57 | 49.805
2023-08-03 | 10:57 | 49.806
2023-08-03 | 10:57 | 49.806
2023-08-03 | 10:57 | 49.806
2023-08-03 | 10:57 | 49.804
2023-08-03 | 10:57 | 49.803
2023-08-03 | 10:57 | 49.8
2023-08-03 | 10:57 | 49.798
2023-08-03 | 10:57 | 49.799
2023-08-03 | 10:57 | 49.8
2023-08-03 | 10:57 | 49.801
2023-08-03 | 10:57 | 49.802
2023-08-03 | 10:57 | 49.803
2023-08-03 | 10:57 | 49.804
2023-08-03 | 10:57 | 49.804
2023-08-03 | 10:57 | 49.803
2023-08-03 | 10:57 | 49.804
2023-08-03 | 10:57 | 49.806
2023-08-03 | 10:57 | 49.807
2023-08-03 | 10:57 | 49.81
2023-08-03 | 10:57 | 49.812
2023-08-03 | 10:57 | 49.811
2023-08-03 | 10:57 | 49.811
2023-08-03 | 10:57 | 49.809
2023-08-03 | 10:57 | 49.81
2023-08-03 | 10:58 | 49.808
2023-08-03 | 10:58 | 49.811
2023-08-03 | 10:58 | 49.813
2023-08-03 | 10:58 | 49.812
2023-08-03 | 10:58 | 49.81
2023-08-03 | 10:58 | 49.809
2023-08-03 | 10:58 | 49.81
2023-08-03 | 10:58 | 49.812
2023-08-03 | 10:58 | 49.813
2023-08-03 | 10:58 | 49.814
2023-08-03 | 10:58 | 49.817
2023-08-03 | 10:58 | 49.814
2023-08-03 | 10:58 | 49.813
2023-08-03 | 10:58 | 49.815
2023-08-03 | 10:58 | 49.817
2023-08-03 | 10:58 | 49.818
2023-08-03 | 10:58 | 49.82
2023-08-03 | 10:58 | 49.816
2023-08-03 | 10:58 | 49.813
2023-08-03 | 10:58 | 49.812
2023-08-03 | 10:58 | 49.814
2023-08-03 | 10:58 | 49.814
2023-08-03 | 10:58 | 49.81
2023-08-03 | 10:58 | 49.805
2023-08-03 | 10:58 | 49.8
2023-08-03 | 10:58 | 49.797
2023-08-03 | 10:58 | 49.799
2023-08-03 | 10:58 | 49.799
2023-08-03 | 10:58 | 49.799
2023-08-03 | 10:58 | 49.8
2023-08-03 | 10:58 | 49.802
2023-08-03 | 10:58 | 49.797
2023-08-03 | 10:58 | 49.794
2023-08-03 | 10:58 | 49.795
2023-08-03 | 10:58 | 49.794
2023-08-03 | 10:58 | 49.794
2023-08-03 | 10:58 | 49.795
2023-08-03 | 10:58 | 49.792
2023-08-03 | 10:58 | 49.79
2023-08-03 | 10:58 | 49.789
2023-08-03 | 10:58 | 49.788
2023-08-03 | 10:58 | 49.788
2023-08-03 | 10:58 | 49.79
2023-08-03 | 10:58 | 49.793
2023-08-03 | 10:58 | 49.792
2023-08-03 | 10:58 | 49.79
2023-08-03 | 10:58 | 49.789
2023-08-03 | 10:58 | 49.792
2023-08-03 | 10:58 | 49.794
2023-08-03 | 10:58 | 49.797
2023-08-03 | 10:58 | 49.799
2023-08-03 | 10:58 | 49.8
2023-08-03 | 10:58 | 49.803
2023-08-03 | 10:58 | 49.808
2023-08-03 | 10:58 | 49.812
2023-08-03 | 10:58 | 49.815
2023-08-03 | 10:58 | 49.819
2023-08-03 | 10:58 | 49.824
2023-08-03 | 10:58 | 49.823
2023-08-03 | 10:58 | 49.822
2023-08-03 | 10:58 | 49.822
2023-08-03 | 10:59 | 49.824
2023-08-03 | 10:59 | 49.824
2023-08-03 | 10:59 | 49.823
2023-08-03 | 10:59 | 49.821
2023-08-03 | 10:59 | 49.824
2023-08-03 | 10:59 | 49.824
2023-08-03 | 10:59 | 49.825
2023-08-03 | 10:59 | 49.825
2023-08-03 | 10:59 | 49.824
2023-08-03 | 10:59 | 49.826
2023-08-03 | 10:59 | 49.826
2023-08-03 | 10:59 | 49.831
2023-08-03 | 10:59 | 49.837
2023-08-03 | 10:59 | 49.844
2023-08-03 | 10:59 | 49.853
2023-08-03 | 10:59 | 49.858
2023-08-03 | 10:59 | 49.862
2023-08-03 | 10:59 | 49.864
2023-08-03 | 10:59 | 49.863
2023-08-03 | 10:59 | 49.864
2023-08-03 | 10:59 | 49.863
2023-08-03 | 10:59 | 49.863
2023-08-03 | 10:59 | 49.87
2023-08-03 | 10:59 | 49.874
2023-08-03 | 10:59 | 49.875
2023-08-03 | 10:59 | 49.877
2023-08-03 | 10:59 | 49.877
2023-08-03 | 10:59 | 49.879
2023-08-03 | 10:59 | 49.88
2023-08-03 | 10:59 | 49.879
2023-08-03 | 10:59 | 49.877
2023-08-03 | 10:59 | 49.876
2023-08-03 | 10:59 | 49.876
2023-08-03 | 10:59 | 49.877
2023-08-03 | 10:59 | 49.878
2023-08-03 | 10:59 | 49.877
2023-08-03 | 10:59 | 49.879
2023-08-03 | 10:59 | 49.88
2023-08-03 | 10:59 | 49.88
2023-08-03 | 10:59 | 49.878
2023-08-03 | 10:59 | 49.875
2023-08-03 | 10:59 | 49.874
2023-08-03 | 10:59 | 49.874
2023-08-03 | 10:59 | 49.873
2023-08-03 | 10:59 | 49.874
2023-08-03 | 10:59 | 49.873
2023-08-03 | 10:59 | 49.873
2023-08-03 | 10:59 | 49.872
2023-08-03 | 10:59 | 49.873
2023-08-03 | 10:59 | 49.87
2023-08-03 | 10:59 | 49.868
2023-08-03 | 10:59 | 49.865
2023-08-03 | 10:59 | 49.862
2023-08-03 | 10:59 | 49.861
2023-08-03 | 10:59 | 49.863
2023-08-03 | 10:59 | 49.865
2023-08-03 | 10:59 | 49.868
2023-08-03 | 10:59 | 49.87
2023-08-03 | 10:59 | 49.871
2023-08-03 | 11:00 | 49.874
2023-08-03 | 11:00 | 49.875
2023-08-03 | 11:00 | 49.877
2023-08-03 | 11:00 | 49.879
2023-08-03 | 11:00 | 49.878
2023-08-03 | 11:00 | 49.878
2023-08-03 | 11:00 | 49.88
2023-08-03 | 11:00 | 49.881
2023-08-03 | 11:00 | 49.883
2023-08-03 | 11:00 | 49.885
2023-08-03 | 11:00 | 49.888
2023-08-03 | 11:00 | 49.894
2023-08-03 | 11:00 | 49.897
2023-08-03 | 11:00 | 49.9
2023-08-03 | 11:00 | 49.903
2023-08-03 | 11:00 | 49.903
2023-08-03 | 11:00 | 49.905
2023-08-03 | 11:00 | 49.906
2023-08-03 | 11:00 | 49.912
2023-08-03 | 11:00 | 49.915
2023-08-03 | 11:00 | 49.918
2023-08-03 | 11:00 | 49.921
2023-08-03 | 11:00 | 49.922
2023-08-03 | 11:00 | 49.921
2023-08-03 | 11:00 | 49.919
2023-08-03 | 11:00 | 49.917
2023-08-03 | 11:00 | 49.916
2023-08-03 | 11:00 | 49.918
2023-08-03 | 11:00 | 49.919
2023-08-03 | 11:00 | 49.915
2023-08-03 | 11:00 | 49.908
2023-08-03 | 11:00 | 49.891
2023-08-03 | 11:00 | 49.882
2023-08-03 | 11:00 | 49.879
2023-08-03 | 11:00 | 49.882
2023-08-03 | 11:00 | 49.885
2023-08-03 | 11:00 | 49.886
2023-08-03 | 11:00 | 49.889
2023-08-03 | 11:00 | 49.885
2023-08-03 | 11:00 | 49.881
2023-08-03 | 11:00 | 49.882
2023-08-03 | 11:00 | 49.878
2023-08-03 | 11:00 | 49.879
2023-08-03 | 11:00 | 49.88
2023-08-03 | 11:00 | 49.881
2023-08-03 | 11:00 | 49.881
2023-08-03 | 11:00 | 49.885
2023-08-03 | 11:00 | 49.887
2023-08-03 | 11:00 | 49.888
2023-08-03 | 11:00 | 49.889
2023-08-03 | 11:00 | 49.893
2023-08-03 | 11:00 | 49.893
2023-08-03 | 11:00 | 49.894
2023-08-03 | 11:00 | 49.894
2023-08-03 | 11:00 | 49.893
2023-08-03 | 11:00 | 49.891
2023-08-03 | 11:00 | 49.888
2023-08-03 | 11:00 | 49.885
2023-08-03 | 11:00 | 49.879
2023-08-03 | 11:00 | 49.875
2023-08-03 | 11:00 | 49.874
2023-08-03 | 11:01 | 49.872
2023-08-03 | 11:01 | 49.872
2023-08-03 | 11:01 | 49.872
2023-08-03 | 11:01 | 49.871
2023-08-03 | 11:01 | 49.87
2023-08-03 | 11:01 | 49.872
2023-08-03 | 11:01 | 49.872
2023-08-03 | 11:01 | 49.871
2023-08-03 | 11:01 | 49.868
2023-08-03 | 11:01 | 49.863
2023-08-03 | 11:01 | 49.859
2023-08-03 | 11:01 | 49.857
2023-08-03 | 11:01 | 49.856
2023-08-03 | 11:01 | 49.856
2023-08-03 | 11:01 | 49.858
2023-08-03 | 11:01 | 49.856
2023-08-03 | 11:01 | 49.858
2023-08-03 | 11:01 | 49.857
2023-08-03 | 11:01 | 49.856
2023-08-03 | 11:01 | 49.856
2023-08-03 | 11:01 | 49.857
2023-08-03 | 11:01 | 49.856
2023-08-03 | 11:01 | 49.858
2023-08-03 | 11:01 | 49.856
2023-08-03 | 11:01 | 49.852
2023-08-03 | 11:01 | 49.855
2023-08-03 | 11:01 | 49.856
2023-08-03 | 11:01 | 49.858
2023-08-03 | 11:01 | 49.863
2023-08-03 | 11:01 | 49.862
2023-08-03 | 11:01 | 49.858
2023-08-03 | 11:01 | 49.855
2023-08-03 | 11:01 | 49.848
2023-08-03 | 11:01 | 49.849
2023-08-03 | 11:01 | 49.852
2023-08-03 | 11:01 | 49.856
2023-08-03 | 11:01 | 49.86
2023-08-03 | 11:01 | 49.86
2023-08-03 | 11:01 | 49.86
2023-08-03 | 11:01 | 49.859
2023-08-03 | 11:01 | 49.859
2023-08-03 | 11:01 | 49.859
2023-08-03 | 11:01 | 49.86
2023-08-03 | 11:01 | 49.861
2023-08-03 | 11:01 | 49.867
2023-08-03 | 11:01 | 49.868
2023-08-03 | 11:01 | 49.87
2023-08-03 | 11:01 | 49.872
2023-08-03 | 11:01 | 49.871
2023-08-03 | 11:01 | 49.872
2023-08-03 | 11:01 | 49.877
2023-08-03 | 11:01 | 49.875
2023-08-03 | 11:01 | 49.874
2023-08-03 | 11:01 | 49.87
2023-08-03 | 11:01 | 49.868
2023-08-03 | 11:01 | 49.867
2023-08-03 | 11:01 | 49.867
2023-08-03 | 11:01 | 49.867
2023-08-03 | 11:01 | 49.866
2023-08-03 | 11:02 | 49.865
2023-08-03 | 11:02 | 49.868
2023-08-03 | 11:02 | 49.867
2023-08-03 | 11:02 | 49.866
2023-08-03 | 11:02 | 49.867
2023-08-03 | 11:02 | 49.868
2023-08-03 | 11:02 | 49.867
2023-08-03 | 11:02 | 49.868
2023-08-03 | 11:02 | 49.869
2023-08-03 | 11:02 | 49.87
2023-08-03 | 11:02 | 49.87
2023-08-03 | 11:02 | 49.871
2023-08-03 | 11:02 | 49.873
2023-08-03 | 11:02 | 49.873
2023-08-03 | 11:02 | 49.867
2023-08-03 | 11:02 | 49.865
2023-08-03 | 11:02 | 49.867
2023-08-03 | 11:02 | 49.869
2023-08-03 | 11:02 | 49.868
2023-08-03 | 11:02 | 49.867
2023-08-03 | 11:02 | 49.867
2023-08-03 | 11:02 | 49.866
2023-08-03 | 11:02 | 49.863
2023-08-03 | 11:02 | 49.862
2023-08-03 | 11:02 | 49.861
2023-08-03 | 11:02 | 49.861
2023-08-03 | 11:02 | 49.862
2023-08-03 | 11:02 | 49.862
2023-08-03 | 11:02 | 49.865
2023-08-03 | 11:02 | 49.865
2023-08-03 | 11:02 | 49.865
2023-08-03 | 11:02 | 49.864
2023-08-03 | 11:02 | 49.861
2023-08-03 | 11:02 | 49.86
2023-08-03 | 11:02 | 49.861
2023-08-03 | 11:02 | 49.862
2023-08-03 | 11:02 | 49.86
2023-08-03 | 11:02 | 49.857
2023-08-03 | 11:02 | 49.854
2023-08-03 | 11:02 | 49.852
2023-08-03 | 11:02 | 49.848
2023-08-03 | 11:02 | 49.842
2023-08-03 | 11:02 | 49.841
2023-08-03 | 11:02 | 49.841
2023-08-03 | 11:02 | 49.839
2023-08-03 | 11:02 | 49.842
2023-08-03 | 11:02 | 49.844
2023-08-03 | 11:02 | 49.845
2023-08-03 | 11:02 | 49.843
2023-08-03 | 11:02 | 49.841
2023-08-03 | 11:02 | 49.839
2023-08-03 | 11:02 | 49.836
2023-08-03 | 11:02 | 49.836
2023-08-03 | 11:02 | 49.836
2023-08-03 | 11:02 | 49.838
2023-08-03 | 11:02 | 49.838
2023-08-03 | 11:02 | 49.833
2023-08-03 | 11:02 | 49.828
2023-08-03 | 11:02 | 49.828
2023-08-03 | 11:02 | 49.826
2023-08-03 | 11:02 | 49.824
2023-08-03 | 11:03 | 49.826
2023-08-03 | 11:03 | 49.826
2023-08-03 | 11:03 | 49.825
2023-08-03 | 11:03 | 49.825
2023-08-03 | 11:03 | 49.826
2023-08-03 | 11:03 | 49.824
2023-08-03 | 11:03 | 49.822
2023-08-03 | 11:03 | 49.823
2023-08-03 | 11:03 | 49.823
2023-08-03 | 11:03 | 49.822
2023-08-03 | 11:03 | 49.82
2023-08-03 | 11:03 | 49.819
2023-08-03 | 11:03 | 49.817
2023-08-03 | 11:03 | 49.815
2023-08-03 | 11:03 | 49.816
2023-08-03 | 11:03 | 49.813
2023-08-03 | 11:03 | 49.811
2023-08-03 | 11:03 | 49.811
2023-08-03 | 11:03 | 49.812
2023-08-03 | 11:03 | 49.812
2023-08-03 | 11:03 | 49.814
2023-08-03 | 11:03 | 49.815
2023-08-03 | 11:03 | 49.816
2023-08-03 | 11:03 | 49.818
2023-08-03 | 11:03 | 49.818
2023-08-03 | 11:03 | 49.816
2023-08-03 | 11:03 | 49.816
2023-08-03 | 11:03 | 49.816
2023-08-03 | 11:03 | 49.816
2023-08-03 | 11:03 | 49.815
2023-08-03 | 11:03 | 49.81
2023-08-03 | 11:03 | 49.808
2023-08-03 | 11:03 | 49.807
2023-08-03 | 11:03 | 49.811
2023-08-03 | 11:03 | 49.809
2023-08-03 | 11:03 | 49.808
2023-08-03 | 11:03 | 49.811
2023-08-03 | 11:03 | 49.811
2023-08-03 | 11:03 | 49.812
2023-08-03 | 11:03 | 49.806
2023-08-03 | 11:03 | 49.808
2023-08-03 | 11:03 | 49.811
2023-08-03 | 11:03 | 49.813
2023-08-03 | 11:03 | 49.816
2023-08-03 | 11:03 | 49.816
2023-08-03 | 11:03 | 49.811
2023-08-03 | 11:03 | 49.807
2023-08-03 | 11:03 | 49.806
2023-08-03 | 11:03 | 49.807
2023-08-03 | 11:03 | 49.806
2023-08-03 | 11:03 | 49.805
2023-08-03 | 11:03 | 49.804
2023-08-03 | 11:03 | 49.807
2023-08-03 | 11:03 | 49.812
2023-08-03 | 11:03 | 49.815
2023-08-03 | 11:03 | 49.817
2023-08-03 | 11:03 | 49.819
2023-08-03 | 11:03 | 49.822
2023-08-03 | 11:03 | 49.822
2023-08-03 | 11:04 | 49.825
2023-08-03 | 11:04 | 49.825
2023-08-03 | 11:04 | 49.825
2023-08-03 | 11:04 | 49.824
2023-08-03 | 11:04 | 49.822
2023-08-03 | 11:04 | 49.824
2023-08-03 | 11:04 | 49.827
2023-08-03 | 11:04 | 49.83
2023-08-03 | 11:04 | 49.831
2023-08-03 | 11:04 | 49.831
2023-08-03 | 11:04 | 49.831
2023-08-03 | 11:04 | 49.83
2023-08-03 | 11:04 | 49.831
2023-08-03 | 11:04 | 49.829
2023-08-03 | 11:04 | 49.826
2023-08-03 | 11:04 | 49.826
2023-08-03 | 11:04 | 49.826
2023-08-03 | 11:04 | 49.826
2023-08-03 | 11:04 | 49.824
2023-08-03 | 11:04 | 49.823
2023-08-03 | 11:04 | 49.824
2023-08-03 | 11:04 | 49.826
2023-08-03 | 11:04 | 49.829
2023-08-03 | 11:04 | 49.832
2023-08-03 | 11:04 | 49.833
2023-08-03 | 11:04 | 49.835
2023-08-03 | 11:04 | 49.838
2023-08-03 | 11:04 | 49.837
2023-08-03 | 11:04 | 49.833
2023-08-03 | 11:04 | 49.828
2023-08-03 | 11:04 | 49.826
2023-08-03 | 11:04 | 49.825
2023-08-03 | 11:04 | 49.826
2023-08-03 | 11:04 | 49.827
2023-08-03 | 11:04 | 49.832
2023-08-03 | 11:04 | 49.833
2023-08-03 | 11:04 | 49.839
2023-08-03 | 11:04 | 49.843
2023-08-03 | 11:04 | 49.847
2023-08-03 | 11:04 | 49.849
2023-08-03 | 11:04 | 49.85
2023-08-03 | 11:04 | 49.85
2023-08-03 | 11:04 | 49.849
2023-08-03 | 11:04 | 49.848
2023-08-03 | 11:04 | 49.847
2023-08-03 | 11:04 | 49.851
2023-08-03 | 11:04 | 49.853
2023-08-03 | 11:04 | 49.853
2023-08-03 | 11:04 | 49.854
2023-08-03 | 11:04 | 49.85
2023-08-03 | 11:04 | 49.849
2023-08-03 | 11:04 | 49.844
2023-08-03 | 11:04 | 49.847
2023-08-03 | 11:04 | 49.85
2023-08-03 | 11:04 | 49.853
2023-08-03 | 11:04 | 49.856
2023-08-03 | 11:04 | 49.858
2023-08-03 | 11:04 | 49.86
2023-08-03 | 11:04 | 49.86
2023-08-03 | 11:04 | 49.861
2023-08-03 | 11:04 | 49.859
2023-08-03 | 11:05 | 49.863
2023-08-03 | 11:05 | 49.866
2023-08-03 | 11:05 | 49.87
2023-08-03 | 11:05 | 49.874
2023-08-03 | 11:05 | 49.877
2023-08-03 | 11:05 | 49.88
2023-08-03 | 11:05 | 49.881
2023-08-03 | 11:05 | 49.882
2023-08-03 | 11:05 | 49.88
2023-08-03 | 11:05 | 49.878
2023-08-03 | 11:05 | 49.874
2023-08-03 | 11:05 | 49.874
2023-08-03 | 11:05 | 49.87
2023-08-03 | 11:05 | 49.868
2023-08-03 | 11:05 | 49.863
2023-08-03 | 11:05 | 49.86
2023-08-03 | 11:05 | 49.858
2023-08-03 | 11:05 | 49.856
2023-08-03 | 11:05 | 49.855
2023-08-03 | 11:05 | 49.852
2023-08-03 | 11:05 | 49.853
2023-08-03 | 11:05 | 49.853
2023-08-03 | 11:05 | 49.854
2023-08-03 | 11:05 | 49.854
2023-08-03 | 11:05 | 49.857
2023-08-03 | 11:05 | 49.857
2023-08-03 | 11:05 | 49.858
2023-08-03 | 11:05 | 49.859
2023-08-03 | 11:05 | 49.862
2023-08-03 | 11:05 | 49.865
2023-08-03 | 11:05 | 49.86
2023-08-03 | 11:05 | 49.86
2023-08-03 | 11:05 | 49.859
2023-08-03 | 11:05 | 49.858
2023-08-03 | 11:05 | 49.858
2023-08-03 | 11:05 | 49.86
2023-08-03 | 11:05 | 49.858
2023-08-03 | 11:05 | 49.858
2023-08-03 | 11:05 | 49.858
2023-08-03 | 11:05 | 49.857
2023-08-03 | 11:05 | 49.858
2023-08-03 | 11:05 | 49.859
2023-08-03 | 11:05 | 49.855
2023-08-03 | 11:05 | 49.856
2023-08-03 | 11:05 | 49.858
2023-08-03 | 11:05 | 49.856
2023-08-03 | 11:05 | 49.857
2023-08-03 | 11:05 | 49.856
2023-08-03 | 11:05 | 49.851
2023-08-03 | 11:05 | 49.843
2023-08-03 | 11:05 | 49.838
2023-08-03 | 11:05 | 49.837
2023-08-03 | 11:05 | 49.838
2023-08-03 | 11:05 | 49.839
2023-08-03 | 11:05 | 49.841
2023-08-03 | 11:05 | 49.843
2023-08-03 | 11:05 | 49.849
2023-08-03 | 11:05 | 49.85
2023-08-03 | 11:05 | 49.856
2023-08-03 | 11:06 | 49.859
2023-08-03 | 11:06 | 49.861
2023-08-03 | 11:06 | 49.861
2023-08-03 | 11:06 | 49.862
2023-08-03 | 11:06 | 49.861
2023-08-03 | 11:06 | 49.857
2023-08-03 | 11:06 | 49.851
2023-08-03 | 11:06 | 49.851
2023-08-03 | 11:06 | 49.846
2023-08-03 | 11:06 | 49.843
2023-08-03 | 11:06 | 49.84
2023-08-03 | 11:06 | 49.841
2023-08-03 | 11:06 | 49.842
2023-08-03 | 11:06 | 49.842
2023-08-03 | 11:06 | 49.841
2023-08-03 | 11:06 | 49.842
2023-08-03 | 11:06 | 49.839
2023-08-03 | 11:06 | 49.836
2023-08-03 | 11:06 | 49.833
2023-08-03 | 11:06 | 49.831
2023-08-03 | 11:06 | 49.83
2023-08-03 | 11:06 | 49.83
2023-08-03 | 11:06 | 49.834
2023-08-03 | 11:06 | 49.838
2023-08-03 | 11:06 | 49.837
2023-08-03 | 11:06 | 49.837
2023-08-03 | 11:06 | 49.84
2023-08-03 | 11:06 | 49.841
2023-08-03 | 11:06 | 49.844
2023-08-03 | 11:06 | 49.845
2023-08-03 | 11:06 | 49.85
2023-08-03 | 11:06 | 49.849
2023-08-03 | 11:06 | 49.852
2023-08-03 | 11:06 | 49.853
2023-08-03 | 11:06 | 49.853
2023-08-03 | 11:06 | 49.856
2023-08-03 | 11:06 | 49.856
2023-08-03 | 11:06 | 49.856
2023-08-03 | 11:06 | 49.854
2023-08-03 | 11:06 | 49.848
2023-08-03 | 11:06 | 49.847
2023-08-03 | 11:06 | 49.845
2023-08-03 | 11:06 | 49.844
2023-08-03 | 11:06 | 49.843
2023-08-03 | 11:06 | 49.84
2023-08-03 | 11:06 | 49.839
2023-08-03 | 11:06 | 49.835
2023-08-03 | 11:06 | 49.833
2023-08-03 | 11:06 | 49.831
2023-08-03 | 11:06 | 49.831
2023-08-03 | 11:06 | 49.83
2023-08-03 | 11:06 | 49.831
2023-08-03 | 11:06 | 49.83
2023-08-03 | 11:06 | 49.832
2023-08-03 | 11:06 | 49.835
2023-08-03 | 11:06 | 49.839
2023-08-03 | 11:06 | 49.841
2023-08-03 | 11:06 | 49.842
2023-08-03 | 11:06 | 49.845
2023-08-03 | 11:06 | 49.846
2023-08-03 | 11:06 | 49.844
2023-08-03 | 11:07 | 49.841
2023-08-03 | 11:07 | 49.844
2023-08-03 | 11:07 | 49.843
2023-08-03 | 11:07 | 49.846
2023-08-03 | 11:07 | 49.847
2023-08-03 | 11:07 | 49.849
2023-08-03 | 11:07 | 49.848
2023-08-03 | 11:07 | 49.848
2023-08-03 | 11:07 | 49.845
2023-08-03 | 11:07 | 49.843
2023-08-03 | 11:07 | 49.845
2023-08-03 | 11:07 | 49.846
2023-08-03 | 11:07 | 49.845
2023-08-03 | 11:07 | 49.84
2023-08-03 | 11:07 | 49.835
2023-08-03 | 11:07 | 49.834
2023-08-03 | 11:07 | 49.836
2023-08-03 | 11:07 | 49.832
2023-08-03 | 11:07 | 49.828
2023-08-03 | 11:07 | 49.829
2023-08-03 | 11:07 | 49.833
2023-08-03 | 11:07 | 49.836
2023-08-03 | 11:07 | 49.838
2023-08-03 | 11:07 | 49.838
2023-08-03 | 11:07 | 49.839
2023-08-03 | 11:07 | 49.84
2023-08-03 | 11:07 | 49.844
2023-08-03 | 11:07 | 49.848
2023-08-03 | 11:07 | 49.849
2023-08-03 | 11:07 | 49.85
2023-08-03 | 11:07 | 49.851
2023-08-03 | 11:07 | 49.856
2023-08-03 | 11:07 | 49.854
2023-08-03 | 11:07 | 49.856
2023-08-03 | 11:07 | 49.855
2023-08-03 | 11:07 | 49.857
2023-08-03 | 11:07 | 49.86
2023-08-03 | 11:07 | 49.862
2023-08-03 | 11:07 | 49.861
2023-08-03 | 11:07 | 49.86
2023-08-03 | 11:07 | 49.859
2023-08-03 | 11:07 | 49.861
2023-08-03 | 11:07 | 49.867
2023-08-03 | 11:07 | 49.871
2023-08-03 | 11:07 | 49.871
2023-08-03 | 11:07 | 49.87
2023-08-03 | 11:07 | 49.871
2023-08-03 | 11:07 | 49.873
2023-08-03 | 11:07 | 49.872
2023-08-03 | 11:07 | 49.872
2023-08-03 | 11:07 | 49.875
2023-08-03 | 11:07 | 49.877
2023-08-03 | 11:07 | 49.881
2023-08-03 | 11:07 | 49.881
2023-08-03 | 11:07 | 49.88
2023-08-03 | 11:07 | 49.882
2023-08-03 | 11:07 | 49.884
2023-08-03 | 11:07 | 49.89
2023-08-03 | 11:07 | 49.894
2023-08-03 | 11:08 | 49.894
2023-08-03 | 11:08 | 49.896
2023-08-03 | 11:08 | 49.895
2023-08-03 | 11:08 | 49.893
2023-08-03 | 11:08 | 49.89
2023-08-03 | 11:08 | 49.892
2023-08-03 | 11:08 | 49.893
2023-08-03 | 11:08 | 49.893
2023-08-03 | 11:08 | 49.897
2023-08-03 | 11:08 | 49.896
2023-08-03 | 11:08 | 49.895
2023-08-03 | 11:08 | 49.895
2023-08-03 | 11:08 | 49.892
2023-08-03 | 11:08 | 49.894
2023-08-03 | 11:08 | 49.895
2023-08-03 | 11:08 | 49.895
2023-08-03 | 11:08 | 49.9
2023-08-03 | 11:08 | 49.898
2023-08-03 | 11:08 | 49.898
2023-08-03 | 11:08 | 49.899
2023-08-03 | 11:08 | 49.903
2023-08-03 | 11:08 | 49.906
2023-08-03 | 11:08 | 49.906
2023-08-03 | 11:08 | 49.904
2023-08-03 | 11:08 | 49.902
2023-08-03 | 11:08 | 49.899
2023-08-03 | 11:08 | 49.892
2023-08-03 | 11:08 | 49.887
2023-08-03 | 11:08 | 49.881
2023-08-03 | 11:08 | 49.878
2023-08-03 | 11:08 | 49.878
2023-08-03 | 11:08 | 49.875
2023-08-03 | 11:08 | 49.877
2023-08-03 | 11:08 | 49.879
2023-08-03 | 11:08 | 49.883
2023-08-03 | 11:08 | 49.885
2023-08-03 | 11:08 | 49.883
2023-08-03 | 11:08 | 49.882
2023-08-03 | 11:08 | 49.882
2023-08-03 | 11:08 | 49.883
2023-08-03 | 11:08 | 49.883
2023-08-03 | 11:08 | 49.886
2023-08-03 | 11:08 | 49.89
2023-08-03 | 11:08 | 49.888
2023-08-03 | 11:08 | 49.888
2023-08-03 | 11:08 | 49.891
2023-08-03 | 11:08 | 49.893
2023-08-03 | 11:08 | 49.893
2023-08-03 | 11:08 | 49.891
2023-08-03 | 11:08 | 49.893
2023-08-03 | 11:08 | 49.891
2023-08-03 | 11:08 | 49.887
2023-08-03 | 11:08 | 49.882
2023-08-03 | 11:08 | 49.879
2023-08-03 | 11:08 | 49.881
2023-08-03 | 11:08 | 49.879
2023-08-03 | 11:08 | 49.881
2023-08-03 | 11:08 | 49.878
2023-08-03 | 11:08 | 49.879
2023-08-03 | 11:08 | 49.879
2023-08-03 | 11:08 | 49.879
2023-08-03 | 11:09 | 49.877
2023-08-03 | 11:09 | 49.875
2023-08-03 | 11:09 | 49.874
2023-08-03 | 11:09 | 49.872
2023-08-03 | 11:09 | 49.869
2023-08-03 | 11:09 | 49.867
2023-08-03 | 11:09 | 49.865
2023-08-03 | 11:09 | 49.87
2023-08-03 | 11:09 | 49.87
2023-08-03 | 11:09 | 49.871
2023-08-03 | 11:09 | 49.872
2023-08-03 | 11:09 | 49.871
2023-08-03 | 11:09 | 49.875
2023-08-03 | 11:09 | 49.876
2023-08-03 | 11:09 | 49.88
2023-08-03 | 11:09 | 49.882
2023-08-03 | 11:09 | 49.882
2023-08-03 | 11:09 | 49.883
2023-08-03 | 11:09 | 49.879
2023-08-03 | 11:09 | 49.878
2023-08-03 | 11:09 | 49.879
2023-08-03 | 11:09 | 49.879
2023-08-03 | 11:09 | 49.879
2023-08-03 | 11:09 | 49.879
2023-08-03 | 11:09 | 49.876
2023-08-03 | 11:09 | 49.874
2023-08-03 | 11:09 | 49.871
2023-08-03 | 11:09 | 49.873
2023-08-03 | 11:09 | 49.877
2023-08-03 | 11:09 | 49.878
2023-08-03 | 11:09 | 49.878
2023-08-03 | 11:09 | 49.879
2023-08-03 | 11:09 | 49.881
2023-08-03 | 11:09 | 49.882
2023-08-03 | 11:09 | 49.884
2023-08-03 | 11:09 | 49.884
2023-08-03 | 11:09 | 49.881
2023-08-03 | 11:09 | 49.879
2023-08-03 | 11:09 | 49.881
2023-08-03 | 11:09 | 49.886
2023-08-03 | 11:09 | 49.886
2023-08-03 | 11:09 | 49.887
2023-08-03 | 11:09 | 49.885
2023-08-03 | 11:09 | 49.883
2023-08-03 | 11:09 | 49.883
2023-08-03 | 11:09 | 49.887
2023-08-03 | 11:09 | 49.89
2023-08-03 | 11:09 | 49.892
2023-08-03 | 11:09 | 49.892
2023-08-03 | 11:09 | 49.894
2023-08-03 | 11:09 | 49.895
2023-08-03 | 11:09 | 49.9
2023-08-03 | 11:09 | 49.903
2023-08-03 | 11:09 | 49.902
2023-08-03 | 11:09 | 49.899
2023-08-03 | 11:09 | 49.902
2023-08-03 | 11:09 | 49.903
2023-08-03 | 11:09 | 49.9
2023-08-03 | 11:09 | 49.9
2023-08-03 | 11:10 | 49.901
2023-08-03 | 11:10 | 49.9
2023-08-03 | 11:10 | 49.902
2023-08-03 | 11:10 | 49.903
2023-08-03 | 11:10 | 49.902
2023-08-03 | 11:10 | 49.904
2023-08-03 | 11:10 | 49.905
2023-08-03 | 11:10 | 49.902
2023-08-03 | 11:10 | 49.899
2023-08-03 | 11:10 | 49.893
2023-08-03 | 11:10 | 49.891
2023-08-03 | 11:10 | 49.889
2023-08-03 | 11:10 | 49.89
2023-08-03 | 11:10 | 49.89
2023-08-03 | 11:10 | 49.889
2023-08-03 | 11:10 | 49.887
2023-08-03 | 11:10 | 49.887
2023-08-03 | 11:10 | 49.886
2023-08-03 | 11:10 | 49.884
2023-08-03 | 11:10 | 49.882
2023-08-03 | 11:10 | 49.884
2023-08-03 | 11:10 | 49.886
2023-08-03 | 11:10 | 49.889
2023-08-03 | 11:10 | 49.891
2023-08-03 | 11:10 | 49.893
2023-08-03 | 11:10 | 49.894
2023-08-03 | 11:10 | 49.895
2023-08-03 | 11:10 | 49.89
2023-08-03 | 11:10 | 49.888
2023-08-03 | 11:10 | 49.886
2023-08-03 | 11:10 | 49.883
2023-08-03 | 11:10 | 49.878
2023-08-03 | 11:10 | 49.878
2023-08-03 | 11:10 | 49.881
2023-08-03 | 11:10 | 49.882
2023-08-03 | 11:10 | 49.882
2023-08-03 | 11:10 | 49.882
2023-08-03 | 11:10 | 49.881
2023-08-03 | 11:10 | 49.88
2023-08-03 | 11:10 | 49.875
2023-08-03 | 11:10 | 49.875
2023-08-03 | 11:10 | 49.876
2023-08-03 | 11:10 | 49.878
2023-08-03 | 11:10 | 49.878
2023-08-03 | 11:10 | 49.88
2023-08-03 | 11:10 | 49.882
2023-08-03 | 11:10 | 49.883
2023-08-03 | 11:10 | 49.884
2023-08-03 | 11:10 | 49.885
2023-08-03 | 11:10 | 49.886
2023-08-03 | 11:10 | 49.885
2023-08-03 | 11:10 | 49.884
2023-08-03 | 11:10 | 49.884
2023-08-03 | 11:10 | 49.885
2023-08-03 | 11:10 | 49.882
2023-08-03 | 11:10 | 49.88
2023-08-03 | 11:10 | 49.879
2023-08-03 | 11:10 | 49.874
2023-08-03 | 11:10 | 49.875
2023-08-03 | 11:10 | 49.877
2023-08-03 | 11:10 | 49.878
2023-08-03 | 11:11 | 49.878
2023-08-03 | 11:11 | 49.877
2023-08-03 | 11:11 | 49.878
2023-08-03 | 11:11 | 49.882
2023-08-03 | 11:11 | 49.882
2023-08-03 | 11:11 | 49.881
2023-08-03 | 11:11 | 49.881
2023-08-03 | 11:11 | 49.879
2023-08-03 | 11:11 | 49.878
2023-08-03 | 11:11 | 49.876
2023-08-03 | 11:11 | 49.879
2023-08-03 | 11:11 | 49.882
2023-08-03 | 11:11 | 49.886
2023-08-03 | 11:11 | 49.888
2023-08-03 | 11:11 | 49.89
2023-08-03 | 11:11 | 49.894
2023-08-03 | 11:11 | 49.894
2023-08-03 | 11:11 | 49.896
2023-08-03 | 11:11 | 49.898
2023-08-03 | 11:11 | 49.901
2023-08-03 | 11:11 | 49.902
2023-08-03 | 11:11 | 49.903
2023-08-03 | 11:11 | 49.903
2023-08-03 | 11:11 | 49.907
2023-08-03 | 11:11 | 49.909
2023-08-03 | 11:11 | 49.911
2023-08-03 | 11:11 | 49.914
2023-08-03 | 11:11 | 49.912
2023-08-03 | 11:11 | 49.912
2023-08-03 | 11:11 | 49.915
2023-08-03 | 11:11 | 49.916
2023-08-03 | 11:11 | 49.916
2023-08-03 | 11:11 | 49.917
2023-08-03 | 11:11 | 49.919
2023-08-03 | 11:11 | 49.921
2023-08-03 | 11:11 | 49.927
2023-08-03 | 11:11 | 49.927
2023-08-03 | 11:11 | 49.93
2023-08-03 | 11:11 | 49.932
2023-08-03 | 11:11 | 49.934
2023-08-03 | 11:11 | 49.933
2023-08-03 | 11:11 | 49.936
2023-08-03 | 11:11 | 49.939
2023-08-03 | 11:11 | 49.946
2023-08-03 | 11:11 | 49.948
2023-08-03 | 11:11 | 49.945
2023-08-03 | 11:11 | 49.941
2023-08-03 | 11:11 | 49.938
2023-08-03 | 11:11 | 49.937
2023-08-03 | 11:11 | 49.934
2023-08-03 | 11:11 | 49.926
2023-08-03 | 11:11 | 49.917
2023-08-03 | 11:11 | 49.914
2023-08-03 | 11:11 | 49.913
2023-08-03 | 11:11 | 49.91
2023-08-03 | 11:11 | 49.906
2023-08-03 | 11:11 | 49.901
2023-08-03 | 11:11 | 49.897
2023-08-03 | 11:11 | 49.893
2023-08-03 | 11:12 | 49.89
2023-08-03 | 11:12 | 49.884
2023-08-03 | 11:12 | 49.88
2023-08-03 | 11:12 | 49.878
2023-08-03 | 11:12 | 49.878
2023-08-03 | 11:12 | 49.878
2023-08-03 | 11:12 | 49.88
2023-08-03 | 11:12 | 49.884
2023-08-03 | 11:12 | 49.888
2023-08-03 | 11:12 | 49.891
2023-08-03 | 11:12 | 49.893
2023-08-03 | 11:12 | 49.896
2023-08-03 | 11:12 | 49.897
2023-08-03 | 11:12 | 49.9
2023-08-03 | 11:12 | 49.899
2023-08-03 | 11:12 | 49.902
2023-08-03 | 11:12 | 49.899
2023-08-03 | 11:12 | 49.9
2023-08-03 | 11:12 | 49.902
2023-08-03 | 11:12 | 49.901
2023-08-03 | 11:12 | 49.906
2023-08-03 | 11:12 | 49.911
2023-08-03 | 11:12 | 49.919
2023-08-03 | 11:12 | 49.92
2023-08-03 | 11:12 | 49.921
2023-08-03 | 11:12 | 49.92
2023-08-03 | 11:12 | 49.921
2023-08-03 | 11:12 | 49.919
2023-08-03 | 11:12 | 49.919
2023-08-03 | 11:12 | 49.921
2023-08-03 | 11:12 | 49.918
2023-08-03 | 11:12 | 49.916
2023-08-03 | 11:12 | 49.915
2023-08-03 | 11:12 | 49.917
2023-08-03 | 11:12 | 49.919
2023-08-03 | 11:12 | 49.926
2023-08-03 | 11:12 | 49.93
2023-08-03 | 11:12 | 49.935
2023-08-03 | 11:12 | 49.931
2023-08-03 | 11:12 | 49.931
2023-08-03 | 11:12 | 49.93
2023-08-03 | 11:12 | 49.93
2023-08-03 | 11:12 | 49.929
2023-08-03 | 11:12 | 49.934
2023-08-03 | 11:12 | 49.936
2023-08-03 | 11:12 | 49.935
2023-08-03 | 11:12 | 49.932
2023-08-03 | 11:12 | 49.93
2023-08-03 | 11:12 | 49.931
2023-08-03 | 11:12 | 49.936
2023-08-03 | 11:12 | 49.942
2023-08-03 | 11:12 | 49.946
2023-08-03 | 11:12 | 49.95
2023-08-03 | 11:12 | 49.949
2023-08-03 | 11:12 | 49.948
2023-08-03 | 11:12 | 49.95
2023-08-03 | 11:12 | 49.951
2023-08-03 | 11:12 | 49.952
2023-08-03 | 11:12 | 49.952
2023-08-03 | 11:12 | 49.954
2023-08-03 | 11:12 | 49.954
2023-08-03 | 11:13 | 49.957
2023-08-03 | 11:13 | 49.962
2023-08-03 | 11:13 | 49.967
2023-08-03 | 11:13 | 49.973
2023-08-03 | 11:13 | 49.976
2023-08-03 | 11:13 | 49.977
2023-08-03 | 11:13 | 49.98
2023-08-03 | 11:13 | 49.98
2023-08-03 | 11:13 | 49.979
2023-08-03 | 11:13 | 49.978
2023-08-03 | 11:13 | 49.975
2023-08-03 | 11:13 | 49.971
2023-08-03 | 11:13 | 49.967
2023-08-03 | 11:13 | 49.966
2023-08-03 | 11:13 | 49.963
2023-08-03 | 11:13 | 49.964
2023-08-03 | 11:13 | 49.966
2023-08-03 | 11:13 | 49.971
2023-08-03 | 11:13 | 49.976
2023-08-03 | 11:13 | 49.976
2023-08-03 | 11:13 | 49.979
2023-08-03 | 11:13 | 49.978
2023-08-03 | 11:13 | 49.979
2023-08-03 | 11:13 | 49.977
2023-08-03 | 11:13 | 49.977
2023-08-03 | 11:13 | 49.975
2023-08-03 | 11:13 | 49.968
2023-08-03 | 11:13 | 49.965
2023-08-03 | 11:13 | 49.964
2023-08-03 | 11:13 | 49.961
2023-08-03 | 11:13 | 49.957
2023-08-03 | 11:13 | 49.954
2023-08-03 | 11:13 | 49.952
2023-08-03 | 11:13 | 49.95
2023-08-03 | 11:13 | 49.95
2023-08-03 | 11:13 | 49.949
2023-08-03 | 11:13 | 49.949
2023-08-03 | 11:13 | 49.949
2023-08-03 | 11:13 | 49.948
2023-08-03 | 11:13 | 49.947
2023-08-03 | 11:13 | 49.948
2023-08-03 | 11:13 | 49.947
2023-08-03 | 11:13 | 49.948
2023-08-03 | 11:13 | 49.951
2023-08-03 | 11:13 | 49.957
2023-08-03 | 11:13 | 49.961
2023-08-03 | 11:13 | 49.964
2023-08-03 | 11:13 | 49.965
2023-08-03 | 11:13 | 49.965
2023-08-03 | 11:13 | 49.961
2023-08-03 | 11:13 | 49.956
2023-08-03 | 11:13 | 49.953
2023-08-03 | 11:13 | 49.954
2023-08-03 | 11:13 | 49.956
2023-08-03 | 11:13 | 49.961
2023-08-03 | 11:13 | 49.969
2023-08-03 | 11:13 | 49.975
2023-08-03 | 11:13 | 49.976
2023-08-03 | 11:13 | 49.979
2023-08-03 | 11:14 | 49.98
2023-08-03 | 11:14 | 49.977
2023-08-03 | 11:14 | 49.975
2023-08-03 | 11:14 | 49.971
2023-08-03 | 11:14 | 49.969
2023-08-03 | 11:14 | 49.966
2023-08-03 | 11:14 | 49.964
2023-08-03 | 11:14 | 49.962
2023-08-03 | 11:14 | 49.969
2023-08-03 | 11:14 | 49.974
2023-08-03 | 11:14 | 49.984
2023-08-03 | 11:14 | 49.986
2023-08-03 | 11:14 | 49.987
2023-08-03 | 11:14 | 49.987
2023-08-03 | 11:14 | 49.983
2023-08-03 | 11:14 | 49.984
2023-08-03 | 11:14 | 49.982
2023-08-03 | 11:14 | 49.979
2023-08-03 | 11:14 | 49.975
2023-08-03 | 11:14 | 49.977
2023-08-03 | 11:14 | 49.976
2023-08-03 | 11:14 | 49.976
2023-08-03 | 11:14 | 49.972
2023-08-03 | 11:14 | 49.968
2023-08-03 | 11:14 | 49.966
2023-08-03 | 11:14 | 49.964
2023-08-03 | 11:14 | 49.959
2023-08-03 | 11:14 | 49.956
2023-08-03 | 11:14 | 49.956
2023-08-03 | 11:14 | 49.958
2023-08-03 | 11:14 | 49.959
2023-08-03 | 11:14 | 49.956
2023-08-03 | 11:14 | 49.957
2023-08-03 | 11:14 | 49.959
2023-08-03 | 11:14 | 49.959
2023-08-03 | 11:14 | 49.958
2023-08-03 | 11:14 | 49.956
2023-08-03 | 11:14 | 49.955
2023-08-03 | 11:14 | 49.952
2023-08-03 | 11:14 | 49.953
2023-08-03 | 11:14 | 49.949
2023-08-03 | 11:14 | 49.949
2023-08-03 | 11:14 | 49.95
2023-08-03 | 11:14 | 49.948
2023-08-03 | 11:14 | 49.947
2023-08-03 | 11:14 | 49.946
2023-08-03 | 11:14 | 49.946
2023-08-03 | 11:14 | 49.945
2023-08-03 | 11:14 | 49.947
2023-08-03 | 11:14 | 49.948
2023-08-03 | 11:14 | 49.947
2023-08-03 | 11:14 | 49.947
2023-08-03 | 11:14 | 49.945
2023-08-03 | 11:14 | 49.942
2023-08-03 | 11:14 | 49.938
2023-08-03 | 11:14 | 49.936
2023-08-03 | 11:14 | 49.935
2023-08-03 | 11:14 | 49.935
2023-08-03 | 11:14 | 49.931
2023-08-03 | 11:14 | 49.928
2023-08-03 | 11:14 | 49.929
2023-08-03 | 11:15 | 49.929
2023-08-03 | 11:15 | 49.932
2023-08-03 | 11:15 | 49.935
2023-08-03 | 11:15 | 49.935
2023-08-03 | 11:15 | 49.935
2023-08-03 | 11:15 | 49.932
2023-08-03 | 11:15 | 49.931
2023-08-03 | 11:15 | 49.933
2023-08-03 | 11:15 | 49.933
2023-08-03 | 11:15 | 49.934
2023-08-03 | 11:15 | 49.933
2023-08-03 | 11:15 | 49.934
2023-08-03 | 11:15 | 49.932
2023-08-03 | 11:15 | 49.932
2023-08-03 | 11:15 | 49.934
2023-08-03 | 11:15 | 49.937
2023-08-03 | 11:15 | 49.941
2023-08-03 | 11:15 | 49.941
2023-08-03 | 11:15 | 49.945
2023-08-03 | 11:15 | 49.946
2023-08-03 | 11:15 | 49.946
2023-08-03 | 11:15 | 49.947
2023-08-03 | 11:15 | 49.948
2023-08-03 | 11:15 | 49.951
2023-08-03 | 11:15 | 49.953
2023-08-03 | 11:15 | 49.956
2023-08-03 | 11:15 | 49.956
2023-08-03 | 11:15 | 49.955
2023-08-03 | 11:15 | 49.954
2023-08-03 | 11:15 | 49.953
2023-08-03 | 11:15 | 49.948
2023-08-03 | 11:15 | 49.944
2023-08-03 | 11:15 | 49.938
2023-08-03 | 11:15 | 49.936
2023-08-03 | 11:15 | 49.94
2023-08-03 | 11:15 | 49.942
2023-08-03 | 11:15 | 49.941
2023-08-03 | 11:15 | 49.939
2023-08-03 | 11:15 | 49.941
2023-08-03 | 11:15 | 49.938
2023-08-03 | 11:15 | 49.936
2023-08-03 | 11:15 | 49.933
2023-08-03 | 11:15 | 49.933
2023-08-03 | 11:15 | 49.935
2023-08-03 | 11:15 | 49.94
2023-08-03 | 11:15 | 49.945
2023-08-03 | 11:15 | 49.95
2023-08-03 | 11:15 | 49.949
2023-08-03 | 11:15 | 49.948
2023-08-03 | 11:15 | 49.943
2023-08-03 | 11:15 | 49.941
2023-08-03 | 11:15 | 49.942
2023-08-03 | 11:15 | 49.939
2023-08-03 | 11:15 | 49.937
2023-08-03 | 11:15 | 49.934
2023-08-03 | 11:15 | 49.937
2023-08-03 | 11:15 | 49.94
2023-08-03 | 11:15 | 49.942
2023-08-03 | 11:15 | 49.944
2023-08-03 | 11:16 | 49.944
2023-08-03 | 11:16 | 49.945
2023-08-03 | 11:16 | 49.945
2023-08-03 | 11:16 | 49.949
2023-08-03 | 11:16 | 49.951
2023-08-03 | 11:16 | 49.952
2023-08-03 | 11:16 | 49.959
2023-08-03 | 11:16 | 49.964
2023-08-03 | 11:16 | 49.969
2023-08-03 | 11:16 | 49.973
2023-08-03 | 11:16 | 49.974
2023-08-03 | 11:16 | 49.976
2023-08-03 | 11:16 | 49.975
2023-08-03 | 11:16 | 49.977
2023-08-03 | 11:16 | 49.979
2023-08-03 | 11:16 | 49.979
2023-08-03 | 11:16 | 49.983
2023-08-03 | 11:16 | 49.986
2023-08-03 | 11:16 | 49.984
2023-08-03 | 11:16 | 49.985
2023-08-03 | 11:16 | 49.987
2023-08-03 | 11:16 | 49.988
2023-08-03 | 11:16 | 49.985
2023-08-03 | 11:16 | 49.982
2023-08-03 | 11:16 | 49.978
2023-08-03 | 11:16 | 49.977
2023-08-03 | 11:16 | 49.971
2023-08-03 | 11:16 | 49.966
2023-08-03 | 11:16 | 49.964
2023-08-03 | 11:16 | 49.963
2023-08-03 | 11:16 | 49.961
2023-08-03 | 11:16 | 49.96
2023-08-03 | 11:16 | 49.96
2023-08-03 | 11:16 | 49.96
2023-08-03 | 11:16 | 49.96
2023-08-03 | 11:16 | 49.961
2023-08-03 | 11:16 | 49.963
2023-08-03 | 11:16 | 49.963
2023-08-03 | 11:16 | 49.962
2023-08-03 | 11:16 | 49.966
2023-08-03 | 11:16 | 49.972
2023-08-03 | 11:16 | 49.976
2023-08-03 | 11:16 | 49.977
2023-08-03 | 11:16 | 49.976
2023-08-03 | 11:16 | 49.972
2023-08-03 | 11:16 | 49.966
2023-08-03 | 11:16 | 49.961
2023-08-03 | 11:16 | 49.958
2023-08-03 | 11:16 | 49.959
2023-08-03 | 11:16 | 49.962
2023-08-03 | 11:16 | 49.963
2023-08-03 | 11:16 | 49.963
2023-08-03 | 11:16 | 49.966
2023-08-03 | 11:16 | 49.967
2023-08-03 | 11:16 | 49.968
2023-08-03 | 11:16 | 49.972
2023-08-03 | 11:16 | 49.973
2023-08-03 | 11:16 | 49.972
2023-08-03 | 11:16 | 49.975
2023-08-03 | 11:16 | 49.975
2023-08-03 | 11:16 | 49.974
2023-08-03 | 11:17 | 49.973
2023-08-03 | 11:17 | 49.972
2023-08-03 | 11:17 | 49.973
2023-08-03 | 11:17 | 49.977
2023-08-03 | 11:17 | 49.976
2023-08-03 | 11:17 | 49.975
2023-08-03 | 11:17 | 49.971
2023-08-03 | 11:17 | 49.968
2023-08-03 | 11:17 | 49.971
2023-08-03 | 11:17 | 49.974
2023-08-03 | 11:17 | 49.975
2023-08-03 | 11:17 | 49.977
2023-08-03 | 11:17 | 49.977
2023-08-03 | 11:17 | 49.974
2023-08-03 | 11:17 | 49.97
2023-08-03 | 11:17 | 49.97
2023-08-03 | 11:17 | 49.972
2023-08-03 | 11:17 | 49.975
2023-08-03 | 11:17 | 49.982
2023-08-03 | 11:17 | 49.987
2023-08-03 | 11:17 | 49.987
2023-08-03 | 11:17 | 49.987
2023-08-03 | 11:17 | 49.985
2023-08-03 | 11:17 | 49.982
2023-08-03 | 11:17 | 49.986
2023-08-03 | 11:17 | 49.987
2023-08-03 | 11:17 | 49.985
2023-08-03 | 11:17 | 49.982
2023-08-03 | 11:17 | 49.984
2023-08-03 | 11:17 | 49.986
2023-08-03 | 11:17 | 49.984
2023-08-03 | 11:17 | 49.983
2023-08-03 | 11:17 | 49.983
2023-08-03 | 11:17 | 49.981
2023-08-03 | 11:17 | 49.98
2023-08-03 | 11:17 | 49.977
2023-08-03 | 11:17 | 49.979
2023-08-03 | 11:17 | 49.977
2023-08-03 | 11:17 | 49.978
2023-08-03 | 11:17 | 49.977
2023-08-03 | 11:17 | 49.978
2023-08-03 | 11:17 | 49.98
2023-08-03 | 11:17 | 49.982
2023-08-03 | 11:17 | 49.983
2023-08-03 | 11:17 | 49.983
2023-08-03 | 11:17 | 49.982
2023-08-03 | 11:17 | 49.983
2023-08-03 | 11:17 | 49.984
2023-08-03 | 11:17 | 49.982
2023-08-03 | 11:17 | 49.983
2023-08-03 | 11:17 | 49.986
2023-08-03 | 11:17 | 49.985
2023-08-03 | 11:17 | 49.986
2023-08-03 | 11:17 | 49.985
2023-08-03 | 11:17 | 49.986
2023-08-03 | 11:17 | 49.985
2023-08-03 | 11:17 | 49.986
2023-08-03 | 11:17 | 49.984
2023-08-03 | 11:17 | 49.988
2023-08-03 | 11:18 | 49.987
2023-08-03 | 11:18 | 49.987
2023-08-03 | 11:18 | 49.984
2023-08-03 | 11:18 | 49.983
2023-08-03 | 11:18 | 49.98
2023-08-03 | 11:18 | 49.976
2023-08-03 | 11:18 | 49.973
2023-08-03 | 11:18 | 49.971
2023-08-03 | 11:18 | 49.968
2023-08-03 | 11:18 | 49.966
2023-08-03 | 11:18 | 49.967
2023-08-03 | 11:18 | 49.971
2023-08-03 | 11:18 | 49.973
2023-08-03 | 11:18 | 49.975
2023-08-03 | 11:18 | 49.975
2023-08-03 | 11:18 | 49.977
2023-08-03 | 11:18 | 49.978
2023-08-03 | 11:18 | 49.98
2023-08-03 | 11:18 | 49.978
2023-08-03 | 11:18 | 49.978
2023-08-03 | 11:18 | 49.981
2023-08-03 | 11:18 | 49.981
2023-08-03 | 11:18 | 49.981
2023-08-03 | 11:18 | 49.984
2023-08-03 | 11:18 | 49.985
2023-08-03 | 11:18 | 49.989
2023-08-03 | 11:18 | 49.991
2023-08-03 | 11:18 | 49.992
2023-08-03 | 11:18 | 49.992
2023-08-03 | 11:18 | 49.991
2023-08-03 | 11:18 | 49.985
2023-08-03 | 11:18 | 49.98
2023-08-03 | 11:18 | 49.977
2023-08-03 | 11:18 | 49.978
2023-08-03 | 11:18 | 49.982
2023-08-03 | 11:18 | 49.981
2023-08-03 | 11:18 | 49.981
2023-08-03 | 11:18 | 49.979
2023-08-03 | 11:18 | 49.98
2023-08-03 | 11:18 | 49.978
2023-08-03 | 11:18 | 49.976
2023-08-03 | 11:18 | 49.971
2023-08-03 | 11:18 | 49.968
2023-08-03 | 11:18 | 49.964
2023-08-03 | 11:18 | 49.961
2023-08-03 | 11:18 | 49.961
2023-08-03 | 11:18 | 49.961
2023-08-03 | 11:18 | 49.963
2023-08-03 | 11:18 | 49.963
2023-08-03 | 11:18 | 49.966
2023-08-03 | 11:18 | 49.968
2023-08-03 | 11:18 | 49.97
2023-08-03 | 11:18 | 49.971
2023-08-03 | 11:18 | 49.971
2023-08-03 | 11:18 | 49.969
2023-08-03 | 11:18 | 49.967
2023-08-03 | 11:18 | 49.963
2023-08-03 | 11:18 | 49.96
2023-08-03 | 11:18 | 49.954
2023-08-03 | 11:18 | 49.953
2023-08-03 | 11:18 | 49.956
2023-08-03 | 11:19 | 49.959
2023-08-03 | 11:19 | 49.961
2023-08-03 | 11:19 | 49.962
2023-08-03 | 11:19 | 49.966
2023-08-03 | 11:19 | 49.968
2023-08-03 | 11:19 | 49.967
2023-08-03 | 11:19 | 49.968
2023-08-03 | 11:19 | 49.972
2023-08-03 | 11:19 | 49.975
2023-08-03 | 11:19 | 49.978
2023-08-03 | 11:19 | 49.98
2023-08-03 | 11:19 | 49.981
2023-08-03 | 11:19 | 49.983
2023-08-03 | 11:19 | 49.985
2023-08-03 | 11:19 | 49.987
2023-08-03 | 11:19 | 49.987
2023-08-03 | 11:19 | 49.991
2023-08-03 | 11:19 | 49.995
2023-08-03 | 11:19 | 50.002
2023-08-03 | 11:19 | 50.008
2023-08-03 | 11:19 | 50.011
2023-08-03 | 11:19 | 50.013
2023-08-03 | 11:19 | 50.014
2023-08-03 | 11:19 | 50.016
2023-08-03 | 11:19 | 50.014
2023-08-03 | 11:19 | 50.01
2023-08-03 | 11:19 | 50.009
2023-08-03 | 11:19 | 50.01
2023-08-03 | 11:19 | 50.008
2023-08-03 | 11:19 | 50.005
2023-08-03 | 11:19 | 49.998
2023-08-03 | 11:19 | 49.992
2023-08-03 | 11:19 | 49.985
2023-08-03 | 11:19 | 49.983
2023-08-03 | 11:19 | 49.981
2023-08-03 | 11:19 | 49.98
2023-08-03 | 11:19 | 49.979
2023-08-03 | 11:19 | 49.979
2023-08-03 | 11:19 | 49.983
2023-08-03 | 11:19 | 49.98
2023-08-03 | 11:19 | 49.984
2023-08-03 | 11:19 | 49.984
2023-08-03 | 11:19 | 49.984
2023-08-03 | 11:19 | 49.984
2023-08-03 | 11:19 | 49.982
2023-08-03 | 11:19 | 49.986
2023-08-03 | 11:19 | 49.986
2023-08-03 | 11:19 | 49.99
2023-08-03 | 11:19 | 49.988
2023-08-03 | 11:19 | 49.987
2023-08-03 | 11:19 | 49.981
2023-08-03 | 11:19 | 49.981
2023-08-03 | 11:19 | 49.983
2023-08-03 | 11:19 | 49.981
2023-08-03 | 11:19 | 49.982
2023-08-03 | 11:19 | 49.984
2023-08-03 | 11:19 | 49.99
2023-08-03 | 11:19 | 49.991
2023-08-03 | 11:19 | 49.992
2023-08-03 | 11:20 | 49.993
2023-08-03 | 11:20 | 49.996
2023-08-03 | 11:20 | 49.995
2023-08-03 | 11:20 | 49.996
2023-08-03 | 11:20 | 49.996
2023-08-03 | 11:20 | 49.997
2023-08-03 | 11:20 | 50.001
2023-08-03 | 11:20 | 50.005
2023-08-03 | 11:20 | 50.006
2023-08-03 | 11:20 | 50.005
2023-08-03 | 11:20 | 50.008
2023-08-03 | 11:20 | 50.01
2023-08-03 | 11:20 | 50.011
2023-08-03 | 11:20 | 50.008
2023-08-03 | 11:20 | 50.004
2023-08-03 | 11:20 | 50.003
2023-08-03 | 11:20 | 50.001
2023-08-03 | 11:20 | 49.997
2023-08-03 | 11:20 | 49.993
2023-08-03 | 11:20 | 49.991
2023-08-03 | 11:20 | 49.989
2023-08-03 | 11:20 | 49.987
2023-08-03 | 11:20 | 49.988
2023-08-03 | 11:20 | 49.987
2023-08-03 | 11:20 | 49.984
2023-08-03 | 11:20 | 49.988
2023-08-03 | 11:20 | 49.988
2023-08-03 | 11:20 | 49.987
2023-08-03 | 11:20 | 49.99
2023-08-03 | 11:20 | 49.991

## 20230803-2
In GMT
Date | Time | Freq
2023-08-03 | 14:01 | 49.894
2023-08-03 | 14:01 | 49.892
2023-08-03 | 14:01 | 49.892
2023-08-03 | 14:01 | 49.891
2023-08-03 | 14:01 | 49.893
2023-08-03 | 14:01 | 49.89
2023-08-03 | 14:01 | 49.887
2023-08-03 | 14:01 | 49.887
2023-08-03 | 14:01 | 49.89
2023-08-03 | 14:01 | 49.889
2023-08-03 | 14:01 | 49.889
2023-08-03 | 14:01 | 49.891
2023-08-03 | 14:01 | 49.891
2023-08-03 | 14:01 | 49.894
2023-08-03 | 14:01 | 49.894
2023-08-03 | 14:01 | 49.893
2023-08-03 | 14:01 | 49.893
2023-08-03 | 14:01 | 49.895
2023-08-03 | 14:01 | 49.895
2023-08-03 | 14:01 | 49.893
2023-08-03 | 14:01 | 49.893
2023-08-03 | 14:01 | 49.893
2023-08-03 | 14:01 | 49.891
2023-08-03 | 14:01 | 49.888
2023-08-03 | 14:01 | 49.886
2023-08-03 | 14:01 | 49.88
2023-08-03 | 14:01 | 49.877
2023-08-03 | 14:01 | 49.876
2023-08-03 | 14:01 | 49.875
2023-08-03 | 14:01 | 49.872
2023-08-03 | 14:02 | 49.873
2023-08-03 | 14:02 | 49.876
2023-08-03 | 14:02 | 49.879
2023-08-03 | 14:02 | 49.88
2023-08-03 | 14:02 | 49.883
2023-08-03 | 14:02 | 49.883
2023-08-03 | 14:02 | 49.885
2023-08-03 | 14:02 | 49.887
2023-08-03 | 14:02 | 49.889
2023-08-03 | 14:02 | 49.892
2023-08-03 | 14:02 | 49.893
2023-08-03 | 14:02 | 49.894
2023-08-03 | 14:02 | 49.896
2023-08-03 | 14:02 | 49.898
2023-08-03 | 14:02 | 49.902
2023-08-03 | 14:02 | 49.904
2023-08-03 | 14:02 | 49.904
2023-08-03 | 14:02 | 49.902
2023-08-03 | 14:02 | 49.899
2023-08-03 | 14:02 | 49.9
2023-08-03 | 14:02 | 49.901
2023-08-03 | 14:02 | 49.898
2023-08-03 | 14:02 | 49.896
2023-08-03 | 14:02 | 49.893
2023-08-03 | 14:02 | 49.894
2023-08-03 | 14:02 | 49.892
2023-08-03 | 14:02 | 49.889
2023-08-03 | 14:02 | 49.885
2023-08-03 | 14:02 | 49.881
2023-08-03 | 14:02 | 49.877
2023-08-03 | 14:02 | 49.876
2023-08-03 | 14:02 | 49.873
2023-08-03 | 14:02 | 49.87
2023-08-03 | 14:02 | 49.867
2023-08-03 | 14:02 | 49.867
2023-08-03 | 14:02 | 49.864
2023-08-03 | 14:02 | 49.862
2023-08-03 | 14:02 | 49.861
2023-08-03 | 14:02 | 49.861
2023-08-03 | 14:02 | 49.86
2023-08-03 | 14:02 | 49.858
2023-08-03 | 14:02 | 49.855
2023-08-03 | 14:02 | 49.851
2023-08-03 | 14:02 | 49.849
2023-08-03 | 14:02 | 49.846
2023-08-03 | 14:02 | 49.844
2023-08-03 | 14:02 | 49.839
2023-08-03 | 14:02 | 49.833
2023-08-03 | 14:02 | 49.827
2023-08-03 | 14:02 | 49.824
2023-08-03 | 14:02 | 49.825
2023-08-03 | 14:02 | 49.822
2023-08-03 | 14:02 | 49.817
2023-08-03 | 14:02 | 49.814
2023-08-03 | 14:02 | 49.81
2023-08-03 | 14:02 | 49.806
2023-08-03 | 14:02 | 49.803
2023-08-03 | 14:02 | 49.797
2023-08-03 | 14:02 | 49.796
2023-08-03 | 14:02 | 49.798
2023-08-03 | 14:02 | 49.801
2023-08-03 | 14:03 | 49.801
2023-08-03 | 14:03 | 49.8
2023-08-03 | 14:03 | 49.797
2023-08-03 | 14:03 | 49.8
2023-08-03 | 14:03 | 49.798
2023-08-03 | 14:03 | 49.798
2023-08-03 | 14:03 | 49.798
2023-08-03 | 14:03 | 49.798
2023-08-03 | 14:03 | 49.79
2023-08-03 | 14:03 | 49.768
2023-08-03 | 14:03 | 49.758
2023-08-03 | 14:03 | 49.751
2023-08-03 | 14:03 | 49.751
2023-08-03 | 14:03 | 49.75
2023-08-03 | 14:03 | 49.75
2023-08-03 | 14:03 | 49.747
2023-08-03 | 14:03 | 49.747
2023-08-03 | 14:03 | 49.747
2023-08-03 | 14:03 | 49.744
2023-08-03 | 14:03 | 49.744
2023-08-03 | 14:03 | 49.742
2023-08-03 | 14:03 | 49.739
2023-08-03 | 14:03 | 49.741
2023-08-03 | 14:03 | 49.741
2023-08-03 | 14:03 | 49.739
2023-08-03 | 14:03 | 49.738
2023-08-03 | 14:03 | 49.739
2023-08-03 | 14:03 | 49.737
2023-08-03 | 14:03 | 49.737
2023-08-03 | 14:03 | 49.739
2023-08-03 | 14:03 | 49.735
2023-08-03 | 14:03 | 49.734
2023-08-03 | 14:03 | 49.735
2023-08-03 | 14:03 | 49.736
2023-08-03 | 14:03 | 49.737
2023-08-03 | 14:03 | 49.737
2023-08-03 | 14:03 | 49.741
2023-08-03 | 14:03 | 49.747
2023-08-03 | 14:03 | 49.751
2023-08-03 | 14:03 | 49.753
2023-08-03 | 14:03 | 49.753
2023-08-03 | 14:03 | 49.753
2023-08-03 | 14:03 | 49.753
2023-08-03 | 14:03 | 49.751
2023-08-03 | 14:03 | 49.751
2023-08-03 | 14:03 | 49.75
2023-08-03 | 14:03 | 49.748
2023-08-03 | 14:03 | 49.743
2023-08-03 | 14:03 | 49.74
2023-08-03 | 14:03 | 49.739
2023-08-03 | 14:03 | 49.739
2023-08-03 | 14:03 | 49.736
2023-08-03 | 14:03 | 49.737
2023-08-03 | 14:03 | 49.738
2023-08-03 | 14:03 | 49.737
2023-08-03 | 14:03 | 49.737
2023-08-03 | 14:03 | 49.737
2023-08-03 | 14:03 | 49.734
2023-08-03 | 14:03 | 49.731
2023-08-03 | 14:04 | 49.731
2023-08-03 | 14:04 | 49.73
2023-08-03 | 14:04 | 49.733
2023-08-03 | 14:04 | 49.737
2023-08-03 | 14:04 | 49.738
2023-08-03 | 14:04 | 49.739
2023-08-03 | 14:04 | 49.741
2023-08-03 | 14:04 | 49.743
2023-08-03 | 14:04 | 49.745
2023-08-03 | 14:04 | 49.75
2023-08-03 | 14:04 | 49.755
2023-08-03 | 14:04 | 49.757
2023-08-03 | 14:04 | 49.761
2023-08-03 | 14:04 | 49.766
2023-08-03 | 14:04 | 49.771
2023-08-03 | 14:04 | 49.776
2023-08-03 | 14:04 | 49.782
2023-08-03 | 14:04 | 49.788
2023-08-03 | 14:04 | 49.792
2023-08-03 | 14:04 | 49.797
2023-08-03 | 14:04 | 49.802
2023-08-03 | 14:04 | 49.806
2023-08-03 | 14:04 | 49.807
2023-08-03 | 14:04 | 49.81
2023-08-03 | 14:04 | 49.813
2023-08-03 | 14:04 | 49.817
2023-08-03 | 14:04 | 49.821
2023-08-03 | 14:04 | 49.822
2023-08-03 | 14:04 | 49.824
2023-08-03 | 14:04 | 49.827
2023-08-03 | 14:04 | 49.827
2023-08-03 | 14:04 | 49.827
2023-08-03 | 14:04 | 49.826
2023-08-03 | 14:04 | 49.825
2023-08-03 | 14:04 | 49.826
2023-08-03 | 14:04 | 49.826
2023-08-03 | 14:04 | 49.827
2023-08-03 | 14:04 | 49.829
2023-08-03 | 14:04 | 49.83
2023-08-03 | 14:04 | 49.832
2023-08-03 | 14:04 | 49.834
2023-08-03 | 14:04 | 49.837
2023-08-03 | 14:04 | 49.839
2023-08-03 | 14:04 | 49.844
2023-08-03 | 14:04 | 49.848
2023-08-03 | 14:04 | 49.853
2023-08-03 | 14:04 | 49.852
2023-08-03 | 14:04 | 49.852
2023-08-03 | 14:04 | 49.85
2023-08-03 | 14:04 | 49.853
2023-08-03 | 14:04 | 49.857
2023-08-03 | 14:04 | 49.86
2023-08-03 | 14:04 | 49.864
2023-08-03 | 14:04 | 49.867
2023-08-03 | 14:04 | 49.87
2023-08-03 | 14:04 | 49.873
2023-08-03 | 14:04 | 49.878
2023-08-03 | 14:04 | 49.88
2023-08-03 | 14:04 | 49.88
2023-08-03 | 14:04 | 49.884
2023-08-03 | 14:04 | 49.888
2023-08-03 | 14:05 | 49.89
2023-08-03 | 14:05 | 49.895
2023-08-03 | 14:05 | 49.895
2023-08-03 | 14:05 | 49.895
2023-08-03 | 14:05 | 49.896
2023-08-03 | 14:05 | 49.894
2023-08-03 | 14:05 | 49.895
2023-08-03 | 14:05 | 49.894
2023-08-03 | 14:05 | 49.894
2023-08-03 | 14:05 | 49.901
2023-08-03 | 14:05 | 49.906
2023-08-03 | 14:05 | 49.911
2023-08-03 | 14:05 | 49.916
2023-08-03 | 14:05 | 49.919
2023-08-03 | 14:05 | 49.917
2023-08-03 | 14:05 | 49.915
2023-08-03 | 14:05 | 49.917
2023-08-03 | 14:05 | 49.918
2023-08-03 | 14:05 | 49.92
2023-08-03 | 14:05 | 49.92
2023-08-03 | 14:05 | 49.921
2023-08-03 | 14:05 | 49.921
2023-08-03 | 14:05 | 49.919
2023-08-03 | 14:05 | 49.915
2023-08-03 | 14:05 | 49.913
2023-08-03 | 14:05 | 49.916
2023-08-03 | 14:05 | 49.916
2023-08-03 | 14:05 | 49.916
2023-08-03 | 14:05 | 49.916
2023-08-03 | 14:05 | 49.915
2023-08-03 | 14:05 | 49.909
2023-08-03 | 14:05 | 49.906
2023-08-03 | 14:05 | 49.9
2023-08-03 | 14:05 | 49.897
2023-08-03 | 14:05 | 49.895
2023-08-03 | 14:05 | 49.894
2023-08-03 | 14:05 | 49.895
2023-08-03 | 14:05 | 49.896
2023-08-03 | 14:05 | 49.895
2023-08-03 | 14:05 | 49.895
2023-08-03 | 14:05 | 49.895
2023-08-03 | 14:05 | 49.896
2023-08-03 | 14:05 | 49.901
2023-08-03 | 14:05 | 49.906
2023-08-03 | 14:05 | 49.907
2023-08-03 | 14:05 | 49.91
2023-08-03 | 14:05 | 49.912
2023-08-03 | 14:05 | 49.91
2023-08-03 | 14:05 | 49.909
2023-08-03 | 14:05 | 49.912
2023-08-03 | 14:05 | 49.913
2023-08-03 | 14:05 | 49.914
2023-08-03 | 14:05 | 49.915
2023-08-03 | 14:05 | 49.912
2023-08-03 | 14:05 | 49.912
2023-08-03 | 14:05 | 49.913
2023-08-03 | 14:05 | 49.919
2023-08-03 | 14:05 | 49.924
2023-08-03 | 14:05 | 49.927
2023-08-03 | 14:06 | 49.929
2023-08-03 | 14:06 | 49.931
2023-08-03 | 14:06 | 49.932
2023-08-03 | 14:06 | 49.932
2023-08-03 | 14:06 | 49.933
2023-08-03 | 14:06 | 49.934
2023-08-03 | 14:06 | 49.93
2023-08-03 | 14:06 | 49.924
2023-08-03 | 14:06 | 49.918
2023-08-03 | 14:06 | 49.916
2023-08-03 | 14:06 | 49.916
2023-08-03 | 14:06 | 49.916
2023-08-03 | 14:06 | 49.92
2023-08-03 | 14:06 | 49.923
2023-08-03 | 14:06 | 49.923
2023-08-03 | 14:06 | 49.924
2023-08-03 | 14:06 | 49.924
2023-08-03 | 14:06 | 49.924
2023-08-03 | 14:06 | 49.923
2023-08-03 | 14:06 | 49.922
2023-08-03 | 14:06 | 49.922
2023-08-03 | 14:06 | 49.921
2023-08-03 | 14:06 | 49.924
2023-08-03 | 14:06 | 49.926
2023-08-03 | 14:06 | 49.923
2023-08-03 | 14:06 | 49.924
2023-08-03 | 14:06 | 49.923
2023-08-03 | 14:06 | 49.922
2023-08-03 | 14:06 | 49.921
2023-08-03 | 14:06 | 49.922
2023-08-03 | 14:06 | 49.925
2023-08-03 | 14:06 | 49.929
2023-08-03 | 14:06 | 49.934
2023-08-03 | 14:06 | 49.935
2023-08-03 | 14:06 | 49.938
2023-08-03 | 14:06 | 49.939
2023-08-03 | 14:06 | 49.939
2023-08-03 | 14:06 | 49.943
2023-08-03 | 14:06 | 49.942
2023-08-03 | 14:06 | 49.943
2023-08-03 | 14:06 | 49.944
2023-08-03 | 14:06 | 49.942
2023-08-03 | 14:06 | 49.942
2023-08-03 | 14:06 | 49.937
2023-08-03 | 14:06 | 49.937
2023-08-03 | 14:06 | 49.936
2023-08-03 | 14:06 | 49.935
2023-08-03 | 14:06 | 49.934
2023-08-03 | 14:06 | 49.931
2023-08-03 | 14:06 | 49.929
2023-08-03 | 14:06 | 49.932
2023-08-03 | 14:06 | 49.933
2023-08-03 | 14:06 | 49.94
2023-08-03 | 14:06 | 49.945
2023-08-03 | 14:06 | 49.95
2023-08-03 | 14:06 | 49.955
2023-08-03 | 14:06 | 49.959
2023-08-03 | 14:06 | 49.959
2023-08-03 | 14:06 | 49.96
2023-08-03 | 14:06 | 49.958
2023-08-03 | 14:06 | 49.958
2023-08-03 | 14:07 | 49.956
2023-08-03 | 14:07 | 49.956
2023-08-03 | 14:07 | 49.954
2023-08-03 | 14:07 | 49.953
2023-08-03 | 14:07 | 49.951
2023-08-03 | 14:07 | 49.949
2023-08-03 | 14:07 | 49.949
2023-08-03 | 14:07 | 49.949
2023-08-03 | 14:07 | 49.946
2023-08-03 | 14:07 | 49.95
2023-08-03 | 14:07 | 49.952
2023-08-03 | 14:07 | 49.956
2023-08-03 | 14:07 | 49.958
2023-08-03 | 14:07 | 49.958
2023-08-03 | 14:07 | 49.959
2023-08-03 | 14:07 | 49.957
2023-08-03 | 14:07 | 49.959
2023-08-03 | 14:07 | 49.961
2023-08-03 | 14:07 | 49.962
2023-08-03 | 14:07 | 49.967
2023-08-03 | 14:07 | 49.968
2023-08-03 | 14:07 | 49.969
2023-08-03 | 14:07 | 49.969
2023-08-03 | 14:07 | 49.971
2023-08-03 | 14:07 | 49.969
2023-08-03 | 14:07 | 49.969
2023-08-03 | 14:07 | 49.974
2023-08-03 | 14:07 | 49.975
2023-08-03 | 14:07 | 49.975
2023-08-03 | 14:07 | 49.978
2023-08-03 | 14:07 | 49.974
2023-08-03 | 14:07 | 49.976
2023-08-03 | 14:07 | 49.979
2023-08-03 | 14:07 | 49.98
2023-08-03 | 14:07 | 49.983
2023-08-03 | 14:07 | 49.987
2023-08-03 | 14:07 | 49.989
2023-08-03 | 14:07 | 49.992
2023-08-03 | 14:07 | 49.992
2023-08-03 | 14:07 | 49.994
2023-08-03 | 14:07 | 49.997
2023-08-03 | 14:07 | 49.999
2023-08-03 | 14:07 | 50.001
2023-08-03 | 14:07 | 50.002
2023-08-03 | 14:07 | 50.004
2023-08-03 | 14:07 | 50.005
2023-08-03 | 14:07 | 50.005
2023-08-03 | 14:07 | 50.006
2023-08-03 | 14:07 | 50.006
2023-08-03 | 14:07 | 50.003
2023-08-03 | 14:07 | 50.001
2023-08-03 | 14:07 | 50.003
2023-08-03 | 14:07 | 50.003
2023-08-03 | 14:07 | 50.004
2023-08-03 | 14:07 | 50.003
2023-08-03 | 14:07 | 49.999
2023-08-03 | 14:07 | 49.997
2023-08-03 | 14:07 | 49.995
2023-08-03 | 14:07 | 49.992
2023-08-03 | 14:08 | 49.989
2023-08-03 | 14:08 | 49.985
2023-08-03 | 14:08 | 49.98
2023-08-03 | 14:08 | 49.979
2023-08-03 | 14:08 | 49.982
2023-08-03 | 14:08 | 49.983
2023-08-03 | 14:08 | 49.983
2023-08-03 | 14:08 | 49.983
2023-08-03 | 14:08 | 49.983
2023-08-03 | 14:08 | 49.981
2023-08-03 | 14:08 | 49.98
2023-08-03 | 14:08 | 49.976
2023-08-03 | 14:08 | 49.976
2023-08-03 | 14:08 | 49.976
2023-08-03 | 14:08 | 49.981
2023-08-03 | 14:08 | 49.986
2023-08-03 | 14:08 | 49.99
2023-08-03 | 14:08 | 49.994
2023-08-03 | 14:08 | 50
2023-08-03 | 14:08 | 50.006
2023-08-03 | 14:08 | 50.014
2023-08-03 | 14:08 | 50.021
2023-08-03 | 14:08 | 50.028
2023-08-03 | 14:08 | 50.034
2023-08-03 | 14:08 | 50.036
2023-08-03 | 14:08 | 50.041
2023-08-03 | 14:08 | 50.043
2023-08-03 | 14:08 | 50.047
2023-08-03 | 14:08 | 50.047
2023-08-03 | 14:08 | 50.047

## 20230823-1
In GMT
Date | Time | Freq
2023-08-23 | 8:55 | 50.132
2023-08-23 | 8:55 | 50.132
2023-08-23 | 8:55 | 50.131
2023-08-23 | 8:55 | 50.129
2023-08-23 | 8:55 | 50.128
2023-08-23 | 8:55 | 50.128
2023-08-23 | 8:55 | 50.127
2023-08-23 | 8:55 | 50.126
2023-08-23 | 8:55 | 50.126
2023-08-23 | 8:55 | 50.125
2023-08-23 | 8:55 | 50.122
2023-08-23 | 8:55 | 50.118
2023-08-23 | 8:55 | 50.12
2023-08-23 | 8:55 | 50.12
2023-08-23 | 8:55 | 50.122
2023-08-23 | 8:55 | 50.121
2023-08-23 | 8:55 | 50.119
2023-08-23 | 8:55 | 50.117
2023-08-23 | 8:55 | 50.115
2023-08-23 | 8:55 | 50.114
2023-08-23 | 8:55 | 50.114
2023-08-23 | 8:55 | 50.114
2023-08-23 | 8:55 | 50.114
2023-08-23 | 8:55 | 50.115
2023-08-23 | 8:55 | 50.116
2023-08-23 | 8:55 | 50.117
2023-08-23 | 8:55 | 50.116
2023-08-23 | 8:55 | 50.115
2023-08-23 | 8:55 | 50.113
2023-08-23 | 8:55 | 50.11
2023-08-23 | 8:56 | 50.109
2023-08-23 | 8:56 | 50.11
2023-08-23 | 8:56 | 50.109
2023-08-23 | 8:56 | 50.11
2023-08-23 | 8:56 | 50.112
2023-08-23 | 8:56 | 50.115
2023-08-23 | 8:56 | 50.119
2023-08-23 | 8:56 | 50.123
2023-08-23 | 8:56 | 50.126
2023-08-23 | 8:56 | 50.131
2023-08-23 | 8:56 | 50.133
2023-08-23 | 8:56 | 50.134
2023-08-23 | 8:56 | 50.134
2023-08-23 | 8:56 | 50.134
2023-08-23 | 8:56 | 50.134
2023-08-23 | 8:56 | 50.133
2023-08-23 | 8:56 | 50.131
2023-08-23 | 8:56 | 50.132
2023-08-23 | 8:56 | 50.131
2023-08-23 | 8:56 | 50.131
2023-08-23 | 8:56 | 50.13
2023-08-23 | 8:56 | 50.133
2023-08-23 | 8:56 | 50.133
2023-08-23 | 8:56 | 50.134
2023-08-23 | 8:56 | 50.133
2023-08-23 | 8:56 | 50.133
2023-08-23 | 8:56 | 50.133
2023-08-23 | 8:56 | 50.132
2023-08-23 | 8:56 | 50.133
2023-08-23 | 8:56 | 50.132
2023-08-23 | 8:56 | 50.13
2023-08-23 | 8:56 | 50.126
2023-08-23 | 8:56 | 50.121
2023-08-23 | 8:56 | 50.12
2023-08-23 | 8:56 | 50.12
2023-08-23 | 8:56 | 50.12
2023-08-23 | 8:56 | 50.119
2023-08-23 | 8:56 | 50.119
2023-08-23 | 8:56 | 50.117
2023-08-23 | 8:56 | 50.116
2023-08-23 | 8:56 | 50.115
2023-08-23 | 8:56 | 50.114
2023-08-23 | 8:56 | 50.111
2023-08-23 | 8:56 | 50.11
2023-08-23 | 8:56 | 50.107
2023-08-23 | 8:56 | 50.106
2023-08-23 | 8:56 | 50.106
2023-08-23 | 8:56 | 50.108
2023-08-23 | 8:56 | 50.109
2023-08-23 | 8:56 | 50.109
2023-08-23 | 8:56 | 50.11
2023-08-23 | 8:56 | 50.108
2023-08-23 | 8:56 | 50.092
2023-08-23 | 8:56 | 50.056
2023-08-23 | 8:56 | 50.021
2023-08-23 | 8:56 | 49.994
2023-08-23 | 8:56 | 49.972
2023-08-23 | 8:56 | 49.951
2023-08-23 | 8:56 | 49.934
2023-08-23 | 8:56 | 49.924
2023-08-23 | 8:56 | 49.915
2023-08-23 | 8:57 | 49.908
2023-08-23 | 8:57 | 49.905
2023-08-23 | 8:57 | 49.901
2023-08-23 | 8:57 | 49.894
2023-08-23 | 8:57 | 49.891
2023-08-23 | 8:57 | 49.889
2023-08-23 | 8:57 | 49.887
2023-08-23 | 8:57 | 49.887
2023-08-23 | 8:57 | 49.884
2023-08-23 | 8:57 | 49.881
2023-08-23 | 8:57 | 49.878
2023-08-23 | 8:57 | 49.877
2023-08-23 | 8:57 | 49.874
2023-08-23 | 8:57 | 49.871
2023-08-23 | 8:57 | 49.871
2023-08-23 | 8:57 | 49.87
2023-08-23 | 8:57 | 49.87
2023-08-23 | 8:57 | 49.869
2023-08-23 | 8:57 | 49.871
2023-08-23 | 8:57 | 49.869
2023-08-23 | 8:57 | 49.873
2023-08-23 | 8:57 | 49.877
2023-08-23 | 8:57 | 49.88
2023-08-23 | 8:57 | 49.882
2023-08-23 | 8:57 | 49.881
2023-08-23 | 8:57 | 49.883
2023-08-23 | 8:57 | 49.886
2023-08-23 | 8:57 | 49.885
2023-08-23 | 8:57 | 49.886
2023-08-23 | 8:57 | 49.885
2023-08-23 | 8:57 | 49.884
2023-08-23 | 8:57 | 49.881
2023-08-23 | 8:57 | 49.882
2023-08-23 | 8:57 | 49.883
2023-08-23 | 8:57 | 49.884
2023-08-23 | 8:57 | 49.886
2023-08-23 | 8:57 | 49.886
2023-08-23 | 8:57 | 49.889
2023-08-23 | 8:57 | 49.889
2023-08-23 | 8:57 | 49.89
2023-08-23 | 8:57 | 49.891
2023-08-23 | 8:57 | 49.892
2023-08-23 | 8:57 | 49.887
2023-08-23 | 8:57 | 49.886
2023-08-23 | 8:57 | 49.885
2023-08-23 | 8:57 | 49.884
2023-08-23 | 8:57 | 49.887
2023-08-23 | 8:57 | 49.887
2023-08-23 | 8:57 | 49.886
2023-08-23 | 8:57 | 49.887
2023-08-23 | 8:57 | 49.889
2023-08-23 | 8:57 | 49.891
2023-08-23 | 8:57 | 49.892
2023-08-23 | 8:57 | 49.894
2023-08-23 | 8:57 | 49.893
2023-08-23 | 8:57 | 49.893
2023-08-23 | 8:57 | 49.894
2023-08-23 | 8:57 | 49.894
2023-08-23 | 8:57 | 49.897
2023-08-23 | 8:58 | 49.9
2023-08-23 | 8:58 | 49.903
2023-08-23 | 8:58 | 49.903
2023-08-23 | 8:58 | 49.907
2023-08-23 | 8:58 | 49.908
2023-08-23 | 8:58 | 49.913
2023-08-23 | 8:58 | 49.912
2023-08-23 | 8:58 | 49.915
2023-08-23 | 8:58 | 49.914
2023-08-23 | 8:58 | 49.916
2023-08-23 | 8:58 | 49.918
2023-08-23 | 8:58 | 49.918
2023-08-23 | 8:58 | 49.917
2023-08-23 | 8:58 | 49.914
2023-08-23 | 8:58 | 49.911
2023-08-23 | 8:58 | 49.91
2023-08-23 | 8:58 | 49.911
2023-08-23 | 8:58 | 49.908
2023-08-23 | 8:58 | 49.908
2023-08-23 | 8:58 | 49.909
2023-08-23 | 8:58 | 49.909
2023-08-23 | 8:58 | 49.907
2023-08-23 | 8:58 | 49.909
2023-08-23 | 8:58 | 49.91
2023-08-23 | 8:58 | 49.909
2023-08-23 | 8:58 | 49.91
2023-08-23 | 8:58 | 49.914
2023-08-23 | 8:58 | 49.916
2023-08-23 | 8:58 | 49.921
2023-08-23 | 8:58 | 49.92
2023-08-23 | 8:58 | 49.922
2023-08-23 | 8:58 | 49.92
2023-08-23 | 8:58 | 49.922
2023-08-23 | 8:58 | 49.923
2023-08-23 | 8:58 | 49.922
2023-08-23 | 8:58 | 49.924
2023-08-23 | 8:58 | 49.924
2023-08-23 | 8:58 | 49.926
2023-08-23 | 8:58 | 49.925
2023-08-23 | 8:58 | 49.928
2023-08-23 | 8:58 | 49.928
2023-08-23 | 8:58 | 49.927
2023-08-23 | 8:58 | 49.928
2023-08-23 | 8:58 | 49.923
2023-08-23 | 8:58 | 49.924
2023-08-23 | 8:58 | 49.927
2023-08-23 | 8:58 | 49.928
2023-08-23 | 8:58 | 49.93
2023-08-23 | 8:58 | 49.937
2023-08-23 | 8:58 | 49.94
2023-08-23 | 8:58 | 49.94
2023-08-23 | 8:58 | 49.94
2023-08-23 | 8:58 | 49.94
2023-08-23 | 8:58 | 49.947
2023-08-23 | 8:58 | 49.948
2023-08-23 | 8:58 | 49.948
2023-08-23 | 8:58 | 49.952
2023-08-23 | 8:58 | 49.955
2023-08-23 | 8:58 | 49.955
2023-08-23 | 8:58 | 49.956
2023-08-23 | 8:58 | 49.961
2023-08-23 | 8:59 | 49.96
2023-08-23 | 8:59 | 49.96
2023-08-23 | 8:59 | 49.96
2023-08-23 | 8:59 | 49.957
2023-08-23 | 8:59 | 49.958
2023-08-23 | 8:59 | 49.961
2023-08-23 | 8:59 | 49.961
2023-08-23 | 8:59 | 49.962
2023-08-23 | 8:59 | 49.963
2023-08-23 | 8:59 | 49.964
2023-08-23 | 8:59 | 49.968
2023-08-23 | 8:59 | 49.97
2023-08-23 | 8:59 | 49.969
2023-08-23 | 8:59 | 49.971
2023-08-23 | 8:59 | 49.972
2023-08-23 | 8:59 | 49.971
2023-08-23 | 8:59 | 49.972
2023-08-23 | 8:59 | 49.973
2023-08-23 | 8:59 | 49.977
2023-08-23 | 8:59 | 49.979
2023-08-23 | 8:59 | 49.98
2023-08-23 | 8:59 | 49.984
2023-08-23 | 8:59 | 49.987
2023-08-23 | 8:59 | 49.991
2023-08-23 | 8:59 | 49.991
2023-08-23 | 8:59 | 49.994
2023-08-23 | 8:59 | 49.995
2023-08-23 | 8:59 | 49.996
2023-08-23 | 8:59 | 49.999
2023-08-23 | 8:59 | 50.002
2023-08-23 | 8:59 | 50.002
2023-08-23 | 8:59 | 50.002
2023-08-23 | 8:59 | 50.003
2023-08-23 | 8:59 | 50.005
2023-08-23 | 8:59 | 50.009
2023-08-23 | 8:59 | 50.013
2023-08-23 | 8:59 | 50.015
2023-08-23 | 8:59 | 50.019
2023-08-23 | 8:59 | 50.021
2023-08-23 | 8:59 | 50.026
2023-08-23 | 8:59 | 50.03
2023-08-23 | 8:59 | 50.036
2023-08-23 | 8:59 | 50.044
2023-08-23 | 8:59 | 50.053
2023-08-23 | 8:59 | 50.062
2023-08-23 | 8:59 | 50.073
2023-08-23 | 8:59 | 50.082
2023-08-23 | 8:59 | 50.091
2023-08-23 | 8:59 | 50.097
2023-08-23 | 8:59 | 50.103
2023-08-23 | 8:59 | 50.107
2023-08-23 | 8:59 | 50.11
2023-08-23 | 8:59 | 50.114
2023-08-23 | 8:59 | 50.116
2023-08-23 | 8:59 | 50.115
2023-08-23 | 8:59 | 50.111
2023-08-23 | 8:59 | 50.105
2023-08-23 | 8:59 | 50.097
2023-08-23 | 8:59 | 50.09
2023-08-23 | 9:00 | 50.086
2023-08-23 | 9:00 | 50.085
2023-08-23 | 9:00 | 50.089
2023-08-23 | 9:00 | 50.098
2023-08-23 | 9:00 | 50.099
2023-08-23 | 9:00 | 50.104
2023-08-23 | 9:00 | 50.102
2023-08-23 | 9:00 | 50.097
2023-08-23 | 9:00 | 50.099
2023-08-23 | 9:00 | 50.102
2023-08-23 | 9:00 | 50.108
2023-08-23 | 9:00 | 50.108
2023-08-23 | 9:00 | 50.107
2023-08-23 | 9:00 | 50.107
2023-08-23 | 9:00 | 50.107
2023-08-23 | 9:00 | 50.11
2023-08-23 | 9:00 | 50.113
2023-08-23 | 9:00 | 50.12
2023-08-23 | 9:00 | 50.126
2023-08-23 | 9:00 | 50.138
2023-08-23 | 9:00 | 50.147
2023-08-23 | 9:00 | 50.16
2023-08-23 | 9:00 | 50.164
2023-08-23 | 9:00 | 50.171
2023-08-23 | 9:00 | 50.175
2023-08-23 | 9:00 | 50.177
2023-08-23 | 9:00 | 50.177
2023-08-23 | 9:00 | 50.178
2023-08-23 | 9:00 | 50.18
2023-08-23 | 9:00 | 50.18
2023-08-23 | 9:00 | 50.179
2023-08-23 | 9:00 | 50.177
2023-08-23 | 9:00 | 50.18
2023-08-23 | 9:00 | 50.181
2023-08-23 | 9:00 | 50.183
2023-08-23 | 9:00 | 50.187
2023-08-23 | 9:00 | 50.192
2023-08-23 | 9:00 | 50.197
2023-08-23 | 9:00 | 50.199
2023-08-23 | 9:00 | 50.203
2023-08-23 | 9:00 | 50.204
2023-08-23 | 9:00 | 50.205
2023-08-23 | 9:00 | 50.205
2023-08-23 | 9:00 | 50.207
2023-08-23 | 9:00 | 50.212
2023-08-23 | 9:00 | 50.216
2023-08-23 | 9:00 | 50.22
2023-08-23 | 9:00 | 50.22
2023-08-23 | 9:00 | 50.221
2023-08-23 | 9:00 | 50.219
2023-08-23 | 9:00 | 50.216
2023-08-23 | 9:00 | 50.215
2023-08-23 | 9:00 | 50.215
2023-08-23 | 9:00 | 50.214
2023-08-23 | 9:00 | 50.213
2023-08-23 | 9:00 | 50.214
2023-08-23 | 9:00 | 50.212
2023-08-23 | 9:00 | 50.212
2023-08-23 | 9:00 | 50.212
2023-08-23 | 9:00 | 50.215
2023-08-23 | 9:00 | 50.215
2023-08-23 | 9:01 | 50.213
2023-08-23 | 9:01 | 50.214
2023-08-23 | 9:01 | 50.215
2023-08-23 | 9:01 | 50.215
2023-08-23 | 9:01 | 50.216
2023-08-23 | 9:01 | 50.213
2023-08-23 | 9:01 | 50.214
2023-08-23 | 9:01 | 50.215
2023-08-23 | 9:01 | 50.214
2023-08-23 | 9:01 | 50.215
2023-08-23 | 9:01 | 50.219
2023-08-23 | 9:01 | 50.219
2023-08-23 | 9:01 | 50.217
2023-08-23 | 9:01 | 50.218
2023-08-23 | 9:01 | 50.217
2023-08-23 | 9:01 | 50.22
2023-08-23 | 9:01 | 50.222
2023-08-23 | 9:01 | 50.226
2023-08-23 | 9:01 | 50.226
2023-08-23 | 9:01 | 50.226
2023-08-23 | 9:01 | 50.225
2023-08-23 | 9:01 | 50.224
2023-08-23 | 9:01 | 50.223
2023-08-23 | 9:01 | 50.222
2023-08-23 | 9:01 | 50.221
2023-08-23 | 9:01 | 50.223
2023-08-23 | 9:01 | 50.225
2023-08-23 | 9:01 | 50.227
2023-08-23 | 9:01 | 50.23

## 20230826-1
In GMT
Date | Time | Freq
2023-08-26 | 11:30 | 50.023
2023-08-26 | 11:30 | 50.026
2023-08-26 | 11:30 | 50.026
2023-08-26 | 11:30 | 50.027
2023-08-26 | 11:30 | 50.026
2023-08-26 | 11:30 | 50.027
2023-08-26 | 11:30 | 50.031
2023-08-26 | 11:30 | 50.034
2023-08-26 | 11:30 | 50.035
2023-08-26 | 11:30 | 50.035
2023-08-26 | 11:30 | 50.033
2023-08-26 | 11:30 | 50.031
2023-08-26 | 11:30 | 50.027
2023-08-26 | 11:30 | 50.027
2023-08-26 | 11:30 | 49.917
2023-08-26 | 11:30 | 49.79
2023-08-26 | 11:30 | 49.716
2023-08-26 | 11:30 | 49.697
2023-08-26 | 11:30 | 49.703
2023-08-26 | 11:30 | 49.713
2023-08-26 | 11:30 | 49.722
2023-08-26 | 11:30 | 49.73
2023-08-26 | 11:30 | 49.737
2023-08-26 | 11:30 | 49.741
2023-08-26 | 11:30 | 49.746
2023-08-26 | 11:30 | 49.749
2023-08-26 | 11:30 | 49.748
2023-08-26 | 11:30 | 49.745
2023-08-26 | 11:30 | 49.745
2023-08-26 | 11:30 | 49.745
2023-08-26 | 11:30 | 49.742
2023-08-26 | 11:31 | 49.741
2023-08-26 | 11:31 | 49.742
2023-08-26 | 11:31 | 49.742
2023-08-26 | 11:31 | 49.745
2023-08-26 | 11:31 | 49.747
2023-08-26 | 11:31 | 49.753
2023-08-26 | 11:31 | 49.755
2023-08-26 | 11:31 | 49.757
2023-08-26 | 11:31 | 49.758
2023-08-26 | 11:31 | 49.762
2023-08-26 | 11:31 | 49.764
2023-08-26 | 11:31 | 49.768
2023-08-26 | 11:31 | 49.771
2023-08-26 | 11:31 | 49.775
2023-08-26 | 11:31 | 49.775
2023-08-26 | 11:31 | 49.774
2023-08-26 | 11:31 | 49.772
2023-08-26 | 11:31 | 49.774
2023-08-26 | 11:31 | 49.772
2023-08-26 | 11:31 | 49.77
2023-08-26 | 11:31 | 49.766
2023-08-26 | 11:31 | 49.763
2023-08-26 | 11:31 | 49.761
2023-08-26 | 11:31 | 49.758
2023-08-26 | 11:31 | 49.758
2023-08-26 | 11:31 | 49.758
2023-08-26 | 11:31 | 49.758
2023-08-26 | 11:31 | 49.759
2023-08-26 | 11:31 | 49.76
2023-08-26 | 11:31 | 49.763
2023-08-26 | 11:31 | 49.763
2023-08-26 | 11:31 | 49.761
2023-08-26 | 11:31 | 49.759
2023-08-26 | 11:31 | 49.758
2023-08-26 | 11:31 | 49.759
2023-08-26 | 11:31 | 49.76
2023-08-26 | 11:31 | 49.763
2023-08-26 | 11:31 | 49.764
2023-08-26 | 11:31 | 49.763
2023-08-26 | 11:31 | 49.762
2023-08-26 | 11:31 | 49.761
2023-08-26 | 11:31 | 49.766
2023-08-26 | 11:31 | 49.765
2023-08-26 | 11:31 | 49.764
2023-08-26 | 11:31 | 49.764
2023-08-26 | 11:31 | 49.763
2023-08-26 | 11:31 | 49.764
2023-08-26 | 11:31 | 49.764
2023-08-26 | 11:31 | 49.764
2023-08-26 | 11:31 | 49.762
2023-08-26 | 11:31 | 49.758
2023-08-26 | 11:31 | 49.759
2023-08-26 | 11:31 | 49.759
2023-08-26 | 11:31 | 49.758
2023-08-26 | 11:31 | 49.758
2023-08-26 | 11:31 | 49.758
2023-08-26 | 11:31 | 49.76
2023-08-26 | 11:31 | 49.762
2023-08-26 | 11:31 | 49.765
2023-08-26 | 11:32 | 49.765
2023-08-26 | 11:32 | 49.762
2023-08-26 | 11:32 | 49.761
2023-08-26 | 11:32 | 49.76
2023-08-26 | 11:32 | 49.76
2023-08-26 | 11:32 | 49.762
2023-08-26 | 11:32 | 49.762
2023-08-26 | 11:32 | 49.763
2023-08-26 | 11:32 | 49.767
2023-08-26 | 11:32 | 49.772
2023-08-26 | 11:32 | 49.773
2023-08-26 | 11:32 | 49.773
2023-08-26 | 11:32 | 49.774
2023-08-26 | 11:32 | 49.778
2023-08-26 | 11:32 | 49.781
2023-08-26 | 11:32 | 49.782
2023-08-26 | 11:32 | 49.785
2023-08-26 | 11:32 | 49.786
2023-08-26 | 11:32 | 49.785
2023-08-26 | 11:32 | 49.785
2023-08-26 | 11:32 | 49.786
2023-08-26 | 11:32 | 49.787
2023-08-26 | 11:32 | 49.787
2023-08-26 | 11:32 | 49.787
2023-08-26 | 11:32 | 49.787
2023-08-26 | 11:32 | 49.786
2023-08-26 | 11:32 | 49.784
2023-08-26 | 11:32 | 49.785
2023-08-26 | 11:32 | 49.786
2023-08-26 | 11:32 | 49.786
2023-08-26 | 11:32 | 49.785
2023-08-26 | 11:32 | 49.781
2023-08-26 | 11:32 | 49.779
2023-08-26 | 11:32 | 49.777
2023-08-26 | 11:32 | 49.772
2023-08-26 | 11:32 | 49.772
2023-08-26 | 11:32 | 49.773
2023-08-26 | 11:32 | 49.772
2023-08-26 | 11:32 | 49.774
2023-08-26 | 11:32 | 49.776
2023-08-26 | 11:32 | 49.777
2023-08-26 | 11:32 | 49.776
2023-08-26 | 11:32 | 49.774
2023-08-26 | 11:32 | 49.774
2023-08-26 | 11:32 | 49.775
2023-08-26 | 11:32 | 49.776
2023-08-26 | 11:32 | 49.776
2023-08-26 | 11:32 | 49.774
2023-08-26 | 11:32 | 49.771
2023-08-26 | 11:32 | 49.765
2023-08-26 | 11:32 | 49.763
2023-08-26 | 11:32 | 49.764
2023-08-26 | 11:32 | 49.767
2023-08-26 | 11:32 | 49.77
2023-08-26 | 11:32 | 49.769
2023-08-26 | 11:32 | 49.768
2023-08-26 | 11:32 | 49.766
2023-08-26 | 11:32 | 49.765
2023-08-26 | 11:32 | 49.765
2023-08-26 | 11:32 | 49.764
2023-08-26 | 11:32 | 49.764
2023-08-26 | 11:33 | 49.761
2023-08-26 | 11:33 | 49.757
2023-08-26 | 11:33 | 49.754
2023-08-26 | 11:33 | 49.75
2023-08-26 | 11:33 | 49.747
2023-08-26 | 11:33 | 49.746
2023-08-26 | 11:33 | 49.748
2023-08-26 | 11:33 | 49.75
2023-08-26 | 11:33 | 49.751
2023-08-26 | 11:33 | 49.754
2023-08-26 | 11:33 | 49.76
2023-08-26 | 11:33 | 49.765
2023-08-26 | 11:33 | 49.765
2023-08-26 | 11:33 | 49.766
2023-08-26 | 11:33 | 49.769
2023-08-26 | 11:33 | 49.773
2023-08-26 | 11:33 | 49.772
2023-08-26 | 11:33 | 49.773
2023-08-26 | 11:33 | 49.773
2023-08-26 | 11:33 | 49.771
2023-08-26 | 11:33 | 49.772
2023-08-26 | 11:33 | 49.776
2023-08-26 | 11:33 | 49.777
2023-08-26 | 11:33 | 49.773
2023-08-26 | 11:33 | 49.771
2023-08-26 | 11:33 | 49.772
2023-08-26 | 11:33 | 49.773
2023-08-26 | 11:33 | 49.772
2023-08-26 | 11:33 | 49.772
2023-08-26 | 11:33 | 49.774
2023-08-26 | 11:33 | 49.772
2023-08-26 | 11:33 | 49.773
2023-08-26 | 11:33 | 49.771
2023-08-26 | 11:33 | 49.774
2023-08-26 | 11:33 | 49.778
2023-08-26 | 11:33 | 49.782
2023-08-26 | 11:33 | 49.786
2023-08-26 | 11:33 | 49.788
2023-08-26 | 11:33 | 49.785
2023-08-26 | 11:33 | 49.783
2023-08-26 | 11:33 | 49.782
2023-08-26 | 11:33 | 49.783
2023-08-26 | 11:33 | 49.782
2023-08-26 | 11:33 | 49.781
2023-08-26 | 11:33 | 49.781
2023-08-26 | 11:33 | 49.78
2023-08-26 | 11:33 | 49.778
2023-08-26 | 11:33 | 49.778
2023-08-26 | 11:33 | 49.779
2023-08-26 | 11:33 | 49.777
2023-08-26 | 11:33 | 49.777
2023-08-26 | 11:33 | 49.774
2023-08-26 | 11:33 | 49.775
2023-08-26 | 11:33 | 49.772
2023-08-26 | 11:33 | 49.767
2023-08-26 | 11:33 | 49.767
2023-08-26 | 11:33 | 49.768
2023-08-26 | 11:33 | 49.772
2023-08-26 | 11:33 | 49.773
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.776
2023-08-26 | 11:34 | 49.778
2023-08-26 | 11:34 | 49.779
2023-08-26 | 11:34 | 49.777
2023-08-26 | 11:34 | 49.776
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.772
2023-08-26 | 11:34 | 49.773
2023-08-26 | 11:34 | 49.774
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.776
2023-08-26 | 11:34 | 49.777
2023-08-26 | 11:34 | 49.773
2023-08-26 | 11:34 | 49.773
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.774
2023-08-26 | 11:34 | 49.773
2023-08-26 | 11:34 | 49.772
2023-08-26 | 11:34 | 49.774
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.773
2023-08-26 | 11:34 | 49.774
2023-08-26 | 11:34 | 49.774
2023-08-26 | 11:34 | 49.774
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.774
2023-08-26 | 11:34 | 49.772
2023-08-26 | 11:34 | 49.769
2023-08-26 | 11:34 | 49.771
2023-08-26 | 11:34 | 49.771
2023-08-26 | 11:34 | 49.77
2023-08-26 | 11:34 | 49.769
2023-08-26 | 11:34 | 49.771
2023-08-26 | 11:34 | 49.771
2023-08-26 | 11:34 | 49.773
2023-08-26 | 11:34 | 49.774
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.773
2023-08-26 | 11:34 | 49.775
2023-08-26 | 11:34 | 49.777
2023-08-26 | 11:34 | 49.777
2023-08-26 | 11:34 | 49.778
2023-08-26 | 11:34 | 49.785
2023-08-26 | 11:34 | 49.79
2023-08-26 | 11:34 | 49.792
2023-08-26 | 11:34 | 49.793
2023-08-26 | 11:34 | 49.793
2023-08-26 | 11:34 | 49.794
2023-08-26 | 11:34 | 49.794
2023-08-26 | 11:34 | 49.795
2023-08-26 | 11:34 | 49.795
2023-08-26 | 11:34 | 49.792
2023-08-26 | 11:34 | 49.79
2023-08-26 | 11:34 | 49.791
2023-08-26 | 11:34 | 49.792
2023-08-26 | 11:34 | 49.794
2023-08-26 | 11:35 | 49.795
2023-08-26 | 11:35 | 49.796
2023-08-26 | 11:35 | 49.798
2023-08-26 | 11:35 | 49.798
2023-08-26 | 11:35 | 49.8
2023-08-26 | 11:35 | 49.803
2023-08-26 | 11:35 | 49.806
2023-08-26 | 11:35 | 49.808
2023-08-26 | 11:35 | 49.805
2023-08-26 | 11:35 | 49.803
2023-08-26 | 11:35 | 49.801
2023-08-26 | 11:35 | 49.801
2023-08-26 | 11:35 | 49.805
2023-08-26 | 11:35 | 49.812
2023-08-26 | 11:35 | 49.816
2023-08-26 | 11:35 | 49.818
2023-08-26 | 11:35 | 49.821
2023-08-26 | 11:35 | 49.825
2023-08-26 | 11:35 | 49.827
2023-08-26 | 11:35 | 49.83
2023-08-26 | 11:35 | 49.832
2023-08-26 | 11:35 | 49.835
2023-08-26 | 11:35 | 49.837
2023-08-26 | 11:35 | 49.836
2023-08-26 | 11:35 | 49.834
2023-08-26 | 11:35 | 49.835
2023-08-26 | 11:35 | 49.835
2023-08-26 | 11:35 | 49.833
2023-08-26 | 11:35 | 49.834
2023-08-26 | 11:35 | 49.837
2023-08-26 | 11:35 | 49.842
2023-08-26 | 11:35 | 49.846
2023-08-26 | 11:35 | 49.85
2023-08-26 | 11:35 | 49.855
2023-08-26 | 11:35 | 49.856
2023-08-26 | 11:35 | 49.852
2023-08-26 | 11:35 | 49.853
2023-08-26 | 11:35 | 49.856
2023-08-26 | 11:35 | 49.857
2023-08-26 | 11:35 | 49.854
2023-08-26 | 11:35 | 49.85
2023-08-26 | 11:35 | 49.849
2023-08-26 | 11:35 | 49.848
2023-08-26 | 11:35 | 49.847
2023-08-26 | 11:35 | 49.847
2023-08-26 | 11:35 | 49.848
2023-08-26 | 11:35 | 49.848
2023-08-26 | 11:35 | 49.848
2023-08-26 | 11:35 | 49.851
2023-08-26 | 11:35 | 49.853
2023-08-26 | 11:35 | 49.854
2023-08-26 | 11:35 | 49.855
2023-08-26 | 11:35 | 49.861
2023-08-26 | 11:35 | 49.867
2023-08-26 | 11:35 | 49.869
2023-08-26 | 11:35 | 49.875
2023-08-26 | 11:35 | 49.881
2023-08-26 | 11:35 | 49.885
2023-08-26 | 11:35 | 49.888
2023-08-26 | 11:36 | 49.889
2023-08-26 | 11:36 | 49.89
2023-08-26 | 11:36 | 49.893
2023-08-26 | 11:36 | 49.892
2023-08-26 | 11:36 | 49.893
2023-08-26 | 11:36 | 49.894
2023-08-26 | 11:36 | 49.896
2023-08-26 | 11:36 | 49.895
2023-08-26 | 11:36 | 49.897
2023-08-26 | 11:36 | 49.896
2023-08-26 | 11:36 | 49.896
2023-08-26 | 11:36 | 49.896
2023-08-26 | 11:36 | 49.9
2023-08-26 | 11:36 | 49.904
2023-08-26 | 11:36 | 49.908
2023-08-26 | 11:36 | 49.909
2023-08-26 | 11:36 | 49.911
2023-08-26 | 11:36 | 49.911
2023-08-26 | 11:36 | 49.917
2023-08-26 | 11:36 | 49.926
2023-08-26 | 11:36 | 49.932
2023-08-26 | 11:36 | 49.939
2023-08-26 | 11:36 | 49.944
2023-08-26 | 11:36 | 49.948
2023-08-26 | 11:36 | 49.95
2023-08-26 | 11:36 | 49.952
2023-08-26 | 11:36 | 49.954
2023-08-26 | 11:36 | 49.954
2023-08-26 | 11:36 | 49.954
2023-08-26 | 11:36 | 49.955
2023-08-26 | 11:36 | 49.954
2023-08-26 | 11:36 | 49.952
2023-08-26 | 11:36 | 49.95
2023-08-26 | 11:36 | 49.951
2023-08-26 | 11:36 | 49.952
2023-08-26 | 11:36 | 49.958
2023-08-26 | 11:36 | 49.962
2023-08-26 | 11:36 | 49.964
2023-08-26 | 11:36 | 49.962
2023-08-26 | 11:36 | 49.961
2023-08-26 | 11:36 | 49.962
2023-08-26 | 11:36 | 49.963
2023-08-26 | 11:36 | 49.964
2023-08-26 | 11:36 | 49.965
2023-08-26 | 11:36 | 49.97
2023-08-26 | 11:36 | 49.971
2023-08-26 | 11:36 | 49.972
2023-08-26 | 11:36 | 49.971
2023-08-26 | 11:36 | 49.973
2023-08-26 | 11:36 | 49.974
2023-08-26 | 11:36 | 49.976
2023-08-26 | 11:36 | 49.977
2023-08-26 | 11:36 | 49.978
2023-08-26 | 11:36 | 49.981
2023-08-26 | 11:36 | 49.98
2023-08-26 | 11:36 | 49.98
2023-08-26 | 11:36 | 49.981
2023-08-26 | 11:36 | 49.981
2023-08-26 | 11:36 | 49.984
2023-08-26 | 11:36 | 49.989
2023-08-26 | 11:36 | 49.993
2023-08-26 | 11:37 | 49.997
2023-08-26 | 11:37 | 50.001
2023-08-26 | 11:37 | 50.004
2023-08-26 | 11:37 | 50.005
2023-08-26 | 11:37 | 50.002
2023-08-26 | 11:37 | 49.998
2023-08-26 | 11:37 | 49.998
2023-08-26 | 11:37 | 49.997
2023-08-26 | 11:37 | 49.996
2023-08-26 | 11:37 | 49.997
2023-08-26 | 11:37 | 49.999
2023-08-26 | 11:37 | 50.001
2023-08-26 | 11:37 | 50.001
2023-08-26 | 11:37 | 50.002
2023-08-26 | 11:37 | 50.004
2023-08-26 | 11:37 | 50.008
2023-08-26 | 11:37 | 50.012
2023-08-26 | 11:37 | 50.018
2023-08-26 | 11:37 | 50.021
2023-08-26 | 11:37 | 50.019
2023-08-26 | 11:37 | 50.015
2023-08-26 | 11:37 | 50.015
2023-08-26 | 11:37 | 50.014
2023-08-26 | 11:37 | 50.016
2023-08-26 | 11:37 | 50.016
2023-08-26 | 11:37 | 50.015
2023-08-26 | 11:37 | 50.014
2023-08-26 | 11:37 | 50.014
2023-08-26 | 11:37 | 50.018
2023-08-26 | 11:37 | 50.023
2023-08-26 | 11:37 | 50.027
2023-08-26 | 11:37 | 50.028
2023-08-26 | 11:37 | 50.028
2023-08-26 | 11:37 | 50.029
2023-08-26 | 11:37 | 50.029
2023-08-26 | 11:37 | 50.027
2023-08-26 | 11:37 | 50.029
2023-08-26 | 11:37 | 50.036
2023-08-26 | 11:37 | 50.044
2023-08-26 | 11:37 | 50.05
2023-08-26 | 11:37 | 50.053
2023-08-26 | 11:37 | 50.055
2023-08-26 | 11:37 | 50.055
2023-08-26 | 11:37 | 50.054
2023-08-26 | 11:37 | 50.052
2023-08-26 | 11:37 | 50.053
2023-08-26 | 11:37 | 50.051
2023-08-26 | 11:37 | 50.048
2023-08-26 | 11:37 | 50.045
2023-08-26 | 11:37 | 50.043
2023-08-26 | 11:37 | 50.037
2023-08-26 | 11:37 | 50.032
2023-08-26 | 11:37 | 50.026
2023-08-26 | 11:37 | 50.022
2023-08-26 | 11:37 | 50.022
2023-08-26 | 11:37 | 50.026
2023-08-26 | 11:37 | 50.03
2023-08-26 | 11:37 | 50.032
2023-08-26 | 11:37 | 50.031
2023-08-26 | 11:38 | 50.033
2023-08-26 | 11:38 | 50.036
2023-08-26 | 11:38 | 50.039
2023-08-26 | 11:38 | 50.04
2023-08-26 | 11:38 | 50.04
2023-08-26 | 11:38 | 50.038
2023-08-26 | 11:38 | 50.036
2023-08-26 | 11:38 | 50.034
2023-08-26 | 11:38 | 50.034
2023-08-26 | 11:38 | 50.035
2023-08-26 | 11:38 | 50.033
2023-08-26 | 11:38 | 50.032
2023-08-26 | 11:38 | 50.031
2023-08-26 | 11:38 | 50.034
2023-08-26 | 11:38 | 50.037
2023-08-26 | 11:38 | 50.039
2023-08-26 | 11:38 | 50.039
2023-08-26 | 11:38 | 50.041
2023-08-26 | 11:38 | 50.042
2023-08-26 | 11:38 | 50.04
2023-08-26 | 11:38 | 50.043
2023-08-26 | 11:38 | 50.046
2023-08-26 | 11:38 | 50.048
2023-08-26 | 11:38 | 50.048
2023-08-26 | 11:38 | 50.049
2023-08-26 | 11:38 | 50.049
2023-08-26 | 11:38 | 50.048
2023-08-26 | 11:38 | 50.05
2023-08-26 | 11:38 | 50.053
2023-08-26 | 11:38 | 50.054