## Contents
Introduction
The workbook contains all graphs and data from our 2023 Winter Outlook publication. The Winter Outlook can be downloaded from the National Grid ESO website. (Publication 28th Sep 2023)
Chart Contents
| Figure Title | Figure
Base Case | Supply margin in relation to generation capacity and demand | Figure 1
| Day-by-day view of operational surplus for winter 2023/24 | Figure 2
| Range of outcomes for de-rated margin winter 2023/24 for the base case under different supply and demand scenarios | Figure 3
| Historic de-rated margin forecasts ahead of each winter in the Winter Outlook Report | Figure 4
| Range of outcomes for de-rated margin winter 2023/24 and 2022/23 | Figure 5
Winter Scenarios | Range of outcomes for de-rated margin winter 2023/24 for a reduced supplies scenario | Figure 6
Demand | Historical and forecast normalised daily peak winter demand | Figure 7
Supply | Daily generation availability by fuel type (based on market submissions and including breakdown rates) | Figure 8
Europe and interconnected markets | Historical flows on the interconnectors for winter 2022/23 | Figure 9
| Capacity Market agreements for interconnectors in Delivery Year 2023/24 | Figure 10
| Electricity forward price spreads Winter 2023/24 compared to Winter 2022/23 | Figure 11
| Winter 2023/24 electricity peak forward prices | Figure 12
| Winter 2023/24 electricity baseload forward prices | Figure 12b
| French nuclear capacity from planned outages in 2023/24 and actuals from a range of previous winters | Figure 13
Market Prices | How the expectations of winter prices have changed in the preceeding months (previous winters compared) | Figure 14

## Figure 1
Figure 1 - Supply margin in relation to generation capacity and demand
Chart label | De-rated margin of 4.4 GW (7.4%)
Table 1 | Supply margin in relation to generation capacity and demand
Category | Technical capability (generation) | De-rated generation capacity | ACS peak underlying demand | De-rated capacity margin (GW) | De-rated capacity margin (%)
Nuclear | 6075 | 4738.6336
Thermal | 40391.957 | 36963.2479
Renewable | 52884.2706 | 12727.8878
Storage | 7461.572 | 4018.7417
Other | 1526.3379 | 1206.1732
Interconnector Imports | 8400 | 5092
Demand |  |  | 58500
Operating reserve |  |  | 1800
| 116739.1374 | 64746.6842 | 60300 | 4446.6842 | 7.374%
Table 2 | Generation Capacities and Derating Factors
| Type | De-rating Factor or Wind EFC (%) | Installed Capacity (MW) | De-rated Capacity (MW)
| Biomass | 88.52% | 4450.6037 | 3867.2807
| Waste (incl. ACT, AD, Biogas, Sewage) | Various | 3500.7441 | 2699.3599
| Coal | 79.33% | 1988 | 1577.1457
| Gas - CCGT | 91.59% | 27020 | 24747.0299
| Gas - CHP | 92.28% | 3680.8866 | 3371.362
| Gas - Reciprocating Engines | 94.35% | 2879.7303 | 2716.9745
| Diesel - Reciprocating Engines | 94.35% | 1691.1951 | 1595.6126
| Nuclear | 78% | 6075 | 4738.6336
| OCGT | 94.35% | 3132.145 | 2955.1233
| Storage - Battery | 53.86% | 4717.572 | 2540.8457
| Storage - Pumped | 53.86% | 2744 | 1477.896
| Hydro | 91.2% | 1921.5253 | 1752.4914
| Solar | 0% | 14740.7472 | 0
| Marine | 22% | 30.708 | 6.7558
| Wind - Offshore | 15.59% | 14502.7 | 2260.6592
| Wind - Onshore | 15.59% | 13737.2423 | 2141.3408
| DSR | 79.02% | 1526.3379 | 1206.1732
Total Generation |  |  | 108339.1374 | 59654.6842

## Figure 2
Figure 2 - Day-by-day view of operational surplus for winter 2023/24
| Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun
Date | 2023-10-30 | 2023-10-31 | 2023-11-01 | 2023-11-02 | 2023-11-03 | 2023-11-04 | 2023-11-05 | 2023-11-06 | 2023-11-07 | 2023-11-08 | 2023-11-09 | 2023-11-10 | 2023-11-11 | 2023-11-12 | 2023-11-13 | 2023-11-14 | 2023-11-15 | 2023-11-16 | 2023-11-17 | 2023-11-18 | 2023-11-19 | 2023-11-20 | 2023-11-21 | 2023-11-22 | 2023-11-23 | 2023-11-24 | 2023-11-25 | 2023-11-26 | 2023-11-27 | 2023-11-28 | 2023-11-29 | 2023-11-30 | 2023-12-01 | 2023-12-02 | 2023-12-03 | 2023-12-04 | 2023-12-05 | 2023-12-06 | 2023-12-07 | 2023-12-08 | 2023-12-09 | 2023-12-10 | 2023-12-11 | 2023-12-12 | 2023-12-13 | 2023-12-14 | 2023-12-15 | 2023-12-16 | 2023-12-17 | 2023-12-18 | 2023-12-19 | 2023-12-20 | 2023-12-21 | 2023-12-22 | 2023-12-23 | 2023-12-24 | 2023-12-25 | 2023-12-26 | 2023-12-27 | 2023-12-28 | 2023-12-29 | 2023-12-30 | 2023-12-31 | 2024-01-01 | 2024-01-02 | 2024-01-03 | 2024-01-04 | 2024-01-05 | 2024-01-06 | 2024-01-07 | 2024-01-08 | 2024-01-09 | 2024-01-10 | 2024-01-11 | 2024-01-12 | 2024-01-13 | 2024-01-14 | 2024-01-15 | 2024-01-16 | 2024-01-17 | 2024-01-18 | 2024-01-19 | 2024-01-20 | 2024-01-21 | 2024-01-22 | 2024-01-23 | 2024-01-24 | 2024-01-25 | 2024-01-26 | 2024-01-27 | 2024-01-28 | 2024-01-29 | 2024-01-30 | 2024-01-31 | 2024-02-01 | 2024-02-02 | 2024-02-03 | 2024-02-04 | 2024-02-05 | 2024-02-06 | 2024-02-07 | 2024-02-08 | 2024-02-09 | 2024-02-10 | 2024-02-11 | 2024-02-12 | 2024-02-13 | 2024-02-14 | 2024-02-15 | 2024-02-16 | 2024-02-17 | 2024-02-18 | 2024-02-19 | 2024-02-20 | 2024-02-21 | 2024-02-22 | 2024-02-23 | 2024-02-24 | 2024-02-25 | 2024-02-26 | 2024-02-27 | 2024-02-28 | 2024-02-29 | 2024-03-01 | 2024-03-02 | 2024-03-03 | 2024-03-04 | 2024-03-05 | 2024-03-06 | 2024-03-07 | 2024-03-08 | 2024-03-09 | 2024-03-10 | 2024-03-11 | 2024-03-12 | 2024-03-13 | 2024-03-14 | 2024-03-15 | 2024-03-16 | 2024-03-17 | 2024-03-18 | 2024-03-19 | 2024-03-20 | 2024-03-21 | 2024-03-22 | 2024-03-23 | 2024-03-24 | 2024-03-25 | 2024-03-26 | 2024-03-27 | 2024-03-28 | 2024-03-29 | 2024-03-30 | 2024-03-31
Max normalised national demand (plus station load, no triad avoidance) | 38652 | 38744 | 38902 | 38929 | 37843 | 34881 | 36080 | 39751 | 39851 | 40025 | 39848 | 38563 | 35489 | 36695 | 40300 | 40325 | 40444 | 40345 | 39331 | 36448 | 37752 | 41467 | 41671 | 41800 | 41521 | 40243 | 37080 | 38187 | 41709 | 41862 | 42018 | 41896 | 40686 | 37668 | 38846 | 42383 | 42447 | 42532 | 42376 | 41134 | 38050 | 39210 | 42761 | 42847 | 42947 | 42780 | 41479 | 38368 | 39502 | 42976 | 43063 | 43100 | 42866 | 38386 | 35369 | 33300 | 30006 | 29885 | 36605 | 37462 | 36998 | 35254 | 35009 | 33542 | 42236 | 43041 | 42899 | 41533 | 38355 | 39442 | 42950 | 43150 | 43250 | 43350 | 40961 | 37885 | 39044 | 42850 | 43050 | 43350 | 43150 | 42350 | 38337 | 39510 | 43039 | 43012 | 42956 | 42628 | 41268 | 38188 | 39205 | 42694 | 42679 | 42659 | 42241 | 40783 | 37527 | 38535 | 42000 | 41980 | 42025 | 41779 | 40487 | 37307 | 38301 | 41713 | 41636 | 41432 | 40941 | 39272 | 36115 | 37353 | 40846 | 40775 | 40716 | 40388 | 39056 | 35880 | 36927 | 40331 | 40363 | 40425 | 40184 | 38861 | 35720 | 36815 | 40136 | 39906 | 39673 | 39221 | 37875 | 34633 | 35529 | 39057 | 38937 | 38711 | 38295 | 36895 | 33826 | 35019 | 38453 | 38477 | 38353 | 37887 | 36403 | 33063 | 34086 | 37506 | 37577 | 36724 | 34960 | 31138 | 32532 | 31225
Assumed transmission generation with CM imports from Continental Europe and 750MW export to Ireland | 46792 | 47213 | 47414 | 47414 | 47414 | 46801 | 47414 | 47154 | 47483 | 47483 | 47483 | 47547 | 47141 | 48115 | 48115 | 48904 | 48904 | 48904 | 48904 | 48338 | 48951 | 48951 | 48951 | 49308 | 48741 | 48747 | 48134 | 48747 | 48747 | 48747 | 48747 | 48988 | 49300 | 48476 | 49089 | 49394 | 49394 | 49732 | 49732 | 49732 | 48814 | 49607 | 50042 | 50339 | 50728 | 50728 | 50728 | 49810 | 50422 | 50728 | 50728 | 50728 | 50728 | 50743 | 50131 | 50743 | 50743 | 50743 | 50743 | 50743 | 50743 | 50131 | 50748 | 50748 | 50748 | 50748 | 50111 | 50111 | 49498 | 49967 | 49608 | 49608 | 49608 | 49608 | 48818 | 47672 | 48285 | 49059 | 49059 | 49059 | 49059 | 49065 | 48693 | 49615 | 49796 | 49970 | 50011 | 50119 | 50119 | 49625 | 50385 | 50464 | 50543 | 50652 | 50492 | 50492 | 49879 | 50492 | 50492 | 50492 | 50492 | 50492 | 50517 | 49556 | 50169 | 50169 | 50169 | 49949 | 49949 | 49239 | 48627 | 49239 | 49949 | 49385 | 49385 | 49893 | 49893 | 49280 | 49893 | 49893 | 49893 | 49893 | 50056 | 49604 | 48814 | 49426 | 50440 | 50440 | 50440 | 50440 | 50460 | 49848 | 50460 | 49890 | 49890 | 49890 | 49890 | 49910 | 48860 | 49473 | 48884 | 48884 | 48884 | 48878 | 48878 | 47732 | 48345 | 48060 | 48060 | 48060 | 48060 | 48060 | 47317 | 48187
Reserve requirement | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800
Max normalised national demand (plus station load, no triad avoidance) | 38653 | 38745 | 38903 | 38929 | 37844 | 34882 | 36081 | 39752 | 39852 | 40026 | 39849 | 38563 | 35490 | 36695 | 40301 | 40326 | 40445 | 40345 | 39332 | 36448 | 37753 | 41468 | 41671 | 41801 | 41522 | 40243 | 37081 | 38187 | 41709 | 41863 | 42018 | 41897 | 40687 | 37669 | 38847 | 42383 | 42447 | 42533 | 42376 | 41135 | 38051 | 39211 | 42761 | 42847 | 42948 | 42780 | 41480 | 38369 | 39503 | 42976 | 43063 | 43100 | 42866 | 38386 | 35369 | 33300 | 30006 | 29885 | 36605 | 37462 | 36998 | 35254 | 35009 | 33542 | 42236 | 43041 | 42899 | 41533 | 38355 | 39442 | 42879 | 42828 | 42759 | 42384 | 40961 | 37885 | 39044 | 42636 | 42717 | 42858 | 42635 | 41338 | 38337 | 39510 | 43039 | 43012 | 42956 | 42628 | 41268 | 38188 | 39205 | 42694 | 42679 | 42659 | 42241 | 40783 | 37527 | 38535 | 42000 | 41980 | 42025 | 41779 | 40487 | 37307 | 38301 | 41713 | 41636 | 41432 | 40941 | 39272 | 36115 | 37353 | 40846 | 40775 | 40716 | 40388 | 39056 | 35880 | 36927 | 40331 | 40363 | 40425 | 40184 | 38861 | 35720 | 36815 | 40136 | 39906 | 39673 | 39221 | 37875 | 34633 | 35529 | 39057 | 38937 | 38711 | 38295 | 36895 | 33826 | 35019 | 38453 | 38477 | 38353 | 37887 | 36403 | 33063 | 34086 | 37506 | 37577 | 36724 | 34960 | 31138 | 32532 | 31225
ACS national demand (plus station load and including reserve requirement) | Mon: 48200; Tue: 48200; Wed: 48200; Thu: 48200; Fri: 48200; Mon: 48200; Tue: 48200; Wed: 48200; Thu: 48200; Fri: 48200; Mon: 48200; Tue: 48200; Wed: 48200; Thu: 48200; Fri: 48200; Mon: 48200; Tue: 48200; Wed: 48200; Thu: 48200; Fri: 48200; Mon: 48200; Tue: 48200; Wed: 48200; Thu: 48200; Fri: 48200; Mon: 48200; Tue: 48200; Wed: 48200; Thu: 48200; Fri: 48200; Mon: 48200; Tue: 48200; Wed: 48200; Thu: 48200; Fri: 48200; Mon: 48200; Tue: 48200; Wed: 48200; Thu: 48200; Fri: 48200
Operational Surplus (for Figure 3) | 6340 | 6669 | 6712 | 6685 | 7771 | 10120 | 9534 | 5603 | 5832 | 5658 | 5835 | 7184 | 9852 | 9620 | 6015 | 6779 | 6660 | 6759 | 7773 | 10090 | 9399 | 5684 | 5480 | 5708 | 5420 | 6704 | 9254 | 8760 | 5238 | 5085 | 4929 | 5292 | 6814 | 9008 | 8443 | 5211 | 5147 | 5400 | 5556 | 6798 | 8964 | 8597 | 5481 | 5692 | 5981 | 6148 | 7449 | 9642 | 9120 | 5952 | 5865 | 5828 | 6062 | 10557 | 12962 | 15643 | 18937 | 19058 | 12338 | 11481 | 11945 | 13077 | 13939 | 15406 | 6712 | 5907 | 5412 | 6778 | 9343 | 8725 | 4858 | 4658 | 4558 | 4458 | 6057 | 7987 | 7441 | 4409 | 4209 | 3909 | 4109 | 4915 | 8556 | 8305 | 4957 | 5158 | 5255 | 5691 | 7051 | 9637 | 9380 | 5970 | 6064 | 6193 | 6451 | 7909 | 10552 | 10157 | 6692 | 6712 | 6667 | 6913 | 8230 | 10449 | 10068 | 6656 | 6733 | 6717 | 7208 | 8167 | 10712 | 10086 | 7303 | 6810 | 6869 | 7705 | 9037 | 11600 | 11166 | 7762 | 7730 | 7668 | 8072 | 8943 | 11294 | 10811 | 8504 | 8734 | 8967 | 9419 | 10785 | 13415 | 13131 | 9033 | 9153 | 9379 | 9795 | 11215 | 13234 | 12654 | 8631 | 8607 | 8731 | 9191 | 10675 | 12869 | 12459 | 8754 | 8683 | 9536 | 11300 | 15122 | 12985 | 15162

## Figure 3
Figure 3 - Range of outcomes for de-rated margin winter 2023/24 for the base case under different supply and demand scenarios
Date | 2023-10-30 | 2023-10-31 | 2023-11-01 | 2023-11-02 | 2023-11-03 | 2023-11-04 | 2023-11-05 | 2023-11-06 | 2023-11-07 | 2023-11-08 | 2023-11-09 | 2023-11-10 | 2023-11-11 | 2023-11-12 | 2023-11-13 | 2023-11-14 | 2023-11-15 | 2023-11-16 | 2023-11-17 | 2023-11-18 | 2023-11-19 | 2023-11-20 | 2023-11-21 | 2023-11-22 | 2023-11-23 | 2023-11-24 | 2023-11-25 | 2023-11-26 | 2023-11-27 | 2023-11-28 | 2023-11-29 | 2023-11-30 | 2023-12-01 | 2023-12-02 | 2023-12-03 | 2023-12-04 | 2023-12-05 | 2023-12-06 | 2023-12-07 | 2023-12-08 | 2023-12-09 | 2023-12-10 | 2023-12-11 | 2023-12-12 | 2023-12-13 | 2023-12-14 | 2023-12-15 | 2023-12-16 | 2023-12-17 | 2023-12-18 | 2023-12-19 | 2023-12-20 | 2023-12-21 | 2023-12-22 | 2023-12-23 | 2023-12-24 | 2023-12-25 | 2023-12-26 | 2023-12-27 | 2023-12-28 | 2023-12-29 | 2023-12-30 | 2023-12-31 | 2024-01-01 | 2024-01-02 | 2024-01-03 | 2024-01-04 | 2024-01-05 | 2024-01-06 | 2024-01-07 | 2024-01-08 | 2024-01-09 | 2024-01-10 | 2024-01-11 | 2024-01-12 | 2024-01-13 | 2024-01-14 | 2024-01-15 | 2024-01-16 | 2024-01-17 | 2024-01-18 | 2024-01-19 | 2024-01-20 | 2024-01-21 | 2024-01-22 | 2024-01-23 | 2024-01-24 | 2024-01-25 | 2024-01-26 | 2024-01-27 | 2024-01-28 | 2024-01-29 | 2024-01-30 | 2024-01-31 | 2024-02-01 | 2024-02-02 | 2024-02-03 | 2024-02-04 | 2024-02-05 | 2024-02-06 | 2024-02-07 | 2024-02-08 | 2024-02-09 | 2024-02-10 | 2024-02-11 | 2024-02-12 | 2024-02-13 | 2024-02-14 | 2024-02-15 | 2024-02-16 | 2024-02-17 | 2024-02-18 | 2024-02-19 | 2024-02-20 | 2024-02-21 | 2024-02-22 | 2024-02-23 | 2024-02-24 | 2024-02-25 | 2024-02-26 | 2024-02-27 | 2024-02-28 | 2024-02-29 | 2024-03-01 | 2024-03-02 | 2024-03-03 | 2024-03-04 | 2024-03-05 | 2024-03-06 | 2024-03-07 | 2024-03-08 | 2024-03-09 | 2024-03-10 | 2024-03-11 | 2024-03-12 | 2024-03-13 | 2024-03-14 | 2024-03-15 | 2024-03-16 | 2024-03-17 | 2024-03-18 | 2024-03-19 | 2024-03-20 | 2024-03-21 | 2024-03-22 | 2024-03-23 | 2024-03-24 | 2024-03-25 | 2024-03-26 | 2024-03-27 | 2024-03-28 | 2024-03-29 | 2024-03-30
Surplus daily credible lower bound | 5671.4358 | 4107.0551 | 4033.6337 | 4055.7214 | 5052.219 | 7467.6442 | 6923.9665 | 3181.3404 | 3507.4478 | 3275.2539 | 3628.1293 | 4663.7701 | 7140.489 | 6732.9321 | 3254.9121 | 3752.422 | 3569.9662 | 3656.4213 | 4843.4424 | 7326.625 | 6624.5674 | 3209.5644 | 3105.9081 | 3268.8516 | 2759.7067 | 3792.498 | 6044.8911 | 5382.952 | 2142.2025 | 2074.3735 | 1963.1004 | 2413.0924 | 3816.319 | 5890.0426 | 5226.7642 | 2276.1552 | 2175.3094 | 2313.6903 | 2305.0029 | 3485.7097 | 5721.1628 | 5212.9394 | 2394.8853 | 2704.3145 | 2855.0007 | 3045.1412 | 4121.3206 | 6138.9254 | 5489.2132 | 2680.1293 | 2607.896 | 2641.8568 | 2776.3977 | 6843.0811 | 8856.5124 | 11417.8737 | 18177.8206 | 14829.0351 | 8412.2923 | 7707.3885 | 8395.7172 | 9347.9101 | 10036.6479 | 11664.6936 | 3523.2848 | 2817.19 | 2261.9119 | 3484.8856 | 5913.4087 | 5374.0125 | 2103.897 | 1996.2077 | 1977.2966 | 2174.4626 | 2402.1559 | 4187.9879 | 3752.8623 | 1509.2988 | 1479.8439 | 1314.5773 | 1603.8659 | 2703.5288 | 5277.2192 | 5147.2923 | 2071.299 | 2070.0236 | 2192.2792 | 2398.6693 | 3574.8857 | 6277.6164 | 6026.5039 | 2919.5976 | 2988.744 | 2926.856 | 3182.4812 | 4322.4013 | 6743.6778 | 6233.8219 | 3055.2302 | 3211.1662 | 3399.6692 | 3678.4929 | 4932.0085 | 7214.5091 | 6704.3769 | 3473.8321 | 3591.7824 | 3517.5051 | 3839.3018 | 4549.9558 | 7131.2925 | 6731.6305 | 4333.0798 | 3960.0921 | 4183.622 | 4920.1208 | 6253.1276 | 8845.8916 | 8560.0043 | 5336.0094 | 5342.8102 | 5497.1143 | 6139.4281 | 7025.6435 | 9391.8648 | 9251.7517 | 6964.7709 | 7117.0952 | 7197.3727 | 7581.9989 | 9105.0881 | 11822.2002 | 11593.016 | 7710.6069 | 7883.0253 | 8190.1773 | 8521.1061 | 9986.1057 | 12092.8353 | 11655.0563 | 7732.666 | 7718.6303 | 7778.0232 | 8184.6132 | 9559.8547 | 11285.886 | 10955.0074 | 7336.1976 | 7336.2529 | 8145.0073 | 9830.7242 | 13613.0668 | 20467.7486
Surplus daily credible upper bound | 16670 | 16541.8523 | 16495.9743 | 16520.6652 | 17276.3742 | 19346.0238 | 18867.6947 | 15316.087 | 15623.8137 | 15578.0728 | 15880.7418 | 16920.7731 | 19312.3547 | 19191.3197 | 15891.9314 | 16770.794 | 16514.6281 | 16716.1589 | 17823.7602 | 19853.3109 | 19336.9546 | 16232.1032 | 16070.8552 | 16513.1856 | 16146.3098 | 17426.6357 | 19482.1067 | 18843.224 | 15733.6032 | 15833.9433 | 15690.3696 | 16255.0908 | 17876.7787 | 19660.1875 | 19250.5583 | 16313.7051 | 16381.3634 | 16693.4851 | 16926.9961 | 17904.2362 | 19588.1091 | 19340.2362 | 16615.5405 | 16963.1127 | 17315.3616 | 17565.2232 | 18426.2982 | 20287.9883 | 19944.4805 | 16997.6137 | 17118.4076 | 17042.3258 | 17197.7372 | 21149.2439 | 23074.2937 | 25601.7226 | 32155.6189 | 28890.2924 | 22964.4941 | 22296.7384 | 22538.9188 | 23536.8896 | 24376.8558 | 26091.6108 | 18227.0117 | 17645.18 | 17113.1643 | 18284.6685 | 20307.6544 | 19933.4643 | 16410.3741 | 16299.9468 | 16401.7453 | 16588.8442 | 17022.9799 | 18560.8905 | 18243.5057 | 15704.3467 | 15695.7976 | 15602.8798 | 15898.5414 | 17064.4793 | 19413.8594 | 19397.8442 | 16532.2367 | 16728.1129 | 16884.8985 | 17329.6927 | 18506.4264 | 20825.2142 | 20732.1448 | 17567.8252 | 17784.8165 | 17955.4947 | 18138.8218 | 19252.2364 | 21501.4322 | 21151.9272 | 18029.1208 | 17877.7533 | 17867.3267 | 18188.4099 | 19324.3867 | 21067.3129 | 20629.3659 | 17463.3173 | 17586.4243 | 17627.9173 | 17955.0711 | 18373.7987 | 20666.3083 | 20308.6828 | 17960.9374 | 17593.8115 | 17652.7573 | 18537.3786 | 19773.8173 | 21984.3866 | 21604.09 | 18601.5077 | 18795.9189 | 18825.4489 | 19271.2578 | 20171.1953 | 22233.5934 | 21910.8217 | 19980.6195 | 20061.9928 | 20098.8902 | 20479.6466 | 21797.7694 | 24049.994 | 23842.7698 | 20122.3232 | 20287.2299 | 20348.2756 | 20697.6578 | 21910.4259 | 23653.9235 | 23232.5227 | 19673.5814 | 19831.5828 | 19950.731 | 20313.1805 | 21440.1312 | 23234.075 | 22942.4236 | 19539.2315 | 19458.2682 | 20262.2278 | 21767.488 | 25374.5223 | 32788.7475
Surplus under average conditions | 10344.9466 | 9766.4087 | 9811.1223 | 9868.2168 | 10772.4071 | 12934.0174 | 12520.3736 | 9037.0453 | 9392.4012 | 9234.1213 | 9547.8975 | 10647.1417 | 13008.5708 | 12820.433 | 9583.0769 | 10257.5016 | 10052.4785 | 10121.8183 | 11263.3918 | 13449.3924 | 12856.2922 | 9600.6411 | 9576.7712 | 9798.7727 | 9333.2148 | 10423.8004 | 12515.1391 | 12038.2652 | 8883.3748 | 8831.0992 | 8719.9891 | 9355.6942 | 10881.8426 | 12847.5939 | 12378.8625 | 9561.3386 | 9456.7609 | 9496.441 | 9678.6148 | 10847.5388 | 12654.452 | 12352.0389 | 9603.5855 | 9780.2996 | 9986.2272 | 10115.9163 | 11086.639 | 12953.2437 | 12453.7883 | 9676.1277 | 9621.9818 | 9506.948 | 9662.5708 | 13615.0945 | 15503.0992 | 18013.4795 | 24576.4906 | 21520.7495 | 15693.8532 | 15078.6704 | 15539.7291 | 16445.4539 | 17151.9298 | 18775.7585 | 10944.891 | 10494.298 | 10036.9352 | 11269.8353 | 13615.4295 | 13196.353 | 9759.4542 | 9718.9308 | 9745.989 | 9962.898 | 10382.7561 | 11894.2889 | 11436.0584 | 9046.2563 | 9077.5678 | 8984.2106 | 9163.2077 | 10296.3542 | 12599.9307 | 12515.6876 | 9570.8201 | 9667.7498 | 9671.951 | 10054.8762 | 11013.6965 | 13464.3092 | 13343.9488 | 10365.7431 | 10560.7539 | 10675.7628 | 10839.0004 | 12081.8049 | 14155.3321 | 13724.0566 | 10573.737 | 10539.2768 | 10722.2643 | 11070.987 | 12152.0146 | 13828.7696 | 13454.6242 | 10321.8654 | 10439.3317 | 10250.8866 | 10662.3262 | 11363.9687 | 13667.5994 | 13423.0923 | 11160.7973 | 10834.3859 | 10865.6067 | 11672.5158 | 12828.3662 | 15081.7831 | 14914.2843 | 11846.0098 | 11952.6475 | 12030.1803 | 12590.9918 | 13414.0676 | 15587.9792 | 15344.799 | 13359.5114 | 13358.2667 | 13422.9216 | 13906.4612 | 15278.3254 | 17634.1341 | 17325.8376 | 13651.1694 | 13801.159 | 13885.5813 | 14227.3485 | 15442.37 | 17267.1958 | 16912.5279 | 13138.279 | 13231.3672 | 13404.8384 | 13714.131 | 14969.1668 | 16604.4968 | 16189.0958 | 12833.0382 | 12911.9818 | 13675.2683 | 15295.1243 | 18834.1661 | 26091.9932
90% confidence bound for daily fluctuations | 10998.5642 | 12434.7973 | 12462.3406 | 12464.9437 | 12224.1552 | 11878.3796 | 11943.7282 | 12134.7466 | 12116.366 | 12302.8189 | 12252.6126 | 12257.0031 | 12171.8658 | 12458.3877 | 12637.0192 | 13018.372 | 12944.6619 | 13059.7377 | 12980.3177 | 12526.6858 | 12712.3872 | 13022.5388 | 12964.9471 | 13244.334 | 13386.6031 | 13634.1377 | 13437.2156 | 13460.272 | 13591.4007 | 13759.5698 | 13727.2692 | 13841.9984 | 14060.4597 | 13770.1449 | 14023.794 | 14037.5499 | 14206.0539 | 14379.7948 | 14621.9932 | 14418.5265 | 13866.9463 | 14127.2968 | 14220.6552 | 14258.7982 | 14460.3609 | 14520.082 | 14304.9776 | 14149.0629 | 14455.2672 | 14317.4844 | 14510.5116 | 14400.469 | 14421.3396 | 14306.1628 | 14217.7813 | 14183.8489 | 13977.7984 | 14061.2573 | 14552.2017 | 14589.3499 | 14143.2016 | 14188.9796 | 14340.2079 | 14426.9172 | 14703.7269 | 14827.99 | 14851.2524 | 14799.7829 | 14394.2457 | 14559.4518 | 14306.4771 | 14303.7392 | 14424.4487 | 14414.3816 | 14620.824 | 14372.9026 | 14490.6434 | 14195.0479 | 14215.9537 | 14288.3025 | 14294.6755 | 14360.9505 | 14136.6402 | 14250.5519 | 14460.9376 | 14658.0893 | 14692.6193 | 14931.0234 | 14931.5407 | 14547.5978 | 14705.6409 | 14648.2276 | 14796.0725 | 15028.6386 | 14956.3406 | 14929.8351 | 14757.7544 | 14918.1053 | 14973.8906 | 14666.5872 | 14467.6575 | 14509.917 | 14392.3782 | 13852.8038 | 13924.989 | 13989.4853 | 13994.6419 | 14110.4122 | 14115.7693 | 13823.8429 | 13535.0159 | 13577.0523 | 13627.8575 | 13633.7194 | 13469.1353 | 13617.2578 | 13520.6897 | 13138.4949 | 13044.0857 | 13265.4983 | 13453.1087 | 13328.3346 | 13131.8297 | 13145.5518 | 12841.7285 | 12659.07 | 13015.8486 | 12944.8976 | 12901.5175 | 12897.6477 | 12692.6813 | 12227.7938 | 12249.7538 | 12411.7162 | 12404.2046 | 12158.0983 | 12176.5516 | 11924.3203 | 11561.0882 | 11577.4664 | 11940.9155 | 12112.9525 | 12172.7077 | 12128.5673 | 11880.2765 | 11948.189 | 11987.4162 | 12203.0339 | 12122.0152 | 12117.2205 | 11936.7638 | 11761.4555 | 12320.9988
Operational Surplus (from Figure 2) | 6340 | 6669 | 6712 | 6685 | 7771 | 10120 | 9534 | 5603 | 5832 | 5658 | 5835 | 7184 | 9852 | 9620 | 6015 | 6779 | 6660 | 6759 | 7773 | 10090 | 9399 | 5684 | 5480 | 5708 | 5420 | 6704 | 9254 | 8760 | 5238 | 5085 | 4929 | 5292 | 6814 | 9008 | 8443 | 5211 | 5147 | 5400 | 5556 | 6798 | 8964 | 8597 | 5481 | 5692 | 5981 | 6148 | 7449 | 9642 | 9120 | 5952 | 5865 | 5828 | 6062 | 10557 | 12962 | 15643 | 18937 | 19058 | 12338 | 11481 | 11945 | 13077 | 13939 | 15406 | 6712 | 5907 | 5412 | 6778 | 9343 | 8725 | 4858 | 4658 | 4558 | 4458 | 6057 | 7987 | 7441 | 4409 | 4209 | 3909 | 4109 | 4915 | 8556 | 8305 | 4957 | 5158 | 5255 | 5691 | 7051 | 9637 | 9380 | 5970 | 6064 | 6193 | 6451 | 7909 | 10552 | 10157 | 6692 | 6712 | 6667 | 6913 | 8230 | 10449 | 10068 | 6656 | 6733 | 6717 | 7208 | 8167 | 10712 | 10086 | 7303 | 6810 | 6869 | 7705 | 9037 | 11600 | 11166 | 7762 | 7730 | 7668 | 8072 | 8943 | 11294 | 10811 | 8504 | 8734 | 8967 | 9419 | 10785 | 13415 | 13131 | 9033 | 9153 | 9379 | 9795 | 11215 | 13234 | 12654 | 8631 | 8607 | 8731 | 9191 | 10675 | 12869 | 12459 | 8754 | 8683 | 9536 | 11300 | 15122 | 12985

## Figure 4
Figure 4 - Historic de-rated margin forecasts ahead of each winter in the Winter Outlook Report
Winter | De-rated margin (%)
2015/16 | 5.1%
2016/17 | 6.6%
2017/18 | 10.3%
2018/19 | 11.7%
2019/20 | 12.9%
2020/21 | 8.3%
2021/22 | 6.6%
2022/23 | 6.3%
2023/24 | 7.374%

## Figure 5
Figure 5 - Range of outcomes for de-rated margin winter 2023/24 and 2022/23
Date | 2023-10-30 | 2023-10-31 | 2023-11-01 | 2023-11-02 | 2023-11-03 | 2023-11-04 | 2023-11-05 | 2023-11-06 | 2023-11-07 | 2023-11-08 | 2023-11-09 | 2023-11-10 | 2023-11-11 | 2023-11-12 | 2023-11-13 | 2023-11-14 | 2023-11-15 | 2023-11-16 | 2023-11-17 | 2023-11-18 | 2023-11-19 | 2023-11-20 | 2023-11-21 | 2023-11-22 | 2023-11-23 | 2023-11-24 | 2023-11-25 | 2023-11-26 | 2023-11-27 | 2023-11-28 | 2023-11-29 | 2023-11-30 | 2023-12-01 | 2023-12-02 | 2023-12-03 | 2023-12-04 | 2023-12-05 | 2023-12-06 | 2023-12-07 | 2023-12-08 | 2023-12-09 | 2023-12-10 | 2023-12-11 | 2023-12-12 | 2023-12-13 | 2023-12-14 | 2023-12-15 | 2023-12-16 | 2023-12-17 | 2023-12-18 | 2023-12-19 | 2023-12-20 | 2023-12-21 | 2023-12-22 | 2023-12-23 | 2023-12-24 | 2023-12-25 | 2023-12-26 | 2023-12-27 | 2023-12-28 | 2023-12-29 | 2023-12-30 | 2023-12-31 | 2024-01-01 | 2024-01-02 | 2024-01-03 | 2024-01-04 | 2024-01-05 | 2024-01-06 | 2024-01-07 | 2024-01-08 | 2024-01-09 | 2024-01-10 | 2024-01-11 | 2024-01-12 | 2024-01-13 | 2024-01-14 | 2024-01-15 | 2024-01-16 | 2024-01-17 | 2024-01-18 | 2024-01-19 | 2024-01-20 | 2024-01-21 | 2024-01-22 | 2024-01-23 | 2024-01-24 | 2024-01-25 | 2024-01-26 | 2024-01-27 | 2024-01-28 | 2024-01-29 | 2024-01-30 | 2024-01-31 | 2024-02-01 | 2024-02-02 | 2024-02-03 | 2024-02-04 | 2024-02-05 | 2024-02-06 | 2024-02-07 | 2024-02-08 | 2024-02-09 | 2024-02-10 | 2024-02-11 | 2024-02-12 | 2024-02-13 | 2024-02-14 | 2024-02-15 | 2024-02-16 | 2024-02-17 | 2024-02-18 | 2024-02-19 | 2024-02-20 | 2024-02-21 | 2024-02-22 | 2024-02-23 | 2024-02-24 | 2024-02-25 | 2024-02-26 | 2024-02-27 | 2024-02-28 | 2024-02-29 | 2024-03-01 | 2024-03-02 | 2024-03-03 | 2024-03-04 | 2024-03-05 | 2024-03-06 | 2024-03-07 | 2024-03-08 | 2024-03-09 | 2024-03-10 | 2024-03-11 | 2024-03-12 | 2024-03-13 | 2024-03-14 | 2024-03-15 | 2024-03-16 | 2024-03-17 | 2024-03-18 | 2024-03-19 | 2024-03-20 | 2024-03-21 | 2024-03-22 | 2024-03-23 | 2024-03-24 | 2024-03-25 | 2024-03-26 | 2024-03-27 | 2024-03-28 | 2024-03-29 | 2024-03-30
Surplus daily credible lower bound 23/24 | 5671.4358 | 4107.0551 | 4033.6337 | 4055.7214 | 5052.219 | 7467.6442 | 6923.9665 | 3181.3404 | 3507.4478 | 3275.2539 | 3628.1293 | 4663.7701 | 7140.489 | 6732.9321 | 3254.9121 | 3752.422 | 3569.9662 | 3656.4213 | 4843.4424 | 7326.625 | 6624.5674 | 3209.5644 | 3105.9081 | 3268.8516 | 2759.7067 | 3792.498 | 6044.8911 | 5382.952 | 2142.2025 | 2074.3735 | 1963.1004 | 2413.0924 | 3816.319 | 5890.0426 | 5226.7642 | 2276.1552 | 2175.3094 | 2313.6903 | 2305.0029 | 3485.7097 | 5721.1628 | 5212.9394 | 2394.8853 | 2704.3145 | 2855.0007 | 3045.1412 | 4121.3206 | 6138.9254 | 5489.2132 | 2680.1293 | 2607.896 | 2641.8568 | 2776.3977 | 6843.0811 | 8856.5124 | 11417.8737 | 18177.8206 | 14829.0351 | 8412.2923 | 7707.3885 | 8395.7172 | 9347.9101 | 10036.6479 | 11664.6936 | 3523.2848 | 2817.19 | 2261.9119 | 3484.8856 | 5913.4087 | 5374.0125 | 2103.897 | 1996.2077 | 1977.2966 | 2174.4626 | 2402.1559 | 4187.9879 | 3752.8623 | 1509.2988 | 1479.8439 | 1314.5773 | 1603.8659 | 2703.5288 | 5277.2192 | 5147.2923 | 2071.299 | 2070.0236 | 2192.2792 | 2398.6693 | 3574.8857 | 6277.6164 | 6026.5039 | 2919.5976 | 2988.744 | 2926.856 | 3182.4812 | 4322.4013 | 6743.6778 | 6233.8219 | 3055.2302 | 3211.1662 | 3399.6692 | 3678.4929 | 4932.0085 | 7214.5091 | 6704.3769 | 3473.8321 | 3591.7824 | 3517.5051 | 3839.3018 | 4549.9558 | 7131.2925 | 6731.6305 | 4333.0798 | 3960.0921 | 4183.622 | 4920.1208 | 6253.1276 | 8845.8916 | 8560.0043 | 5336.0094 | 5342.8102 | 5497.1143 | 6139.4281 | 7025.6435 | 9391.8648 | 9251.7517 | 6964.7709 | 7117.0952 | 7197.3727 | 7581.9989 | 9105.0881 | 11822.2002 | 11593.016 | 7710.6069 | 7883.0253 | 8190.1773 | 8521.1061 | 9986.1057 | 12092.8353 | 11655.0563 | 7732.666 | 7718.6303 | 7778.0232 | 8184.6132 | 9559.8547 | 11285.886 | 10955.0074 | 7336.1976 | 7336.2529 | 8145.0073 | 9830.7242 | 13613.0668 | 20467.7486
Surplus daily credible upper bound 23/24 | 16670 | 16541.8523 | 16495.9743 | 16520.6652 | 17276.3742 | 19346.0238 | 18867.6947 | 15316.087 | 15623.8137 | 15578.0728 | 15880.7418 | 16920.7731 | 19312.3547 | 19191.3197 | 15891.9314 | 16770.794 | 16514.6281 | 16716.1589 | 17823.7602 | 19853.3109 | 19336.9546 | 16232.1032 | 16070.8552 | 16513.1856 | 16146.3098 | 17426.6357 | 19482.1067 | 18843.224 | 15733.6032 | 15833.9433 | 15690.3696 | 16255.0908 | 17876.7787 | 19660.1875 | 19250.5583 | 16313.7051 | 16381.3634 | 16693.4851 | 16926.9961 | 17904.2362 | 19588.1091 | 19340.2362 | 16615.5405 | 16963.1127 | 17315.3616 | 17565.2232 | 18426.2982 | 20287.9883 | 19944.4805 | 16997.6137 | 17118.4076 | 17042.3258 | 17197.7372 | 21149.2439 | 23074.2937 | 25601.7226 | 32155.6189 | 28890.2924 | 22964.4941 | 22296.7384 | 22538.9188 | 23536.8896 | 24376.8558 | 26091.6108 | 18227.0117 | 17645.18 | 17113.1643 | 18284.6685 | 20307.6544 | 19933.4643 | 16410.3741 | 16299.9468 | 16401.7453 | 16588.8442 | 17022.9799 | 18560.8905 | 18243.5057 | 15704.3467 | 15695.7976 | 15602.8798 | 15898.5414 | 17064.4793 | 19413.8594 | 19397.8442 | 16532.2367 | 16728.1129 | 16884.8985 | 17329.6927 | 18506.4264 | 20825.2142 | 20732.1448 | 17567.8252 | 17784.8165 | 17955.4947 | 18138.8218 | 19252.2364 | 21501.4322 | 21151.9272 | 18029.1208 | 17877.7533 | 17867.3267 | 18188.4099 | 19324.3867 | 21067.3129 | 20629.3659 | 17463.3173 | 17586.4243 | 17627.9173 | 17955.0711 | 18373.7987 | 20666.3083 | 20308.6828 | 17960.9374 | 17593.8115 | 17652.7573 | 18537.3786 | 19773.8173 | 21984.3866 | 21604.09 | 18601.5077 | 18795.9189 | 18825.4489 | 19271.2578 | 20171.1953 | 22233.5934 | 21910.8217 | 19980.6195 | 20061.9928 | 20098.8902 | 20479.6466 | 21797.7694 | 24049.994 | 23842.7698 | 20122.3232 | 20287.2299 | 20348.2756 | 20697.6578 | 21910.4259 | 23653.9235 | 23232.5227 | 19673.5814 | 19831.5828 | 19950.731 | 20313.1805 | 21440.1312 | 23234.075 | 22942.4236 | 19539.2315 | 19458.2682 | 20262.2278 | 21767.488 | 25374.5223 | 32788.7475
Surplus daily credible lower bound 22/23 |  | 6281 | 3848 | 3696 | 3537 | 4611 | 7154 | 6747 | 3295 | 3153 | 3013 | 3039 | 4001 | 5167 | 5266 | 2870 | 2948 | 3198 | 3077 | 4197 | 5487 | 5344 | 2741 | 2511 | 2509 | 2354 | 3389 | 4435 | 4322 | 869 | 782 | 675 | 1101 | 2148 | 2554 | 2435 | 612 | 518 | 439 | -484 | -50 | 2390 | 2408 | -154 | -298 | -164 | 122 | 1721 | 3729 | 4016 | 977 | 1138 | 1020 | 2655 | 5267 | 7606 | 16813 | 13096 | 8690 | 5979 | 5905 | 6674 | 7482 | 11842 | 6434 | 1979 | 1253 | 1346 | 2558 | 5004 | 4628 | 629 | 716 | 703 | 467 | 1537 | 3841 | 4356 | 1175 | 1081 | 1074 | 1158 | 1576 | 4160 | 3853 | 1463 | 1430 | 1361 | 1605 | 3187 | 5411 | 5067 | 2271 | 2283 | 2423 | 2316 | 3085 | 4900 | 4521 | 1641 | 2474 | 2629 | 2591 | 3902 | 5662 | 5270 | 2355 | 2421 | 2080 | 2227 | 2726 | 5559 | 5297 | 1811 | 1874 | 2539 | 2626 | 4033 | 6996 | 6944 | 3444 | 3585 | 3800 | 3935 | 4800 | 7721 | 7549 | 4632 | 4726 | 5008 | 4818 | 6587 | 9102 | 8958 | 5812 | 6106 | 5939 | 6203 | 7709 | 10701 | 9721 | 6110 | 6421 | 6554 | 6607 | 7781
Surplus daily credible upper bound 22/23 |  | 17216 | 15305 | 15299 | 15114 | 16466 | 18705 | 18413 | 14729 | 14680 | 14658 | 14542 | 15903 | 17061 | 17227 | 14957 | 15014 | 15359 | 15297 | 16785 | 17921 | 17953 | 14998 | 15107 | 15115 | 15074 | 16439 | 17348 | 17510 | 14002 | 14034 | 14026 | 14445 | 15786 | 16247 | 16160 | 14308 | 14316 | 14325 | 13324 | 13857 | 16073 | 16214 | 13553 | 13516 | 13693 | 13913 | 15599 | 17706 | 17979 | 14901 | 14823 | 14924 | 16990 | 19439 | 21632 | 30226 | 26730 | 22684 | 19984 | 19852 | 20627 | 21389 | 25812 | 20758 | 16125 | 15504 | 15478 | 16735 | 19215 | 18698 | 14578 | 14603 | 14616 | 14641 | 16072 | 18182 | 18552 | 14955 | 14963 | 15002 | 15083 | 15708 | 18263 | 18199 | 15648 | 15704 | 15760 | 16107 | 17804 | 19723 | 19373 | 16445 | 16601 | 16710 | 16708 | 17484 | 19291 | 18995 | 15843 | 16521 | 16510 | 16514 | 17897 | 19194 | 18794 | 16007 | 16151 | 15832 | 15872 | 16244 | 18715 | 18421 | 14967 | 15128 | 15785 | 15836 | 17145 | 19808 | 19619 | 16496 | 16538 | 16747 | 16840 | 17618 | 20099 | 19958 | 17306 | 17375 | 17458 | 17405 | 18931 | 20910 | 20727 | 17914 | 17982 | 17653 | 17763 | 19134 | 21733 | 20780 | 17493 | 17682 | 17739 | 17854 | 18756

## Figure 6
Figure 6 - Range of outcomes for de-rated margin winter 2023/24 for a reduced supplies scenario
Date | 2023-10-30 | 2023-10-31 | 2023-11-01 | 2023-11-02 | 2023-11-03 | 2023-11-04 | 2023-11-05 | 2023-11-06 | 2023-11-07 | 2023-11-08 | 2023-11-09 | 2023-11-10 | 2023-11-11 | 2023-11-12 | 2023-11-13 | 2023-11-14 | 2023-11-15 | 2023-11-16 | 2023-11-17 | 2023-11-18 | 2023-11-19 | 2023-11-20 | 2023-11-21 | 2023-11-22 | 2023-11-23 | 2023-11-24 | 2023-11-25 | 2023-11-26 | 2023-11-27 | 2023-11-28 | 2023-11-29 | 2023-11-30 | 2023-12-01 | 2023-12-02 | 2023-12-03 | 2023-12-04 | 2023-12-05 | 2023-12-06 | 2023-12-07 | 2023-12-08 | 2023-12-09 | 2023-12-10 | 2023-12-11 | 2023-12-12 | 2023-12-13 | 2023-12-14 | 2023-12-15 | 2023-12-16 | 2023-12-17 | 2023-12-18 | 2023-12-19 | 2023-12-20 | 2023-12-21 | 2023-12-22 | 2023-12-23 | 2023-12-24 | 2023-12-25 | 2023-12-26 | 2023-12-27 | 2023-12-28 | 2023-12-29 | 2023-12-30 | 2023-12-31 | 2024-01-01 | 2024-01-02 | 2024-01-03 | 2024-01-04 | 2024-01-05 | 2024-01-06 | 2024-01-07 | 2024-01-08 | 2024-01-09 | 2024-01-10 | 2024-01-11 | 2024-01-12 | 2024-01-13 | 2024-01-14 | 2024-01-15 | 2024-01-16 | 2024-01-17 | 2024-01-18 | 2024-01-19 | 2024-01-20 | 2024-01-21 | 2024-01-22 | 2024-01-23 | 2024-01-24 | 2024-01-25 | 2024-01-26 | 2024-01-27 | 2024-01-28 | 2024-01-29 | 2024-01-30 | 2024-01-31 | 2024-02-01 | 2024-02-02 | 2024-02-03 | 2024-02-04 | 2024-02-05 | 2024-02-06 | 2024-02-07 | 2024-02-08 | 2024-02-09 | 2024-02-10 | 2024-02-11 | 2024-02-12 | 2024-02-13 | 2024-02-14 | 2024-02-15 | 2024-02-16 | 2024-02-17 | 2024-02-18 | 2024-02-19 | 2024-02-20 | 2024-02-21 | 2024-02-22 | 2024-02-23 | 2024-02-24 | 2024-02-25 | 2024-02-26 | 2024-02-27 | 2024-02-28 | 2024-02-29 | 2024-03-01 | 2024-03-02 | 2024-03-03 | 2024-03-04 | 2024-03-05 | 2024-03-06 | 2024-03-07 | 2024-03-08 | 2024-03-09 | 2024-03-10 | 2024-03-11 | 2024-03-12 | 2024-03-13 | 2024-03-14 | 2024-03-15 | 2024-03-16 | 2024-03-17 | 2024-03-18 | 2024-03-19 | 2024-03-20 | 2024-03-21 | 2024-03-22 | 2024-03-23 | 2024-03-24 | 2024-03-25 | 2024-03-26 | 2024-03-27 | 2024-03-28 | 2024-03-29 | 2024-03-30
Surplus daily credible lower bound | 928 | 815.1126 | 821.2205 | 810.0306 | 1814.4412 | 4307.4002 | 3739.5398 | 44.6184 | 280.2979 | 38.0402 | 405.7359 | 1459.1639 | 3934.3434 | 3461.0008 | 39.2609 | 442.8077 | 415.9058 | 470.8488 | 1638.0127 | 4100.9218 | 3414.91 | 31.9952 | -109.5039 | 83.9181 | -513.2813 | 433.8478 | 2761.1554 | 2205.1836 | -1050.2847 | -1125.9147 | -1204.3765 | -730.5524 | 659.8848 | 2717.7091 | 2018.7251 | -934.323 | -1171.2052 | -929.4682 | -760.9102 | 391.3336 | 2568.5558 | 2090.9632 | -797.9157 | -529.4619 | -329.9732 | -139.4284 | 1012.0525 | 3025.1419 | 2372.3975 | -413.7534 | -543.6439 | -457.2577 | -359.5816 | 3664.7443 | 5723.3929 | 8279.1424 | 15082.9632 | 11705.7836 | 5303.4297 | 4593.0744 | 5251.9242 | 6333.9582 | 6910.0409 | 8386.9795 | 230.6446 | -381.3644 | -967.9056 | 399.043 | 2781.0916 | 2123.2668 | -1053.1209 | -1285.0405 | -1316.2364 | -1070.5262 | -859.0401 | 950.3932 | 539.7097 | -1788.9674 | -1682.4133 | -1859.3356 | -1663.7878 | -515.4255 | 2035.4114 | 1826.8635 | -1170.3011 | -1115.6684 | -1131.1233 | -803.6604 | 318.0381 | 3069.1816 | 2759.3499 | -265.836 | -179.433 | -136.3864 | 104.0674 | 1125.9705 | 3551.3077 | 3066.4467 | -20.0864 | 22.5968 | 227.5514 | 509.8451 | 1804.94 | 4013.9007 | 3621.5166 | 323.7946 | 392.5341 | 344.5662 | 655.6865 | 1456.4035 | 4000.1894 | 3639.4163 | 1208.5615 | 851.8167 | 925.504 | 1772.4182 | 3106.9742 | 5706.6185 | 5328.4403 | 2092.5307 | 2178.6211 | 2266.9038 | 2959.8322 | 3940.8296 | 6294.2925 | 6109.5352 | 3829.8346 | 4014.6387 | 4022.2931 | 4426.4011 | 5887.6505 | 8701.0065 | 8529.4533 | 4670.7204 | 4799.33 | 5104.6789 | 5583.5724 | 6890.158 | 8998.3377 | 8577.5974 | 4594.161 | 4727.0953 | 4737.2426 | 5124.9775 | 6488.8194 | 8360.0171 | 7967.0321 | 4377.3683 | 4338.6997 | 5121.7873 | 6839.8659 | 10475.9985 | 16271.7974
Surplus daily credible upper bound | 12900 | 12429.3858 | 12364.7166 | 12315.6139 | 13320.5067 | 15275.3554 | 14770.1062 | 11214.4729 | 11508.1708 | 11464.2205 | 11821.3819 | 12940.2936 | 15241.2684 | 15128.7867 | 11883.7982 | 12732.9983 | 12503.4082 | 12701.9457 | 13915.0538 | 15865.1751 | 15375.2156 | 12302.7705 | 12122.664 | 12616.8566 | 12135.5667 | 13378.4488 | 15407.9693 | 14862.4922 | 11726.056 | 11868.6516 | 11754.1183 | 12297.3447 | 13908.856 | 15750.4936 | 15308.6561 | 12437.1051 | 12506.51 | 12766.174 | 12996.8171 | 13972.9531 | 15636.649 | 15452.4758 | 12701.4387 | 13036.1596 | 13323.1446 | 13623.0998 | 14593.4002 | 16444.3399 | 16016.5295 | 13104.6029 | 13192.9281 | 13136.0179 | 13276.6352 | 17193.0122 | 19103.2383 | 21701.3286 | 28187.1185 | 24898.5794 | 18943.4918 | 18224.7138 | 18530.4376 | 19559.0011 | 20425.9826 | 22141.7655 | 14264.2503 | 13699.7281 | 13140.925 | 14312.3082 | 16413.3087 | 15925.141 | 12323.5772 | 12329.9968 | 12411.9246 | 12593.5113 | 12968.4212 | 14535.2597 | 14180.7454 | 11657.7329 | 11700.2743 | 11631.6909 | 11927.9369 | 13038.0785 | 15453.95 | 15389.2228 | 12564.7173 | 12667.5094 | 12856.4556 | 13283.5663 | 14520.9972 | 16795.2708 | 16686.8644 | 13566.1733 | 13747.7622 | 13988.2149 | 14110.2663 | 15270.2085 | 17488.8233 | 17129.2572 | 14022.8797 | 13935.195 | 13963.9337 | 14264.0748 | 15339.5944 | 17115.033 | 16678.0443 | 13472.5825 | 13714.9937 | 13574.2711 | 13940.3765 | 14473.0452 | 16631.7914 | 16261.2455 | 13981.7541 | 13549.1572 | 13668.269 | 14648.4582 | 15775.7186 | 18005.6822 | 17581.2911 | 14569.0415 | 14803.597 | 14833.946 | 15342.5177 | 16112.2268 | 18297.3223 | 17876.2966 | 15967.4297 | 16026.1441 | 16010.5452 | 16484.5381 | 17882.9776 | 20090.9155 | 19845.7091 | 16107.2318 | 16314.0803 | 16360.9799 | 16638.3927 | 17955.3015 | 19624.66 | 19183.5672 | 15658.4742 | 15820.1765 | 15973.409 | 16324.0001 | 17531.1178 | 19249.1575 | 19008.0417 | 15658.8195 | 15608.0268 | 16297.4654 | 17910.186 | 21499.9609 | 27599.3166
Surplus under average conditions | 6898 | 5931.7358 | 5994.5351 | 6078.7757 | 6985.5773 | 9150.8827 | 8752.0196 | 5262.2373 | 5650.1446 | 5508.2613 | 5737.9382 | 6911.8863 | 9207.56 | 8967.1026 | 5885.3275 | 6503.6879 | 6308.7545 | 6416.9762 | 7570.7219 | 9729.3065 | 9162.2603 | 5888.4888 | 5858.1576 | 6087.968 | 5594.4961 | 6714.1708 | 8811.4086 | 8336.9368 | 5197.4667 | 5063.7115 | 5095.3682 | 5734.154 | 7354.7867 | 9239.8941 | 8754.269 | 6003.9726 | 5849.1443 | 5946.7264 | 6145.0791 | 7322.3256 | 8987.5409 | 8674.0764 | 5943.4539 | 6092.681 | 6284.889 | 6444.205 | 7451.5751 | 9263.0277 | 8774.5072 | 6003.6125 | 5982.5864 | 5924.9324 | 6007.0413 | 9964.3013 | 11803.4587 | 14374.3318 | 20884.6953 | 17882.8981 | 12063.7313 | 11462.6303 | 11885.017 | 12829.8622 | 13516.5793 | 15150.1533 | 7415.0352 | 6856.984 | 6441.7991 | 7709.4347 | 10081.8942 | 9618.1205 | 6142.9649 | 6072.437 | 6118.5809 | 6321.7075 | 6712.7935 | 8179.5515 | 7830.6958 | 5389.28 | 5416.8643 | 5368.5669 | 5518.7564 | 6654.4699 | 8891.9423 | 8831.8842 | 5906.7788 | 5961.5587 | 5994.6301 | 6336.635 | 7414.4707 | 9870.407 | 9690.9579 | 6708.2623 | 6896.3568 | 6995.9932 | 7260.488 | 8461.4246 | 10544.0169 | 10078.1626 | 7011.3173 | 6919.6334 | 7109.8896 | 7437.2161 | 8602.2645 | 10138.6039 | 9744.8233 | 6643.3807 | 6750.7035 | 6593.087 | 7028.9492 | 7632.0992 | 9984.3696 | 9758.8913 | 7525.9282 | 7191.4934 | 7243.954 | 8059.3129 | 9171.7195 | 11417.09 | 11215.075 | 8142.4456 | 8267.2709 | 8384.8641 | 8891.2589 | 9734.3458 | 11830.9451 | 11636.9507 | 9621.4863 | 9633.9267 | 9716.5564 | 10265.3448 | 11634.3952 | 14045.9147 | 13704.5397 | 9991.8814 | 10177.8617 | 10203.2036 | 10546.7476 | 11713.3895 | 13550.3005 | 13218.2493 | 9452.7368 | 9609.997 | 9761.1348 | 10056.7968 | 11290.8074 | 12927.7068 | 12540.4052 | 9176.5561 | 9274.0347 | 9983.2072 | 11651.6061 | 15156.8448 | 21259.9794
90% confidence bound for daily fluctuations | 11972 | 11614.2733 | 11543.4961 | 11505.5833 | 11506.0655 | 10967.9552 | 11030.5664 | 11169.8545 | 11227.8729 | 11426.1803 | 11415.646 | 11481.1297 | 11306.9251 | 11667.786 | 11844.5373 | 12290.1906 | 12087.5024 | 12231.097 | 12277.0411 | 11764.2533 | 11960.3056 | 12270.7752 | 12232.1678 | 12532.9385 | 12648.848 | 12944.6009 | 12646.814 | 12657.3086 | 12776.3407 | 12994.5663 | 12958.4947 | 13027.8971 | 13248.9712 | 13032.7844 | 13289.9311 | 13371.4281 | 13677.7153 | 13695.6423 | 13757.7273 | 13581.6195 | 13068.0932 | 13361.5126 | 13499.3544 | 13565.6215 | 13653.1178 | 13762.5282 | 13581.3477 | 13419.198 | 13644.132 | 13518.3563 | 13736.572 | 13593.2756 | 13636.2169 | 13528.268 | 13379.8454 | 13422.1862 | 13104.1553 | 13192.7958 | 13640.0621 | 13631.6394 | 13278.5133 | 13225.0429 | 13515.9417 | 13754.786 | 14033.6057 | 14081.0925 | 14108.8306 | 13913.2652 | 13632.2171 | 13801.8742 | 13376.6981 | 13615.0374 | 13728.161 | 13664.0376 | 13827.4613 | 13584.8665 | 13641.0357 | 13446.7003 | 13382.6876 | 13491.0264 | 13591.7247 | 13553.504 | 13418.5386 | 13562.3593 | 13735.0184 | 13783.1778 | 13987.5789 | 14087.2267 | 14202.9591 | 13726.0893 | 13927.5145 | 13832.0093 | 13927.1952 | 14124.6013 | 14006.199 | 14144.238 | 13937.5156 | 14062.8106 | 14042.9661 | 13912.5982 | 13736.3822 | 13754.2298 | 13534.6544 | 13101.1323 | 13056.5277 | 13148.7878 | 13322.4597 | 13229.7049 | 13284.69 | 13016.6417 | 12631.602 | 12621.8292 | 12773.1926 | 12697.3405 | 12742.765 | 12876.04 | 12668.7444 | 12299.0637 | 12252.8507 | 12476.5108 | 12624.9758 | 12567.0422 | 12382.6855 | 12171.3971 | 12003.0299 | 11766.7614 | 12137.595 | 12011.5054 | 11988.2521 | 12058.1369 | 11995.3271 | 11389.909 | 11316.2558 | 11436.5114 | 11514.7502 | 11256.301 | 11054.8203 | 11065.1434 | 10626.3224 | 10605.9698 | 11064.3132 | 11093.0812 | 11236.1664 | 11199.0226 | 11042.2984 | 10889.1403 | 11041.0096 | 11281.4513 | 11269.3271 | 11175.678 | 11070.3201 | 11023.9624 | 11327.5192

## Figure 7
Figure 7 - Historical and forecast normalised daily peak winter demand
Date | Normalised Transmission System Demand Outturn | Normalised Transmission System Demand Outturn | Normalised Transmission System Demand Outturn | Normalised Transmission System Demand Forecast
| 2020/21 | 2021/22 | 2022/23 | 2023/24
2022-10-30 | 39.9 | 35.5 | 35.809 | 39.402
2022-10-31 | 37 | 36.8 | 37.996 | 39.494
2022-11-01 | 39 | 41.9 | 39.151 | 39.652
2022-11-02 | 41.5 | 40.6 | 39.691 | 39.679
2022-11-03 | 42.8 | 41.2 | 38.378 | 38.593
2022-11-04 | 42.6 | 42.3 | 37.828 | 35.631
2022-11-05 | 42.3 | 41.5 | 34.866 | 36.83
2022-11-06 | 42.2 | 37.7 | 35.552 | 40.501
2022-11-07 | 38.8 | 38.9 | 39.725 | 40.601
2022-11-08 | 40.7 | 43.3 | 39.187 | 40.775
2022-11-09 | 42.9 | 43.2 | 39.131 | 40.598
2022-11-10 | 43.2 | 43 | 39.838 | 39.313
2022-11-11 | 42.8 | 43.1 | 39.234 | 36.239
2022-11-12 | 42.2 | 41 | 35.859 | 37.445
2022-11-13 | 41.4 | 38.2 | 37.405 | 41.05
2022-11-14 | 38.3 | 40.3 | 40.792 | 41.075
2022-11-15 | 39.5 | 42.5 | 40.336 | 41.194
2022-11-16 | 42.8 | 44.5 | 39.262 | 41.095
2022-11-17 | 43.2 | 43.8 | 39.898 | 40.081
2022-11-18 | 43 | 44.2 | 38.41 | 37.198
2022-11-19 | 44 | 42.2 | 36.733 | 38.502
2022-11-20 | 42.5 | 39.2 | 37.242 | 42.217
2022-11-21 | 39.7 | 40.9 | 42.017 | 42.421
2022-11-22 | 41.7 | 45 | 40.415 | 42.55
2022-11-23 | 44.4 | 44.4 | 41.291 | 42.271
2022-11-24 | 43.5 | 44.2 | 41.097 | 40.993
2022-11-25 | 44.6 | 44.2 | 40.196 | 37.83
2022-11-26 | 42.6 | 42.6 | 37.598 | 38.937
2022-11-27 | 41.4 | 40.6 | 38.965 | 42.459
2022-11-28 | 39.1 | 42.1 | 41.071 | 42.612
2022-11-29 | 41.4 | 45.1 | 40.101 | 42.768
2022-11-30 | 43.8 | 43.8 | 39.961 | 42.646
2022-12-01 | 44.5 | 44.4 | 40.494 | 41.436
2022-12-02 | 44.2 | 45 | 40.433 | 38.418
2022-12-03 | 44.5 | 42.3 | 36.678 | 39.596
2022-12-04 | 44.2 | 40.7 | 38.79 | 43.133
2022-12-05 | 40.6 | 41.8 | 42.198 | 43.197
2022-12-06 | 42.2 | 45.6 | 42.089 | 43.282
2022-12-07 | 44.2 | 46.8 | 42.348 | 43.126
2022-12-08 | 45.1 | 45.6 | 41.859 | 41.884
2022-12-09 | 45.1 | 45.6 | 41.076 | 38.8
2022-12-10 | 45.7 | 44 | 39.114 | 39.96
2022-12-11 | 43.8 | 41.3 | 39.015 | 43.511
2022-12-12 | 41.2 | 41.9 | 42.571 | 43.597
2022-12-13 | 43 | 46.5 | 42.663 | 43.697
2022-12-14 | 46.2 | 45.8 | 41.958 | 43.53
2022-12-15 | 46.4 | 44.9 | 42.807 | 42.229
2022-12-16 | 45.9 | 44.7 | 41.409 | 39.118
2022-12-17 | 45.4 | 44 | 39.199 | 40.252
2022-12-18 | 42.7 | 40.9 | 40.866 | 43.726
2022-12-19 | 40.4 | 41.3 | 42.307 | 43.813
2022-12-20 | 41.5 | 43.5 | 41.786 | 43.85
2022-12-21 | 43.5 | 43.8 | 41.738 | 43.616
2022-12-22 | 43.6 | 43.4 | 40.941 | 39.136
2022-12-23 | 41.2 | 41.8 | 38.51 | 36.119
2022-12-24 | 38.4 | 39.2 | 34.814 | 34.05
2022-12-25 | 36.1 | 34.2 | 31.939 | 30.756
2022-12-26 | 35.1 | 35.6 | 33.123 | 30.635
2022-12-27 | 37.7 | 39.1 | 36.732 | 37.355
2022-12-28 | 39.4 | 40.2 | 38.407 | 38.212
2022-12-29 | 40.7 | 41.9 | 38.442 | 37.748
2022-12-30 | 40.9 | 41.4 | 38.602 | 36.004
2022-12-31 | 40.9 | 40.1 | 36.168 | 35.759
2023-01-01 | 38.4 | 37.9 | 34.844 | 34.292
2023-01-02 | 39.9 | 40.2 | 39.047 | 42.986
2023-01-03 | 41.5 | 43.1 | 42.257 | 43.791
2023-01-04 | 44.7 | 46.5 | 42.078 | 43.649
2023-01-05 | 44.8 | 44.8 | 42.346 | 42.283
2023-01-06 | 44.8 | 46.4 | 41.146 | 39.105
2023-01-07 | 44 | 43.7 | 38.582 | 40.192
2023-01-08 | 41.9 | 41 | 40.157 | 43.7
2023-01-09 | 41.1 | 42.2 | 43.666 | 43.9
2023-01-10 | 42.2 | 45.6 | 44.242 | 44
2023-01-11 | 44 | 45.8 | 43.545 | 44.1
2023-01-12 | 43.5 | 45.3 | 43.712 | 41.711
2023-01-13 | 45.2 | 45.2 | 40.564 | 38.635
2023-01-14 | 44.4 | 43 | 38.389 | 39.794
2023-01-15 | 43.5 | 40.3 | 39.061 | 43.6
2023-01-16 | 40.4 | 41.8 | 43.176 | 43.8
2023-01-17 | 42 | 45.1 | 43.407 | 44.1
2023-01-18 | 44.3 | 45.3 | 43.526 | 43.9
2023-01-19 | 43.5 | 45.1 | 43.061 | 43.1
2023-01-20 | 43.5 | 45.5 | 41.759 | 39.087
2023-01-21 | 44.6 | 45.6 | 39.556 | 40.26
2023-01-22 | 42.5 | 41 | 39.96 | 43.789
2023-01-23 | 40.7 | 42.4 | 43.318 | 43.762
2023-01-24 | 41.1 | 43.1 | 43.164 | 43.706
2023-01-25 | 43.8 | 43.9 | 42.755 | 43.378
2023-01-26 | 44.5 | 45.4 | 42.585 | 42.018
2023-01-27 | 43.6 | 44.1 | 41.679 | 38.938
2023-01-28 | 44 | 44.5 | 39.495 | 39.955
2023-01-29 | 42.1 | 40.9 | 39.486 | 43.444
2023-01-30 | 39.9 | 42.6 | 42.373 | 43.429
2023-01-31 | 42.7 | 45.4 | 42.967 | 43.409
2023-02-01 | 44 | 45.5 | 42.164 | 42.991
2023-02-02 | 44.2 | 44.8 | 42.575 | 41.533
2023-02-03 | 44.1 | 44.7 | 40.641 | 38.277
2023-02-04 | 44.2 | 43.8 | 37.677 | 39.285
2023-02-05 | 42 | 40.7 | 40.392 | 42.75
2023-02-06 | 40.1 | 41.6 | 42.311 | 42.73
2023-02-07 | 41.1 | 45.3 | 42.946 | 42.775
2023-02-08 | 44.5 | 44.7 | 42.428 | 42.529
2023-02-09 | 44.1 | 44.1 | 41.276 | 41.237
2023-02-10 | 44.4 | 44.5 | 41.115 | 38.057
2023-02-11 | 43.6 | 43 | 36.488 | 39.051
2023-02-12 | 42.1 | 39.4 | 37.679 | 42.463
2023-02-13 | 40.2 | 39.6 | 40.172 | 42.386
2023-02-14 | 40.1 | 43.5 | 41.31 | 42.182
2023-02-15 | 42.1 | 44.5 | 41.229 | 41.691
2023-02-16 | 42.1 | 43.9 | 40.31 | 40.022
2023-02-17 | 43.2 | 42.5 | 38.476 | 36.865
2023-02-18 | 41.6 | 41.7 | 35.849 | 38.103
2023-02-19 | 40.9 | 37.6 | 37.241 | 41.596
2023-02-20 | 38.2 | 39.9 | 40.67 | 41.525
2023-02-21 | 40.2 | 42.8 | 39.694 | 41.466
2023-02-22 | 42.3 | 42.9 | 40.238 | 41.138
2023-02-23 | 41.9 | 43.9 | 40.437 | 39.806
2023-02-24 | 41.6 | 42.6 | 38.491 | 36.63
2023-02-25 | 41.4 | 39.9 | 35.52 | 37.677
2023-02-26 | 40.8 | 37.2 | 36.47 | 41.081
2023-02-27 | 37.8 | 38.5 | 39.471 | 41.113
2023-02-28 | 38.9 | 43 | 39.828 | 41.175
2023-03-01 | 41.7 | 41.7 | 40.274 | 40.934
2023-03-02 | 40.7 | 43.4 | 39.378 | 39.611
2023-03-03 | 41.1 | 41.1 | 38.345 | 36.47
2023-03-04 | 41 | 40 | 34.869 | 37.565
2023-03-05 | 39.4 | 37.1 | 35.061 | 40.886
2023-03-06 | 36.4 | 38.1 | 40.15 | 40.656
2023-03-07 | 36.9 | 41.5 | 38.193 | 40.423
2023-03-08 | 40.7 | 41.5 | 39.369 | 39.971
2023-03-09 | 41 | 40.2 | 38.999 | 38.625
2023-03-10 | 41 | 40.4 | 36.747 | 35.383
2023-03-11 | 38.6 | 39.6 | 34.133 | 36.279
2023-03-12 | 37.3 | 36.7 | 34.717 | 39.807
2023-03-13 | 35.5 | 37.5 | 38.734 | 39.687
2023-03-14 | 36 | 40.1 | 38.913 | 39.461
2023-03-15 | 39.6 | 40.4 | 38.273 | 39.045
2023-03-16 | 39.8 | 40.3 | 36.592 | 37.645
2023-03-17 | 39 | 39.1 | 35.219 | 34.576
2023-03-18 | 40.1 | 37.9 | 32.823 | 35.769
2023-03-19 | 37.4 | 35.7 | 33.778 | 39.203
2023-03-20 | 36.2 | 36.3 | 38.102 | 39.227
2023-03-21 | 36 | 39.7 | 37.4 | 39.103
2023-03-22 | 38.7 | 39.3 | 37.361 | 38.637
2023-03-23 | 39.1 | 39.3 | 36.71 | 37.153
2023-03-24 | 38.9 | 38.7 | 34.967 | 33.813
2023-03-25 | 38.1 | 37.1 | 32.391 | 34.836

## Figure 8
Figure 8 - Daily generation availability by fuel type (based on market submissions and including breakdown rates)
Date | 2023-10-29 | 2023-10-30 | 2023-10-31 | 2023-11-01 | 2023-11-02 | 2023-11-03 | 2023-11-04 | 2023-11-05 | 2023-11-06 | 2023-11-07 | 2023-11-08 | 2023-11-09 | 2023-11-10 | 2023-11-11 | 2023-11-12 | 2023-11-13 | 2023-11-14 | 2023-11-15 | 2023-11-16 | 2023-11-17 | 2023-11-18 | 2023-11-19 | 2023-11-20 | 2023-11-21 | 2023-11-22 | 2023-11-23 | 2023-11-24 | 2023-11-25 | 2023-11-26 | 2023-11-27 | 2023-11-28 | 2023-11-29 | 2023-11-30 | 2023-12-01 | 2023-12-02 | 2023-12-03 | 2023-12-04 | 2023-12-05 | 2023-12-06 | 2023-12-07 | 2023-12-08 | 2023-12-09 | 2023-12-10 | 2023-12-11 | 2023-12-12 | 2023-12-13 | 2023-12-14 | 2023-12-15 | 2023-12-16 | 2023-12-17 | 2023-12-18 | 2023-12-19 | 2023-12-20 | 2023-12-21 | 2023-12-22 | 2023-12-23 | 2023-12-24 | 2023-12-25 | 2023-12-26 | 2023-12-27 | 2023-12-28 | 2023-12-29 | 2023-12-30 | 2023-12-31 | 2024-01-01 | 2024-01-02 | 2024-01-03 | 2024-01-04 | 2024-01-05 | 2024-01-06 | 2024-01-07 | 2024-01-08 | 2024-01-09 | 2024-01-10 | 2024-01-11 | 2024-01-12 | 2024-01-13 | 2024-01-14 | 2024-01-15 | 2024-01-16 | 2024-01-17 | 2024-01-18 | 2024-01-19 | 2024-01-20 | 2024-01-21 | 2024-01-22 | 2024-01-23 | 2024-01-24 | 2024-01-25 | 2024-01-26 | 2024-01-27 | 2024-01-28 | 2024-01-29 | 2024-01-30 | 2024-01-31 | 2024-02-01 | 2024-02-02 | 2024-02-03 | 2024-02-04 | 2024-02-05 | 2024-02-06 | 2024-02-07 | 2024-02-08 | 2024-02-09 | 2024-02-10 | 2024-02-11 | 2024-02-12 | 2024-02-13 | 2024-02-14 | 2024-02-15 | 2024-02-16 | 2024-02-17 | 2024-02-18 | 2024-02-19 | 2024-02-20 | 2024-02-21 | 2024-02-22 | 2024-02-23 | 2024-02-24 | 2024-02-25 | 2024-02-26 | 2024-02-27 | 2024-02-28 | 2024-02-29 | 2024-03-01 | 2024-03-02 | 2024-03-03 | 2024-03-04 | 2024-03-05 | 2024-03-06 | 2024-03-07 | 2024-03-08 | 2024-03-09 | 2024-03-10 | 2024-03-11 | 2024-03-12 | 2024-03-13 | 2024-03-14 | 2024-03-15 | 2024-03-16 | 2024-03-17 | 2024-03-18 | 2024-03-19 | 2024-03-20 | 2024-03-21 | 2024-03-22 | 2024-03-23 | 2024-03-24 | 2024-03-25 | 2024-03-26 | 2024-03-27 | 2024-03-28 | 2024-03-29 | 2024-03-30 | 2024-03-31
Nuclear | 4055 | 4132 | 4212 | 4322 | 4322 | 4322 | 4322 | 4322 | 3771 | 3771 | 3771 | 3771 | 3771 | 3978 | 4339 | 4339 | 4339 | 4339 | 4339 | 4339 | 4339 | 4339 | 4339 | 4339 | 4339 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 3771 | 4012 | 4227 | 4322 | 4322 | 4322 | 4322 | 4322 | 4322 | 4322 | 4322 | 4502 | 4631 | 4929 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 4767 | 4767 | 4767 | 4623 | 4264 | 4264 | 4264 | 4264 | 4264 | 3731 | 3731 | 3731 | 3731 | 3731 | 3731 | 3731 | 3971 | 4281 | 4462 | 4635 | 4677 | 4784 | 4784 | 4904 | 5051 | 5130 | 5208 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 4750 | 4750 | 4750 | 4750 | 4750 | 4750 | 4750 | 4750 | 4750 | 4750 | 4750 | 4750 | 4750 | 4750 | 4750 | 4913 | 5128 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 5317 | 4767 | 4767 | 4767 | 4767 | 4767 | 4767 | 4767 | 4199 | 4199 | 4199 | 4199 | 4199 | 3666 | 3666 | 3666 | 3666 | 3666 | 3666 | 3666 | 3959 | 4217
Biomass | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405 | 3405 | 3405 | 3405 | 3405 | 3405 | 2792 | 3405
CCGT | 25330 | 25330 | 25763 | 25763 | 25763 | 25763 | 25763 | 25763 | 25763 | 26092 | 26092 | 26092 | 26092 | 26092 | 26092 | 26092 | 26881 | 26881 | 26881 | 26881 | 26881 | 26881 | 26881 | 26881 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 26933 | 26933 | 27238 | 27238 | 27238 | 27238 | 27238 | 26933 | 26933 | 27238 | 27238 | 27238 | 27238 | 27238 | 26933 | 26933 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 26449 | 26449 | 26449 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27238 | 27079 | 27079 | 27079 | 27079 | 27079 | 27079 | 27079 | 27079 | 27079 | 26731 | 26731 | 26731 | 26731 | 27079 | 27079 | 26369 | 26369 | 26369 | 27079 | 26515 | 26515 | 27022 | 27022 | 27022 | 27022 | 27022 | 27022 | 27022 | 27022 | 26355 | 25988 | 25988 | 27022 | 27022 | 27022 | 27022 | 27022 | 27022 | 27022 | 27022 | 27022 | 27022 | 27022 | 27022 | 26585 | 26585 | 26585 | 26585 | 26585 | 26585 | 26585 | 26585 | 26585 | 26585 | 26585 | 26585 | 26585 | 26585 | 26162 | 26162
Coal | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856
Hydro | 952 | 911 | 911 | 911 | 911 | 911 | 911 | 911 | 911 | 911 | 911 | 911 | 975 | 975 | 975 | 975 | 975 | 975 | 975 | 975 | 975 | 975 | 975 | 975 | 975 | 975 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 981 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 996 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 992 | 992 | 992 | 992 | 1012 | 1012 | 1012 | 992 | 992 | 992 | 992 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012 | 1012
OCGT | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920 | 920
Other | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762 | 762
Pumped storage | 1950 | 2047 | 2047 | 2047 | 2047 | 2047 | 2047 | 2047 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2338 | 2435 | 2435 | 2435 | 2435 | 2435 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2726 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2638 | 2347 | 2347 | 2347 | 2347 | 2347 | 2347 | 2347
Wind (Base Case EFC 15.6%) | 3147 | 3147 | 3055 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3147 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3194 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3240 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3230 | 3230 | 3230 | 3230 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3236 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3245 | 3224 | 3224 | 3224 | 3218 | 3218 | 3218 | 3218 | 3224 | 3224 | 3224 | 3224 | 3224 | 3224 | 3224
22/23 Total | 40731.568 | 41618.408 | 42161.5277 | 42161.5277 | 42161.5277 | 42177.1677 | 41570.8677 | 42177.1677 | 41797.3677 | 41968.3677 | 42015.1677 | 42127.6677 | 42127.6677 | 40463.8677 | 41394.4677 | 42127.6677 | 42127.6677 | 42127.6677 | 42127.6677 | 42146.0677 | 40566.8677 | 41499.548 | 42166.948 | 42382.948 | 42760.948 | 42760.948 | 42774.748 | 40867.848 | 42104.448 | 42792.748 | 42792.748 | 42792.748 | 43192.248 | 43210.648 | 40722.468 | 41653.068 | 42634.648 | 42634.648 | 42634.648 | 41807.448 | 41140.048 | 40334.548 | 41419.048 | 42167.448 | 42250.248 | 42365.448 | 42656.448 | 42656.448 | 41725.848 | 42656.448 | 42656.448 | 43495.868 | 43495.868 | 43801.868 | 44071.868 | 43465.568 | 44071.868 | 44071.868 | 44071.868 | 44071.868 | 43630.068 | 43630.068 | 43474.9984 | 44422.5184 | 44422.5184 | 44422.5184 | 44422.5184 | 44422.5184 | 44422.5184 | 43816.2184 | 44253.3184 | 43974.3184 | 43974.3184 | 43974.3184 | 43974.3184 | 43974.3184 | 42938.4384 | 44371.9384 | 44320.3184 | 44320.3184 | 44320.3184 | 44320.3184 | 43610.6184 | 43004.3184 | 43610.6184 | 43940.5184 | 44068.3184 | 44165.5184 | 44192.5184 | 44192.5184 | 43149.1184 | 43755.4184 | 44192.5184 | 44192.5184 | 44192.5184 | 44364.4184 | 44710.9184 | 43402.9184 | 43998.4184 | 44405.8184 | 44773.0184 | 44762.2184 | 44751.4184 | 44740.6184 | 43135.9384 | 43731.4384 | 44150.2184 | 44148.4184 | 43748.8184 | 43748.8184 | 42782.3184 | 42176.0184 | 42782.3184 | 42617.8184 | 42617.8184 | 43125.4184 | 43125.4184 | 43075.9184 | 42588.4184 | 43327.9184 | 43400.8184 | 43471.0184 | 43566.4184 | 43552.9184 | 42486.0184 | 41866.2184 | 42158.9184 | 42735.1974 | 42721.6974 | 42721.6974 | 42708.1974 | 42716.5184 | 41673.1184 | 42265.9184 | 43102.5184 | 43102.5184 | 42706.5184 | 42706.5184 | 42706.5184 | 42706.5184 | 41879.3184 | 42102.5184 | 42257.3184 | 42300.5184 | 42405.8184 | 42006.3184 | 41576.7384

## Figure 9
Figure 9 - Historical flows on the interconnectors for winter 2022/23

## Figure 10
Figure 10 - Capacity Market agreements for interconnectors in Delivery Year 2023/24
MW
| Interconnectors | Auction acquired capacity obligation 2023/24* | Connection capacity | Comments
| BritNed | 475.2 | 1320 | T-3 auction
| EWIC | 220 | 500 | T-3 auction
| IFA | 1260 | 2000 | T-3 auction
| IFA2 | 715 | 1100 | T-3 auction
| Moyle | 220 | 500 | T-3 auction
| Nemo Link | 460 | 1000 | T-3 auction
| NSL | 1232 | 1400 | T-3 auction
| ElecLink | 690 | 1000 | T-3 auction
*Our Base Case assumes net imports of 5.1 GW from interconnectors. This is based on applying the de-rating factors from the auction with our view of connection capacity set out in Table 3 in the document.

## Figure 11
Figure 11 - Electricity forward price spreads Winter 2023/24 compared to Winter 2022/23
£/MWh
| Latest Values Only | French peak | GB peak | Netherlands peak | Belgian Peak | GB baseload | French baseload | Netherlands baseload | Belgian baseload
| Winter 22/23 | 1517.677 | 630 | 472.6292 | N/A | 418 | 608 | 623 | 414
| Winter 23/24 | 138.5047 | 134.45 | 118.1243 | N/A | 103 | 110 | 102 | 97
| GB-France Price Spread £/MWh | Baseload | Peak
| Winter 22/23 | -190 | -887.677
| Winter 23/24 | -7 | -4.0547
| Winter 22/23 - Labels | -£190/MWh | -£888/MWh
| Winter 23/24 - Labels | -£7/MWh | -£4/MWh
| GB-Netherlands Price Spread £/MWh | Baseload | Peak
| Winter 22/23 | -205 | 157.3708
| Winter 23/24 | 1 | 16.3257
| Winter 22/23 - Labels | -£205/MWh | £157/MWh
| Winter 23/24 - Labels | £1/MWh | £16/MWh
| GB-Belgium Price Spread £/MWh | Baseload
| Winter 22/23 | 4
| Winter 23/24 | 6
| Winter 22/23 - Labels | £4/MWh
| Winter 23/24 - Labels | £6/MWh

## Figure 12
Figure 12 - Winter 2023/24 electricity peak forward prices
£/MWh
| Date | French peak | GB peak | Netherlands peak
| 2023-09-12 | 138.5047 | 134.45 | 118.1243
| 2023-09-11 | 138.5047 | 136.25 | 119.9861
| 2023-09-10 | 141.3055 | 134.25 | 119.2075
| 2023-09-09 | 140.1087 | 134.25 | 119.2075
| 2023-09-08 | 140.1087 | 134.25 | 119.2075
| 2023-09-07 | 140.1087 | 134.875 | 117.9016
| 2023-09-06 | 139.1506 | 133.5 | 117.2063
| 2023-09-05 | 140.7722 | 140.25 | 121.5207
| 2023-09-04 | 148.6416 | 138.75 | 123.3401
| 2023-09-03 | 151.823 | 143.25 | 123.3433
| 2023-09-02 | 159.8696 | 143.25 | 123.3433
| 2023-09-01 | 159.8696 | 143.25 | 123.3433
| 2023-08-31 | 159.8696 | 143 | 124.0246
| 2023-08-30 | 162.5046 | 148.5 | 130.9341
| 2023-08-29 | 174.8372 | 146.5 | 130.145
| 2023-08-28 | 183.5997 | 145.95 | 125.8046
| 2023-08-27 | 187.6312 | 145.95 | 125.8046
| 2023-08-26 | 187.6312 | 145.95 | 125.8046
| 2023-08-25 | 187.6312 | 145.95 | 125.8046
| 2023-08-24 | 187.6312 | 142 | 125.7246
| 2023-08-23 | 187.243 | 151.75 | 131.3951
| 2023-08-22 | 195.7427 | 160.125 | 136.0236
| 2023-08-21 | 205.5316 | 156.9 | 134.0672
| 2023-08-20 | 199.5564 | 150.875 | 131.6804
| 2023-08-19 | 200.6375 | 150.875 | 131.6804
| 2023-08-18 | 200.6375 | 150.875 | 131.6804
| 2023-08-17 | 200.6375 | 148.15 | 128.7473
| 2023-08-16 | 199.9906 | 149.1 | 131.0549
| 2023-08-15 | 203.8679 | 147.75 | 130.5593
| 2023-08-14 | 211.6072 | 140.75 | 129.2646
| 2023-08-13 | 204.2587 | 145 | 128.6298
| 2023-08-12 | 205.3184 | 145 | 128.6298
| 2023-08-11 | 205.3184 | 145 | 128.6298
| 2023-08-10 | 205.3184 | 143.325 | 127.405
| 2023-08-09 | 211.7698 | 145.025 | 128.7411
| 2023-08-08 | 192.9492 | 138 | 123.2302
| 2023-08-07 | 220.3932 | 138.475 | 124.5016
| 2023-08-06 | 221.9104 | 137 | 122.6909
| 2023-08-05 | 221.8457 | 137 | 122.6909
| 2023-08-04 | 221.8457 | 137 | 122.6909
| 2023-08-03 | 221.8457 | 137.65 | 124.3874
| 2023-08-02 | 223.3397 | 135.9 | 122.819
| 2023-08-01 | 227.0055 | 137.3 | 125.9094
| 2023-07-31 | 229.3974 | 140 | 124.14
| 2023-07-30 | 235.2999 | 138.5 | 126.8495
| 2023-07-29 | 236.2917 | 138.5 | 126.8495 | Update 13/09/2023
| 2023-07-28 | 236.2917 | 138.5 | 126.8495 | Note change to a blend of Argus data as better availability and coverage then Bloomber. Blend serves as anonymising
| 2023-07-27 | 236.2917 | 142.65 | 130.4798
| 2023-07-26 | 252.6959 | 142.75 | 130.0871 | Update 14/09/2023
| 2023-07-25 | 264.3033 | 147.5 | 134.1972 | change to blended agrus and bloomberg fair value
| 2023-07-24 | 269.7756 | 146.4 | 131.5927
| 2023-07-23 | 266.2668 | 144.05 | 131.1384
| 2023-07-22 | 272.4079 | 144.05 | 131.1384
| 2023-07-21 | 272.4079 | 144.05 | 131.1384
| 2023-07-20 | 272.4079 | 146.7 | 132.1121
| 2023-07-19 | 274.0717 | 144.15 | 130.9483
| 2023-07-18 | 266.96 | 143 | 129.1656
| 2023-07-17 | 268.3483 | 139 | 123.0347
| 2023-07-16 | 272.0146 | 140.25 | 120.0024
| 2023-07-15 | 273.0636 | 140.25 | 120.0024
| 2023-07-14 | 273.0636 | 140.25 | 120.0024
| 2023-07-13 | 273.0636 | 140.25 | 121.3405
| 2023-07-12 | 271.051 | 140.25 | 121.2069
| 2023-07-11 | 275.9007 | 142.15 | 126.611
| 2023-07-10 | 286.2576 | 148.25 | 126.1669
| 2023-07-09 | 288.5261 | 154.975 | 133.6017
| 2023-07-08 | 295.722 | 154.975 | 133.6017
| 2023-07-07 | 295.722 | 154.975 | 133.6017
| 2023-07-06 | 295.722 | 152.475 | 127.1621
| 2023-07-05 | 288.0948 | 154.475 | 129.1895
| 2023-07-04 | 284.6814 | 156.8 | 130.3362
| 2023-07-03 | 283.6375 | 155.25 | 127.6508
| 2023-07-02 | 278.7588 | 162.5 | 128.9329
| 2023-07-01 | 312.1183 | 162.5 | 128.9329
| 2023-06-30 | 312.1183 | 162.5 | 128.9329
| 2023-06-29 | 312.1183 | 159 | 123.7076
| 2023-06-28 | 330.773 | 157.5 | 126.1115
| 2023-06-27 | 332.6861 | 160.5 | 129.8785
| 2023-06-26 | 346.8234 | 161 | 126.0463
| 2023-06-25 | 326.427 | 166.25 | 124.3287
| 2023-06-24 | 359.453 | 166.25 | 124.3287
| 2023-06-23 | 359.453 | 166.25 | 124.3287
| 2023-06-22 | 359.453 | 168.35 | 127.4983
| 2023-06-21 | 373.6647 | 173 | 130.4938
| 2023-06-20 | 385.6429 | 171.5 | 136.2865
| 2023-06-19 | 386.756 | 169.05 | 126.3056
| 2023-06-18 | 369.9347 | 167.85 | 125.1078
| 2023-06-17 | 377.5865 | 167.85 | 125.1078
| 2023-06-16 | 377.5865 | 167.85 | 125.1078
| 2023-06-15 | 377.5865 | 182 | 137.0416
| 2023-06-14 | 392.0315 | 175.5 | 133.3085
| 2023-06-13 | 389.0073 | 168.25 | 128.3542
| 2023-06-12 | 372.3664 | 160.5 | 122.8075
| 2023-06-11 | 366.3117 | 159.075 | 123.896
| 2023-06-10 | 363.0141 | 159.075 | 123.896
| 2023-06-09 | 363.0141 | 159.075 | 123.896
| 2023-06-08 | 363.0141 | 150.5 | 115.4584

## Figure 12b
Figure 12b - Winter 2023/24 electricity baseload forward prices
£/MWh
| Date | GB baseload | French baseload | Netherlands baseload | Belgian baseload
| 2023-09-12 | 103 | 110 | 102 | 97
| 2023-09-11 | 105 | 112 | 103 | 98
| 2023-09-10 | 104 | 111 | 102 | 98
| 2023-09-09 | 104 | 111 | 102 | 98
| 2023-09-08 | 103 | 111 | 102 | 98
| 2023-09-07 | 102 | 111 | 101 | 94
| 2023-09-06 | 100 | 111 | 99 | 92
| 2023-09-05 | 106 | 115 | 104 | 97
| 2023-09-04 | 105 | 116 | 105 | 99
| 2023-09-03 | 108 | 118 | 107 | 100
| 2023-09-02 | 108 | 118 | 107 | 100
| 2023-09-01 | 109 | 119 | 109 | 101
| 2023-08-31 | 117 | 120 | 123 | 112
| 2023-08-30 | 122 | 123 | 128 | 115
| 2023-08-29 | 120 | 124 | 131 | 114
| 2023-08-28 | 121 | 129 | 134 | 115
| 2023-08-27 | 121 | 129 | 134 | 115
| 2023-08-26 | 121 | 129 | 134 | 115
| 2023-08-25 | 119 | 126 | 133 | 113
| 2023-08-24 | 117 | 124 | 132 | 111
| 2023-08-23 | 125 | 131 | 138 | 121
| 2023-08-22 | 131 | 138 | 145 | 126
| 2023-08-21 | 128 | 134 | 142 | 123
| 2023-08-20 | 126 | 134 | 140 | 120
| 2023-08-19 | 126 | 134 | 140 | 120
| 2023-08-18 | 124 | 131 | 140 | 119
| 2023-08-17 | 123 | 130 | 139 | 118
| 2023-08-16 | 123 | 131 | 139 | 120
| 2023-08-15 | 123 | 133 | 142 | 121
| 2023-08-14 | 118 | 129 | 138 | 114
| 2023-08-13 | 118 | 126 | 137 | 113
| 2023-08-12 | 118 | 126 | 137 | 113
| 2023-08-11 | 118 | 126 | 135 | 113
| 2023-08-10 | 118 | 128 | 137 | 114
| 2023-08-09 | 119 | 132 | 143 | 117
| 2023-08-08 | 114 | 127 | 138 | 110
| 2023-08-07 | 114 | 127 | 139 | 109
| 2023-08-06 | 114 | 127 | 138 | 109
| 2023-08-05 | 114 | 127 | 138 | 109
| 2023-08-04 | 113 | 127 | 139 | 109
| 2023-08-03 | 113 | 128 | 140 | 110
| 2023-08-02 | 112 | 127 | 139 | 110
| 2023-08-01 | 113 | 129 | 141 | 110
| 2023-07-31 | 116 | 132 | 144 | 112
| 2023-07-30 | 115 | 132 | 144 | 113
| 2023-07-29 | 115 | 132 | 144 | 113
| 2023-07-28 | 115 | 131 | 144 | 113
| 2023-07-27 | 120 | 136 | 148 | 117
| 2023-07-26 | 120 | 139 | 154 | 119
| 2023-07-25 | 124 | 143 | 158 | 123
| 2023-07-24 | 123 | 139 | 155 | 120
| 2023-07-23 | 122 | 142 | 154 | 119
| 2023-07-22 | 122 | 142 | 154 | 119
| 2023-07-21 | 121 | 142 | 159 | 119
| 2023-07-20 | 123 | 144 | 161 | 121
| 2023-07-19 | 121 | 139 | 158 | 120
| 2023-07-18 | 119 | 138 | 158 | 116
| 2023-07-17 | 114 | 136 | 157 | 111
| 2023-07-16 | 114 | 138 | 156 | 110
| 2023-07-15 | 114 | 138 | 156 | 110
| 2023-07-14 | 115 | 138 | 159 | 111
| 2023-07-13 | 114 | 137 | 157 | 110
| 2023-07-12 | 114 | 136 | 157 | 109
| 2023-07-11 | 116 | 140 | 160 | 113
| 2023-07-10 | 119 | 145 | 164 | 117
| 2023-07-09 | 123 | 148 | 167 | 119
| 2023-07-08 | 123 | 148 | 167 | 119
| 2023-07-07 | 126 | 151 | 172 | 122
| 2023-07-06 | 122 | 148 | 166 | 121
| 2023-07-05 | 123 | 145 | 161 | 121
| 2023-07-04 | 125 | 145 | 162 | 119
| 2023-07-03 | 123 | 143 | 160 | 118
| 2023-07-02 | 126 | 150 | 162 | 118
| 2023-07-01 | 126 | 150 | 162 | 118
| 2023-06-30 | 122 | 150 | 133 | 121
| 2023-06-29 | 119 | 150 | 130 | 113
| 2023-06-28 | 118 | 150 | 130 | 113
| 2023-06-27 | 120 | 158 | 135 | 114
| 2023-06-26 | 118 | 148 | 126 | 112
| 2023-06-25 | 119 | 156 | 127 | 112
| 2023-06-24 | 119 | 156 | 127 | 112
| 2023-06-23 | 119 | 157 | 131 | 112
| 2023-06-22 | 123 | 165 | 140 | 113
| 2023-06-21 | 128 | 172 | 145 | 116
| 2023-06-20 | 130 | 174 | 147 | 119
| 2023-06-19 | 125 | 165 | 139 | 115
| 2023-06-18 | 124 | 163 | 138 | 115
| 2023-06-17 | 124 | 163 | 138 | 115
| 2023-06-16 | 124 | 163 | 137 | 115
| 2023-06-15 | 136 | 174 | 149 | 120
| 2023-06-14 | 131 | 171 | 145 | 119
| 2023-06-13 | 124 | 162 | 139 | 116
| 2023-06-12 | 116 | 154 | 132 | 111
| 2023-06-11 | 116 | 155 | 133 | 111
| 2023-06-10 | 116 | 155 | 133 | 111
| 2023-06-09 | 116 | 154 | 133 | 111
| 2023-06-08 | 108 | 145 | 124 | 107
| 2023-06-07 | 104 | 138 | 120 | 106
| 2023-06-06 | 105 | 134 | 117 | 105
| 2023-06-05 | 110 | 139 | 123 | 110
| 2023-06-04 | 108 | 132 | 117 | 110
| 2023-06-03 | 108 | 132 | 117 | 110
| 2023-06-02 | 102 | 130 | 112 | 103
| 2023-06-01 | 102 | 131 | 114 | 103
| 2023-05-31 | 115 | 140 | 157 | 112
| 2023-05-30 | 114 | 139 | 157 | 112
| 2023-05-29 | 115 | 144 | 160 | 112
| 2023-05-28 | 115 | 144 | 160 | 112
| 2023-05-27 | 115 | 144 | 160 | 112
| 2023-05-26 | 116 | 144 | 160 | 113
| 2023-05-25 | 119 | 141 | 156 | 114
| 2023-05-24 | 126 | 152 | 170 | 118
| 2023-05-23 | 129 | 158 | 179 | 119
| 2023-05-22 | 131 | 164 | 187 | 120
| 2023-05-21 | 132 | 176 | 187 | 120
| 2023-05-20 | 132 | 176 | 187 | 120
| 2023-05-19 | 133 | 176 | 202 | 120
| 2023-05-18 | 132 | 173 | 201 | 120
| 2023-05-17 | 133 | 175 | 204 | 121
| 2023-05-16 | 130 | 178 | 207 | 118
| 2023-05-15 | 133 | 184 | 217 | 120
| 2023-05-14 | 136 | 191 | 220 | 120
| 2023-05-13 | 136 | 191 | 220 | 120
| 2023-05-12 | 141 | 194 | 225 | 125

## Figure 13
Figure 13 - French nuclear capacity from planned outages in 2023/24 and actuals from a range of previous winters
Date | Outages during Winter 17/18 | Outages during Winter 18/19 | Outages during Winter 19/20 | Outages during Winter 20/21 | Outages during Winter 21/22 | Outages during Winter 22/23 | Expected outages during Winter 23/24
2020-10-28 | 23.833 | 19.42 | 16.095 | 20.1 | 12.96 | 15.71 | 15.02
2020-10-29 | 23.148 | 18.685 | 16.095 | 20.1 | 12.96 | 15.71 | 15.02
2020-10-30 | 21.163 | 18.495 | 16.095 | 20.1 | 12.96 | 15.71 | 15.02
2020-10-31 | 21.498 | 18.495 | 16.095 | 21 | 12.575 | 15.71 | 15.02
2020-11-01 | 21.365 | 18.905 | 16.095 | 19.2 | 10.35 | 15.71 | 15.02
2020-11-02 | 23.09 | 19.815 | 16.095 | 18.3 | 10.35 | 15.71 | 13.52
2020-11-03 | 23.405 | 21.65 | 16.095 | 18.3 | 10.35 | 15.71 | 16.315
2020-11-04 | 22.295 | 20.49 | 15.185 | 18.3 | 10.35 | 15.71 | 16.315
2020-11-05 | 21.395 | 18.285 | 15.185 | 17.4 | 10.35 | 15.71 | 13.93
2020-11-06 | 21.555 | 18.285 | 14.275 | 16.1 | 10.35 | 15.71 | 13.93
2020-11-07 | 21.395 | 18.285 | 14.275 | 16.1 | 11.68 | 15.71 | 13.93
2020-11-08 | 21.395 | 17.58 | 13.36 | 16.1 | 11.68 | 15.71 | 13.93
2020-11-09 | 22.705 | 17.715 | 13.545 | 16.1 | 11.68 | 15.71 | 13.93
2020-11-10 | 22.705 | 19.62 | 12.05 | 15.2 | 11.68 | 15.71 | 13.93
2020-11-11 | 22.705 | 19.62 | 10.74 | 15.2 | 11.68 | 15.71 | 13.93
2020-11-12 | 20.92 | 19.62 | 10.74 | 15.2 | 11.68 | 15.71 | 13.93
2020-11-13 | 20.485 | 22.31 | 10.74 | 15.2 | 11.68 | 15.71 | 13.93
2020-11-14 | 20.685 | 19.42 | 10.74 | 15.2 | 11.68 | 15.71 | 13.93
2020-11-15 | 20.685 | 18.27 | 10.74 | 15.2 | 11.68 | 15.71 | 13.93
2020-11-16 | 20.685 | 17.36 | 9.41 | 15.2 | 11.68 | 15.71 | 13.93
2020-11-17 | 19.686 | 19.78 | 9.41 | 15.2 | 11.68 | 15.71 | 15.26
2020-11-18 | 19.971 | 18.275 | 9.41 | 15.2 | 11.68 | 15.71 | 15.26
2020-11-19 | 19.832 | 18.605 | 9.41 | 15.2 | 11.68 | 15.71 | 15.26
2020-11-20 | 19.546 | 18.605 | 9.41 | 15.2 | 11.68 | 15.71 | 15.26
2020-11-21 | 19.546 | 18.105 | 8.075 | 14.3 | 11.68 | 15.71 | 15.26
2020-11-22 | 18.656 | 17.175 | 8.075 | 15.2 | 11.68 | 15.71 | 12.525
2020-11-23 | 16.744 | 17.175 | 8.075 | 15.2 | 11.68 | 15.71 | 12.525
2020-11-24 | 16.1 | 18.75 | 8.075 | 15.2 | 11.68 | 15.71 | 14.02
2020-11-25 | 19.705 | 16.555 | 8.075 | 15.2 | 11.68 | 15.71 | 14.02
2020-11-26 | 15.255 | 15.295 | 8.075 | 15.2 | 11.68 | 15.71 | 13.105
2020-11-27 | 13.535 | 15.1 | 8.075 | 14.3 | 11.68 | 15.71 | 11.61
2020-11-28 | 14.505 | 15.37 | 7.16 | 14.3 | 11.68 | 15.71 | 11.61
2020-11-29 | 14.355 | 16.198 | 7.16 | 14.3 | 11.68 | 15.71 | 11.61
2020-11-30 | 16.465 | 12.48 | 7.16 | 14.3 | 11.68 | 15.71 | 11.61
2020-12-01 | 13.58 | 17.145 | 6.245 | 14.3 | 11.68 | 15.71 | 11.61
2020-12-02 | 16.09 | 16.282 | 6.245 | 14.3 | 11.68 | 15.71 | 12.52
2020-12-03 | 13.643 | 11.355 | 6.245 | 14.3 | 11.68 | 15.71 | 12.52
2020-12-04 | 11.84 | 11.225 | 5.355 | 13 | 11.68 | 15.71 | 12.52
2020-12-05 | 11.84 | 11.49 | 5.355 | 13 | 11.68 | 16.625 | 12.52
2020-12-06 | 10.83 | 11.49 | 4.025 | 13 | 11.68 | 16.625 | 12.52
2020-12-07 | 12.095 | 10.425 | 4.025 | 13 | 11.68 | 16.625 | 12.52
2020-12-08 | 12.445 | 13.3 | 4.025 | 12.1 | 11.68 | 16.625 | 12.52
2020-12-09 | 13.36 | 9.88 | 3.115 | 12.1 | 11.68 | 16.625 | 12.52
2020-12-10 | 13.44 | 8.615 | 3.115 | 12.1 | 11.68 | 17.96 | 12.52
2020-12-11 | 12.422 | 8.325 | 3.115 | 12.1 | 11.68 | 17.96 | 12.52
2020-12-12 | 12.272 | 8.29 | 3.115 | 12.1 | 8.975 | 17.96 | 12.52
2020-12-13 | 11.512 | 8.405 | 3.115 | 11.1 | 8.975 | 17.96 | 12.52
2020-12-14 | 13.882 | 9.313 | 3.115 | 11.1 | 8.975 | 17.96 | 12.52
2020-12-15 | 11.81 | 9.565 | 1.785 | 11.1 | 8.975 | 17.96 | 12.52
2020-12-16 | 12.656 | 7.875 | 1.785 | 11.1 | 8.975 | 17.96 | 11.22
2020-12-17 | 11.326 | 7.15 | 0.88 | 11.1 | 8.975 | 17.96 | 11.22
2020-12-18 | 10.956 | 7.475 | 0.88 | 11.1 | 8.975 | 17.96 | 11.22
2020-12-19 | 9.205 | 8.355 | 0.88 | 11.1 | 8.975 | 17.96 | 11.22
2020-12-20 | 9.09 | 8.645 | 0.88 | 11.1 | 8.975 | 17.96 | 11.22
2020-12-21 | 9.035 | 8.01 | 0.88 | 11.1 | 8.085 | 17.96 | 11.22
2020-12-22 | 7.29 | 11.62 | 0.88 | 11.1 | 8.085 | 17.96 | 11.22
2020-12-23 | 9.076 | 11.27 | 0.88 | 11.1 | 8.085 | 17.96 | 10.305
2020-12-24 | 11.91 | 10.425 | 0.88 | 11.1 | 8.085 | 17.96 | 10.305
2020-12-25 | 10.189 | 10.83 | 0.88 | 10.2 | 8.085 | 17.96 | 10.305
2020-12-26 | 9.979 | 6.57 | 0.88 | 10.2 | 8.085 | 17.96 | 10.305
2020-12-27 | 8.479 | 6.49 | 0.88 | 10.2 | 8.085 | 17.96 | 8.995
2020-12-28 | 10.049 | 6.7 | 0.88 | 10.2 | 8.085 | 17.96 | 8.995
2020-12-29 | 9.164 | 6.6 | 0.88 | 9.3 | 8.085 | 17.96 | 8.995
2020-12-30 | 10.82 | 6.6 | 0.88 | 9.3 | 6.755 | 17.96 | 8.995
2020-12-31 | 15.195 | 6.6 | 0.88 | 9.3 | 6.755 | 18.865 | 8.995
2021-01-01 | 10.61 | 6.755 | 0.88 | 7.1 | 6.755 | 18.865 | 8.995
2021-01-02 | 5.46 | 6.755 | 0.88 | 7.1 | 5.84 | 18.865 | 8.995
2021-01-03 | 6.559 | 6.755 | 0.88 | 7.1 | 5.84 | 18.865 | 8.995
2021-01-04 | 6.764 | 6.755 | 0.88 | 5.8 | 5.84 | 18.865 | 8.995
2021-01-05 | 6.449 | 7.975 | 0.88 | 5.8 | 5.84 | 18.865 | 7.665
2021-01-06 | 6.449 | 7.475 | 0.88 | 5.8 | 5.84 | 18.865 | 8.965
2021-01-07 | 5.809 | 6.64 | 0.88 | 5.8 | 5.84 | 20.195 | 8.965
2021-01-08 | 5.575 | 7.06 | 0.88 | 5.8 | 5.84 | 20.195 | 8.965
2021-01-09 | 4.57 | 7.06 | 0.88 | 4.9 | 5.84 | 20.195 | 8.965
2021-01-10 | 4.57 | 7.725 | 0.88 | 4.9 | 5.84 | 20.195 | 8.965
2021-01-11 | 4.57 | 7.94 | 0.88 | 4.9 | 5.84 | 21.105 | 8.965
2021-01-12 | 6.785 | 9.158 | 0 | 4.9 | 5.84 | 22.02 | 8.965
2021-01-13 | 8.095 | 10.068 | 0 | 4.9 | 5.84 | 22.02 | 8.05
2021-01-14 | 7.96 | 10.558 | 0 | 4.9 | 4.345 | 22.02 | 8.05
2021-01-15 | 6.395 | 9.093 | 0 | 4.9 | 4.345 | 27.385 | 7.145
2021-01-16 | 5.985 | 9.227 | 0 | 4.9 | 5.675 | 22.02 | 7.145
2021-01-17 | 5.35 | 8.839 | 0 | 4.9 | 5.675 | 21.105 | 7.145
2021-01-18 | 5.35 | 9.394 | 0.91 | 4.9 | 5.675 | 21.105 | 7.145
2021-01-19 | 7.145 | 13.264 | 0.91 | 4.9 | 5.675 | 21.105 | 6.235
2021-01-20 | 7.145 | 10.322 | 0.91 | 4.9 | 5.675 | 21.105 | 6.235
2021-01-21 | 7.195 | 9.859 | 0.91 | 4.9 | 5.675 | 22.435 | 5.325
2021-01-22 | 6.65 | 9.104 | 0.91 | 4 | 5.675 | 21.105 | 4.41
2021-01-23 | 4.435 | 8.529 | 0.91 | 4 | 6.975 | 21.105 | 4.41
2021-01-24 | 4.435 | 7.614 | 0.91 | 5.3 | 6.975 | 21.105 | 4.41
2021-01-25 | 4.435 | 8.039 | 1.8 | 5.3 | 6.975 | 21.995 | 4.41
2021-01-26 | 4.435 | 8.748 | 1.8 | 5.3 | 6.975 | 20.5 | 4.41
2021-01-27 | 5.465 | 7.418 | 1.8 | 5.3 | 6.975 | 20.5 | 4.41
2021-01-28 | 6.755 | 7.418 | 1.8 | 5.3 | 6.975 | 20.5 | 4.41
2021-01-29 | 7.975 | 7.418 | 1.8 | 5.3 | 6.975 | 22.74 | 4.41
2021-01-30 | 6.645 | 7.793 | 1.8 | 5.3 | 9.2 | 22.74 | 4.41
2021-01-31 | 6.4 | 7.46 | 1.8 | 7.7 | 9.2 | 21.41 | 4.41
2021-02-01 | 6.4 | 7.585 | 1.8 | 7.7 | 9.2 | 22.3 | 4.41
2021-02-02 | 6.25 | 6.68 | 1.8 | 7.7 | 9.2 | 22.3 | 4.41
2021-02-03 | 9.795 | 7.21 | 1.8 | 7.7 | 9.2 | 21.81 | 4.41
2021-02-04 | 8.505 | 7.21 | 1.8 | 7.7 | 9.2 | 21.81 | 4.41
2021-02-05 | 7.745 | 8.09 | 1.8 | 7.7 | 9.2 | 21.81 | 4.41
2021-02-06 | 7.745 | 7.21 | 1.8 | 6.4 | 9.225 | 20.51 | 4.41
2021-02-07 | 6.835 | 7.485 | 1.8 | 9.7 | 9.225 | 20.51 | 4.41
2021-02-08 | 8.801 | 7.21 | 2.715 | 9.7 | 9.225 | 20.51 | 4.41
2021-02-09 | 7.086 | 8.62 | 2.715 | 9.7 | 9.225 | 20.51 | 4.41
2021-02-10 | 6.771 | 7.21 | 2.715 | 9.7 | 9.225 | 18.1 | 4.41
2021-02-11 | 6.68 | 7.21 | 2.715 | 9.7 | 9.225 | 18.1 | 4.41
2021-02-12 | 7.015 | 7.21 | 2.715 | 9.7 | 9.225 | 19.01 | 4.41
2021-02-13 | 7.145 | 7.21 | 2.715 | 9.7 | 10.725 | 19.01 | 4.41
2021-02-14 | 7.145 | 8.52 | 2.715 | 11 | 10.725 | 19.01 | 4.41
2021-02-15 | 7.145 | 8.63 | 4.025 | 11 | 10.725 | 19.01 | 4.41
2021-02-16 | 7.145 | 10.635 | 4.025 | 11 | 10.725 | 19.9 | 4.41
2021-02-17 | 11.32 | 9.305 | 4.025 | 11 | 10.725 | 21.2 | 6.235
2021-02-18 | 10.98 | 8.085 | 4.025 | 11 | 9.815 | 20.815 | 6.235
2021-02-19 | 13.135 | 8.96 | 4.025 | 11 | 9.815 | 21.21 | 6.235
2021-02-20 | 13.135 | 8.96 | 4.025 | 11 | 10.725 | 21.21 | 6.235
2021-02-21 | 13.135 | 8.32 | 4.025 | 12.8 | 10.725 | 21.21 | 6.235
2021-02-22 | 11.64 | 8.32 | 7.285 | 12.8 | 10.725 | 21.21 | 6.235
2021-02-23 | 11.64 | 11.405 | 7.285 | 12.8 | 10.725 | 20.32 | 6.235
2021-02-24 | 10.98 | 9.104 | 7.285 | 12.8 | 10.725 | 20.32 | 6.235
2021-02-25 | 12.02 | 9.104 | 7.285 | 12.8 | 12.055 | 21.225 | 6.235
2021-02-26 | 12.31 | 9.104 | 7.285 | 12.8 | 11.145 | 22.135 | 6.235
2021-02-27 | 12.31 | 9.104 | 7.285 | 12.8 | 12.055 | 22.135 | 6.235
2021-02-28 | 15.46 | 9.104 | 7.285 | 15 | 12.055 | 21.225 | 6.235
2021-03-01 | 10.965 | 11.314 | 8.2 | 15 | 12.055 | 21.225 | 6.235
2021-03-02 | 11.09 | 11.204 | 8.2 | 15 | 12.055 | 21.225 | 6.235
2021-03-03 | 12.065 | 17.464 | 8.2 | 15 | 12.055 | 21.225 | 9.365
2021-03-04 | 13.085 | 11.574 | 8.2 | 15 | 12.055 | 23.44 | 9.365
2021-03-05 | 12.485 | 10.774 | 8.2 | 13.7 | 12.055 | 23.435 | 9.365
2021-03-06 | 12.485 | 10.819 | 8.2 | 13.7 | 12.055 | 22.525 | 8.055
2021-03-07 | 12.485 | 10.839 | 8.2 | 13.7 | 12.055 | 22.525 | 8.055
2021-03-08 | 12.485 | 10.839 | 11.325 | 13.7 | 12.055 | 22.525 | 8.055
2021-03-09 | 12.485 | 14.849 | 11.325 | 13.7 | 12.055 | 22.525 | 8.055
2021-03-10 | 14.115 | 15.364 | 11.325 | 13.7 | 12.055 | 23.415 | 9.55
2021-03-11 | 13.4 | 11.519 | 11.325 | 13.7 | 12.055 | 23.415 | 9.55
2021-03-12 | 13.745 | 12.049 | 11.325 | 13.7 | 12.055 | 23.415 | 9.55
2021-03-13 | 12.83 | 10.919 | 11.325 | 13.7 | 16.105 | 25.155 | 9.55
2021-03-14 | 12.83 | 10.494 | 11.325 | 14.6 | 14.775 | 22.525 | 9.55
2021-03-15 | 14.925 | 13.021 | 12.82 | 14.6 | 14.775 | 22.525 | 9.55
2021-03-16 | 16.27 | 19.619 | 12.82 | 14.6 | 14.775 | 22.525 | 9.55
2021-03-17 | 19.39 | 19.91 | 12.82 | 14.6 | 14.775 | 22.525 | 10.455
2021-03-18 | 17.86 | 16.46 | 12.82 | 14.6 | 14.775 | 22.525 | 10.455
2021-03-19 | 15.55 | 14.53 | 12.82 | 14.6 | 14.775 | 22.525 | 10.455
2021-03-20 | 15.55 | 14.53 | 12.82 | 14.6 | 14.775 | 22.525 | 10.455
2021-03-21 | 15.475 | 15.84 | 12.82 | 15.9 | 14.775 | 22.525 | 10.455
2021-03-22 | 16.115 | 14.53 | 12.82 | 15.9 | 13.445 | 22.525 | 10.455
2021-03-23 | 15.475 | 14.835 | 12.82 | 15.9 | 13.445 | 22.525 | 11.955
2021-03-24 | 20.897 | 13.185 | 12.82 | 14.4 | 13.445 | 22.525 | 13.285
2021-03-25 | 20.685 | 11.645 | 12.82 | 14.4 | 13.445 | 23.44 | 13.285
2021-03-26 | 17.655 | 10.985 | 12.82 | 14.4 | 13.445 | 22.525 | 13.285
2021-03-27 | 17.655 | 12.125 | 12.82 | 14.4 | 15.685 | 22.525 | 13.285
2021-03-28 | 18.255 | 12.125 | 12.82 | 16.2 | 15.685 | 22.525 | 13.285
2021-03-29 | 18.7 | 12.96 | 11.94 | 16.2 | 15.685 | 22.525 | 13.285
2021-03-30 | 16.685 | 13.63 | 11.94 | 16.2 | 15.685 | 22.525 | 13.285
2021-03-31 | 18.485 | 15.46 | 11.05 | 16.2 | 15.685 | 22.525 | 13.285

## Figure 14
Figure 14 - How the expectations of winter prices have changed in the preceeding months (previous winters compared)
Date | £/MWh
| 2020/21 GB baseload | 2021/22 GB baseload | 2022/23 GB baseload | 2023/24 GB baseload
2021-09-12 | 48.2 | 141.1 | 457 | 103
2021-09-11 | 48.2 | 141.1 | 488 | 105
2021-09-10 | 48 | 141.1 | 488 | 104
2021-09-09 | 47.7 | 139.05 | 488 | 104
2021-09-08 | 47.4 | 136.05 | 554.95 | 103
2021-09-07 | 47.95 | 132 | 584 | 102
2021-09-06 | 48.85 | 130.3 | 625 | 100
2021-09-05 | 48.85 | 127.55 | 655 | 106
2021-09-04 | 48.85 | 127.55 | 610 | 105
2021-09-03 | 49 | 127.55 | 610 | 108
2021-09-02 | 48.05 | 127 | 610 | 108
2021-09-01 | 48.55 | 124 | 667 | 109
2021-08-31 | 49.2 | 124.7 | 663 | 117
2021-08-30 | 49.2 | 120.25 | 732 | 122
2021-08-29 | 49.2 | 120.25 | 830 | 120
2021-08-28 | 49.2 | 120.25 | 830 | 121
2021-08-27 | 47.4 | 120.25 | 830 | 121
2021-08-26 | 48.1 | 115.7 | 830 | 121
2021-08-25 | 47.8 | 115.05 | 781 | 119
2021-08-24 | 46.05 | 114.3 | 735 | 117
2021-08-23 | 44.4 | 110.2 | 686 | 125
2021-08-22 | 44.4 | 108.85 | 709.05 | 131
2021-08-21 | 44.4 | 108.85 | 649 | 128
2021-08-20 | 45.7 | 108.85 | 649 | 126
2021-08-19 | 45.9 | 105.75 | 649 | 126
2021-08-18 | 46.05 | 113.6 | 635 | 124
2021-08-17 | 45.05 | 117.9 | 626 | 123
2021-08-16 | 44.55 | 119.15 | 630 | 123
2021-08-15 | 44.55 | 113.6 | 626.5 | 123
2021-08-14 | 44.55 | 113.6 | 597 | 118
2021-08-13 | 44.05 | 113.6 | 597 | 118
2021-08-12 | 43.7 | 115 | 597 | 118
2021-08-11 | 44.15 | 114.75 | 599.9 | 118
2021-08-10 | 44.3 | 111.9 | 597.5 | 118
2021-08-09 | 44.55 | 109.8 | 575 | 119
2021-08-08 | 44.55 | 109.35 | 585.5 | 114
2021-08-07 | 44.55 | 109.35 | 590.5 | 114
2021-08-06 | 44.25 | 109.35 | 590.5 | 114
2021-08-05 | 43.7 | 109.3 | 590.5 | 114
2021-08-04 | 43.3 | 107.45 | 600 | 113
2021-08-03 | 42.65 | 105.75 | 560 | 113
2021-08-02 | 41.65 | 106.45 | 559 | 112
2021-08-01 | 41.65 | 104.35 | 555 | 113
2021-07-31 | 41.65 | 104.35 | 539 | 116
2021-07-30 | 41.45 | 104.35 | 539 | 115
2021-07-29 | 41.55 | 104.4 | 539 | 115
2021-07-28 | 40.9 | 101.5 | 558 | 115
2021-07-27 | 40.55 | 98 | 556 | 120
2021-07-26 | 41.35 | 97.6 | 540 | 120
2021-07-25 | 41.35 | 94.7 | 495 | 124
2021-07-24 | 41.35 | 94.7 | 470 | 123
2021-07-23 | 41.8 | 94.7 | 470 | 122
2021-07-22 | 41.4 | 95.8 | 470 | 122
2021-07-21 | 41.6 | 96.35 | 465 | 121
2021-07-20 | 41.05 | 95.2 | 477.5 | 123
2021-07-19 | 43 | 96.25 | 467.5 | 121
2021-07-18 | 43 | 94.35 | 473.3 | 119
2021-07-17 | 43 | 94.35 | 450 | 114
2021-07-16 | 42.8 | 94.35 | 450 | 114
2021-07-15 | 44 | 91.9 | 450 | 114
2021-07-14 | 44.25 | 92.4 | 468 | 115
2021-07-13 | 44.35 | 94.9 | 465 | 114
2021-07-12 | 44 | 93.4 | 446 | 114
2021-07-11 | 44 | 98.05 | 423 | 116