## Generic Tender Query Log
NATIONAL GRID ESO Voltage 2026 EOI Query Log
Tender Reference |  | Voltage 2026 - EOI Stage
Date |  | 2023-11-01
Version Number |  | V1
| TQ Date (dd/mm/yy) | Do you class this Tender Query as Confidential (Yes/No) | Technical/ Commercial Query | Tender Stage (Pre-tender, RFI, EOI, ITT, Contract Award) | Document Reference (if applicable) | Question Reference (if applicable) | Query | Received Attachments | Query Response | Associated Attachments (if applicable) | Open or Closed? | Date Response Issued
1 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Why does this tender consider only two regions? | none | Voltage management is a locational issue, and the London and North England regions are the ones where a requirement has been identified with a lack of existing cost-effective solutions to manage high voltage issues. Voltage compensation connected far from the region of need will not be effective. | none | Closed | 2023-10-20
2 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | How are the effectiveness factors calculated? | none | Voltage sensitivities with respect to reactive power compensation are extracted from the load flow equations. They are then normalised in relation to the sensitivity at the reference point to obtain the effectiveness factors for each location. | none | Closed | 2023-10-20
3 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Will injection capability impact in the solution's assessment? | none | No, at this stage the intention is the assessment will be based on the absorption capability only. However, the declared Mvar range must be accessible and meet the availability requirement. Please note at this stage we have not published the assessment methodology for the Voltage 2026 tender, this will be shared at the ITT stage and will detail how solutions will be assessed. | none | Closed | 2023-10-20
4 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | What were the assumptions used to perform high voltage studies? | none | High voltage studies consider credible future scenarios of minimal demand conditions. | none | Closed | 2023-10-20
5 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | For the bay reserved at Neepsend 275kV, what is the reserved SCL and MW? | none | There is no reserved SCL or MW values. The reservation is for reactive power only. For more details please refer to the Technical Specification document and Connections Approach document. | none | Closed | 2023-10-20
6 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Are there additionality criteria for existing connections? | none | No, existing connections can participate without additional capability. Please refer to Section 8 and Appendix B of our instructions to tenderers document for more information (https://www.nationalgrideso.com/document/289716/download) | none | Closed | 2023-10-20
7 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Can hybrid technologies be tendered, such as battery and reactor? | none | Hybrid technologies can be tendered provided they are submitted as one solution at the same connection point. They will then be treated and assessed as a single asset/solution. | none | Closed | 2023-10-20
8 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Can you put the links to the Technical Document, here or in the chat please. | none | After the webinar we will send a follow up email to everyone who registered with links to the voltage 2026 webpage on the ESO website, specifically pointing out the Technical Document, to ensure everyone has access. | none | Closed | 2023-10-20
9 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | How does the -200MVar requirement for each region compare to the requirements of previous pathfinders? how much was required and procured in previous rounds? | none | Pennines Voltage Pathfinder tendered 200MVar in the North East region and 500MVar in West Yorkshire. Mersey Voltage Pathfinder tendered for 230MVAr. | none | Closed | 2023-10-20
10 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Could you kindly provide the link for downloading the EOI require form? | none | After the webinar we will send a follow up email to everyone who registered with links to the voltage 2026 webpage on the ESO website, specifically pointing out the consultation feedback form, to ensure everyone has access. | none | Closed | 2023-10-20
11 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Are NGET 132kV connected solutions barred from participating, even as a smaller solution/contributor? | none | For clarity we understand this question to refers to third party solutions that are connected to NGET's 132kV network. The current tender rules are that solutions must be connected at 275kV and above, or directly connected to the transmission system. If you have any specific queries about how this applies to you please reach out to the Voltage 2026 team at box.voltage2026@nationalgrideso.com | none | Closed | 2023-10-20
12 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Are NGET allowed to compete in this tender? | none | This procurement process will adopt the same approach as other Voltage and Stability Pathfinders where TOs will be able to provide TO counterfactual options. | none | Closed | 2023-10-20
13 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Who is paying for the losses associated with providing MVArh? Is this paid at the ORPS rate? | none | At this stage the intention is that bidders submitted prices should cover all costs associated with providing the reactive power service, including losses and energy costs. For more information on commercial aspects we encourage attendance at our contract and commercial webinar. | none | Closed | 2023-10-20
14 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Do you need static or dynamic? | none | The requirement is for steady-state voltage control, However, the tender is on a technology agnostic basis. For more information please refer to the technical specification available on the ESO website (https://www.nationalgrideso.com/document/289721/download) | none | Closed | 2023-10-20
15 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | What is the contract length? | none | This procurement process is seeking to award 10-year long contracts between 2026 and 2036. There will be more information on the details of the draft contract in the commercial webinar on 26 October 2023. | none | Closed | 2023-10-20
16 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Is it possible to aggregate different reactive power sources for provision and make an offer. Or is it necessary to offer one particular asset for provision only. | none | Our understanding of this question is it is asking about aggregating a number of different assets which each have a different connection point. For the purpose of this tender aggregated solutions that are based on a number of assets which each have a different connection point are not being accepted. A change in the connection point is being treated as a separate solution. For more details please refer to Section 14 of the Instructions to Tenderers - EOI document and the Glossary of the same (https://www.nationalgrideso.com/document/289716/download). | none | Closed | 2023-10-20
17 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Are distribution connected sites allowed to compete in the tender? | none | The current tender rules are that solutions must be connected at 275kV and above, or directly connected to the transmission system. If you have any specific queries about how this applies to you please reach out to the Voltage 2026 team at box.voltage2026@nationalgrideso.com | none | Closed | 2023-10-20
18 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | can you reiterate the range of reactive power absorption acceptable per bid? | none | In our technical specification we have indicated potential maximum sizes (-200Mvar at 400kV and -100Mvar at 275kV) based on the usual figures that can be switched by a single circuit breaker without violating voltage step change limits at different voltage levels. However, this is subject to the actual maximum as defined by your connection. So bidders should see the maximum size they can bid as equivalent to the maximum that is catered for by their connection. Please use this link to access the technical specification https://www.nationalgrideso.com/document/289721/download | none | Closed | 2023-10-20
19 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | A lot of connections points featuring in the North of England also featured in the Pennines tender. Was there under-procurement in that pathfinder? | none | No, ESO keep monitoring future system conditions and the regions of need have been identified based on updated analysis which has indicated further needs. | none | Closed | 2023-10-20
20 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | If the TO can bid but they don't pay for losses, is this a fair playing field? | none | As we are only at the EOI stage, we have not yet published the assessment methodology which will set out how third-party market participant bids or TO options would be assessed. The intention is this document would be provided at ITT stage and set out how a fair playing field will be enabled. This will be in line with approaches taken on previous Pathfinders to ensure a fair playing field. | none | Closed | 2023-10-20
21 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | Will you be taking any other factors into consideration other than solution capability when awarding the tender. i.e is this going to support new entrants and smaller organisations? | none | As we are only at the EOI stage, we have not yet published the assessment methodology which will set out how third-party market participant bids or TO options would be assessed. The intention is this document would be provided at ITT stage. | none | Closed | 2023-10-20
22 | 2023-10-20 | No | Technical | EOI | Technical webinar | Technical webinar | What is meant by Directly Connected to the Transmission System | none | A direct connection to any node inside the National Electricity Transmission System including tertiaries of transformers. | none | Closed | 2023-10-20
23 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | Who is paying for the losses associated with providing MVArh? Is this paid at the ORPS rate? | none | The intention is that bidders submitted prices should cover all costs associated with providing the reactive power service, including losses and energy costs. (Please note this was also covered in the technical webinar Q&A). | none | Closed | 2023-10-26
24 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | Will you be taking any other factors into consideration other than solution capability when awarding the tender. i.e is this going to support new entrants and smaller organisations? | none | As we are only at the EOI stage, we have not yet published the assessment methodology which will set out how third-party market participant bids or TO options would be assessed. The intention is this document would be provided at ITT stage. (Please note this was also covered in the technical webinar Q&A). | none | Closed | 2023-10-26
25 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | Are NGET allowed to compete in this tender? | none | This procurement process will adopt the same approach as other Voltage and Stability Pathfinders where TOs will be able to prove a TO counterfactual option. (Please note this was also covered in the technical webinar Q&A). | none | Closed | 2023-10-26
26 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | Will injection capability impact in the solution's assessment? | none | No, at this stage the intention is the assessment will be based on the absorption capability only. However, the declared Mvar range must be accessible and meet the availability requirement. At this stage we have not published the assessment methodology for the Voltage 2026 tender, this will be shared at the ITT stage and will detail how solutions will be assessed. (Please note this was also covered in the technical webinar Q&A). | none | Closed | 2023-10-26
27 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | could you clarify that providers will only submit 1 final offer to then be considered? i.e. there are no multiple bids or bidding rounds etc. | none | As we are only at the EOI stage, we have not yet published the assessment methodology which will set out how third-party market participant bids would be assessed, with reference to any negotiations or BAFO stages. The intention is this document would be provided at ITT stage to confirm these details. | none | Closed | 2023-10-26
28 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | In the contract is there Starting Late costs where there are delays caused by the TO in NGET connection date for particular substations ? | none | Generally, in the event a Provider does not meet their contracted service start date, then they become liable for liquidated damages at the LAD rate for each day of delay. The only exception to that is in the event of Delay Event which is defined by the Contract. | none | Closed | 2023-10-26
29 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | Will there be any potential extension in the contract post 2036? | none | The draft contract does include extension options up to a further 10 years in aggregate. Please refer to clause 2.5 for details where it is drafted such that both parties need to agree to extend the contract and for what duration. | none | Closed | 2023-10-26
30 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | Is the LAD Cap based on 160 days or 180 days? Both were stated within the webinar? | none | Apologies - this was an error during the presentation. We can confirm that the LAD cap is based on 180 days and NOT 160 days. | none | Closed | 2023-10-26
31 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | Can a project commissioning after 2026 bid in the auction with a caveat of 0 support offered in 2026 and services commencing in 2027/2028 as applicable? Would this project still be eligible for the auction? [redacted] | none | As we are only at the EOI stage, we have not yet published any latest acceptable start dates which may be required for the tender. The intention is this information would be provided at ITT stage. We encourage you to register and then consider the additional information made available at ITT to make your final decisions regarding whether you will bid. | none | Closed | 2023-10-26
32 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | These contracts are from April 2026 to 2036. But in terms of Scheduled Operations Date is that going to be the same for all providers i.e 1st April 2026 or is there some flexibility in agreeing an operations date? | none | As with previous pathfinders there will be some flexibility in commercial operations date as we appreciate this may vary slightly project by project. We may put a latest start date in place, if we do decide to take this approach it will be published at ITT stage. Please also refer to the question above as it is similar (TQ31). | none | Closed | 2023-10-26
33 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | How do PTMs apply to a delayed grid connection where the delay is the fault of the TO? If a termination sum could apply due to a delayed connection, then how does this allow fair treatment between TO and non-TO providers (since the TO can obviously control the risk whereas the non-TO provider cannot) | none | As currently drafted, the PTMs within the contract cover elements of the project that we would reasonably expect to be completed by twelve months prior to the scheduled commercial operations date. These include but are not limited to (and in no particular order): obtaining land, signing a connection agreement, securing funding and commencing onsite construction. A delayed grid connection wouldn’t necessarily impact progression on all of these PTMs so these would continue to be monitored. Additionally, there is provision within the contract for ESO to grant a two month extension to the PTM date if ESO believes there is a reasonable chance of them being completed within this time frame. If you have any feedback on any of the specific PTMs you think could be impacted by a TO caused delay then please do provide feedback for us to consider when finalising terms for ITT. If you are in doubt, we encourage you to submit an EOI and review any additional information made available at ITT to make your final decisions regarding whether you will bid. | none | Closed | 2023-10-26
34 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | does parent company guarantee require the same S&P rating as the stability mid-term tender, i.e. A- long-term S&P rating? | none | As we are only at the EOI stage, we have not yet published the assessment methodology which will set out how third-party market participant bids or TO options would be assessed. The intention is this document would be provided at ITT stage. | none | Closed | 2023-10-26
35 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | were previous pathfinders procuring and paying for absorption and injection , or just absorption only? | none | Previous Pathfinders were procuring absorption of reactive power only and availabiity payments were based on the ability to absort react power. | none | Closed | 2023-10-26
36 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | You mention that the GEP will be where the reactive capability is delivered. Can I clarify that in respect to offshore wind farms, (where GEP is on offshore platform) what you actually mean is the TIP (Transmission Interface Point)? | none | For offshore solutions, the onshore location of the Transmission Interface Point must be located within the regions of need. Refer to the Part 2 of the "V2026 Technical Specification". | none | Closed | 2023-10-26
37 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | Can you explain the MSA/ ORPS applicability in a bit more detail? Does MSA cover the capability for existing asset or connection point? i.e. if you connect a new asset , does existing MSA apply to that additional capability? | none | The MSA (Mandatory Services Agreement) covers the Mandated capability as part of the Grid Code requirements. Some assets have additional capability (over & above what is mandated in the Grid Code). Any additional capability over & above what is mandated is usually captured in a CSA (Commercial Services Agreement). | none | Closed | 2023-10-26
38 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | Hi, are 132kV-connected assets eligible for this service, or is it just 275 & 400? | none | For clarity we understand this question to refer to third party solutions that are connected to NGET's 132kV network. The current tender rules are that solutions must be connected at 275kV and above, or directly connected to the transmission system. If you have any specific queries about how this applies to you please reach out to the Voltage 2026 team at box.voltage2026@nationalgrideso.com | none | Closed | 2023-10-26
39 | 2023-10-26 | No | Commercial | EOI | Commercial webinar | Commercial webinar | Will HVDC interconnectors be able to take part? | none | Please can we refer you to Section 2 of our Instructions to Tenderers, specifically the latter part of the table on page 6, for what has been published with regards to participation rules. If you have any specific questions about whether you would be eligible to participate based on specific details please reach out to us directly by email at box.voltage2026@nationalgrideso.com | none | Closed | 2023-10-26
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91

## ProcInspection (hidden)
Procurement Excel Wookbook Inspection
Date: | 2023-10-27 15:33
UserName: | alexandra.millar
Workbook Secure: | TRUE
HyperLinks List
| Worksheet Name | No of Embedded Documents | Is Worksheet Hidden | HyperLinks | Protected | External Excel Links | Worksheet Name | Cell Reference | HyperLink
| Generic Tender Query Log | 0 | No | 0 | Yes