## Slide 1: The Application of EREC P2 and EREP 130 to Electricity Storage
Steve Quinn
  03/08/2023

## Slide 3: What
Annex 1 Standard EREC P2 (Security of Supply) sets out engineering requirements to limit the socioeconomic disruption that would result from reasonably foreseeable distribution system outages.
Although intended to benefit final demand customers (i.e., electricity consumers), the current version (EREC P2 Issue 8) extends the same security of supply to electricity imported by Electricity Storage customers.

## Slide 4: Why
Applying EREC P2 to the import of fungible customers such as Electricity Storage can result in a requirement to reinforce the system to provide enhanced security of supply which may be uneconomic.
This issue is most profound when Electricity Storage customers come to dominate groups. The final demand customers in groups without significant Electricity Storage capacity receive lower security of supply than those in otherwise similar groups with Electricity Storage; this is a source of inconsistency.
The unprecedented growth in Electricity Storage projects, and the application of EREC P2, has triggered extensive reinforcement, preventing the timely and economic connection of subsequent final demand customers. This has the potential to delay societal decarbonisation.

## Slide 5: How
Redefine Group Demand in Annex 1 Standards EREC P2 and EREP 130 to not count the import behaviour of premises whose primary purpose is wholly or mainly Electricity Storage towards Group Demand.
A wider review of how access rights are defined and governed for different types of customers might prove necessary.

## Slide 7: Timeline
 | Aug 23 | Sep 23 | Oct 23 | Nov 23 | Dec 23 | Jan 24 | Feb 24 | Mar 24 | Apr 24 | May 24 | Jun 24 | 
Interim report to DCRP
Workgroup
Authority decision
Implementation
Consultation
Final report to DCRP

## Slide 8: Appendix A: Relevant Objectives
Objective | Identified Impact | Rationale
Permit the development, maintenance, and operation of an efficient, co-ordinated, and economical system for the distribution of electricity | Positive | The distribution system would be made more economical by avoiding inappropriate reinforcement. It would be made more coordinated by better alignment with SQSS.
Facilitate competition in the generation and supply of electricity | Neutral to Positive | A more economical distribution system is likely to lead to less onerous Minimum Schemes, so reducing barriers to entry.
Efficiently discharge the obligations imposed upon distribution licensees by the distribution licences and comply with the Regulation and any relevant legally binding decision of the European Commission and/or the Agency for the Co-operation of Energy Regulators | Neutral | No impact identified by the Proposer.
Promote efficiency in the implementation and administration of the Distribution Code | Neutral | No impact identified by the Proposer.

## Slide 9: Appendix B: Consumer Impacts
Customers applying for new or augmented connections would be less likely to be subject to long delays and/or expensive reinforcement because of capacity contracted to Electricity Storage sites.
The EREC P2 Class of Supply (and so level of security) afforded to groups of final demand customers would not depend upon whether there happens to be significant Electricity Storage connected within the group. As such it would be possible to apply the intended principles of EREC P2 more consistently between groups with and without Electricity Storage.

## Slide 10: Appendix C: Cross-Code Impacts
Ongoing SQSS modification GSR029 (“Review of Demand Connection Criteria to Align with EREC P2/7”) is intended to amend the demand data provided by Network Operators used by NGESO when undertaking a SQSS Section 3 compliance assessment to better align to that in EREC P2/7 (now P2/8). is understood that the treatment of Electricity Storage is under consideration as part of this modification. The Proposer recommends that this modification’s Workgroup coordinates with GSR029’s Workgroup to promote cross-code consistency where appropriate.
This modification would clarify the applicability of EREC P2 to the import access rights of Electricity Storage and potentially Distributed Generation customers. It is not entirely clear whether access rights are a DCode or DCUSA matter, however it is important that the access rights, security of supply and Minimum Scheme implications stated or implied by these two codes are harmonised. The Proposer recommends that this modification’s Workgroup considers this issue in more detail and, if appropriate, raises a consequential modification proposal to DCode or DCUSA.

## Slide 11: Appendix D: Considerations for the Workgroup
Undue discrimination: it might be appropriate to extend the scope to include the import supplies to premises whose purpose is wholly or mainly Electricity Generation.
Final Demand at Electricity Storage sites: It might remain necessary to secure that fraction of an Electricity Storage customer’s import as is necessary for safety, security, and staff welfare. This might be via alternative exit points (like station transformers) rather than via the main exit point (like unit transformers).
EREP 130: Examples that refer to Electricity Storage will need to be updated to align to the new definition of Group Demand. New examples might also be needed.
Access rights: the proposal doesn’t change individual customers’ access rights in connection agreements but would affect aggregate security of supply to groups of customers. Curtailment makes the description of access rights more complex than “on” or “off”. See also Cross-Code Impacts.
Network capability: The proposed solution would increase the distinction between EREC P2 compliance and ensuring that network capability is not exceeded. This is a pre-existing issue (e.g. three-circuit groups <100MW). It might be necessary to set a general requirement to ensure that network capability is not exceeded for reasonably foreseeable combinations of network loading and outages.
DSR: It might be necessary to distinguish between V&C of final demand and import to Electricity Storage.