## Cover
TO COMPLIANCE MONITORING STATEMENT v4_20240710 Please select onshore or offshore from the tabs below. V4_20240710 published 10th July 2024. For the latest version please visit the NGESO website or talk to a NGESO Compliance Manager. This is a template. Please ensure that you update the TO Compliance Monitoring Statement with technical requirements from the TOCA. For more information on the TO Compliance Monitoring Statement please see STCP 19-3 PLEASE DO NOT DELETE THIS COVER SHEET

## TO Compliance Outputs
TO Compliance Monitoring Statement
The TO Compliance Monitoring Statement should be provided to ESO alongside the TO Agreement for Energisation and the TO Agreement for ION/ION A/ION B. The final version, with all items closed and signed off, should be provided to ESO before FON.
Although ESO provide a template, STCP 19 3 (3.2.16) specifies that the TO should produce the TO Compliance Monitoring Statement and share it with ESO. The TO Lead Representative should update each Project's TO Compliance Monitoring Statement as needed.
Certificates of Readiness
For Onshore Direct Connections the TO should countersign: - CoR to Commence Commissioning - CoR to Complete Commissioning - CoR to Energise HV equipment For Embedded Connections where there is a TOCO the TO should countersign: - CoR to Use the Transmission System
The process for Offshore Direct Connections (AC and DC) is being finalised (April 2024)
Agreement for Energisation / Agreement for ION
For onshore direct connections and embedded connections where there is a TOCO the TO should provide to ESO the following Letters of Agreement: - Letter of Agreement for Energisation - Letter of Agreement to Issue ION (which should include a schedule of unresolved issues)
For offshore direct connections the TO should provide to ESO the following Letters of Agreement: - Letter of Agreement for Energisation - Letter of Agreement for ION A (which should include a schedule of unresolved issues) - Letter of Agreement for ION B (which should include a schedule of unresolved issues)
Examples of these Letters of Agreement can be found in the Appendices to STCP 19-3
Email confirmation that FON can be issued
For direct connections and embedded connections where there is a TOCO: the TO should confirm to ESO, via email, that they have no objection to a FON being issued. This should be accompanied by the final TO Compliance Monitoring Statement.

## Onshore
TO COMPLIANCE MONITORING STATEMENT
Customer:
Connection Site:
Date of Bilateral/Construction Agreement:
Comm. Prog. Commencement Date:
Transmission Owner
TO Lead Representative
Item No. | Information/Data and Activity Requirements | Code | User Data File Structure Ref. | Initiator | TO Responsible Unit has approved Y/N | Date of Approval | Approved Signature | Required before EON / ION / FON? | TO Comments
BEFORE ENERGISATION (ENERGISATION OPERATIONAL NOTIFICATION)
1 | TO representative confirms ONCC requirements cross checked with TOCO/no additional requirements from TOCO |  |  | TO
2 | User has received safety rules (or relevant extracts) from the TO | STC | 1.2 | User
3 | Safety Rules applicable during commissioning agreed with Transmission Owner | OC8/ ECC5.2.1(c) CONSAG 2.1 | 1.2 | User
4 | Safety Rules applicable after commissioning: agreed with Transmission Owner | OC8/ ECC5.2.1(c) CUSC 2.10 | 1.2 | User
5 | Local Safety Instructions applicable during commissioning agreed with Transmission Owner / OC8 Compliance | OC8/ ECC5.2.1(c) CONSAG 2.1 | 1.9 | User
6 | Local Safety Instructions applicable after commissioning agreed with the Transmission Owner /OC8 Compliance | OC8/ ECC5.2.1(c) CUSC 2.10 | 1.9 | User
7 | RISSP prefixes agreed | ECC 5.2(h) | 1.11 | User
8 | AC system Voltage Variations | ECC.6.1.4 - 8/ PC.4.4.1/ PC.4.4.2/ PC.4.5/ PC.A.5.4.2 (h) / PC.A.4.8 | 2.1.3, 3.5 | User
9 | Harmonic Assessment Information: TO to carry out harmonic assessment and provide Performance Specification (harmonic emission limits) to User for inclusion in App F5 | ECC.6.1.5 - 8 App F5 | 2.1.3, 3.4 | TO
10 | Commissioning Programme issued | CONSAG 2.10 | A.2 | TO
11 | Special Automatic Facilities - Confirmation of design assurance | CONSAG 5.3.1 & BCA App F3 | 2.3 | TO
12 | Control Telephony and exchange of numbers for Joint System Incidences | ECC.6.5.2/ ECC.6.5.5 TOCA | 1.8 | User
13 | For Black Start Providers: Local Joint Restoration Plan | OC9.4.5 | 1.14 | User/ TO
14 | Operation Diagrams and Gas Zone Diagram for the Connection Point | ECC5.2.1(e)/ ECC7.4 CONSAG 5.2 | 1.6 | User / TO
15 | Site Common Drawings – to be agreed and exchanged | ECC5.2.1(k)/ ECC7.5 CONSAG 5.2 | 1.7 | User / TO
16 | Protection Settings Report (inc. Protection of Interconnecting Connections) | ECC6.2.2.3.1 BCA 8 & App F5 & App F4 Schedule 1 | 2.2 | TO / User
17 | Circuit Breaker fail | ECC6.2.2.3.1 BCA 8 & App F5 | 2.1.2 | TO
18 | Earthing | ECC6.3.11 (ECC6.2.1.1.(b), BCA App F5 | 1.4 | TO
19 | Fault Disconnection Facilities (Trip User CB from GB Transmission System protection) | ECC6.2.3.2 BCA App F5 | 2.1.2 | TO
20 | Power Quality Monitoring: Immediately Pre-conection - Undertake power quality voltage measure ments to establish a baseline for compliance. | ECC.6.1.5-8 | 3.1.4, 2.7.3 | TO
21 | Safety Co-ordinators - confirmation of authorisation and competence | ECC 5.2.1(g)/ OC 8 A4.2.1 CONSAG 5.4 | 1.9 | User
22 | Harmonic Assessment Information: User to procure/ install / commission harmonic mitigation measures as required by Performance Specification. | ECC.6.1.5 - 8 | 2.1.3, 3.4 | User
23 | Interface Agreement(s) with Transmission Owner | ECC7.6 / CUSC 2.11 | 1.1 | User / TO
23a | TO Lead Representative confirms no additional Compliance Requirements as a result of Interface Agreement
24 | Site Responsibility Schedules - Exchange of Information for preparation and confirmation of who is authorised to sign | ECC5.2/ECC7.3/ECC.A.1/ CONSAG 5.4 | 1.5 | User / TO
25 | Site Responsibility Schedules - Issue | ECC5.2/ECC7.3/ECC.A.1 | 1.5 | TO
26 | Commissioning Switching Programme | ECC5.2/ECC7.3/ECC.A.1 | A.2 | User
26a | Plant Status Indications being received |  |  | TO
26b | Sub synchronous resonance | Appendix F5 |  | User
27 | Action: TO to sign CoR to Commence Commissioning Programme (Proforma initiated by User) | STC |  | User | n/a | n/a | n/a
28 | Action: TO to sign CoR to Complete Commissioning Programme (Proforma initiated by User) | STC |  | User | n/a | n/a | n/a
29 | Action: TO to sign CoR to Energise High Voltage Equipment (Proforma initiated by User) | STC |  | User | n/a | n/a | n/a
30 | Action: TO to issue Letter of Authorisation to issue EON to NGESO | STC |  | TO | n/a | n/a | n/a
BEFORE EXPORT OF ACTIVE POWER (INTERIM OPERATIONAL NOTIFICATION)
31 | TO has received control system model | STC |  | User
32 | Action: TO to issue Letter of Authorisation to issue ION to NGESO and TO Compliance Monitoring Statement | STC |  | TO | n/a | n/a | n/a
33 | Action: TO to provide items for inclusion in the Schedule of Unresolved Issues to NGESO | STC |  | TO | n/a | n/a | n/a
BEFORE FINAL OPERATIONAL NOTIFICATION (FON)
34 | Power Quality Monitoring: Confirm mitigating measures to meet potential distortion limits as specified in Bilateral Agreement during and after commissioning.
35 | TO confirms that they have a valid control system model | STC |  | TO
36 | Action: TO to provide email confirmation agreeing to issue of FON. The TO Compliance Monitoring Statement should be attached to this email. | STC |  | TO | n/a | n/a | n/a
Note on I14: Whitty(ESO), Rhiannon: Please enter the name of the person who has received approval in the TO. For example, this could be a Project Engineer who is collating feedback from multiple departments
Note on J14: Whitty(ESO), Rhiannon: The yellow headings are intended as a guideline, if you have an agreement with a User which differs please update this column
Note on C39: Rhiannon Whitty (ESO): For example, if Interface agreement allows for User acess to TO HV Compound is there any additional security etc checks needed on User CPs?

## Offshore
TO COMPLIANCE MONITORING STATEMENT
Customer:
Connection Site:
Date of Bilateral/Construction Agreement:
Comm. Prog. Commencement Date:
Transmission Owner
TO Lead Representative
Item No. | Information/Data and Activity Requirements | Code | User Data File Structure Ref. | Initiator | TO Responsible Unit has approved Y/N | Date of Approval | Approved Signature | Required before EON / ION / FON? | TO Comments
BEFORE ENERGISATION OPERATIONAL NOTIFICATION (EON) AND INTERIM OPERATIONAL NOTIFICATION PART A (ION A)
1 | TO representative confirms ONCC requirements cross checked with TOCO/no additional requirements from TOCO
2 | User has received safety rules (or relevant extracts) from the TO | STC | 1.2 | User
3 | Safety Rules applicable at the Interface Point during commissioning - agreed with the Transmission Owner | OC8 / ECC.5.2.1(c) ConsAg 2.1 | 1.2 | OTSDUW User
4 | Safety Rules applicable at the Interface Point after commissioning - agreed with the Transmission Owner | OC8 / ECC5.2.1(c) CUSC 2.10 | 1.2 | OTSDUW User
5 | Local Safety Instructions applicable at the Interface Point during commissioning agreed - with the Transmission Owner / OC8 Compliance | OC 8/ ECC5.2.1(c) ConsAg 2.1 | 1.9 | OTSDUW User
6 | Local Safety Instructions applicable at the Interface Point after commissioning - agreed with the Transmision Owner / OC8 Compliance | OC8 / ECC.5.2.1(c) CUSC 2.10 | 1.9 | OTSDUW User
7 | RISSP prefixes agreed | ECC 5.2(h) | 1.11 | User
8 | Safety Co-ordinators - confirmation of authorisation and competence in respect of the Interface Point | ECC 5.2.1(g ) / OC8, A4.2.1 a7 ConsAg 5.4 | 1.9 | OTSDUW User
9 | Commissioning Programme issued in respect of the Interface Point | ConsAg 2.10 | A.2 | User
10 | Special Automatic Facilities applicable to the Interface Point | ConsAg 5.3.1 & 8 - App OF3 Items 1.1, 1.3, 2, 3 & 4.1
|  | OF3 Item 1.1: Facilitation of Category 2 Transmission System to Generating Unit Intertripping Schems | 2.3 | TO / OTSDUW User
OF3 Item 1.3: Facilitation of Category 4 Transmission System to Generating Unit Intertripping Schemes
OF3 Item 1: Automatic Open / Closure Schemes
OF3 Item 1: System Splitting / Islanding Schemes
OF3 Item 2: Syncronising Requirements at the Interface Point
| Special Automatic Facilities applicable to the Offshore Connection Site | ConsAg 5.3.1 & BCA 8 - App F3 items 1.1, 1.2, 2, 3 & 4 plus App OF3 item 4.2 |  | TO / OTSDUW User / User
|  | F3 Item 1: Category 2 Transmission System to Generating Unit Intertripping Schemes | 2.3 | TO / OTSDUW User / User
F3 Item 1.2: Category 4 Transmission System to Generating Unit Intertripping Schemes
F3 Item 1: Automatic Open / Closure Schemes
F3 Item 3: System Splitting / Islanding Schemes
F3 Item 2: Syncronising Requirements at the Offshore Grid Entry Point
OF3 Item 2.2: Syncronising Requirements at the Offshore Grid Entry Point
11 | Control Telephony and exchange of numbers for Joint System Incidences | ECC.6.5.2/ ECC.6.5.5 TOCA | 1.8 | User
12 | For Black Start Providers: Local Joint Restoration Plan | OC9.4.5 | 1.14 | User/ TO
13 | Maintenance Standards (on request) applicable to the Interface Point | ECC.7.7 | 1.3 | TO / OTSDUW user
14 | Safety and Operational Interlocking applicable to the Interface Point | App OF5 item 10 | 2.1.2 | TO / OTSDUW User
15 | Operation Diagrams and Gas Zone Diagram applicable to Iinterface Point. | ECC.5.2.1(e) / ECC.7.4 & ConsAg 5.1 & 5.2 | 1.6 | TO / OTSDUW User (via Comm Panel)
| Operation Diagrams and Gas Zone Diagram applicable to Connection Site | ECC.5.2.1(e) / ECC.7.4 & ConsAg 5.1 & 5.2 | 1.6 | OTSDUW User & User
16 | Site Common Drawings applicable to the Iinterface Point | ECC.5.2.1(k) / ECC.7.5 ConsAg 5.2 | 1.7 | TO / OTSDUW User (via Comm Panel)
| Site Common Drawings applicable to the Offshore Connection Site | ECC.5.2.1(k) / ECC.7.5 ConsAg 5.1 & 5.2 | 1.7 | TO / User
17 | Relay Settings and Protection Arrangements applicable to the Interface Point | ECC.6.2.2.5 & ECC.6.2.2.2 - App OF4 items 1.1 plus App OF4 Schedule 1 and 2.1 |  | TO / OTSDUW User
|  | OF4 Item 1.1: Relay Settings | 2.2 | TO / OTSDUW User
OF4 Item 1.1: Schedule 1
OF4 Item 2.1: Protection Arrangements
18 | Protection Settings Report (inc. Protection of Interconnecting Connections) applicable to the Interface Point | ECC.6.2.2.3.1 - App OF5 Item 1.1 | 2.2 | TO / OTSDUW User
19 | Circuit Breaker Fail Protection applicable to the Interface Point | ECC.6.2.2.3.2 - App OF5 item 2.1 | 2.1.2 | TO / OTSDUW User
20 | Earthing applicable to the Interface Point | ECC.6.3.11 (ECC.6.2.1.1.(b)) - App OF5 item 11.1 | 1.4 | TO / OTSDUW User
21 | Fault Disconnection Facilities (Trip User Circuit Breakers from NETS protection) - applicable to the Interface Point | ECC.6.2.3.2 - App OF5 item 3 | 2.1.2 | TO / OTSDUW User
22 | Safety and Operational Interlocking applicable to the Interface Point | App OF5 item 10 | 2.1.2 | TO / OTSDUW User
23 | Confirm mitigating measures to meet potential distortion limits in ConsAg (Harmonic distortion, flicker, NPS) applicable to the Interface Point | ECC.6.1.5 to ECC.6.1.8 - App OF5 items 4.6.1, 4.6.2, 4.7 and 4.8 plus Schdule 1 |  | User
|  | App OF5 Item 4.6.1: Harmonic Performance | 3.1.4, 2.7.3 | OTSDUW User
|  | App OF5 Item 4.6.2: Voltage Phase Unbalance | 3.1.4, 2.7.3 | OTSDUW User
|  | App OF5 Item 4.7: Power Quality Monitoring | 3.1.4, 2.7.4 | OTSDUW User
|  | App OF5 Item 4.7: Power Quality Monitoring - background measurement | 3.1.4, 2.7.5 | OTSDUW User
|  | App OF5 Item 4.8: Electro Magnetic Transients | 3.1.4, 2.7.5 | OTSDUW User
|  | App OF5 Schedule 1 |  | NGESO / OTSDUW User
| Confirm mitigating measures to meet potential distortion limits in Bilateral Agreement (Harmonic distortion, flicker, NPS) applicable to the Offshore Connection Site | ECC.6.1.5 to ECC.6.1.8 - App F5 items 5.7.1, 5.7.2, 5.7.3 and 5.8
|  | App F5 Item 5.7.1: Voltage Waveform Quality Assessment | 3.1.4, 2.7.3 | User / TO / OTSDUW User
|  | App F5 Item 5.7.2: Voltage Phase Unbalance | 3.1.4, 2.7.4 | OTSDUW USER / TO / User
|  | App F5 Item 5.7.3: Power Quality Monitoring | 3.1.4, 2.7.5 | OTSDUW USER / TO / User
|  | App F5 Item 5.8: Electro Magnetic Transients | 3.1.4, 2.7.3 | User
24 | AC system Voltage Variations | ECC.6.1.4 - 8/ PC.4.4.1/ PC.4.4.2/ PC.4.5/ PC.A.5.4.2 (h) / PC.A.4.8 | 2.1.3, 3.5 | User
25 | Interface Agreement(s) with National Grid applicable to the Interface Point | ECC.7.6 / CUSC 2.11 | 1.1 | TO / OTSDUW User
25a | TO Lead Representative confirms no additional Compliance Requirements as a result of Interface Agreement
26 | Site Responsibility Schedules - Persons authorised to sign applicable to the Interface Point | ECC.5.2 / ECC.7.3 / ECC.A.1 / ConsAg 5.4 | 1.5 | TO / OTSDUW User
27 | Site Responsibility Schedules - Exchange of Information for preparation applicable to the Interface Point | ECC.5.2 / ECC.7.3 / ECC.A.1 / ConsAg 5.4 | 1.5 | TO / OTSDUW User
28 | Site Responsibility Schedules - Issue applicable to the Interface Point | ECC.5.2 / ECC.7.3 / ECC.A.1 | 1.5 | TO / OTSDUW User
28a | Plant Status Indications being received
28b | Sub synchronous resonance | Appendix F5 |  | User
29 | Power Quality Monitoring: Immediately Pre-conection - Undertake power quality voltage measure ments to establish a baseline for compliance. | ECC.6.1.5-8 | 3.1.4, 2.7.3 | TO
30 | Action: TO to sign CoR to Commence Commissioning Programme (Proforma initiated by User)
31 | Action: TO to sign CoR to Complete Commissioning Programme (Proforma initiated by User)
32 | Action: TO to sign CoR to Energise High Voltage Equipment (Proforma initiated by User)
33 | Action: TO to issue Letter of Authorisation to Issue EON to NGESO
34 | Action: TO to issue Letter of Authorisation to issue ION A to NGESO and TO Compliance Monitoring Statement
35 | Action: TO to provide items for inclusion in the Schedule of Unresolved Issues to NGESO
BEFORE SYNCHRONISATION (INTERIM OPERATIONAL NOTIFICATION PART B)
36 | Action: TO to issue Letter of Authorisation to issue ION B and TO Compliance Monitoring Statement to NGESO
37 | Action: TO to provide items for inclusion in the Schedule of Unresolved Issues to NGESO
BEFORE FINAL OPERATIONAL NOTIFICATION
38 | Power Quality Monitoring: Confirm mitigating measures to meet potential distortion limits as specified in Bilateral Agreement during and after commissioning.
39 | TO confirms that they have a valid control system model
40 | Action: TO to provide email confirmation agreeing to issue of FON. The TO Compliance Monitoring Statement should be attached to this email.
Note on I13: Whitty(ESO), Rhiannon: Please enter the name of the person who has received approval in the TO. For example, this could be a Project Engineer who is collating feedback from multiple departments
Note on J13: Whitty(ESO), Rhiannon: The yellow headings are intended as a guideline, if you have an agreement with a User which differs please update this column
Note on C68: Rhiannon Whitty (ESO): For example, if Interface agreement allows for User acess to TO HV Compound is there any additional security etc checks needed on User CPs?

## Changes
Version | Onshore/Offshore | Item Number | Change | Reason for Change
v2_20240215 | Offshore | 10 | remove reference to BP117 | BP117 is an ESO process, not relevant to TOs
v2_20240215 | Offshore | 11 | added requirement for joint system incidents | sign off required
v2_20240215 | Offshore | 12 | added requirement: For Black Start Providers: Local Joint Restoration Plan | sign off required where applicable
v2_20240215 | Both | N/A | removed heading 'before start of commissioning' | Commissioning does not align to an ESO issued Operational Notification
v3_20240424 | Both | 1 | Updated to prompt TO Lead Representative to check against TOCO not BCA | TO does not have visiblity of BCA. TO technical requirements are captured in TOCO
v3_20240424 | Onshore | 23a | Item added | Raised at TO-SO workshop that additional Compliance Requirements might be needed after Interface Agreement (eg security checks of User staff accessing TO HV Compounds)
v3_20240424 | Offshore | 25a | Item added | Raised at TO-SO workshop that additional Compliance Requirements might be needed after Interface Agreement (eg security checks of User staff accessing TO HV Compounds)
v3_20240424 | Both | 5 | wording updated | updated to include 'OC8 Compliance'
v3_20240424 | Both | 6 | wording updated | updated to include 'OC8 Compliance'
v4_20240710 | Both | 26a / 28a | Item added | TO to confirm that they have visibility of plant status indications for issue of EON
v4_20240710 | Both | 26b / 28b | Item added | Sub Synchronous Resonance