## Version
Date | Version | Details
2024-03-14 | 1 | This file only contains the indicative reporting associated with draft data for GC0151 for March 2024. This file will be updated in April 2024 to reflect the full data set.
2024-04-15 | 2 | This file only contains the indicative reporting associated with data for GC0151 for March 2024. This file is updated in April 2024 to reflect the full data set.
2023-05-31 | 3 | This file only contains the reporting associated with data for GC0105 & GC151 for March 2024.

## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.
MW trip/loss of all generation/ interconnection related to the incident | Positive sign: indicates a loss of infeed, generator or importing interconnector. Negative sign: indicates a loss of outfeed, exporting interconnector.

## Transmission Faults (GC0151)
Location | Network Operator | Date Time | Voltage Trace (Refer to sheet) | Notes
Fault of Arbroath 132/33kV GT2 Circuit | SHETL | 2024-03-07 02:56
Tongland - Glenlee 132kV | SPT | 2024-03-16 05:59
Neepsend - Pitsmoor 275kV circuit and Pitsmoor SGT3 | NGET | 2024-03-26 01:43
Drax-Keady-Thorpe Marsh 400kV circuit | NGET | 2024-03-28 00:29 | V20240328-1
Fernoch-Inverary-Taynuilt 132kV circuit and the Inveraray-NantTaynuilt 132kV Double Circuit | SHETL | 2024-03-30 12:48
Beauly-Nairn-Elgin-Keith North and Beauly-Inverness-Nairn-Elgin-Keith 132kV South Double Circuit | SHETL | 2024-03-30 15:12

## System Incidents (GC0105)
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident |  | Where known, MW trip/loss of all DNO demand related to the incident; |  | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) |  | Demand (MW) |  | Transmission fault | Voltage Dip | Additional data
20240301-1 | Trip of IFA2 | IFA2 tripped while delivering 848MW from France to GB | 2024-03-01 06:12 | 20240301-1 | 50.029 | 49.771 | -0.11953 | 193 | IFA2 | 847.99
20240304-1 | Trip of BRITNED | BRITNED tripped while delivering 676MW from Netherland to GB | 2024-03-04 14:00 | 20240304-1 | 49.964 | 49.823 | -0.069701 | 222 | BRITNED | 676.211
20240306-1 | Trip of WBURB-2 |  | 2024-03-06 07:46 | 20240306-1 | 50.039 | 49.878 | -0.032656 | 268 | WBURB-2 | 428.156
20240307-1 | Loss of Supply at Arbroath 33KV substation |  | 2024-03-07 02:55 | 20240307-1 |  |  |  | 160 |  |  |  |  | Arbroath | 14 | Fault of Arbroath 132/33kV GT2 Circuit
20240308-1 | Trip of Viking Link | Viking link tripped while delivering 676MW from GB to Denmark | 2024-03-08 04:02 | 20240308-1 | 50.116 | 50.243 | 0.098964 | 130 | Viking Link | -648.9
20240311-1 | Trip of Viking Link | Viking link tripped while delivering 1399MW from Denmark to GB | 2024-03-11 09:56 | 20240311-1 | 49.891 | 49.634 | -0.13628 | 267 | Viking Link | 1398.96
20240313-1 | Trip of DRAXX-3 |  | 2024-03-13 15:31 | 20240313-1 | 50.118 | 49.914 | -0.08551 | 209 | DRAXX-3 | 626.95
20240319-1 | Trip of CDCL-1 |  | 2024-03-19 09:29 | 20240319-1 | 49.913 | 49.812 | -0.065575 | 154 | CDCL-1 | 391.57
20240326-1 | Trip of ROCK-1 |  | 2024-03-26 18:34 | 20240326-1 | 49.97 | 49.829 | -0.053087 | 268 | ROCK-1 | 468.495
20240328-1 | Trip of IFA Bipole1 | IFA Bipole 1 tripped while delivering 945MW from France to GB | 2024-03-28 10:20 | 20240328-1 | 50.042 | 49.714 | -0.15984 | 148 | IFA Bipole1 | 945.473
20240329-1 | Trip of IFA Bipole1 | IFA Bipole 1 tripped while delivering 999MW from France to GB | 2024-03-29 07:34 | 20240329-1 | 49.978 | 49.704 | -0.18831 | 132 | IFA Bipole1 | 999.1
20240329-2 | Trip of IFA Bipole2 | IFA Bipole 2 tripped while delivering 1000MW from France to GB | 2024-03-29 11:30 | 20240329-2 | 49.988 | 49.699 | -0.19842 | 141 | IFA Bipole2 | 1000
20240329-3 | Trip of IFA Bipole1 | IFA Bipole 1 tripped while delivering 996MW from France to GB | 2024-03-29 12:30 | 20240329-3 | 50.011 | 49.679 | -0.21207 | 135 | IFA Bipole1 | 996.75
20240330-1 | Loss of Supply at Taynuilt 33KV substation |  | 2024-03-30 12:48 | 20240330-1 |  |  |  | 165 |  |  | Carraig Gheal windfarm | 14 | Taynuilt | 20 | Fernoch-Inverary-Taynuilt 132kV circuit and the Inveraray-NantTaynuilt 132kV Double Circuit tripped
[11 empty] | Bienn Ghlas windfarm | 1
[11 empty] | Inverawe hydro generation | 25

## V20240328-1
Date | Time GMT | VA PU | VB PU | VC PU
03/28/2024 | 0:41 | 0.15849 | 1.1282 | 1.3305
03/28/2024 | 1:41 | 0.11356 | 1.1832 | 1.2879
03/28/2024 | 0:41 | 0.14843 | 1.2321 | 1.2401
03/28/2024 | 0:41 | 0.22443 | 1.2742 | 1.1883
03/28/2024 | 1:41 | 0.31138 | 1.309 | 1.1331
03/28/2024 | 2:41 | 0.40162 | 1.3351 | 1.0754
03/28/2024 | 3:41 | 0.49235 | 1.3518 | 1.0167
03/28/2024 | 4:41 | 0.58128 | 1.3593 | 0.95938
03/28/2024 | 0:41 | 0.66645 | 1.3581 | 0.90624
03/28/2024 | 0:41 | 0.74598 | 1.349 | 0.85976
03/28/2024 | 0:41 | 0.8185 | 1.3327 | 0.82185
03/28/2024 | 0:41 | 0.88301 | 1.31 | 0.7938
03/28/2024 | 0:41 | 0.93872 | 1.282 | 0.77654
03/28/2024 | 0:41 | 0.98515 | 1.25 | 0.77062
03/28/2024 | 0:41 | 1.022 | 1.2155 | 0.77595
03/28/2024 | 0:41 | 1.0494 | 1.1801 | 0.79151
03/28/2024 | 0:41 | 1.0679 | 1.1455 | 0.81541
03/28/2024 | 0:41 | 1.0783 | 1.1133 | 0.84507
03/28/2024 | 0:41 | 1.0814 | 1.0845 | 0.87791
03/28/2024 | 0:41 | 1.0782 | 1.0603 | 0.91152
03/28/2024 | 0:41 | 1.0693 | 1.0413 | 0.94386
03/28/2024 | 0:41 | 1.0557 | 1.0283 | 0.97315
03/28/2024 | 0:41 | 1.0386 | 1.0214 | 0.9981
03/28/2024 | 0:41 | 1.0193 | 1.0207 | 1.0179
03/28/2024 | 0:41 | 0.99923 | 1.0253 | 1.0322
03/28/2024 | 0:41 | 0.97984 | 1.0343 | 1.0411
03/28/2024 | 0:41 | 0.9623 | 1.0465 | 1.0449
03/28/2024 | 0:41 | 0.94756 | 1.0609 | 1.044
03/28/2024 | 0:41 | 0.93638 | 1.0762 | 1.0387
03/28/2024 | 0:41 | 0.92942 | 1.0912 | 1.0297
03/28/2024 | 0:41 | 0.92714 | 1.1045 | 1.0177
03/28/2024 | 0:41 | 0.92965 | 1.1154 | 1.0036
03/28/2024 | 0:41 | 0.93663 | 1.1231 | 0.98875
03/28/2024 | 0:41 | 0.94738 | 1.1275 | 0.97411
03/28/2024 | 0:41 | 0.9609 | 1.1284 | 0.96065
03/28/2024 | 0:41 | 0.97609 | 1.1257 | 0.94914
03/28/2024 | 0:41 | 0.9918 | 1.1197 | 0.94023
03/28/2024 | 0:41 | 1.0069 | 1.1109 | 0.9345
03/28/2024 | 0:41 | 1.0204 | 1.0998 | 0.93237
03/28/2024 | 0:41 | 1.0314 | 1.0874 | 0.93404
03/28/2024 | 0:41 | 1.0397 | 1.0743 | 0.93935
03/28/2024 | 0:41 | 1.045 | 1.0614 | 0.94781
03/28/2024 | 0:41 | 1.0472 | 1.0495 | 0.9587
03/28/2024 | 0:41 | 1.0464 | 1.039 | 0.97114
03/28/2024 | 0:41 | 1.0429 | 1.0304 | 0.98419
03/28/2024 | 0:41 | 1.0368 | 1.0242 | 0.99692
03/28/2024 | 0:41 | 1.0287 | 1.0209 | 1.0084
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0204 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0191 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0205 | 1.0181
03/28/2024 | 0:41 | 1.0193 | 1.0205 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0205 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0205 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0205 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0205 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0205 | 1.0183
03/28/2024 | 0:41 | 1.0193 | 1.0205 | 1.0183
03/28/2024 | 0:41 | 1.0193 | 1.0205 | 1.0183
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0204 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0193 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0182
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0193 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0193 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0193 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0193 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0193 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0193 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0193 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0193 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0203 | 1.0181
03/28/2024 | 0:41 | 1.0192 | 1.0206 | 1.0162
03/28/2024 | 0:41 | 1.0194 | 1.0224 | 1.0075
03/28/2024 | 0:41 | 1.0195 | 1.0253 | 0.99448
03/28/2024 | 0:41 | 1.0193 | 1.0269 | 0.9818
03/28/2024 | 0:41 | 1.0193 | 1.0268 | 0.97133
03/28/2024 | 0:41 | 1.0198 | 1.026 | 0.96345
03/28/2024 | 0:41 | 1.0209 | 1.0243 | 0.95819
03/28/2024 | 0:41 | 1.0226 | 1.0221 | 0.9552
03/28/2024 | 0:41 | 1.0242 | 1.0206 | 0.95391
03/28/2024 | 0:41 | 1.0254 | 1.0201 | 0.95363
03/28/2024 | 0:41 | 1.0268 | 1.0191 | 0.95362
03/28/2024 | 0:41 | 1.0285 | 1.0179 | 0.95326
03/28/2024 | 0:41 | 1.0303 | 1.0166 | 0.95195
03/28/2024 | 0:41 | 1.0321 | 1.0151 | 0.94916
03/28/2024 | 0:41 | 1.0333 | 1.0139 | 0.94436
03/28/2024 | 0:41 | 1.0337 | 1.0133 | 0.93705
03/28/2024 | 0:41 | 1.0334 | 1.013 | 0.92685
03/28/2024 | 0:41 | 1.0329 | 1.013 | 0.91346
03/28/2024 | 0:41 | 1.0326 | 1.013 | 0.89693
03/28/2024 | 0:41 | 1.0326 | 1.013 | 0.87756
03/28/2024 | 0:41 | 1.0323 | 1.0129 | 0.85578
03/28/2024 | 0:41 | 1.0318 | 1.0127 | 0.8322
03/28/2024 | 0:41 | 1.031 | 1.0124 | 0.80761
03/28/2024 | 0:41 | 1.0303 | 1.0117 | 0.78289
03/28/2024 | 0:41 | 1.0299 | 1.011 | 0.75896
03/28/2024 | 0:41 | 1.0298 | 1.0102 | 0.73665
03/28/2024 | 0:41 | 1.0298 | 1.0089 | 0.71668
03/28/2024 | 0:41 | 1.0301 | 1.0074 | 0.69961
03/28/2024 | 0:41 | 1.0307 | 1.0054 | 0.6858
03/28/2024 | 0:41 | 1.0317 | 1.003 | 0.67548
03/28/2024 | 0:41 | 1.033 | 1.0006 | 0.66859
03/28/2024 | 0:41 | 1.0344 | 0.99829 | 0.66478
03/28/2024 | 0:41 | 1.0358 | 0.99614 | 0.66332
03/28/2024 | 0:41 | 1.0371 | 0.99407 | 0.6632
03/28/2024 | 0:41 | 1.0383 | 0.99191 | 0.66335
03/28/2024 | 0:41 | 1.0392 | 0.98986 | 0.6628
03/28/2024 | 0:41 | 1.0395 | 0.98803 | 0.66072
03/28/2024 | 0:41 | 1.0391 | 0.98657 | 0.65633
03/28/2024 | 0:41 | 1.0381 | 0.98558 | 0.64881
03/28/2024 | 0:41 | 1.0368 | 0.98503 | 0.63733
03/28/2024 | 0:41 | 1.0355 | 0.98483 | 0.62116
03/28/2024 | 0:41 | 1.0343 | 0.98482 | 0.59973
03/28/2024 | 0:41 | 1.0332 | 0.98482 | 0.57271
03/28/2024 | 0:41 | 1.032 | 0.98465 | 0.53993
03/28/2024 | 0:41 | 1.0308 | 0.98422 | 0.50134
03/28/2024 | 0:41 | 1.0297 | 0.98349 | 0.45696
03/28/2024 | 0:41 | 1.0288 | 0.98244 | 0.40697
03/28/2024 | 0:41 | 1.0281 | 0.98106 | 0.35146
03/28/2024 | 0:41 | 1.0276 | 0.97902 | 0.29671
03/28/2024 | 0:41 | 1.0272 | 0.97499 | 0.26432
03/28/2024 | 0:41 | 1.0272 | 0.96954 | 0.25475
03/28/2024 | 0:41 | 1.0277 | 0.96523 | 0.25261
03/28/2024 | 0:41 | 1.028 | 0.96248 | 0.25174
03/28/2024 | 0:41 | 1.028 | 0.96056 | 0.25106
03/28/2024 | 0:41 | 1.0275 | 0.95974 | 0.25023
03/28/2024 | 0:41 | 1.0263 | 0.95976 | 0.24955
03/28/2024 | 0:41 | 1.0252 | 0.95931 | 0.24922
03/28/2024 | 0:41 | 1.0244 | 0.95837 | 0.24912
03/28/2024 | 0:41 | 1.0231 | 0.9582 | 0.24917
03/28/2024 | 0:41 | 1.021 | 0.95863 | 0.24922
03/28/2024 | 0:41 | 1.0185 | 0.95926 | 0.24925
03/28/2024 | 0:41 | 1.0156 | 0.96035 | 0.24917
03/28/2024 | 0:41 | 1.013 | 0.96134 | 0.24896
03/28/2024 | 0:41 | 1.0112 | 0.962 | 0.24847
03/28/2024 | 0:41 | 1.0101 | 0.96249 | 0.24768
03/28/2024 | 0:41 | 1.0094 | 0.96274 | 0.24673
03/28/2024 | 0:41 | 1.0086 | 0.96275 | 0.24553
03/28/2024 | 0:41 | 1.0079 | 0.96241 | 0.2439
03/28/2024 | 0:41 | 1.0075 | 0.96184 | 0.24185
03/28/2024 | 0:41 | 1.0076 | 0.96099 | 0.23943
03/28/2024 | 0:41 | 1.0081 | 0.95991 | 0.23692
03/28/2024 | 0:41 | 1.0086 | 0.9588 | 0.23456
03/28/2024 | 0:41 | 1.0089 | 0.95747 | 0.23248
03/28/2024 | 0:41 | 1.009 | 0.95624 | 0.23066
03/28/2024 | 0:41 | 1.009 | 0.95544 | 0.22894
03/28/2024 | 0:41 | 1.0087 | 0.95504 | 0.22713
03/28/2024 | 0:41 | 1.0081 | 0.95535 | 0.2254
03/28/2024 | 0:41 | 1.0072 | 0.95627 | 0.22376
03/28/2024 | 0:41 | 1.0061 | 0.95749 | 0.22234
03/28/2024 | 0:41 | 1.0049 | 0.95911 | 0.22119
03/28/2024 | 0:41 | 1.0038 | 0.96112 | 0.22023
03/28/2024 | 0:41 | 1.0026 | 0.96347 | 0.21953
03/28/2024 | 0:41 | 1.0015 | 0.96611 | 0.2191
03/28/2024 | 0:41 | 1.0006 | 0.96871 | 0.21896
03/28/2024 | 0:41 | 1.0002 | 0.97108 | 0.21914
03/28/2024 | 0:41 | 1.0003 | 0.97308 | 0.21961
03/28/2024 | 0:41 | 1.001 | 0.97465 | 0.22038
03/28/2024 | 0:41 | 1.0021 | 0.9758 | 0.22147
03/28/2024 | 0:41 | 1.0033 | 0.97656 | 0.22291
03/28/2024 | 0:41 | 1.0047 | 0.97693 | 0.2247
03/28/2024 | 0:41 | 1.0062 | 0.97698 | 0.22676
03/28/2024 | 0:41 | 1.008 | 0.97683 | 0.2291
03/28/2024 | 0:41 | 1.0098 | 0.97653 | 0.23167
03/28/2024 | 0:41 | 1.0114 | 0.97614 | 0.23449
03/28/2024 | 0:41 | 1.0128 | 0.97574 | 0.23749
03/28/2024 | 0:41 | 1.0138 | 0.97546 | 0.24062
03/28/2024 | 0:41 | 1.0144 | 0.97546 | 0.24378
03/28/2024 | 0:41 | 1.0146 | 0.97595 | 0.24688
03/28/2024 | 0:41 | 1.0145 | 0.97694 | 0.24981
03/28/2024 | 0:41 | 1.0143 | 0.97836 | 0.25252
03/28/2024 | 0:41 | 1.014 | 0.98013 | 0.25491
03/28/2024 | 0:41 | 1.0137 | 0.98209 | 0.25693
03/28/2024 | 0:41 | 1.0135 | 0.98419 | 0.25853
03/28/2024 | 0:41 | 1.0135 | 0.98639 | 0.2597
03/28/2024 | 0:41 | 1.0137 | 0.98858 | 0.26047
03/28/2024 | 0:41 | 1.0141 | 0.99064 | 0.26087
03/28/2024 | 0:41 | 1.0149 | 0.9925 | 0.26095
03/28/2024 | 0:41 | 1.016 | 0.99411 | 0.26073
03/28/2024 | 0:41 | 1.0173 | 0.99555 | 0.26026
03/28/2024 | 0:41 | 1.0188 | 0.99676 | 0.25958
03/28/2024 | 0:41 | 1.0204 | 0.99768 | 0.25873
03/28/2024 | 0:41 | 1.022 | 0.99831 | 0.25772
03/28/2024 | 0:41 | 1.0237 | 0.99865 | 0.25661
03/28/2024 | 0:41 | 1.0253 | 0.99878 | 0.25543
03/28/2024 | 0:41 | 1.0268 | 0.9988 | 0.25423
03/28/2024 | 0:41 | 1.0282 | 0.99878 | 0.25305
03/28/2024 | 0:41 | 1.0293 | 0.99879 | 0.2519
03/28/2024 | 0:41 | 1.0302 | 0.99883 | 0.25077
03/28/2024 | 0:41 | 1.0309 | 0.99895 | 0.24975
03/28/2024 | 0:41 | 1.0312 | 0.99919 | 0.24883
03/28/2024 | 0:41 | 1.0314 | 0.99956 | 0.24801
03/28/2024 | 0:41 | 1.0314 | 1.0001 | 0.24731
03/28/2024 | 0:41 | 1.0314 | 1.0007 | 0.24672
03/28/2024 | 0:41 | 1.0315 | 1.0014 | 0.24629
03/28/2024 | 0:41 | 1.0315 | 1.0021 | 0.24598
03/28/2024 | 0:41 | 1.0317 | 1.0027 | 0.24574
03/28/2024 | 0:41 | 1.0319 | 1.0033 | 0.24556
03/28/2024 | 0:41 | 1.0322 | 1.0037 | 0.24544
03/28/2024 | 0:41 | 1.0327 | 1.0039 | 0.24536
03/28/2024 | 0:41 | 1.0332 | 1.004 | 0.24531
03/28/2024 | 0:41 | 1.0338 | 1.0041 | 0.2453
03/28/2024 | 0:41 | 1.0343 | 1.0041 | 0.24531
03/28/2024 | 0:41 | 1.0348 | 1.0042 | 0.24531
03/28/2024 | 0:41 | 1.0352 | 1.0042 | 0.24529
03/28/2024 | 0:41 | 1.0354 | 1.0042 | 0.24524
03/28/2024 | 0:41 | 1.0356 | 1.0041 | 0.24513
03/28/2024 | 0:41 | 1.0357 | 1.004 | 0.24498
03/28/2024 | 0:41 | 1.0357 | 1.004 | 0.24478
03/28/2024 | 0:41 | 1.0356 | 1.004 | 0.24454
03/28/2024 | 0:41 | 1.0355 | 1.004 | 0.24424
03/28/2024 | 0:41 | 1.0354 | 1.0041 | 0.24388
03/28/2024 | 0:41 | 1.0351 | 1.0042 | 0.24341
03/28/2024 | 0:41 | 1.0346 | 1.0043 | 0.24284
03/28/2024 | 0:41 | 1.0339 | 1.0045 | 0.24214
03/28/2024 | 0:41 | 1.0335 | 1.0047 | 0.24133
03/28/2024 | 0:41 | 1.0333 | 1.0049 | 0.24041
03/28/2024 | 0:41 | 1.0334 | 1.0048 | 0.23945
03/28/2024 | 0:41 | 1.0336 | 1.0044 | 0.23853
03/28/2024 | 0:41 | 1.0339 | 1.0039 | 0.23768
03/28/2024 | 0:41 | 1.0342 | 1.0034 | 0.23695
03/28/2024 | 0:41 | 1.0347 | 1.0028 | 0.23634
03/28/2024 | 0:41 | 1.0351 | 1.0022 | 0.23585
03/28/2024 | 0:41 | 1.0354 | 1.0015 | 0.23547
03/28/2024 | 0:41 | 1.0356 | 1.0009 | 0.23523
03/28/2024 | 0:41 | 1.0354 | 1.0003 | 0.23512
03/28/2024 | 0:41 | 1.0351 | 0.99978 | 0.23514
03/28/2024 | 0:41 | 1.0345 | 0.99931 | 0.23525
03/28/2024 | 0:41 | 1.0336 | 0.99896 | 0.23546
03/28/2024 | 0:41 | 1.0325 | 0.99874 | 0.23572
03/28/2024 | 0:41 | 1.0311 | 0.9986 | 0.23605
03/28/2024 | 0:41 | 1.0296 | 0.99853 | 0.23641
03/28/2024 | 0:41 | 1.0282 | 0.99852 | 0.23678
03/28/2024 | 0:41 | 1.0268 | 0.99853 | 0.23714
03/28/2024 | 0:41 | 1.0255 | 0.99851 | 0.23745
03/28/2024 | 0:41 | 1.0243 | 0.99842 | 0.23895
03/28/2024 | 0:41 | 1.023 | 0.99794 | 0.24933
03/28/2024 | 0:41 | 1.0217 | 0.99685 | 0.27922
03/28/2024 | 0:41 | 1.0208 | 0.9957 | 0.3197
03/28/2024 | 0:41 | 1.0204 | 0.99497 | 0.3549
03/28/2024 | 0:41 | 1.0203 | 0.99405 | 0.38339
03/28/2024 | 0:41 | 1.0204 | 0.99288 | 0.40648
03/28/2024 | 0:41 | 1.0204 | 0.99227 | 0.42376
03/28/2024 | 0:41 | 1.0203 | 0.99191 | 0.43674
03/28/2024 | 0:41 | 1.0205 | 0.99075 | 0.44634
03/28/2024 | 0:41 | 1.0208 | 0.98954 | 0.45247
03/28/2024 | 0:41 | 1.0206 | 0.98926 | 0.45578
03/28/2024 | 0:41 | 1.02 | 0.98934 | 0.45718
03/28/2024 | 0:41 | 1.0195 | 0.98953 | 0.45738
03/28/2024 | 0:41 | 1.0186 | 0.99042 | 0.45741
03/28/2024 | 0:41 | 1.0174 | 0.99168 | 0.4581
03/28/2024 | 0:41 | 1.0169 | 0.99255 | 0.46003
03/28/2024 | 0:41 | 1.0167 | 0.99335 | 0.46402
03/28/2024 | 0:41 | 1.016 | 0.99437 | 0.47115
03/28/2024 | 0:41 | 1.0148 | 0.99524 | 0.48172
03/28/2024 | 0:41 | 1.0135 | 0.99583 | 0.49525
03/28/2024 | 0:41 | 1.0124 | 0.9962 | 0.51174
03/28/2024 | 0:41 | 1.0115 | 0.99632 | 0.53115
03/28/2024 | 0:41 | 1.0108 | 0.99623 | 0.55256
03/28/2024 | 0:41 | 1.0101 | 0.99592 | 0.57532
03/28/2024 | 0:41 | 1.0095 | 0.99532 | 0.59917
03/28/2024 | 0:41 | 1.0093 | 0.99449 | 0.62297
03/28/2024 | 0:41 | 1.0095 | 0.99351 | 0.64569
03/28/2024 | 0:41 | 1.0097 | 0.99228 | 0.66765
03/28/2024 | 0:41 | 1.0098 | 0.99109 | 0.68901
03/28/2024 | 0:41 | 1.0098 | 0.99079 | 0.70923
03/28/2024 | 0:41 | 1.0095 | 0.99148 | 0.72763
03/28/2024 | 0:41 | 1.0089 | 0.99266 | 0.74352
03/28/2024 | 0:41 | 1.0079 | 0.99434 | 0.75567
03/28/2024 | 0:41 | 1.0065 | 0.9964 | 0.76377
03/28/2024 | 0:41 | 1.0049 | 0.99816 | 0.76859
03/28/2024 | 0:41 | 1.003 | 0.99947 | 0.77107
03/28/2024 | 0:41 | 1.0012 | 1.0006 | 0.77192
03/28/2024 | 0:41 | 0.99937 | 1.0017 | 0.772
03/28/2024 | 0:41 | 0.99793 | 1.0031 | 0.77208
03/28/2024 | 0:41 | 0.99702 | 1.005 | 0.77287
03/28/2024 | 0:41 | 0.99686 | 1.007 | 0.77505
03/28/2024 | 0:41 | 0.99764 | 1.0085 | 0.77911
03/28/2024 | 0:41 | 0.99923 | 1.0096 | 0.7856
03/28/2024 | 0:41 | 1.0011 | 1.0101 | 0.79509
03/28/2024 | 0:41 | 1.0029 | 1.0103 | 0.8079
03/28/2024 | 0:41 | 1.0044 | 1.0103 | 0.82403
03/28/2024 | 0:41 | 1.0057 | 1.0103 | 0.84321
03/28/2024 | 0:41 | 1.0071 | 1.0105 | 0.86434
03/28/2024 | 0:41 | 1.009 | 1.0111 | 0.8842
03/28/2024 | 0:41 | 1.0111 | 1.0125 | 0.8984
03/28/2024 | 0:41 | 1.0128 | 1.0138 | 0.90756
03/28/2024 | 0:41 | 1.0138 | 1.0146 | 0.91595
03/28/2024 | 0:41 | 1.0142 | 1.0156 | 0.92416
03/28/2024 | 0:41 | 1.0142 | 1.0169 | 0.93176
03/28/2024 | 0:41 | 1.0139 | 1.0181 | 0.93904
03/28/2024 | 0:41 | 1.0134 | 1.0194 | 0.94547
03/28/2024 | 0:41 | 1.0123 | 1.022 | 0.95072
03/28/2024 | 0:41 | 1.0106 | 1.0248 | 0.95497
03/28/2024 | 0:41 | 1.009 | 1.0267 | 0.95808
03/28/2024 | 0:41 | 1.0075 | 1.0283 | 0.95991
03/28/2024 | 0:41 | 1.0059 | 1.0297 | 0.96072
03/28/2024 | 0:41 | 1.0049 | 1.0303 | 0.96081
03/28/2024 | 0:41 | 1.0046 | 1.0307 | 0.96056
03/28/2024 | 0:41 | 1.0045 | 1.0316 | 0.96038
03/28/2024 | 0:41 | 1.0049 | 1.0324 | 0.96034
03/28/2024 | 0:41 | 1.0064 | 1.0328 | 0.96037
03/28/2024 | 0:41 | 1.0088 | 1.0329 | 0.96083
03/28/2024 | 0:41 | 1.0115 | 1.033 | 0.96235
03/28/2024 | 0:41 | 1.014 | 1.0328 | 0.96515
03/28/2024 | 0:41 | 1.0161 | 1.0327 | 0.96916
03/28/2024 | 0:41 | 1.0179 | 1.0329 | 0.97453
03/28/2024 | 0:41 | 1.0198 | 1.0333 | 0.98106
03/28/2024 | 0:41 | 1.0218 | 1.0342 | 0.9881
03/28/2024 | 0:41 | 1.0236 | 1.0353 | 0.99548
03/28/2024 | 0:41 | 1.0249 | 1.0368 | 1.0029
03/28/2024 | 0:41 | 1.0258 | 1.0385 | 1.0093
03/28/2024 | 0:41 | 1.0262 | 1.0403 | 1.0139
03/28/2024 | 0:41 | 1.0262 | 1.0416 | 1.0165
03/28/2024 | 0:41 | 1.0261 | 1.0426 | 1.0176
03/28/2024 | 0:41 | 1.0259 | 1.0435 | 1.0177
03/28/2024 | 0:41 | 1.0257 | 1.0442 | 1.0179
03/28/2024 | 0:41 | 1.0255 | 1.0447 | 1.0186
03/28/2024 | 0:41 | 1.0252 | 1.0456 | 1.0192
03/28/2024 | 0:41 | 1.0248 | 1.0469 | 1.0196
03/28/2024 | 0:41 | 1.0246 | 1.0483 | 1.0198
03/28/2024 | 0:41 | 1.0249 | 1.0494 | 1.0198
03/28/2024 | 0:41 | 1.0255 | 1.05 | 1.0198
03/28/2024 | 0:41 | 1.0267 | 1.0502 | 1.02
03/28/2024 | 0:41 | 1.0279 | 1.0499 | 1.0203
03/28/2024 | 0:41 | 1.029 | 1.0498 | 1.0208
03/28/2024 | 0:41 | 1.0297 | 1.0497 | 1.0215
03/28/2024 | 0:41 | 1.0304 | 1.0497 | 1.0224
03/28/2024 | 0:41 | 1.0311 | 1.0496 | 1.0234
03/28/2024 | 0:41 | 1.0318 | 1.0496 | 1.0246
03/28/2024 | 0:41 | 1.0324 | 1.0497 | 1.0257
03/28/2024 | 0:41 | 1.0329 | 1.0499 | 1.027
03/28/2024 | 0:41 | 1.0331 | 1.0501 | 1.0283
03/28/2024 | 0:41 | 1.0331 | 1.0504 | 1.0297
03/28/2024 | 0:41 | 1.0331 | 1.0509 | 1.031
03/28/2024 | 0:41 | 1.0332 | 1.0516 | 1.032
03/28/2024 | 0:41 | 1.0332 | 1.0523 | 1.0328
03/28/2024 | 0:41 | 1.0332 | 1.0531 | 1.0331
03/28/2024 | 0:41 | 1.0332 | 1.0537 | 1.0331
03/28/2024 | 0:41 | 1.0333 | 1.054 | 1.033
03/28/2024 | 0:41 | 1.0335 | 1.0542 | 1.0327
03/28/2024 | 0:41 | 1.0339 | 1.0543 | 1.0323
03/28/2024 | 0:41 | 1.0343 | 1.0545 | 1.0319
03/28/2024 | 0:41 | 1.0348 | 1.0547 | 1.0315
03/28/2024 | 0:41 | 1.0354 | 1.0547 | 1.0313
03/28/2024 | 0:41 | 1.0362 | 1.0546 | 1.0313
03/28/2024 | 0:41 | 1.037 | 1.0544 | 1.0313
03/28/2024 | 0:41 | 1.0377 | 1.054 | 1.0315
03/28/2024 | 0:41 | 1.0382 | 1.0535 | 1.0319
03/28/2024 | 0:41 | 1.0383 | 1.0529 | 1.0326
03/28/2024 | 0:41 | 1.0383 | 1.0524 | 1.0334
03/28/2024 | 0:41 | 1.0383 | 1.0521 | 1.0342
03/28/2024 | 0:41 | 1.0381 | 1.0519 | 1.0351
03/28/2024 | 0:41 | 1.0378 | 1.0518 | 1.0359
03/28/2024 | 0:41 | 1.0375 | 1.0519 | 1.0366
03/28/2024 | 0:41 | 1.0369 | 1.0521 | 1.0372
03/28/2024 | 0:41 | 1.0364 | 1.0524 | 1.0375
03/28/2024 | 0:41 | 1.0358 | 1.0528 | 1.0374
03/28/2024 | 0:41 | 1.0354 | 1.0533 | 1.0372
03/28/2024 | 0:41 | 1.0351 | 1.0537 | 1.0367
03/28/2024 | 0:41 | 1.0349 | 1.0542 | 1.0361
03/28/2024 | 0:41 | 1.0349 | 1.0544 | 1.0355
03/28/2024 | 0:41 | 1.035 | 1.0545 | 1.0349
03/28/2024 | 0:41 | 1.0351 | 1.0543 | 1.0341
03/28/2024 | 0:41 | 1.0354 | 1.0539 | 1.0333
03/28/2024 | 0:41 | 1.0357 | 1.0534 | 1.0324
03/28/2024 | 0:41 | 1.0362 | 1.0527 | 1.0316
03/28/2024 | 0:41 | 1.0367 | 1.0519 | 1.0311
03/28/2024 | 0:41 | 1.0372 | 1.0509 | 1.0308
03/28/2024 | 0:41 | 1.0376 | 1.0499 | 1.0307
03/28/2024 | 0:41 | 1.0378 | 1.0489 | 1.0308
03/28/2024 | 0:41 | 1.0377 | 1.0478 | 1.0311
03/28/2024 | 0:41 | 1.0375 | 1.0468 | 1.0316
03/28/2024 | 0:41 | 1.0371 | 1.0458 | 1.0323
03/28/2024 | 0:41 | 1.0367 | 1.045 | 1.0332
03/28/2024 | 0:41 | 1.0362 | 1.0445 | 1.0342
03/28/2024 | 0:41 | 1.0356 | 1.0442 | 1.0353
03/28/2024 | 0:41 | 1.0351 | 1.0442 | 1.0363
03/28/2024 | 0:41 | 1.0346 | 1.0443 | 1.0372
03/28/2024 | 0:41 | 1.0341 | 1.0445 | 1.0377
03/28/2024 | 0:41 | 1.0335 | 1.0448 | 1.038
03/28/2024 | 0:41 | 1.0329 | 1.0453 | 1.0381
03/28/2024 | 0:41 | 1.0324 | 1.0458 | 1.038
03/28/2024 | 0:41 | 1.0321 | 1.0464 | 1.0379
03/28/2024 | 0:41 | 1.0319 | 1.0468 | 1.0378
03/28/2024 | 0:41 | 1.0319 | 1.0471 | 1.0376
03/28/2024 | 0:41 | 1.032 | 1.0473 | 1.0373
03/28/2024 | 0:41 | 1.0321 | 1.0473 | 1.0369
03/28/2024 | 0:41 | 1.0323 | 1.047 | 1.0364
03/28/2024 | 0:41 | 1.0326 | 1.0464 | 1.036
03/28/2024 | 0:41 | 1.033 | 1.0457 | 1.0355
03/28/2024 | 0:41 | 1.0333 | 1.0448 | 1.0352
03/28/2024 | 0:41 | 1.0335 | 1.0438 | 1.0351
03/28/2024 | 0:41 | 1.0335 | 1.0429 | 1.0351
03/28/2024 | 0:41 | 1.0333 | 1.0419 | 1.0351
03/28/2024 | 0:41 | 1.0329 | 1.0409 | 1.0352
03/28/2024 | 0:41 | 1.0323 | 1.0399 | 1.0353
03/28/2024 | 0:41 | 1.0316 | 1.0392 | 1.0354
03/28/2024 | 0:41 | 1.0308 | 1.0386 | 1.0356
03/28/2024 | 0:41 | 1.0299 | 1.0382 | 1.0357
03/28/2024 | 0:41 | 1.0291 | 1.038 | 1.0357
03/28/2024 | 0:41 | 1.0284 | 1.038 | 1.0356
03/28/2024 | 0:41 | 1.0277 | 1.0381 | 1.0352
03/28/2024 | 0:41 | 1.0271 | 1.0383 | 1.0346
03/28/2024 | 0:41 | 1.0265 | 1.0385 | 1.0339
03/28/2024 | 0:41 | 1.0259 | 1.0387 | 1.033
03/28/2024 | 0:41 | 1.0255 | 1.039 | 1.032
03/28/2024 | 0:41 | 1.0252 | 1.0393 | 1.0311
03/28/2024 | 0:41 | 1.025 | 1.0395 | 1.0301
03/28/2024 | 0:41 | 1.025 | 1.0396 | 1.0292
03/28/2024 | 0:41 | 1.0251 | 1.0396 | 1.0284
03/28/2024 | 0:41 | 1.0252 | 1.0393 | 1.0276
03/28/2024 | 0:41 | 1.0254 | 1.0389 | 1.0269
03/28/2024 | 0:41 | 1.0256 | 1.0382 | 1.0262
03/28/2024 | 0:41 | 1.0259 | 1.0375 | 1.0256
03/28/2024 | 0:41 | 1.0261 | 1.0367 | 1.0253
03/28/2024 | 0:41 | 1.0262 | 1.0359 | 1.0251
03/28/2024 | 0:41 | 1.0262 | 1.0351 | 1.0251
03/28/2024 | 0:41 | 1.0261 | 1.0345 | 1.0252
03/28/2024 | 0:41 | 1.0258 | 1.0339 | 1.0253
03/28/2024 | 0:41 | 1.0254 | 1.0333 | 1.0255
03/28/2024 | 0:41 | 1.0248 | 1.0329 | 1.0257
03/28/2024 | 0:41 | 1.0243 | 1.0326 | 1.0259
03/28/2024 | 0:41 | 1.0237 | 1.0324 | 1.0261
03/28/2024 | 0:41 | 1.0232 | 1.0323 | 1.0262
03/28/2024 | 0:41 | 1.0227 | 1.0323 | 1.0261
03/28/2024 | 0:41 | 1.0224 | 1.0324 | 1.0258
03/28/2024 | 0:41 | 1.022 | 1.0324 | 1.0254
03/28/2024 | 0:41 | 1.0217 | 1.0324 | 1.0247
03/28/2024 | 0:41 | 1.0214 | 1.0324 | 1.024
03/28/2024 | 0:41 | 1.0212 | 1.0323 | 1.0231
03/28/2024 | 0:41 | 1.0211 | 1.0323 | 1.0223
03/28/2024 | 0:41 | 1.021 | 1.0321 | 1.0215
03/28/2024 | 0:41 | 1.021 | 1.0319 | 1.0208
03/28/2024 | 0:41 | 1.021 | 1.0316 | 1.0202
03/28/2024 | 0:41 | 1.021 | 1.0312 | 1.0196
03/28/2024 | 0:41 | 1.021 | 1.0307 | 1.019
03/28/2024 | 0:41 | 1.0211 | 1.0301 | 1.0185
03/28/2024 | 0:41 | 1.0211 | 1.0295 | 1.0181
03/28/2024 | 0:41 | 1.0211 | 1.0289 | 1.0178
03/28/2024 | 0:41 | 1.0211 | 1.0284 | 1.0177
03/28/2024 | 0:41 | 1.021 | 1.028 | 1.0177
03/28/2024 | 0:41 | 1.0208 | 1.0276 | 1.0177
03/28/2024 | 0:41 | 1.0205 | 1.0273 | 1.0178
03/28/2024 | 0:41 | 1.0201 | 1.027 | 1.018
03/28/2024 | 0:41 | 1.0198 | 1.0268 | 1.0182
03/28/2024 | 0:41 | 1.0194 | 1.0267 | 1.0185
03/28/2024 | 0:41 | 1.0192 | 1.0266 | 1.0188
03/28/2024 | 0:41 | 1.019 | 1.0266 | 1.0192
03/28/2024 | 0:41 | 1.0189 | 1.0266 | 1.0195
03/28/2024 | 0:41 | 1.0189 | 1.0266 | 1.0198
03/28/2024 | 0:41 | 1.0189 | 1.0265 | 1.0201
03/28/2024 | 0:41 | 1.0189 | 1.0264 | 1.0202
03/28/2024 | 0:41 | 1.0189 | 1.0263 | 1.0204
03/28/2024 | 0:41 | 1.0189 | 1.0261 | 1.0206
03/28/2024 | 0:41 | 1.0189 | 1.0258 | 1.0208
03/28/2024 | 0:41 | 1.0189 | 1.0255 | 1.021
03/28/2024 | 0:41 | 1.0189 | 1.0251 | 1.0214
03/28/2024 | 0:41 | 1.0189 | 1.0247 | 1.0218
03/28/2024 | 0:41 | 1.0188 | 1.0243 | 1.0223
03/28/2024 | 0:41 | 1.0186 | 1.0239 | 1.0226
03/28/2024 | 0:41 | 1.0185 | 1.0235 | 1.0229
03/28/2024 | 0:41 | 1.0183 | 1.0232 | 1.0232
03/28/2024 | 0:41 | 1.0181 | 1.0229 | 1.0233
03/28/2024 | 0:41 | 1.018 | 1.0227 | 1.0234
03/28/2024 | 0:41 | 1.0177 | 1.0226 | 1.0234
03/28/2024 | 0:41 | 1.0175 | 1.0226 | 1.0233
03/28/2024 | 0:41 | 1.0173 | 1.0226 | 1.0232
03/28/2024 | 0:41 | 1.017 | 1.0226 | 1.0229
03/28/2024 | 0:41 | 1.0169 | 1.0226 | 1.0226
03/28/2024 | 0:41 | 1.0168 | 1.0227 | 1.0221
03/28/2024 | 0:41 | 1.0168 | 1.0227 | 1.0216
03/28/2024 | 0:41 | 1.0168 | 1.0227 | 1.021
03/28/2024 | 0:41 | 1.017 | 1.0227 | 1.0204
03/28/2024 | 0:41 | 1.0172 | 1.0227 | 1.0197
03/28/2024 | 0:41 | 1.0174 | 1.0226 | 1.019
03/28/2024 | 0:41 | 1.0177 | 1.0224 | 1.0184
03/28/2024 | 0:41 | 1.0179 | 1.0223 | 1.0178
03/28/2024 | 0:41 | 1.018 | 1.022 | 1.0173
03/28/2024 | 0:41 | 1.0181 | 1.0218 | 1.017
03/28/2024 | 0:41 | 1.0182 | 1.0216 | 1.0167
03/28/2024 | 0:41 | 1.0182 | 1.0214 | 1.0165
03/28/2024 | 0:41 | 1.0182 | 1.0211 | 1.0164
03/28/2024 | 0:41 | 1.018 | 1.021 | 1.0163
03/28/2024 | 0:41 | 1.0179 | 1.0209 | 1.0163
03/28/2024 | 0:41 | 1.0177 | 1.0208 | 1.0163
03/28/2024 | 0:41 | 1.0175 | 1.0209 | 1.0163
03/28/2024 | 0:41 | 1.0172 | 1.021 | 1.0163
03/28/2024 | 0:41 | 1.017 | 1.0212 | 1.0163
03/28/2024 | 0:41 | 1.0168 | 1.0214 | 1.0163
03/28/2024 | 0:41 | 1.0166 | 1.0217 | 1.0163
03/28/2024 | 0:41 | 1.0165 | 1.0219 | 1.0163
03/28/2024 | 0:41 | 1.0165 | 1.0222 | 1.0163
03/28/2024 | 0:41 | 1.0165 | 1.0225 | 1.0162
03/28/2024 | 0:41 | 1.0167 | 1.0227 | 1.0161
03/28/2024 | 0:41 | 1.0169 | 1.0228 | 1.0161
03/28/2024 | 0:41 | 1.0171 | 1.0228 | 1.0161
03/28/2024 | 0:41 | 1.0173 | 1.0229 | 1.0161
03/28/2024 | 0:41 | 1.0175 | 1.0228 | 1.016
03/28/2024 | 0:41 | 1.0177 | 1.0227 | 1.016
03/28/2024 | 0:41 | 1.018 | 1.0225 | 1.016
03/28/2024 | 0:41 | 1.0182 | 1.0223 | 1.0162
03/28/2024 | 0:41 | 1.0184 | 1.022 | 1.0163
03/28/2024 | 0:41 | 1.0185 | 1.0217 | 1.0165
03/28/2024 | 0:41 | 1.0186 | 1.0215 | 1.0168
03/28/2024 | 0:41 | 1.0186 | 1.0212 | 1.017
03/28/2024 | 0:41 | 1.0185 | 1.021 | 1.0172
03/28/2024 | 0:41 | 1.0184 | 1.0208 | 1.0174
03/28/2024 | 0:41 | 1.0183 | 1.0207 | 1.0176
03/28/2024 | 0:41 | 1.0182 | 1.0207 | 1.0178
03/28/2024 | 0:41 | 1.018 | 1.0208 | 1.0179
03/28/2024 | 0:41 | 1.0179 | 1.0209 | 1.018
03/28/2024 | 0:41 | 1.0177 | 1.021 | 1.0181
03/28/2024 | 0:41 | 1.0176 | 1.0212 | 1.0181
03/28/2024 | 0:41 | 1.0175 | 1.0214 | 1.0181
03/28/2024 | 0:41 | 1.0175 | 1.0216 | 1.018
03/28/2024 | 0:41 | 1.0176 | 1.0218 | 1.018
03/28/2024 | 0:41 | 1.0177 | 1.022 | 1.0179
03/28/2024 | 0:41 | 1.0179 | 1.0222 | 1.0178
03/28/2024 | 0:41 | 1.0182 | 1.0223 | 1.0178
03/28/2024 | 0:41 | 1.0184 | 1.0224 | 1.0177
03/28/2024 | 0:41 | 1.0187 | 1.0224 | 1.0177
03/28/2024 | 0:41 | 1.0189 | 1.0224 | 1.0178
03/28/2024 | 0:41 | 1.0191 | 1.0223 | 1.0178
03/28/2024 | 0:41 | 1.0193 | 1.0222 | 1.018
03/28/2024 | 0:41 | 1.0195 | 1.022 | 1.0182
03/28/2024 | 0:41 | 1.0196 | 1.0218 | 1.0185
03/28/2024 | 0:41 | 1.0197 | 1.0216 | 1.0187
03/28/2024 | 0:41 | 1.0198 | 1.0214 | 1.0191
03/28/2024 | 0:41 | 1.0198 | 1.0213 | 1.0194
03/28/2024 | 0:41 | 1.0198 | 1.0211 | 1.0197
03/28/2024 | 0:41 | 1.0197 | 1.0209 | 1.02
03/28/2024 | 0:41 | 1.0196 | 1.0209 | 1.0203
03/28/2024 | 0:41 | 1.0195 | 1.0209 | 1.0205
03/28/2024 | 0:41 | 1.0194 | 1.0209 | 1.0208
03/28/2024 | 0:41 | 1.0192 | 1.0209 | 1.0209
03/28/2024 | 0:41 | 1.0191 | 1.021 | 1.021
03/28/2024 | 0:41 | 1.0191 | 1.0211 | 1.021
03/28/2024 | 0:41 | 1.0191 | 1.0212 | 1.0209
03/28/2024 | 0:41 | 1.0191 | 1.0213 | 1.0209
03/28/2024 | 0:41 | 1.0192 | 1.0214 | 1.0208
03/28/2024 | 0:41 | 1.0193 | 1.0215 | 1.0206
03/28/2024 | 0:41 | 1.0194 | 1.0216 | 1.0204
03/28/2024 | 0:41 | 1.0196 | 1.0217 | 1.0202
03/28/2024 | 0:41 | 1.0197 | 1.0217 | 1.02
03/28/2024 | 0:41 | 1.0199 | 1.0217 | 1.0197
03/28/2024 | 0:41 | 1.0201 | 1.0217 | 1.0195
03/28/2024 | 0:41 | 1.0202 | 1.0216 | 1.0192
03/28/2024 | 0:41 | 1.0204 | 1.0216 | 1.019
03/28/2024 | 0:41 | 1.0205 | 1.0215 | 1.0189
03/28/2024 | 0:41 | 1.0206 | 1.0214 | 1.0187
03/28/2024 | 0:41 | 1.0207 | 1.0213 | 1.0186
03/28/2024 | 0:41 | 1.0207 | 1.0212 | 1.0185
03/28/2024 | 0:41 | 1.0207 | 1.0212 | 1.0185
03/28/2024 | 0:41 | 1.0207 | 1.0211 | 1.0184
03/28/2024 | 0:41 | 1.0207 | 1.0211 | 1.0184
03/28/2024 | 0:41 | 1.0206 | 1.0211 | 1.0184
03/28/2024 | 0:41 | 1.0205 | 1.0211 | 1.0184
03/28/2024 | 0:41 | 1.0204 | 1.0212 | 1.0184
03/28/2024 | 0:41 | 1.0203 | 1.0213 | 1.0184
03/28/2024 | 0:41 | 1.0202 | 1.0214 | 1.0184
03/28/2024 | 0:41 | 1.0201 | 1.0215 | 1.0184
03/28/2024 | 0:41 | 1.02 | 1.0216 | 1.0184
03/28/2024 | 0:41 | 1.0199 | 1.0218 | 1.0184
03/28/2024 | 0:41 | 1.0199 | 1.0219 | 1.0184
03/28/2024 | 0:41 | 1.02 | 1.022 | 1.0184
03/28/2024 | 0:41 | 1.02 | 1.0221 | 1.0184
03/28/2024 | 0:41 | 1.02 | 1.0221 | 1.0184
03/28/2024 | 0:41 | 1.0201 | 1.0221 | 1.0184
03/28/2024 | 0:41 | 1.0201 | 1.0222 | 1.0185
03/28/2024 | 0:41 | 1.0202 | 1.0221 | 1.0185
03/28/2024 | 0:41 | 1.0202 | 1.0221 | 1.0186
03/28/2024 | 0:41 | 1.0203 | 1.022 | 1.0186
03/28/2024 | 0:41 | 1.0203 | 1.0219 | 1.0186
03/28/2024 | 0:41 | 1.0204 | 1.0218 | 1.0187
03/28/2024 | 0:41 | 1.0204 | 1.0217 | 1.0188
03/28/2024 | 0:41 | 1.0204 | 1.0216 | 1.0189
03/28/2024 | 0:41 | 1.0204 | 1.0215 | 1.019
03/28/2024 | 0:41 | 1.0204 | 1.0214 | 1.0191
03/28/2024 | 0:41 | 1.0204 | 1.0213 | 1.0193
03/28/2024 | 0:41 | 1.0203 | 1.0213 | 1.0194
03/28/2024 | 0:41 | 1.0203 | 1.0212 | 1.0195
03/28/2024 | 0:41 | 1.0203 | 1.0212 | 1.0195
03/28/2024 | 0:41 | 1.0202 | 1.0212 | 1.0196
03/28/2024 | 0:41 | 1.0202 | 1.0213 | 1.0196
03/28/2024 | 0:41 | 1.0201 | 1.0213 | 1.0196
03/28/2024 | 0:41 | 1.0201 | 1.0214 | 1.0196
03/28/2024 | 0:41 | 1.0201 | 1.0214 | 1.0196
03/28/2024 | 0:41 | 1.0201 | 1.0215 | 1.0195
03/28/2024 | 0:41 | 1.0201 | 1.0216 | 1.0195
03/28/2024 | 0:41 | 1.0202 | 1.0216 | 1.0194
03/28/2024 | 0:41 | 1.0203 | 1.0217 | 1.0193
03/28/2024 | 0:41 | 1.0204 | 1.0217 | 1.0192
03/28/2024 | 0:41 | 1.0205 | 1.0217 | 1.0191
03/28/2024 | 0:41 | 1.0206 | 1.0217 | 1.019
03/28/2024 | 0:41 | 1.0207 | 1.0217 | 1.0189
03/28/2024 | 0:41 | 1.0208 | 1.0216 | 1.0188
03/28/2024 | 0:41 | 1.0208 | 1.0215 | 1.0187
03/28/2024 | 0:41 | 1.0209 | 1.0215 | 1.0186
03/28/2024 | 0:41 | 1.0209 | 1.0214 | 1.0185
03/28/2024 | 0:41 | 1.0209 | 1.0213 | 1.0185
03/28/2024 | 0:41 | 1.0209 | 1.0212 | 1.0185
03/28/2024 | 0:41 | 1.0209 | 1.0212 | 1.0185
03/28/2024 | 0:41 | 1.0209 | 1.0211 | 1.0186
03/28/2024 | 0:41 | 1.0209 | 1.0211 | 1.0186
03/28/2024 | 0:41 | 1.0208 | 1.0211 | 1.0186
03/28/2024 | 0:41 | 1.0208 | 1.0211 | 1.0186
03/28/2024 | 0:41 | 1.0207 | 1.0211 | 1.0186
03/28/2024 | 0:41 | 1.0207 | 1.0211 | 1.0186
03/28/2024 | 0:41 | 1.0207 | 1.0212 | 1.0186
03/28/2024 | 0:41 | 1.0207 | 1.0212 | 1.0186
03/28/2024 | 0:41 | 1.0206 | 1.0213 | 1.0186
03/28/2024 | 0:41 | 1.0207 | 1.0214 | 1.0186
03/28/2024 | 0:41 | 1.0207 | 1.0214 | 1.0186
03/28/2024 | 0:41 | 1.0208 | 1.0215 | 1.0186
03/28/2024 | 0:41 | 1.0209 | 1.0215 | 1.0186
03/28/2024 | 0:41 | 1.021 | 1.0215 | 1.0186
03/28/2024 | 0:41 | 1.0211 | 1.0215 | 1.0187
03/28/2024 | 0:41 | 1.0212 | 1.0215 | 1.0188
03/28/2024 | 0:41 | 1.0213 | 1.0215 | 1.0188
03/28/2024 | 0:41 | 1.0213 | 1.0215 | 1.0189
03/28/2024 | 0:41 | 1.0214 | 1.0215 | 1.019
03/28/2024 | 0:41 | 1.0214 | 1.0214 | 1.0192
03/28/2024 | 0:41 | 1.0215 | 1.0214 | 1.0193
03/28/2024 | 0:41 | 1.0215 | 1.0214 | 1.0194
03/28/2024 | 0:41 | 1.0215 | 1.0214 | 1.0194
03/28/2024 | 0:41 | 1.0215 | 1.0214 | 1.0195
03/28/2024 | 0:41 | 1.0215 | 1.0214 | 1.0196
03/28/2024 | 0:41 | 1.0214 | 1.0214 | 1.0197
03/28/2024 | 0:41 | 1.0214 | 1.0215 | 1.0197
03/28/2024 | 0:41 | 1.0214 | 1.0216 | 1.0198
03/28/2024 | 0:41 | 1.0214 | 1.0217 | 1.0198
03/28/2024 | 0:41 | 1.0214 | 1.0217 | 1.0199
03/28/2024 | 0:41 | 1.0214 | 1.0218 | 1.0199
03/28/2024 | 0:41 | 1.0214 | 1.0219 | 1.0199
03/28/2024 | 0:41 | 1.0214 | 1.0219 | 1.0198
03/28/2024 | 0:41 | 1.0214 | 1.022 | 1.0198
03/28/2024 | 0:41 | 1.0215 | 1.022 | 1.0198
03/28/2024 | 0:41 | 1.0215 | 1.0221 | 1.0197
03/28/2024 | 0:41 | 1.0215 | 1.0221 | 1.0196
03/28/2024 | 0:41 | 1.0215 | 1.0221 | 1.0196
03/28/2024 | 0:41 | 1.0215 | 1.0221 | 1.0195
03/28/2024 | 0:41 | 1.0216 | 1.0221 | 1.0195
03/28/2024 | 0:41 | 1.0216 | 1.0221 | 1.0194
03/28/2024 | 0:41 | 1.0216 | 1.0221 | 1.0193
03/28/2024 | 0:41 | 1.0215 | 1.0221 | 1.0193
03/28/2024 | 0:41 | 1.0216 | 1.0221 | 1.0193
03/28/2024 | 0:41 | 1.0216 | 1.0221 | 1.0192
03/28/2024 | 0:41 | 1.0216 | 1.0221 | 1.0192
03/28/2024 | 0:41 | 1.0216 | 1.0221 | 1.0192
03/28/2024 | 0:41 | 1.0216 | 1.0221 | 1.0191
03/28/2024 | 0:41 | 1.0216 | 1.0221 | 1.0191
03/28/2024 | 0:41 | 1.0216 | 1.0222 | 1.0191
03/28/2024 | 0:41 | 1.0216 | 1.0222 | 1.0191
03/28/2024 | 0:41 | 1.0216 | 1.0223 | 1.0191
03/28/2024 | 0:41 | 1.0217 | 1.0224 | 1.0191
03/28/2024 | 0:41 | 1.0217 | 1.0224 | 1.0191
03/28/2024 | 0:41 | 1.0218 | 1.0225 | 1.0191
03/28/2024 | 0:41 | 1.0218 | 1.0225 | 1.0191
03/28/2024 | 0:41 | 1.0219 | 1.0226 | 1.0191
03/28/2024 | 0:41 | 1.0219 | 1.0226 | 1.0191
03/28/2024 | 0:41 | 1.022 | 1.0226 | 1.0191
03/28/2024 | 0:41 | 1.022 | 1.0227 | 1.0191
03/28/2024 | 0:41 | 1.0221 | 1.0227 | 1.0191
03/28/2024 | 0:41 | 1.0221 | 1.0227 | 1.0191
03/28/2024 | 0:41 | 1.0222 | 1.0227 | 1.0191
03/28/2024 | 0:41 | 1.0222 | 1.0227 | 1.0191
03/28/2024 | 0:41 | 1.0222 | 1.0227 | 1.0191
03/28/2024 | 0:41 | 1.0223 | 1.0227 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0226 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0226 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0226 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0226 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0226 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0226 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0226 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0226 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0226 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0227 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0227 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0228 | 1.019
03/28/2024 | 0:41 | 1.0223 | 1.0229 | 1.019
03/28/2024 | 0:41 | 1.0222 | 1.0229 | 1.019
03/28/2024 | 0:41 | 1.0222 | 1.023 | 1.019
03/28/2024 | 0:41 | 1.0222 | 1.0231 | 1.019
03/28/2024 | 0:41 | 1.0222 | 1.0231 | 1.019
03/28/2024 | 0:41 | 1.0222 | 1.0232 | 1.0189
03/28/2024 | 0:41 | 1.0223 | 1.0232 | 1.0189
03/28/2024 | 0:41 | 1.0223 | 1.0232 | 1.0189
03/28/2024 | 0:41 | 1.0224 | 1.0232 | 1.0189
03/28/2024 | 0:41 | 1.0224 | 1.0232 | 1.019
03/28/2024 | 0:41 | 1.0225 | 1.0232 | 1.019
03/28/2024 | 0:41 | 1.0226 | 1.0232 | 1.0191
03/28/2024 | 0:41 | 1.0226 | 1.0231 | 1.0193
03/28/2024 | 0:41 | 1.0227 | 1.0231 | 1.0194
03/28/2024 | 0:41 | 1.0227 | 1.0231 | 1.0195
03/28/2024 | 0:41 | 1.0227 | 1.023 | 1.0197
03/28/2024 | 0:41 | 1.0227 | 1.023 | 1.0198
03/28/2024 | 0:41 | 1.0227 | 1.023 | 1.02
03/28/2024 | 0:41 | 1.0227 | 1.023 | 1.0201
03/28/2024 | 0:41 | 1.0227 | 1.023 | 1.0202
03/28/2024 | 0:41 | 1.0227 | 1.023 | 1.0203
03/28/2024 | 0:41 | 1.0226 | 1.0231 | 1.0204
03/28/2024 | 0:41 | 1.0226 | 1.0232 | 1.0205
03/28/2024 | 0:41 | 1.0225 | 1.0232 | 1.0205
03/28/2024 | 0:41 | 1.0225 | 1.0233 | 1.0205
03/28/2024 | 0:41 | 1.0225 | 1.0234 | 1.0205
03/28/2024 | 0:41 | 1.0225 | 1.0235 | 1.0205
03/28/2024 | 0:41 | 1.0225 | 1.0236 | 1.0204
03/28/2024 | 0:41 | 1.0224 | 1.0237 | 1.0203
03/28/2024 | 0:41 | 1.0224 | 1.0237 | 1.0201
03/28/2024 | 0:41 | 1.0225 | 1.0238 | 1.02
03/28/2024 | 0:41 | 1.0225 | 1.0238 | 1.0198
03/28/2024 | 0:41 | 1.0225 | 1.0238 | 1.0196
03/28/2024 | 0:41 | 1.0226 | 1.0238 | 1.0195
03/28/2024 | 0:41 | 1.0227 | 1.0238 | 1.0193
03/28/2024 | 0:41 | 1.0227 | 1.0237 | 1.0192
03/28/2024 | 0:41 | 1.0228 | 1.0237 | 1.0191
03/28/2024 | 0:41 | 1.0228 | 1.0236 | 1.019
03/28/2024 | 0:41 | 1.0228 | 1.0236 | 1.019
03/28/2024 | 0:41 | 1.0229 | 1.0236 | 1.0189
03/28/2024 | 0:41 | 1.0229 | 1.0236 | 1.0189
03/28/2024 | 0:41 | 1.0229 | 1.0236 | 1.0189
03/28/2024 | 0:41 | 1.0228 | 1.0237 | 1.0189
03/28/2024 | 0:41 | 1.0228 | 1.0237 | 1.0189
03/28/2024 | 0:41 | 1.0228 | 1.0238 | 1.0189
03/28/2024 | 0:41 | 1.0228 | 1.0238 | 1.0189
03/28/2024 | 0:41 | 1.0228 | 1.0239 | 1.0189
03/28/2024 | 0:41 | 1.0227 | 1.024 | 1.0189
03/28/2024 | 0:41 | 1.0227 | 1.0241 | 1.0189
03/28/2024 | 0:41 | 1.0227 | 1.0242 | 1.0189
03/28/2024 | 0:41 | 1.0227 | 1.0243 | 1.0189
03/28/2024 | 0:41 | 1.0227 | 1.0244 | 1.0189
03/28/2024 | 0:41 | 1.0227 | 1.0245 | 1.0189
03/28/2024 | 0:41 | 1.0227 | 1.0245 | 1.0189
03/28/2024 | 0:41 | 1.0228 | 1.0246 | 1.0189
03/28/2024 | 0:41 | 1.0228 | 1.0246 | 1.0189
03/28/2024 | 0:41 | 1.0228 | 1.0246 | 1.0189
03/28/2024 | 0:41 | 1.0229 | 1.0246 | 1.0189
03/28/2024 | 0:41 | 1.023 | 1.0245 | 1.019
03/28/2024 | 0:41 | 1.023 | 1.0245 | 1.019
03/28/2024 | 0:41 | 1.023 | 1.0245 | 1.0191
03/28/2024 | 0:41 | 1.023 | 1.0245 | 1.0193
03/28/2024 | 0:41 | 1.0231 | 1.0245 | 1.0194
03/28/2024 | 0:41 | 1.0231 | 1.0245 | 1.0195
03/28/2024 | 0:41 | 1.0231 | 1.0245 | 1.0196
03/28/2024 | 0:41 | 1.0231 | 1.0246 | 1.0197
03/28/2024 | 0:41 | 1.0231 | 1.0246 | 1.0198
03/28/2024 | 0:41 | 1.0231 | 1.0247 | 1.0198
03/28/2024 | 0:41 | 1.0231 | 1.0248 | 1.0199
03/28/2024 | 0:41 | 1.0231 | 1.0249 | 1.02
03/28/2024 | 0:41 | 1.0231 | 1.0249 | 1.02
03/28/2024 | 0:41 | 1.0231 | 1.025 | 1.02
03/28/2024 | 0:41 | 1.0231 | 1.025 | 1.02
03/28/2024 | 0:41 | 1.023 | 1.0251 | 1.02
03/28/2024 | 0:41 | 1.023 | 1.0251 | 1.02
03/28/2024 | 0:41 | 1.023 | 1.0252 | 1.02
03/28/2024 | 0:41 | 1.023 | 1.0252 | 1.0199
03/28/2024 | 0:41 | 1.023 | 1.0252 | 1.0199
03/28/2024 | 0:41 | 1.0231 | 1.0252 | 1.0199
03/28/2024 | 0:41 | 1.0231 | 1.0252 | 1.0198
03/28/2024 | 0:41 | 1.0231 | 1.0252 | 1.0198
03/28/2024 | 0:41 | 1.0231 | 1.0252 | 1.0198
03/28/2024 | 0:41 | 1.0231 | 1.0252 | 1.0198
03/28/2024 | 0:41 | 1.0231 | 1.0252 | 1.0198
03/28/2024 | 0:41 | 1.0231 | 1.0252 | 1.0198
03/28/2024 | 0:41 | 1.0231 | 1.0252 | 1.0199
03/28/2024 | 0:41 | 1.0231 | 1.0252 | 1.0199
03/28/2024 | 0:41 | 1.0231 | 1.0252 | 1.0199
03/28/2024 | 0:41 | 1.0231 | 1.0253 | 1.02
03/28/2024 | 0:41 | 1.0231 | 1.0253 | 1.02
03/28/2024 | 0:41 | 1.0231 | 1.0253 | 1.02
03/28/2024 | 0:41 | 1.0231 | 1.0254 | 1.0201
03/28/2024 | 0:41 | 1.0231 | 1.0254 | 1.0201
03/28/2024 | 0:41 | 1.0231 | 1.0255 | 1.0202
03/28/2024 | 0:41 | 1.023 | 1.0255 | 1.0202
03/28/2024 | 0:41 | 1.023 | 1.0255 | 1.0203
03/28/2024 | 0:41 | 1.023 | 1.0255 | 1.0203
03/28/2024 | 0:41 | 1.0229 | 1.0256 | 1.0202
03/28/2024 | 0:41 | 1.0229 | 1.0256 | 1.0202
03/28/2024 | 0:41 | 1.0229 | 1.0256 | 1.0202
03/28/2024 | 0:41 | 1.0229 | 1.0256 | 1.0202
03/28/2024 | 0:41 | 1.0229 | 1.0256 | 1.0201
03/28/2024 | 0:41 | 1.0229 | 1.0256 | 1.0201
03/28/2024 | 0:41 | 1.0229 | 1.0256 | 1.02
03/28/2024 | 0:41 | 1.023 | 1.0256 | 1.0199
03/28/2024 | 0:41 | 1.023 | 1.0256 | 1.0199
03/28/2024 | 0:41 | 1.023 | 1.0256 | 1.0198
03/28/2024 | 0:41 | 1.023 | 1.0256 | 1.0198
03/28/2024 | 0:41 | 1.023 | 1.0256 | 1.0197
03/28/2024 | 0:41 | 1.0231 | 1.0256 | 1.0197
03/28/2024 | 0:41 | 1.0231 | 1.0256 | 1.0197
03/28/2024 | 0:41 | 1.0231 | 1.0255 | 1.0197
03/28/2024 | 0:41 | 1.0231 | 1.0255 | 1.0197
03/28/2024 | 0:41 | 1.0231 | 1.0255 | 1.0197
03/28/2024 | 0:41 | 1.0231 | 1.0255 | 1.0197
03/28/2024 | 0:41 | 1.023 | 1.0255 | 1.0198
03/28/2024 | 0:41 | 1.023 | 1.0256 | 1.0198
03/28/2024 | 0:41 | 1.023 | 1.0256 | 1.0198
03/28/2024 | 0:41 | 1.0229 | 1.0257 | 1.0198
03/28/2024 | 0:41 | 1.0228 | 1.0257 | 1.0198
03/28/2024 | 0:41 | 1.0228 | 1.0258 | 1.0198
03/28/2024 | 0:41 | 1.0228 | 1.0258 | 1.0198
03/28/2024 | 0:41 | 1.0228 | 1.0259 | 1.0198
03/28/2024 | 0:41 | 1.0228 | 1.026 | 1.0198
03/28/2024 | 0:41 | 1.0227 | 1.026 | 1.0198
03/28/2024 | 0:41 | 1.0227 | 1.0261 | 1.0198
03/28/2024 | 0:41 | 1.0228 | 1.0261 | 1.0197
03/28/2024 | 0:41 | 1.0228 | 1.0261 | 1.0197
03/28/2024 | 0:41 | 1.0228 | 1.0261 | 1.0197
03/28/2024 | 0:41 | 1.0229 | 1.0261 | 1.0197
03/28/2024 | 0:41 | 1.023 | 1.0261 | 1.0197
03/28/2024 | 0:41 | 1.023 | 1.0261 | 1.0198
03/28/2024 | 0:41 | 1.0231 | 1.0261 | 1.0199
03/28/2024 | 0:41 | 1.0231 | 1.026 | 1.02
03/28/2024 | 0:41 | 1.0232 | 1.026 | 1.0201
03/28/2024 | 0:41 | 1.0232 | 1.026 | 1.0202
03/28/2024 | 0:41 | 1.0232 | 1.026 | 1.0204
03/28/2024 | 0:41 | 1.0232 | 1.026 | 1.0205
03/28/2024 | 0:41 | 1.0232 | 1.026 | 1.0206
03/28/2024 | 0:41 | 1.0231 | 1.026 | 1.0207
03/28/2024 | 0:41 | 1.0231 | 1.0261 | 1.0208
03/28/2024 | 0:41 | 1.0231 | 1.0261 | 1.0209
03/28/2024 | 0:41 | 1.0231 | 1.0262 | 1.0209
03/28/2024 | 0:41 | 1.023 | 1.0262 | 1.021
03/28/2024 | 0:41 | 1.023 | 1.0263 | 1.021
03/28/2024 | 0:41 | 1.0231 | 1.0264 | 1.021
03/28/2024 | 0:41 | 1.0231 | 1.0265 | 1.0209
03/28/2024 | 0:41 | 1.0232 | 1.0265 | 1.0209
03/28/2024 | 0:41 | 1.0232 | 1.0266 | 1.0209
03/28/2024 | 0:41 | 1.0232 | 1.0266 | 1.0208
03/28/2024 | 0:41 | 1.0232 | 1.0266 | 1.0208
03/28/2024 | 0:41 | 1.0233 | 1.0266 | 1.0207
03/28/2024 | 0:41 | 1.0233 | 1.0266 | 1.0207
03/28/2024 | 0:41 | 1.0233 | 1.0266 | 1.0206
03/28/2024 | 0:41 | 1.0234 | 1.0266 | 1.0206
03/28/2024 | 0:41 | 1.0234 | 1.0266 | 1.0206
03/28/2024 | 0:41 | 1.0234 | 1.0266 | 1.0206
03/28/2024 | 0:41 | 1.0235 | 1.0266 | 1.0207
03/28/2024 | 0:41 | 1.0235 | 1.0266 | 1.0207
03/28/2024 | 0:41 | 1.0235 | 1.0266 | 1.0207
03/28/2024 | 0:41 | 1.0235 | 1.0267 | 1.0207
03/28/2024 | 0:41 | 1.0235 | 1.0267 | 1.0208
03/28/2024 | 0:41 | 1.0235 | 1.0267 | 1.0208
03/28/2024 | 0:41 | 1.0235 | 1.0268 | 1.0208
03/28/2024 | 0:41 | 1.0235 | 1.0269 | 1.0208
03/28/2024 | 0:41 | 1.0235 | 1.0269 | 1.0208
03/28/2024 | 0:41 | 1.0235 | 1.027 | 1.0208
03/28/2024 | 0:41 | 1.0235 | 1.027 | 1.0208
03/28/2024 | 0:41 | 1.0236 | 1.0271 | 1.0208
03/28/2024 | 0:41 | 1.0236 | 1.0271 | 1.0208
03/28/2024 | 0:41 | 1.0236 | 1.0271 | 1.0208
03/28/2024 | 0:41 | 1.0237 | 1.0271 | 1.0208
03/28/2024 | 0:41 | 1.0237 | 1.027 | 1.0208
03/28/2024 | 0:41 | 1.0237 | 1.027 | 1.0209
03/28/2024 | 0:41 | 1.0237 | 1.027 | 1.0209
03/28/2024 | 0:41 | 1.0237 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0237 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0236 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0236 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.0236 | 1.0271 | 1.0211
03/28/2024 | 0:41 | 1.0235 | 1.0271 | 1.0212
03/28/2024 | 0:41 | 1.0235 | 1.0271 | 1.0212
03/28/2024 | 0:41 | 1.0235 | 1.0272 | 1.0212
03/28/2024 | 0:41 | 1.0235 | 1.0272 | 1.0212
03/28/2024 | 0:41 | 1.0235 | 1.0272 | 1.0212
03/28/2024 | 0:41 | 1.0235 | 1.0273 | 1.0212
03/28/2024 | 0:41 | 1.0235 | 1.0273 | 1.0212
03/28/2024 | 0:41 | 1.0235 | 1.0273 | 1.0212
03/28/2024 | 0:41 | 1.0236 | 1.0274 | 1.0212
03/28/2024 | 0:41 | 1.0236 | 1.0274 | 1.0211
03/28/2024 | 0:41 | 1.0236 | 1.0274 | 1.0211
03/28/2024 | 0:41 | 1.0237 | 1.0274 | 1.0211
03/28/2024 | 0:41 | 1.0237 | 1.0274 | 1.0211
03/28/2024 | 0:41 | 1.0237 | 1.0273 | 1.0211
03/28/2024 | 0:41 | 1.0237 | 1.0273 | 1.0211
03/28/2024 | 0:41 | 1.0237 | 1.0272 | 1.0212
03/28/2024 | 0:41 | 1.0237 | 1.0272 | 1.0212
03/28/2024 | 0:41 | 1.0237 | 1.0272 | 1.0212
03/28/2024 | 0:41 | 1.0236 | 1.0271 | 1.0213
03/28/2024 | 0:41 | 1.0236 | 1.0271 | 1.0213
03/28/2024 | 0:41 | 1.0235 | 1.0271 | 1.0213
03/28/2024 | 0:41 | 1.0235 | 1.0271 | 1.0213
03/28/2024 | 0:41 | 1.0234 | 1.0271 | 1.0213
03/28/2024 | 0:41 | 1.0233 | 1.0272 | 1.0213
03/28/2024 | 0:41 | 1.0233 | 1.0272 | 1.0213
03/28/2024 | 0:41 | 1.0232 | 1.0272 | 1.0213
03/28/2024 | 0:41 | 1.0232 | 1.0273 | 1.0212
03/28/2024 | 0:41 | 1.0232 | 1.0273 | 1.0212
03/28/2024 | 0:41 | 1.0232 | 1.0273 | 1.0211
03/28/2024 | 0:41 | 1.0232 | 1.0273 | 1.0211
03/28/2024 | 0:41 | 1.0232 | 1.0273 | 1.0211
03/28/2024 | 0:41 | 1.0232 | 1.0273 | 1.021
03/28/2024 | 0:41 | 1.0232 | 1.0273 | 1.021
03/28/2024 | 0:41 | 1.0232 | 1.0273 | 1.021
03/28/2024 | 0:41 | 1.0233 | 1.0272 | 1.021
03/28/2024 | 0:41 | 1.0233 | 1.0272 | 1.0209
03/28/2024 | 0:41 | 1.0233 | 1.0272 | 1.0209
03/28/2024 | 0:41 | 1.0233 | 1.0271 | 1.021
03/28/2024 | 0:41 | 1.0233 | 1.0271 | 1.021
03/28/2024 | 0:41 | 1.0232 | 1.0271 | 1.021
03/28/2024 | 0:41 | 1.0232 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0232 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0232 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.023 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.023 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.023 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.023 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.023 | 1.0269 | 1.0211
03/28/2024 | 0:41 | 1.0229 | 1.0269 | 1.0211
03/28/2024 | 0:41 | 1.0229 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.0229 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0229 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0229 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0229 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0229 | 1.027 | 1.021
03/28/2024 | 0:41 | 1.0229 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.023 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.023 | 1.027 | 1.0211
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.0212
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.0212
03/28/2024 | 0:41 | 1.0231 | 1.027 | 1.0212
03/28/2024 | 0:41 | 1.0231 | 1.0269 | 1.0213
03/28/2024 | 0:41 | 1.0231 | 1.0269 | 1.0213
03/28/2024 | 0:41 | 1.0231 | 1.0269 | 1.0214
03/28/2024 | 0:41 | 1.0231 | 1.0269 | 1.0214
03/28/2024 | 0:41 | 1.0231 | 1.0269 | 1.0215
03/28/2024 | 0:41 | 1.0231 | 1.0269 | 1.0215
03/28/2024 | 0:41 | 1.0231 | 1.0269 | 1.0216
03/28/2024 | 0:41 | 1.023 | 1.0269 | 1.0216
03/28/2024 | 0:41 | 1.023 | 1.0269 | 1.0217
03/28/2024 | 0:41 | 1.023 | 1.027 | 1.0217
03/28/2024 | 0:41 | 1.023 | 1.027 | 1.0217
03/28/2024 | 0:41 | 1.023 | 1.0271 | 1.0217
03/28/2024 | 0:41 | 1.023 | 1.0271 | 1.0217
03/28/2024 | 0:41 | 1.023 | 1.0271 | 1.0216
03/28/2024 | 0:41 | 1.023 | 1.0272 | 1.0216
03/28/2024 | 0:41 | 1.023 | 1.0272 | 1.0216
03/28/2024 | 0:41 | 1.0231 | 1.0272 | 1.0215
03/28/2024 | 0:41 | 1.0231 | 1.0272 | 1.0215
03/28/2024 | 0:41 | 1.0232 | 1.0272 | 1.0215
03/28/2024 | 0:41 | 1.0233 | 1.0272 | 1.0215
03/28/2024 | 0:41 | 1.0233 | 1.0272 | 1.0215
03/28/2024 | 0:41 | 1.0234 | 1.0272 | 1.0215
03/28/2024 | 0:41 | 1.0234 | 1.0272 | 1.0215
03/28/2024 | 0:41 | 1.0234 | 1.0272 | 1.0216
03/28/2024 | 0:41 | 1.0235 | 1.0272 | 1.0216
03/28/2024 | 0:41 | 1.0235 | 1.0272 | 1.0216
03/28/2024 | 0:41 | 1.0235 | 1.0271 | 1.0216
03/28/2024 | 0:41 | 1.0235 | 1.0271 | 1.0216
03/28/2024 | 0:41 | 1.0235 | 1.0271 | 1.0217
03/28/2024 | 0:41 | 1.0234 | 1.0272 | 1.0217
03/28/2024 | 0:41 | 1.0234 | 1.0272 | 1.0217
03/28/2024 | 0:41 | 1.0234 | 1.0272 | 1.0217
03/28/2024 | 0:41 | 1.0234 | 1.0273 | 1.0217
03/28/2024 | 0:41 | 1.0234 | 1.0273 | 1.0217
03/28/2024 | 0:41 | 1.0234 | 1.0273 | 1.0217
03/28/2024 | 0:41 | 1.0234 | 1.0274 | 1.0217
03/28/2024 | 0:41 | 1.0234 | 1.0274 | 1.0217
03/28/2024 | 0:41 | 1.0235 | 1.0275 | 1.0217
03/28/2024 | 0:41 | 1.0235 | 1.0275 | 1.0217
03/28/2024 | 0:41 | 1.0235 | 1.0275 | 1.0217
03/28/2024 | 0:41 | 1.0236 | 1.0275 | 1.0218
03/28/2024 | 0:41 | 1.0236 | 1.0275 | 1.0218
03/28/2024 | 0:41 | 1.0237 | 1.0275 | 1.0218
03/28/2024 | 0:41 | 1.0238 | 1.0275 | 1.0219
03/28/2024 | 0:41 | 1.0238 | 1.0275 | 1.0219
03/28/2024 | 0:41 | 1.0239 | 1.0275 | 1.022
03/28/2024 | 0:41 | 1.0239 | 1.0275 | 1.022
03/28/2024 | 0:41 | 1.0239 | 1.0275 | 1.0221
03/28/2024 | 0:41 | 1.0239 | 1.0275 | 1.0222
03/28/2024 | 0:41 | 1.0239 | 1.0275 | 1.0222
03/28/2024 | 0:41 | 1.0239 | 1.0275 | 1.0223
03/28/2024 | 0:41 | 1.0239 | 1.0275 | 1.0223
03/28/2024 | 0:41 | 1.0239 | 1.0275 | 1.0224
03/28/2024 | 0:41 | 1.0239 | 1.0275 | 1.0224
03/28/2024 | 0:41 | 1.0239 | 1.0275 | 1.0224
03/28/2024 | 0:41 | 1.0239 | 1.0276 | 1.0224
03/28/2024 | 0:41 | 1.0239 | 1.0276 | 1.0225
03/28/2024 | 0:41 | 1.0239 | 1.0276 | 1.0225
03/28/2024 | 0:41 | 1.0239 | 1.0276 | 1.0225
03/28/2024 | 0:41 | 1.0239 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.024 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.024 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.024 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.0241 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.0241 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.0242 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.0242 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.0242 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.0242 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0225
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0226
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0226
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0226
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0227
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0227
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0227
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0227
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0227
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0227
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0227
03/28/2024 | 0:41 | 1.0243 | 1.0277 | 1.0227
03/28/2024 | 0:41 | 1.0243 | 1.0278 | 1.0227
03/28/2024 | 0:41 | 1.0244 | 1.0278 | 1.0227
03/28/2024 | 0:41 | 1.0244 | 1.0278 | 1.0227
03/28/2024 | 0:41 | 1.0244 | 1.0278 | 1.0227
03/28/2024 | 0:41 | 1.0245 | 1.0278 | 1.0228
03/28/2024 | 0:41 | 1.0245 | 1.0278 | 1.0228
03/28/2024 | 0:41 | 1.0245 | 1.0279 | 1.0228
03/28/2024 | 0:41 | 1.0246 | 1.0279 | 1.0228
03/28/2024 | 0:41 | 1.0246 | 1.0279 | 1.0228
03/28/2024 | 0:41 | 1.0246 | 1.0279 | 1.0228
03/28/2024 | 0:41 | 1.0246 | 1.0279 | 1.0228
03/28/2024 | 0:41 | 1.0246 | 1.0279 | 1.0229
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.0229
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.0229
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.0229
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.0229
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.023
03/28/2024 | 0:41 | 1.0247 | 1.0278 | 1.023
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.023
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.023
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.023
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.023
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.023
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.023
03/28/2024 | 0:41 | 1.0247 | 1.0279 | 1.0229
03/28/2024 | 0:41 | 1.0247 | 1.028 | 1.0229
03/28/2024 | 0:41 | 1.0247 | 1.028 | 1.0229
03/28/2024 | 0:41 | 1.0248 | 1.028 | 1.023
03/28/2024 | 0:41 | 1.0248 | 1.028 | 1.023
03/28/2024 | 0:41 | 1.0248 | 1.028 | 1.023
03/28/2024 | 0:41 | 1.0248 | 1.028 | 1.023
03/28/2024 | 0:41 | 1.0249 | 1.028 | 1.023
03/28/2024 | 0:41 | 1.0249 | 1.028 | 1.0231
03/28/2024 | 0:41 | 1.0249 | 1.028 | 1.0231
03/28/2024 | 0:41 | 1.0249 | 1.028 | 1.0231
03/28/2024 | 0:41 | 1.0249 | 1.028 | 1.0232
03/28/2024 | 0:41 | 1.025 | 1.028 | 1.0232
03/28/2024 | 0:41 | 1.025 | 1.028 | 1.0233
03/28/2024 | 0:41 | 1.025 | 1.028 | 1.0233
03/28/2024 | 0:41 | 1.025 | 1.028 | 1.0233
03/28/2024 | 0:41 | 1.025 | 1.028 | 1.0234
03/28/2024 | 0:41 | 1.025 | 1.0281 | 1.0234
03/28/2024 | 0:41 | 1.025 | 1.0281 | 1.0234
03/28/2024 | 0:41 | 1.025 | 1.0281 | 1.0234
03/28/2024 | 0:41 | 1.025 | 1.0281 | 1.0234
03/28/2024 | 0:41 | 1.025 | 1.0281 | 1.0234
03/28/2024 | 0:41 | 1.025 | 1.0282 | 1.0234
03/28/2024 | 0:41 | 1.025 | 1.0282 | 1.0234
03/28/2024 | 0:41 | 1.025 | 1.0282 | 1.0234
03/28/2024 | 0:41 | 1.025 | 1.0281 | 1.0234
03/28/2024 | 0:41 | 1.025 | 1.0281 | 1.0234
03/28/2024 | 0:41 | 1.0251 | 1.0282 | 1.0234
03/28/2024 | 0:41 | 1.0251 | 1.0282 | 1.0234
03/28/2024 | 0:41 | 1.0252 | 1.0282 | 1.0234
03/28/2024 | 0:41 | 1.0252 | 1.0282 | 1.0235
03/28/2024 | 0:41 | 1.0252 | 1.0282 | 1.0235
03/28/2024 | 0:41 | 1.0253 | 1.0282 | 1.0235
03/28/2024 | 0:41 | 1.0253 | 1.0282 | 1.0235
03/28/2024 | 0:41 | 1.0253 | 1.0282 | 1.0236
03/28/2024 | 0:41 | 1.0253 | 1.0282 | 1.0236
03/28/2024 | 0:41 | 1.0253 | 1.0282 | 1.0236
03/28/2024 | 0:41 | 1.0254 | 1.0282 | 1.0237
03/28/2024 | 0:41 | 1.0254 | 1.0282 | 1.0237
03/28/2024 | 0:41 | 1.0253 | 1.0282 | 1.0237
03/28/2024 | 0:41 | 1.0253 | 1.0283 | 1.0237
03/28/2024 | 0:41 | 1.0253 | 1.0283 | 1.0237
03/28/2024 | 0:41 | 1.0253 | 1.0283 | 1.0237
03/28/2024 | 0:41 | 1.0254 | 1.0283 | 1.0237
03/28/2024 | 0:41 | 1.0254 | 1.0284 | 1.0237
03/28/2024 | 0:41 | 1.0254 | 1.0284 | 1.0237
03/28/2024 | 0:41 | 1.0254 | 1.0284 | 1.0237
03/28/2024 | 0:41 | 1.0255 | 1.0284 | 1.0236
03/28/2024 | 0:41 | 1.0255 | 1.0285 | 1.0236
03/28/2024 | 0:41 | 1.0255 | 1.0285 | 1.0236
03/28/2024 | 0:41 | 1.0256 | 1.0285 | 1.0236
03/28/2024 | 0:41 | 1.0257 | 1.0285 | 1.0237
03/28/2024 | 0:41 | 1.0257 | 1.0285 | 1.0237
03/28/2024 | 0:41 | 1.0258 | 1.0285 | 1.0237
03/28/2024 | 0:41 | 1.0258 | 1.0284 | 1.0237
03/28/2024 | 0:41 | 1.0258 | 1.0284 | 1.0238
03/28/2024 | 0:41 | 1.0259 | 1.0284 | 1.0239
03/28/2024 | 0:41 | 1.0259 | 1.0284 | 1.0239
03/28/2024 | 0:41 | 1.0259 | 1.0284 | 1.024
03/28/2024 | 0:41 | 1.0259 | 1.0284 | 1.0241
03/28/2024 | 0:41 | 1.0259 | 1.0285 | 1.0242
03/28/2024 | 0:41 | 1.0259 | 1.0285 | 1.0242
03/28/2024 | 0:41 | 1.0259 | 1.0285 | 1.0243
03/28/2024 | 0:41 | 1.0258 | 1.0286 | 1.0243
03/28/2024 | 0:41 | 1.0258 | 1.0286 | 1.0243
03/28/2024 | 0:41 | 1.0258 | 1.0287 | 1.0243
03/28/2024 | 0:41 | 1.0258 | 1.0287 | 1.0243
03/28/2024 | 0:41 | 1.0258 | 1.0288 | 1.0243
03/28/2024 | 0:41 | 1.0259 | 1.0288 | 1.0243
03/28/2024 | 0:41 | 1.0259 | 1.0288 | 1.0243
03/28/2024 | 0:41 | 1.026 | 1.0289 | 1.0243
03/28/2024 | 0:41 | 1.026 | 1.0289 | 1.0242
03/28/2024 | 0:41 | 1.0261 | 1.0289 | 1.0242
03/28/2024 | 0:41 | 1.0261 | 1.0289 | 1.0242
03/28/2024 | 0:41 | 1.0262 | 1.0289 | 1.0242
03/28/2024 | 0:41 | 1.0262 | 1.0288 | 1.0242
03/28/2024 | 0:41 | 1.0263 | 1.0288 | 1.0243
03/28/2024 | 0:41 | 1.0263 | 1.0288 | 1.0243
03/28/2024 | 0:41 | 1.0263 | 1.0288 | 1.0244
03/28/2024 | 0:41 | 1.0264 | 1.0287 | 1.0244
03/28/2024 | 0:41 | 1.0264 | 1.0287 | 1.0245
03/28/2024 | 0:41 | 1.0263 | 1.0287 | 1.0246
03/28/2024 | 0:41 | 1.0263 | 1.0287 | 1.0246
03/28/2024 | 0:41 | 1.0263 | 1.0288 | 1.0247
03/28/2024 | 0:41 | 1.0263 | 1.0288 | 1.0247
03/28/2024 | 0:41 | 1.0262 | 1.0288 | 1.0247
03/28/2024 | 0:41 | 1.0262 | 1.0289 | 1.0248
03/28/2024 | 0:41 | 1.0262 | 1.0289 | 1.0247
03/28/2024 | 0:41 | 1.0261 | 1.029 | 1.0247
03/28/2024 | 0:41 | 1.0261 | 1.029 | 1.0247
03/28/2024 | 0:41 | 1.0262 | 1.0291 | 1.0247
03/28/2024 | 0:41 | 1.0262 | 1.0292 | 1.0246
03/28/2024 | 0:41 | 1.0262 | 1.0292 | 1.0246
03/28/2024 | 0:41 | 1.0262 | 1.0292 | 1.0246
03/28/2024 | 0:41 | 1.0263 | 1.0293 | 1.0245
03/28/2024 | 0:41 | 1.0263 | 1.0292 | 1.0245
03/28/2024 | 0:41 | 1.0264 | 1.0292 | 1.0245
03/28/2024 | 0:41 | 1.0264 | 1.0292 | 1.0245
03/28/2024 | 0:41 | 1.0264 | 1.0291 | 1.0245
03/28/2024 | 0:41 | 1.0265 | 1.0291 | 1.0245
03/28/2024 | 0:41 | 1.0265 | 1.029 | 1.0245
03/28/2024 | 0:41 | 1.0265 | 1.029 | 1.0246
03/28/2024 | 0:41 | 1.0265 | 1.0289 | 1.0246
03/28/2024 | 0:41 | 1.0265 | 1.0289 | 1.0247
03/28/2024 | 0:41 | 1.0265 | 1.0289 | 1.0247
03/28/2024 | 0:41 | 1.0265 | 1.0289 | 1.0248
03/28/2024 | 0:41 | 1.0265 | 1.0289 | 1.0248
03/28/2024 | 0:41 | 1.0264 | 1.0289 | 1.0249
03/28/2024 | 0:41 | 1.0264 | 1.029 | 1.0249
03/28/2024 | 0:41 | 1.0264 | 1.029 | 1.0249
03/28/2024 | 0:41 | 1.0263 | 1.0291 | 1.0249
03/28/2024 | 0:41 | 1.0263 | 1.0291 | 1.0248

## 20240301-1
In GMT
Date | Time | Freq
2024-03-01 | 6:11 | 50.023 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-01 | 6:11 | 50.021 | 222 | BRITNED | 676.211
2024-03-01 | 6:11 | 50.021 | 268 | WBURB-2 | 428.156
2024-03-01 | 6:11 | 50.022 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-01 | 6:11 | 50.02 |  | Viking Link | -648.9
2024-03-01 | 6:11 | 50.018 |  | Viking Link | 1398.96
2024-03-01 | 6:11 | 50.016 | 209 | DRAXX-3 | 626.95
2024-03-01 | 6:11 | 50.013 | 154 | CDCL-1 | 391.57
2024-03-01 | 6:11 | 50.013 | 268 | ROCK-1 | 468.495
2024-03-01 | 6:11 | 50.014 | 148 | IFA Bipole1 | 945.473
2024-03-01 | 6:11 | 50.016 | 132 | IFA Bipole1 | 999.1
2024-03-01 | 6:11 | 50.014 | 141 | IFA Bipole2 | 1000
2024-03-01 | 6:11 | 50.014 | 135 | IFA Bipole1 | 996.75
2024-03-01 | 6:11 | 50.013 |  | Viking Link | -780.3
2024-03-01 | 6:11 | 50.012
2024-03-01 | 6:11 | 50.008
2024-03-01 | 6:11 | 50.007
2024-03-01 | 6:11 | 50.004
2024-03-01 | 6:11 | 50.002
2024-03-01 | 6:11 | 49.998 | 130 | HEYM12 | 271.908
2024-03-01 | 6:11 | 49.993 | 228 | HUMR-1 | 303.75
2024-03-01 | 6:11 | 49.988
2024-03-01 | 6:11 | 49.984
2024-03-01 | 6:11 | 49.986
2024-03-01 | 6:11 | 49.99
2024-03-01 | 6:11 | 49.993
2024-03-01 | 6:11 | 49.995
2024-03-01 | 6:11 | 50
2024-03-01 | 6:11 | 50.005
2024-03-01 | 6:11 | 50.009
2024-03-01 | 6:11 | 50.01 | 211 | CDCL-1 | 291.5
2024-03-01 | 6:12 | 50.014 | 199 | STAY-2 | 413.125
2024-03-01 | 6:12 | 50.019 | 173 | CDCL-1 | 397.375
2024-03-01 | 6:12 | 50.02 | 248 | SEAB-2 | 361.25
2024-03-01 | 6:12 | 50.022 | 255 | FRANCE | 995.65
2024-03-01 | 6:12 | 50.025 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-01 | 6:12 | 50.027
2024-03-01 | 6:12 | 50.029
2024-03-01 | 6:12 | 50.028
2024-03-01 | 6:12 | 50.027
2024-03-01 | 6:12 | 50.026
2024-03-01 | 6:12 | 50.026
2024-03-01 | 6:12 | 50.028
2024-03-01 | 6:12 | 50.029
2024-03-01 | 6:12 | 50.029
2024-03-01 | 6:12 | 50.029
2024-03-01 | 6:12 | 50.025
2024-03-01 | 6:12 | 50.022
2024-03-01 | 6:12 | 50.021
2024-03-01 | 6:12 | 50.022
2024-03-01 | 6:12 | 50.023
2024-03-01 | 6:12 | 50.025
2024-03-01 | 6:12 | 50.026
2024-03-01 | 6:12 | 50.028
2024-03-01 | 6:12 | 50.029
2024-03-01 | 6:12 | 50.028
2024-03-01 | 6:12 | 50.029
2024-03-01 | 6:12 | 49.95
2024-03-01 | 6:12 | 49.858
2024-03-01 | 6:12 | 49.795
2024-03-01 | 6:12 | 49.778
2024-03-01 | 6:12 | 49.771
2024-03-01 | 6:12 | 49.772
2024-03-01 | 6:12 | 49.778
2024-03-01 | 6:12 | 49.784
2024-03-01 | 6:12 | 49.786
2024-03-01 | 6:12 | 49.786
2024-03-01 | 6:12 | 49.788
2024-03-01 | 6:12 | 49.788
2024-03-01 | 6:12 | 49.788
2024-03-01 | 6:12 | 49.787
2024-03-01 | 6:12 | 49.787
2024-03-01 | 6:12 | 49.787
2024-03-01 | 6:12 | 49.786
2024-03-01 | 6:12 | 49.785
2024-03-01 | 6:12 | 49.783
2024-03-01 | 6:12 | 49.784
2024-03-01 | 6:12 | 49.783
2024-03-01 | 6:12 | 49.783
2024-03-01 | 6:12 | 49.783
2024-03-01 | 6:12 | 49.783
2024-03-01 | 6:12 | 49.783
2024-03-01 | 6:12 | 49.784
2024-03-01 | 6:12 | 49.785
2024-03-01 | 6:12 | 49.786
2024-03-01 | 6:12 | 49.785
2024-03-01 | 6:12 | 49.785
2024-03-01 | 6:12 | 49.784
2024-03-01 | 6:12 | 49.784
2024-03-01 | 6:12 | 49.784
2024-03-01 | 6:12 | 49.784
2024-03-01 | 6:13 | 49.785
2024-03-01 | 6:13 | 49.785
2024-03-01 | 6:13 | 49.782
2024-03-01 | 6:13 | 49.779
2024-03-01 | 6:13 | 49.778
2024-03-01 | 6:13 | 49.777
2024-03-01 | 6:13 | 49.777
2024-03-01 | 6:13 | 49.776
2024-03-01 | 6:13 | 49.774
2024-03-01 | 6:13 | 49.776
2024-03-01 | 6:13 | 49.778
2024-03-01 | 6:13 | 49.778
2024-03-01 | 6:13 | 49.777
2024-03-01 | 6:13 | 49.777
2024-03-01 | 6:13 | 49.779
2024-03-01 | 6:13 | 49.782
2024-03-01 | 6:13 | 49.786
2024-03-01 | 6:13 | 49.791
2024-03-01 | 6:13 | 49.799
2024-03-01 | 6:13 | 49.802
2024-03-01 | 6:13 | 49.805
2024-03-01 | 6:13 | 49.809
2024-03-01 | 6:13 | 49.812
2024-03-01 | 6:13 | 49.819
2024-03-01 | 6:13 | 49.828
2024-03-01 | 6:13 | 49.838
2024-03-01 | 6:13 | 49.846
2024-03-01 | 6:13 | 49.853
2024-03-01 | 6:13 | 49.859
2024-03-01 | 6:13 | 49.866
2024-03-01 | 6:13 | 49.873
2024-03-01 | 6:13 | 49.878
2024-03-01 | 6:13 | 49.881
2024-03-01 | 6:13 | 49.884
2024-03-01 | 6:13 | 49.887
2024-03-01 | 6:13 | 49.89
2024-03-01 | 6:13 | 49.892
2024-03-01 | 6:13 | 49.892
2024-03-01 | 6:13 | 49.89
2024-03-01 | 6:13 | 49.888
2024-03-01 | 6:13 | 49.888
2024-03-01 | 6:13 | 49.888
2024-03-01 | 6:13 | 49.887
2024-03-01 | 6:13 | 49.886
2024-03-01 | 6:13 | 49.884
2024-03-01 | 6:13 | 49.883
2024-03-01 | 6:13 | 49.883
2024-03-01 | 6:13 | 49.884
2024-03-01 | 6:13 | 49.885
2024-03-01 | 6:13 | 49.887
2024-03-01 | 6:13 | 49.888
2024-03-01 | 6:13 | 49.889
2024-03-01 | 6:13 | 49.893
2024-03-01 | 6:13 | 49.894
2024-03-01 | 6:13 | 49.898
2024-03-01 | 6:13 | 49.897
2024-03-01 | 6:13 | 49.897
2024-03-01 | 6:13 | 49.898
2024-03-01 | 6:13 | 49.9
2024-03-01 | 6:13 | 49.898
2024-03-01 | 6:14 | 49.896
2024-03-01 | 6:14 | 49.896
2024-03-01 | 6:14 | 49.894
2024-03-01 | 6:14 | 49.894
2024-03-01 | 6:14 | 49.892
2024-03-01 | 6:14 | 49.892
2024-03-01 | 6:14 | 49.889
2024-03-01 | 6:14 | 49.89
2024-03-01 | 6:14 | 49.891
2024-03-01 | 6:14 | 49.892
2024-03-01 | 6:14 | 49.89
2024-03-01 | 6:14 | 49.888
2024-03-01 | 6:14 | 49.886
2024-03-01 | 6:14 | 49.885
2024-03-01 | 6:14 | 49.885
2024-03-01 | 6:14 | 49.885
2024-03-01 | 6:14 | 49.883
2024-03-01 | 6:14 | 49.882
2024-03-01 | 6:14 | 49.884
2024-03-01 | 6:14 | 49.884
2024-03-01 | 6:14 | 49.889
2024-03-01 | 6:14 | 49.89
2024-03-01 | 6:14 | 49.891
2024-03-01 | 6:14 | 49.891
2024-03-01 | 6:14 | 49.895
2024-03-01 | 6:14 | 49.899
2024-03-01 | 6:14 | 49.899
2024-03-01 | 6:14 | 49.898
2024-03-01 | 6:14 | 49.902
2024-03-01 | 6:14 | 49.902
2024-03-01 | 6:14 | 49.902
2024-03-01 | 6:14 | 49.903
2024-03-01 | 6:14 | 49.902
2024-03-01 | 6:14 | 49.9
2024-03-01 | 6:14 | 49.896
2024-03-01 | 6:14 | 49.895
2024-03-01 | 6:14 | 49.891
2024-03-01 | 6:14 | 49.889
2024-03-01 | 6:14 | 49.888
2024-03-01 | 6:14 | 49.888
2024-03-01 | 6:14 | 49.889
2024-03-01 | 6:14 | 49.889
2024-03-01 | 6:14 | 49.89
2024-03-01 | 6:14 | 49.891
2024-03-01 | 6:14 | 49.892
2024-03-01 | 6:14 | 49.892
2024-03-01 | 6:14 | 49.892
2024-03-01 | 6:14 | 49.894
2024-03-01 | 6:14 | 49.895
2024-03-01 | 6:14 | 49.898
2024-03-01 | 6:14 | 49.897
2024-03-01 | 6:14 | 49.898
2024-03-01 | 6:14 | 49.9
2024-03-01 | 6:14 | 49.901
2024-03-01 | 6:14 | 49.901
2024-03-01 | 6:14 | 49.904
2024-03-01 | 6:14 | 49.903
2024-03-01 | 6:14 | 49.904
2024-03-01 | 6:14 | 49.906
2024-03-01 | 6:14 | 49.91
2024-03-01 | 6:15 | 49.911
2024-03-01 | 6:15 | 49.914
2024-03-01 | 6:15 | 49.916
2024-03-01 | 6:15 | 49.918
2024-03-01 | 6:15 | 49.915
2024-03-01 | 6:15 | 49.913
2024-03-01 | 6:15 | 49.91
2024-03-01 | 6:15 | 49.907
2024-03-01 | 6:15 | 49.905
2024-03-01 | 6:15 | 49.901
2024-03-01 | 6:15 | 49.899
2024-03-01 | 6:15 | 49.901
2024-03-01 | 6:15 | 49.903
2024-03-01 | 6:15 | 49.903
2024-03-01 | 6:15 | 49.904
2024-03-01 | 6:15 | 49.907
2024-03-01 | 6:15 | 49.911
2024-03-01 | 6:15 | 49.915
2024-03-01 | 6:15 | 49.919
2024-03-01 | 6:15 | 49.925
2024-03-01 | 6:15 | 49.927
2024-03-01 | 6:15 | 49.929
2024-03-01 | 6:15 | 49.93
2024-03-01 | 6:15 | 49.932
2024-03-01 | 6:15 | 49.934
2024-03-01 | 6:15 | 49.933
2024-03-01 | 6:15 | 49.932
2024-03-01 | 6:15 | 49.931
2024-03-01 | 6:15 | 49.929
2024-03-01 | 6:15 | 49.929
2024-03-01 | 6:15 | 49.929
2024-03-01 | 6:15 | 49.93
2024-03-01 | 6:15 | 49.93
2024-03-01 | 6:15 | 49.932
2024-03-01 | 6:15 | 49.935
2024-03-01 | 6:15 | 49.936
2024-03-01 | 6:15 | 49.937
2024-03-01 | 6:15 | 49.941
2024-03-01 | 6:15 | 49.941
2024-03-01 | 6:15 | 49.941
2024-03-01 | 6:15 | 49.942
2024-03-01 | 6:15 | 49.94
2024-03-01 | 6:15 | 49.937
2024-03-01 | 6:15 | 49.934
2024-03-01 | 6:15 | 49.934
2024-03-01 | 6:15 | 49.935
2024-03-01 | 6:15 | 49.934
2024-03-01 | 6:15 | 49.935
2024-03-01 | 6:15 | 49.936
2024-03-01 | 6:15 | 49.937
2024-03-01 | 6:15 | 49.937
2024-03-01 | 6:15 | 49.939
2024-03-01 | 6:15 | 49.94
2024-03-01 | 6:15 | 49.943
2024-03-01 | 6:15 | 49.947
2024-03-01 | 6:15 | 49.948
2024-03-01 | 6:15 | 49.951
2024-03-01 | 6:15 | 49.953
2024-03-01 | 6:15 | 49.952
2024-03-01 | 6:16 | 49.953
2024-03-01 | 6:16 | 49.951
2024-03-01 | 6:16 | 49.95
2024-03-01 | 6:16 | 49.948
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.948
2024-03-01 | 6:16 | 49.948
2024-03-01 | 6:16 | 49.948
2024-03-01 | 6:16 | 49.946
2024-03-01 | 6:16 | 49.946
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.946
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.948
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.948
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.947
2024-03-01 | 6:16 | 49.948
2024-03-01 | 6:16 | 49.951
2024-03-01 | 6:16 | 49.955
2024-03-01 | 6:16 | 49.96
2024-03-01 | 6:16 | 49.964
2024-03-01 | 6:16 | 49.966
2024-03-01 | 6:16 | 49.967
2024-03-01 | 6:16 | 49.966
2024-03-01 | 6:16 | 49.966
2024-03-01 | 6:16 | 49.967
2024-03-01 | 6:16 | 49.968
2024-03-01 | 6:16 | 49.965
2024-03-01 | 6:16 | 49.964
2024-03-01 | 6:16 | 49.963
2024-03-01 | 6:16 | 49.963
2024-03-01 | 6:16 | 49.964
2024-03-01 | 6:16 | 49.967
2024-03-01 | 6:16 | 49.966
2024-03-01 | 6:16 | 49.966
2024-03-01 | 6:16 | 49.967
2024-03-01 | 6:16 | 49.971
2024-03-01 | 6:16 | 49.978
2024-03-01 | 6:16 | 49.985
2024-03-01 | 6:16 | 49.992
2024-03-01 | 6:16 | 49.996
2024-03-01 | 6:16 | 50.001
2024-03-01 | 6:16 | 50.004
2024-03-01 | 6:16 | 50.006
2024-03-01 | 6:16 | 50.008
2024-03-01 | 6:16 | 50.011
2024-03-01 | 6:16 | 50.013
2024-03-01 | 6:16 | 50.014
2024-03-01 | 6:16 | 50.014
2024-03-01 | 6:16 | 50.013
2024-03-01 | 6:16 | 50.01
2024-03-01 | 6:16 | 50.008
2024-03-01 | 6:16 | 50.004
2024-03-01 | 6:16 | 49.999
2024-03-01 | 6:17 | 49.995
2024-03-01 | 6:17 | 49.99
2024-03-01 | 6:17 | 49.985
2024-03-01 | 6:17 | 49.983
2024-03-01 | 6:17 | 49.982
2024-03-01 | 6:17 | 49.979
2024-03-01 | 6:17 | 49.978
2024-03-01 | 6:17 | 49.976
2024-03-01 | 6:17 | 49.975
2024-03-01 | 6:17 | 49.976
2024-03-01 | 6:17 | 49.976
2024-03-01 | 6:17 | 49.976
2024-03-01 | 6:17 | 49.979
2024-03-01 | 6:17 | 49.982
2024-03-01 | 6:17 | 49.983
2024-03-01 | 6:17 | 49.985
2024-03-01 | 6:17 | 49.984
2024-03-01 | 6:17 | 49.984
2024-03-01 | 6:17 | 49.984
2024-03-01 | 6:17 | 49.983
2024-03-01 | 6:17 | 49.984
2024-03-01 | 6:17 | 49.985
2024-03-01 | 6:17 | 49.988
2024-03-01 | 6:17 | 49.991
2024-03-01 | 6:17 | 49.996
2024-03-01 | 6:17 | 50
2024-03-01 | 6:17 | 50.006
2024-03-01 | 6:17 | 50.009
2024-03-01 | 6:17 | 50.013
2024-03-01 | 6:17 | 50.015
2024-03-01 | 6:17 | 50.019
2024-03-01 | 6:17 | 50.02
2024-03-01 | 6:17 | 50.023
2024-03-01 | 6:17 | 50.024
2024-03-01 | 6:17 | 50.027
2024-03-01 | 6:17 | 50.028
2024-03-01 | 6:17 | 50.033
2024-03-01 | 6:17 | 50.035
2024-03-01 | 6:17 | 50.039
2024-03-01 | 6:17 | 50.038
2024-03-01 | 6:17 | 50.041
2024-03-01 | 6:17 | 50.041
2024-03-01 | 6:17 | 50.043
2024-03-01 | 6:17 | 50.045
2024-03-01 | 6:17 | 50.045
2024-03-01 | 6:17 | 50.045
2024-03-01 | 6:17 | 50.045
2024-03-01 | 6:17 | 50.046
2024-03-01 | 6:17 | 50.046
2024-03-01 | 6:17 | 50.046
2024-03-01 | 6:17 | 50.044
2024-03-01 | 6:17 | 50.045
2024-03-01 | 6:17 | 50.046
2024-03-01 | 6:17 | 50.049
2024-03-01 | 6:17 | 50.052
2024-03-01 | 6:17 | 50.053
2024-03-01 | 6:17 | 50.055
2024-03-01 | 6:17 | 50.055
2024-03-01 | 6:17 | 50.054
2024-03-01 | 6:18 | 50.055
2024-03-01 | 6:18 | 50.055
2024-03-01 | 6:18 | 50.052
2024-03-01 | 6:18 | 50.051
2024-03-01 | 6:18 | 50.049
2024-03-01 | 6:18 | 50.047
2024-03-01 | 6:18 | 50.045
2024-03-01 | 6:18 | 50.045
2024-03-01 | 6:18 | 50.047
2024-03-01 | 6:18 | 50.051
2024-03-01 | 6:18 | 50.056
2024-03-01 | 6:18 | 50.059
2024-03-01 | 6:18 | 50.06
2024-03-01 | 6:18 | 50.061
2024-03-01 | 6:18 | 50.061
2024-03-01 | 6:18 | 50.062
2024-03-01 | 6:18 | 50.062
2024-03-01 | 6:18 | 50.06
2024-03-01 | 6:18 | 50.06
2024-03-01 | 6:18 | 50.06
2024-03-01 | 6:18 | 50.063
2024-03-01 | 6:18 | 50.064
2024-03-01 | 6:18 | 50.067
2024-03-01 | 6:18 | 50.069
2024-03-01 | 6:18 | 50.071
2024-03-01 | 6:18 | 50.071
2024-03-01 | 6:18 | 50.071
2024-03-01 | 6:18 | 50.07
2024-03-01 | 6:18 | 50.07
2024-03-01 | 6:18 | 50.07

## 20240304-1
In GMT
Date | Time | Freq
2024-03-04 | 13:58 | 50.002 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-04 | 13:58 | 50.001 | 222 | BRITNED | 676.211
2024-03-04 | 13:58 | 50 | 268 | WBURB-2 | 428.156
2024-03-04 | 13:58 | 50.001 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-04 | 13:58 | 50.004 |  | Viking Link | -648.9
2024-03-04 | 13:58 | 50.005 |  | Viking Link | 1398.96
2024-03-04 | 13:58 | 50.003 | 209 | DRAXX-3 | 626.95
2024-03-04 | 13:58 | 50.003 | 154 | CDCL-1 | 391.57
2024-03-04 | 13:58 | 49.999 | 268 | ROCK-1 | 468.495
2024-03-04 | 13:58 | 49.998 | 148 | IFA Bipole1 | 945.473
2024-03-04 | 13:58 | 49.996 | 132 | IFA Bipole1 | 999.1
2024-03-04 | 13:58 | 49.998 | 141 | IFA Bipole2 | 1000
2024-03-04 | 13:58 | 49.998 | 135 | IFA Bipole1 | 996.75
2024-03-04 | 13:58 | 49.998 |  | Viking Link | -780.3
2024-03-04 | 13:58 | 49.999
2024-03-04 | 13:58 | 49.999
2024-03-04 | 13:58 | 50
2024-03-04 | 13:58 | 50.001
2024-03-04 | 13:58 | 50
2024-03-04 | 13:58 | 50.001 | 130 | HEYM12 | 271.908
2024-03-04 | 13:58 | 50.002 | 228 | HUMR-1 | 303.75
2024-03-04 | 13:58 | 50
2024-03-04 | 13:58 | 49.998
2024-03-04 | 13:58 | 49.997
2024-03-04 | 13:58 | 49.996
2024-03-04 | 13:58 | 49.998
2024-03-04 | 13:58 | 50
2024-03-04 | 13:58 | 50
2024-03-04 | 13:58 | 50
2024-03-04 | 13:58 | 50.001
2024-03-04 | 13:58 | 49.998 | 211 | CDCL-1 | 291.5
2024-03-04 | 13:59 | 50 | 199 | STAY-2 | 413.125
2024-03-04 | 13:59 | 49.999 | 173 | CDCL-1 | 397.375
2024-03-04 | 13:59 | 50 | 248 | SEAB-2 | 361.25
2024-03-04 | 13:59 | 50 | 255 | FRANCE | 995.65
2024-03-04 | 13:59 | 50.003 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-04 | 13:59 | 50.003
2024-03-04 | 13:59 | 50.004
2024-03-04 | 13:59 | 50.006
2024-03-04 | 13:59 | 50.008
2024-03-04 | 13:59 | 50.008
2024-03-04 | 13:59 | 50.008
2024-03-04 | 13:59 | 50.007
2024-03-04 | 13:59 | 50.005
2024-03-04 | 13:59 | 50.001
2024-03-04 | 13:59 | 49.997
2024-03-04 | 13:59 | 49.99
2024-03-04 | 13:59 | 49.984
2024-03-04 | 13:59 | 49.976
2024-03-04 | 13:59 | 49.969
2024-03-04 | 13:59 | 49.965
2024-03-04 | 13:59 | 49.964
2024-03-04 | 13:59 | 49.964
2024-03-04 | 13:59 | 49.964
2024-03-04 | 13:59 | 49.965
2024-03-04 | 13:59 | 49.967
2024-03-04 | 13:59 | 49.968
2024-03-04 | 13:59 | 49.967
2024-03-04 | 13:59 | 49.968
2024-03-04 | 13:59 | 49.969
2024-03-04 | 13:59 | 49.97
2024-03-04 | 13:59 | 49.97
2024-03-04 | 13:59 | 49.969
2024-03-04 | 13:59 | 49.969
2024-03-04 | 13:59 | 49.969
2024-03-04 | 13:59 | 49.968
2024-03-04 | 13:59 | 49.966
2024-03-04 | 13:59 | 49.964
2024-03-04 | 13:59 | 49.96
2024-03-04 | 13:59 | 49.956
2024-03-04 | 13:59 | 49.955
2024-03-04 | 13:59 | 49.953
2024-03-04 | 13:59 | 49.951
2024-03-04 | 13:59 | 49.953
2024-03-04 | 13:59 | 49.954
2024-03-04 | 13:59 | 49.955
2024-03-04 | 13:59 | 49.956
2024-03-04 | 13:59 | 49.957
2024-03-04 | 13:59 | 49.958
2024-03-04 | 13:59 | 49.96
2024-03-04 | 13:59 | 49.96
2024-03-04 | 13:59 | 49.959
2024-03-04 | 13:59 | 49.957
2024-03-04 | 13:59 | 49.957
2024-03-04 | 13:59 | 49.957
2024-03-04 | 13:59 | 49.958
2024-03-04 | 13:59 | 49.956
2024-03-04 | 13:59 | 49.955
2024-03-04 | 13:59 | 49.953
2024-03-04 | 13:59 | 49.951
2024-03-04 | 14:00 | 49.953
2024-03-04 | 14:00 | 49.952
2024-03-04 | 14:00 | 49.954
2024-03-04 | 14:00 | 49.955
2024-03-04 | 14:00 | 49.959
2024-03-04 | 14:00 | 49.964
2024-03-04 | 14:00 | 49.92
2024-03-04 | 14:00 | 49.869
2024-03-04 | 14:00 | 49.841
2024-03-04 | 14:00 | 49.827
2024-03-04 | 14:00 | 49.823
2024-03-04 | 14:00 | 49.823
2024-03-04 | 14:00 | 49.827
2024-03-04 | 14:00 | 49.832
2024-03-04 | 14:00 | 49.835
2024-03-04 | 14:00 | 49.836
2024-03-04 | 14:00 | 49.837
2024-03-04 | 14:00 | 49.838
2024-03-04 | 14:00 | 49.84
2024-03-04 | 14:00 | 49.841
2024-03-04 | 14:00 | 49.844
2024-03-04 | 14:00 | 49.847
2024-03-04 | 14:00 | 49.852
2024-03-04 | 14:00 | 49.857
2024-03-04 | 14:00 | 49.866
2024-03-04 | 14:00 | 49.867
2024-03-04 | 14:00 | 49.869
2024-03-04 | 14:00 | 49.87
2024-03-04 | 14:00 | 49.872
2024-03-04 | 14:00 | 49.873
2024-03-04 | 14:00 | 49.875
2024-03-04 | 14:00 | 49.876
2024-03-04 | 14:00 | 49.88
2024-03-04 | 14:00 | 49.882
2024-03-04 | 14:00 | 49.886
2024-03-04 | 14:00 | 49.891
2024-03-04 | 14:00 | 49.892
2024-03-04 | 14:00 | 49.891
2024-03-04 | 14:00 | 49.89
2024-03-04 | 14:00 | 49.887
2024-03-04 | 14:00 | 49.886
2024-03-04 | 14:00 | 49.884
2024-03-04 | 14:00 | 49.882
2024-03-04 | 14:00 | 49.881
2024-03-04 | 14:00 | 49.882
2024-03-04 | 14:00 | 49.883
2024-03-04 | 14:00 | 49.884
2024-03-04 | 14:00 | 49.885
2024-03-04 | 14:00 | 49.889
2024-03-04 | 14:00 | 49.893
2024-03-04 | 14:00 | 49.898
2024-03-04 | 14:00 | 49.908
2024-03-04 | 14:00 | 49.915
2024-03-04 | 14:00 | 49.922
2024-03-04 | 14:00 | 49.931
2024-03-04 | 14:00 | 49.938
2024-03-04 | 14:00 | 49.945
2024-03-04 | 14:00 | 49.948
2024-03-04 | 14:00 | 49.953
2024-03-04 | 14:00 | 49.955
2024-03-04 | 14:00 | 49.957
2024-03-04 | 14:01 | 49.957
2024-03-04 | 14:01 | 49.954
2024-03-04 | 14:01 | 49.952
2024-03-04 | 14:01 | 49.948
2024-03-04 | 14:01 | 49.946
2024-03-04 | 14:01 | 49.946
2024-03-04 | 14:01 | 49.945
2024-03-04 | 14:01 | 49.947
2024-03-04 | 14:01 | 49.945
2024-03-04 | 14:01 | 49.945
2024-03-04 | 14:01 | 49.943
2024-03-04 | 14:01 | 49.943
2024-03-04 | 14:01 | 49.944
2024-03-04 | 14:01 | 49.942
2024-03-04 | 14:01 | 49.942
2024-03-04 | 14:01 | 49.944
2024-03-04 | 14:01 | 49.945
2024-03-04 | 14:01 | 49.944
2024-03-04 | 14:01 | 49.943
2024-03-04 | 14:01 | 49.94
2024-03-04 | 14:01 | 49.94
2024-03-04 | 14:01 | 49.938
2024-03-04 | 14:01 | 49.939
2024-03-04 | 14:01 | 49.937
2024-03-04 | 14:01 | 49.937
2024-03-04 | 14:01 | 49.936
2024-03-04 | 14:01 | 49.934
2024-03-04 | 14:01 | 49.933
2024-03-04 | 14:01 | 49.931
2024-03-04 | 14:01 | 49.927
2024-03-04 | 14:01 | 49.921
2024-03-04 | 14:01 | 49.915
2024-03-04 | 14:01 | 49.912
2024-03-04 | 14:01 | 49.908
2024-03-04 | 14:01 | 49.904
2024-03-04 | 14:01 | 49.901
2024-03-04 | 14:01 | 49.898
2024-03-04 | 14:01 | 49.897
2024-03-04 | 14:01 | 49.897
2024-03-04 | 14:01 | 49.9
2024-03-04 | 14:01 | 49.901
2024-03-04 | 14:01 | 49.903
2024-03-04 | 14:01 | 49.904
2024-03-04 | 14:01 | 49.905
2024-03-04 | 14:01 | 49.904
2024-03-04 | 14:01 | 49.905
2024-03-04 | 14:01 | 49.907
2024-03-04 | 14:01 | 49.908
2024-03-04 | 14:01 | 49.908
2024-03-04 | 14:01 | 49.906
2024-03-04 | 14:01 | 49.904
2024-03-04 | 14:01 | 49.901
2024-03-04 | 14:01 | 49.9
2024-03-04 | 14:01 | 49.9
2024-03-04 | 14:01 | 49.901
2024-03-04 | 14:01 | 49.901
2024-03-04 | 14:01 | 49.901
2024-03-04 | 14:01 | 49.899
2024-03-04 | 14:01 | 49.9
2024-03-04 | 14:02 | 49.899
2024-03-04 | 14:02 | 49.899
2024-03-04 | 14:02 | 49.899
2024-03-04 | 14:02 | 49.897
2024-03-04 | 14:02 | 49.896
2024-03-04 | 14:02 | 49.895
2024-03-04 | 14:02 | 49.895
2024-03-04 | 14:02 | 49.895
2024-03-04 | 14:02 | 49.896
2024-03-04 | 14:02 | 49.897
2024-03-04 | 14:02 | 49.896
2024-03-04 | 14:02 | 49.896
2024-03-04 | 14:02 | 49.896
2024-03-04 | 14:02 | 49.895
2024-03-04 | 14:02 | 49.897
2024-03-04 | 14:02 | 49.899
2024-03-04 | 14:02 | 49.902
2024-03-04 | 14:02 | 49.906
2024-03-04 | 14:02 | 49.908
2024-03-04 | 14:02 | 49.907
2024-03-04 | 14:02 | 49.906
2024-03-04 | 14:02 | 49.904
2024-03-04 | 14:02 | 49.903
2024-03-04 | 14:02 | 49.904
2024-03-04 | 14:02 | 49.904
2024-03-04 | 14:02 | 49.903
2024-03-04 | 14:02 | 49.9
2024-03-04 | 14:02 | 49.9
2024-03-04 | 14:02 | 49.898
2024-03-04 | 14:02 | 49.897
2024-03-04 | 14:02 | 49.896
2024-03-04 | 14:02 | 49.896
2024-03-04 | 14:02 | 49.897
2024-03-04 | 14:02 | 49.898
2024-03-04 | 14:02 | 49.898
2024-03-04 | 14:02 | 49.899
2024-03-04 | 14:02 | 49.902
2024-03-04 | 14:02 | 49.905
2024-03-04 | 14:02 | 49.906
2024-03-04 | 14:02 | 49.906
2024-03-04 | 14:02 | 49.906
2024-03-04 | 14:02 | 49.903
2024-03-04 | 14:02 | 49.9
2024-03-04 | 14:02 | 49.895
2024-03-04 | 14:02 | 49.891
2024-03-04 | 14:02 | 49.888
2024-03-04 | 14:02 | 49.888
2024-03-04 | 14:02 | 49.886
2024-03-04 | 14:02 | 49.885
2024-03-04 | 14:02 | 49.887
2024-03-04 | 14:02 | 49.886
2024-03-04 | 14:02 | 49.887
2024-03-04 | 14:02 | 49.888
2024-03-04 | 14:02 | 49.889
2024-03-04 | 14:02 | 49.891
2024-03-04 | 14:02 | 49.893
2024-03-04 | 14:02 | 49.895
2024-03-04 | 14:02 | 49.896
2024-03-04 | 14:02 | 49.895
2024-03-04 | 14:02 | 49.898
2024-03-04 | 14:02 | 49.9
2024-03-04 | 14:03 | 49.901
2024-03-04 | 14:03 | 49.898
2024-03-04 | 14:03 | 49.894
2024-03-04 | 14:03 | 49.892
2024-03-04 | 14:03 | 49.889
2024-03-04 | 14:03 | 49.887
2024-03-04 | 14:03 | 49.886
2024-03-04 | 14:03 | 49.885
2024-03-04 | 14:03 | 49.888
2024-03-04 | 14:03 | 49.89
2024-03-04 | 14:03 | 49.891
2024-03-04 | 14:03 | 49.891
2024-03-04 | 14:03 | 49.893
2024-03-04 | 14:03 | 49.895
2024-03-04 | 14:03 | 49.898
2024-03-04 | 14:03 | 49.898
2024-03-04 | 14:03 | 49.897
2024-03-04 | 14:03 | 49.897
2024-03-04 | 14:03 | 49.897
2024-03-04 | 14:03 | 49.899
2024-03-04 | 14:03 | 49.899
2024-03-04 | 14:03 | 49.903
2024-03-04 | 14:03 | 49.903
2024-03-04 | 14:03 | 49.904
2024-03-04 | 14:03 | 49.904
2024-03-04 | 14:03 | 49.903
2024-03-04 | 14:03 | 49.905
2024-03-04 | 14:03 | 49.905
2024-03-04 | 14:03 | 49.905
2024-03-04 | 14:03 | 49.904
2024-03-04 | 14:03 | 49.904
2024-03-04 | 14:03 | 49.904
2024-03-04 | 14:03 | 49.908
2024-03-04 | 14:03 | 49.912
2024-03-04 | 14:03 | 49.914
2024-03-04 | 14:03 | 49.914
2024-03-04 | 14:03 | 49.914
2024-03-04 | 14:03 | 49.914
2024-03-04 | 14:03 | 49.915
2024-03-04 | 14:03 | 49.917
2024-03-04 | 14:03 | 49.918
2024-03-04 | 14:03 | 49.916
2024-03-04 | 14:03 | 49.916
2024-03-04 | 14:03 | 49.914
2024-03-04 | 14:03 | 49.914
2024-03-04 | 14:03 | 49.912
2024-03-04 | 14:03 | 49.911
2024-03-04 | 14:03 | 49.909
2024-03-04 | 14:03 | 49.907
2024-03-04 | 14:03 | 49.907
2024-03-04 | 14:03 | 49.907
2024-03-04 | 14:03 | 49.908
2024-03-04 | 14:03 | 49.91
2024-03-04 | 14:03 | 49.911
2024-03-04 | 14:03 | 49.913
2024-03-04 | 14:03 | 49.916
2024-03-04 | 14:03 | 49.918
2024-03-04 | 14:03 | 49.921
2024-03-04 | 14:03 | 49.924
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.929
2024-03-04 | 14:04 | 49.928
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.929
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.926
2024-03-04 | 14:04 | 49.926
2024-03-04 | 14:04 | 49.926
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.925
2024-03-04 | 14:04 | 49.924
2024-03-04 | 14:04 | 49.922
2024-03-04 | 14:04 | 49.919
2024-03-04 | 14:04 | 49.918
2024-03-04 | 14:04 | 49.917
2024-03-04 | 14:04 | 49.914
2024-03-04 | 14:04 | 49.917
2024-03-04 | 14:04 | 49.918
2024-03-04 | 14:04 | 49.919
2024-03-04 | 14:04 | 49.921
2024-03-04 | 14:04 | 49.924
2024-03-04 | 14:04 | 49.926
2024-03-04 | 14:04 | 49.929
2024-03-04 | 14:04 | 49.929
2024-03-04 | 14:04 | 49.929
2024-03-04 | 14:04 | 49.93
2024-03-04 | 14:04 | 49.929
2024-03-04 | 14:04 | 49.929
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.926
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.928
2024-03-04 | 14:04 | 49.928
2024-03-04 | 14:04 | 49.928
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.929
2024-03-04 | 14:04 | 49.929
2024-03-04 | 14:04 | 49.931
2024-03-04 | 14:04 | 49.932
2024-03-04 | 14:04 | 49.932
2024-03-04 | 14:04 | 49.931
2024-03-04 | 14:04 | 49.929
2024-03-04 | 14:04 | 49.927
2024-03-04 | 14:04 | 49.924
2024-03-04 | 14:04 | 49.924
2024-03-04 | 14:04 | 49.924
2024-03-04 | 14:04 | 49.923
2024-03-04 | 14:04 | 49.922
2024-03-04 | 14:04 | 49.922
2024-03-04 | 14:04 | 49.921
2024-03-04 | 14:04 | 49.92
2024-03-04 | 14:04 | 49.92
2024-03-04 | 14:04 | 49.919
2024-03-04 | 14:04 | 49.917
2024-03-04 | 14:04 | 49.917
2024-03-04 | 14:04 | 49.915
2024-03-04 | 14:04 | 49.915
2024-03-04 | 14:05 | 49.913
2024-03-04 | 14:05 | 49.914
2024-03-04 | 14:05 | 49.914
2024-03-04 | 14:05 | 49.916
2024-03-04 | 14:05 | 49.921
2024-03-04 | 14:05 | 49.924
2024-03-04 | 14:05 | 49.927
2024-03-04 | 14:05 | 49.929
2024-03-04 | 14:05 | 49.932
2024-03-04 | 14:05 | 49.938
2024-03-04 | 14:05 | 49.939
2024-03-04 | 14:05 | 49.939
2024-03-04 | 14:05 | 49.941
2024-03-04 | 14:05 | 49.94
2024-03-04 | 14:05 | 49.938
2024-03-04 | 14:05 | 49.939
2024-03-04 | 14:05 | 49.939
2024-03-04 | 14:05 | 49.942
2024-03-04 | 14:05 | 49.943
2024-03-04 | 14:05 | 49.946
2024-03-04 | 14:05 | 49.946
2024-03-04 | 14:05 | 49.945
2024-03-04 | 14:05 | 49.946
2024-03-04 | 14:05 | 49.948
2024-03-04 | 14:05 | 49.952
2024-03-04 | 14:05 | 49.956
2024-03-04 | 14:05 | 49.956
2024-03-04 | 14:05 | 49.957
2024-03-04 | 14:05 | 49.957
2024-03-04 | 14:05 | 49.955
2024-03-04 | 14:05 | 49.953
2024-03-04 | 14:05 | 49.95
2024-03-04 | 14:05 | 49.95
2024-03-04 | 14:05 | 49.948
2024-03-04 | 14:05 | 49.949
2024-03-04 | 14:05 | 49.948
2024-03-04 | 14:05 | 49.948
2024-03-04 | 14:05 | 49.946
2024-03-04 | 14:05 | 49.947
2024-03-04 | 14:05 | 49.948
2024-03-04 | 14:05 | 49.948
2024-03-04 | 14:05 | 49.947
2024-03-04 | 14:05 | 49.947
2024-03-04 | 14:05 | 49.948
2024-03-04 | 14:05 | 49.947
2024-03-04 | 14:05 | 49.945
2024-03-04 | 14:05 | 49.942
2024-03-04 | 14:05 | 49.943
2024-03-04 | 14:05 | 49.943
2024-03-04 | 14:05 | 49.943
2024-03-04 | 14:05 | 49.943
2024-03-04 | 14:05 | 49.945
2024-03-04 | 14:05 | 49.945
2024-03-04 | 14:05 | 49.945
2024-03-04 | 14:05 | 49.945
2024-03-04 | 14:05 | 49.945
2024-03-04 | 14:05 | 49.945
2024-03-04 | 14:05 | 49.944
2024-03-04 | 14:05 | 49.945
2024-03-04 | 14:06 | 49.942
2024-03-04 | 14:06 | 49.939
2024-03-04 | 14:06 | 49.938
2024-03-04 | 14:06 | 49.937
2024-03-04 | 14:06 | 49.938
2024-03-04 | 14:06 | 49.94
2024-03-04 | 14:06 | 49.941
2024-03-04 | 14:06 | 49.941
2024-03-04 | 14:06 | 49.941
2024-03-04 | 14:06 | 49.943
2024-03-04 | 14:06 | 49.944
2024-03-04 | 14:06 | 49.942
2024-03-04 | 14:06 | 49.943
2024-03-04 | 14:06 | 49.945
2024-03-04 | 14:06 | 49.945
2024-03-04 | 14:06 | 49.947
2024-03-04 | 14:06 | 49.946
2024-03-04 | 14:06 | 49.946
2024-03-04 | 14:06 | 49.948
2024-03-04 | 14:06 | 49.95
2024-03-04 | 14:06 | 49.951
2024-03-04 | 14:06 | 49.95
2024-03-04 | 14:06 | 49.95
2024-03-04 | 14:06 | 49.95
2024-03-04 | 14:06 | 49.95
2024-03-04 | 14:06 | 49.951
2024-03-04 | 14:06 | 49.952
2024-03-04 | 14:06 | 49.951
2024-03-04 | 14:06 | 49.951
2024-03-04 | 14:06 | 49.953
2024-03-04 | 14:06 | 49.953
2024-03-04 | 14:06 | 49.954
2024-03-04 | 14:06 | 49.954
2024-03-04 | 14:06 | 49.955
2024-03-04 | 14:06 | 49.957
2024-03-04 | 14:06 | 49.956
2024-03-04 | 14:06 | 49.955
2024-03-04 | 14:06 | 49.953
2024-03-04 | 14:06 | 49.952
2024-03-04 | 14:06 | 49.95
2024-03-04 | 14:06 | 49.95
2024-03-04 | 14:06 | 49.95
2024-03-04 | 14:06 | 49.949
2024-03-04 | 14:06 | 49.949
2024-03-04 | 14:06 | 49.948
2024-03-04 | 14:06 | 49.948
2024-03-04 | 14:06 | 49.949
2024-03-04 | 14:06 | 49.95
2024-03-04 | 14:06 | 49.948
2024-03-04 | 14:06 | 49.947
2024-03-04 | 14:06 | 49.947
2024-03-04 | 14:06 | 49.949
2024-03-04 | 14:06 | 49.95
2024-03-04 | 14:06 | 49.954
2024-03-04 | 14:06 | 49.958
2024-03-04 | 14:06 | 49.96
2024-03-04 | 14:06 | 49.961
2024-03-04 | 14:06 | 49.962
2024-03-04 | 14:06 | 49.964
2024-03-04 | 14:06 | 49.965
2024-03-04 | 14:06 | 49.964
2024-03-04 | 14:07 | 49.963
2024-03-04 | 14:07 | 49.962
2024-03-04 | 14:07 | 49.963
2024-03-04 | 14:07 | 49.965
2024-03-04 | 14:07 | 49.966
2024-03-04 | 14:07 | 49.965
2024-03-04 | 14:07 | 49.963
2024-03-04 | 14:07 | 49.964
2024-03-04 | 14:07 | 49.963
2024-03-04 | 14:07 | 49.965
2024-03-04 | 14:07 | 49.965
2024-03-04 | 14:07 | 49.964
2024-03-04 | 14:07 | 49.963
2024-03-04 | 14:07 | 49.963
2024-03-04 | 14:07 | 49.963
2024-03-04 | 14:07 | 49.961
2024-03-04 | 14:07 | 49.962
2024-03-04 | 14:07 | 49.969
2024-03-04 | 14:07 | 49.971
2024-03-04 | 14:07 | 49.974
2024-03-04 | 14:07 | 49.974
2024-03-04 | 14:07 | 49.972
2024-03-04 | 14:07 | 49.971
2024-03-04 | 14:07 | 49.968
2024-03-04 | 14:07 | 49.968
2024-03-04 | 14:07 | 49.97
2024-03-04 | 14:07 | 49.972
2024-03-04 | 14:07 | 49.972
2024-03-04 | 14:07 | 49.972
2024-03-04 | 14:07 | 49.973
2024-03-04 | 14:07 | 49.97
2024-03-04 | 14:07 | 49.97
2024-03-04 | 14:07 | 49.969
2024-03-04 | 14:07 | 49.971
2024-03-04 | 14:07 | 49.973
2024-03-04 | 14:07 | 49.976
2024-03-04 | 14:07 | 49.975
2024-03-04 | 14:07 | 49.975
2024-03-04 | 14:07 | 49.974
2024-03-04 | 14:07 | 49.975
2024-03-04 | 14:07 | 49.973
2024-03-04 | 14:07 | 49.975
2024-03-04 | 14:07 | 49.976
2024-03-04 | 14:07 | 49.977
2024-03-04 | 14:07 | 49.979
2024-03-04 | 14:07 | 49.981
2024-03-04 | 14:07 | 49.98
2024-03-04 | 14:07 | 49.983
2024-03-04 | 14:07 | 49.98
2024-03-04 | 14:07 | 49.979
2024-03-04 | 14:07 | 49.98
2024-03-04 | 14:07 | 49.98
2024-03-04 | 14:07 | 49.982
2024-03-04 | 14:07 | 49.984
2024-03-04 | 14:07 | 49.984
2024-03-04 | 14:07 | 49.986
2024-03-04 | 14:07 | 49.987
2024-03-04 | 14:07 | 49.988
2024-03-04 | 14:07 | 49.991
2024-03-04 | 14:08 | 49.992
2024-03-04 | 14:08 | 49.994
2024-03-04 | 14:08 | 49.997
2024-03-04 | 14:08 | 49.997
2024-03-04 | 14:08 | 49.995
2024-03-04 | 14:08 | 49.994
2024-03-04 | 14:08 | 49.991
2024-03-04 | 14:08 | 49.986
2024-03-04 | 14:08 | 49.983
2024-03-04 | 14:08 | 49.98
2024-03-04 | 14:08 | 49.979
2024-03-04 | 14:08 | 49.978
2024-03-04 | 14:08 | 49.978
2024-03-04 | 14:08 | 49.979
2024-03-04 | 14:08 | 49.979
2024-03-04 | 14:08 | 49.979
2024-03-04 | 14:08 | 49.979
2024-03-04 | 14:08 | 49.977
2024-03-04 | 14:08 | 49.976
2024-03-04 | 14:08 | 49.978
2024-03-04 | 14:08 | 49.979
2024-03-04 | 14:08 | 49.981
2024-03-04 | 14:08 | 49.981
2024-03-04 | 14:08 | 49.983
2024-03-04 | 14:08 | 49.986
2024-03-04 | 14:08 | 49.989
2024-03-04 | 14:08 | 49.991
2024-03-04 | 14:08 | 49.991
2024-03-04 | 14:08 | 49.993
2024-03-04 | 14:08 | 49.991
2024-03-04 | 14:08 | 49.989
2024-03-04 | 14:08 | 49.985
2024-03-04 | 14:08 | 49.981
2024-03-04 | 14:08 | 49.981
2024-03-04 | 14:08 | 49.981
2024-03-04 | 14:08 | 49.98
2024-03-04 | 14:08 | 49.98
2024-03-04 | 14:08 | 49.98
2024-03-04 | 14:08 | 49.981
2024-03-04 | 14:08 | 49.98
2024-03-04 | 14:08 | 49.978
2024-03-04 | 14:08 | 49.976
2024-03-04 | 14:08 | 49.976
2024-03-04 | 14:08 | 49.978
2024-03-04 | 14:08 | 49.978
2024-03-04 | 14:08 | 49.98
2024-03-04 | 14:08 | 49.984
2024-03-04 | 14:08 | 49.987
2024-03-04 | 14:08 | 49.99
2024-03-04 | 14:08 | 49.99
2024-03-04 | 14:08 | 49.989
2024-03-04 | 14:08 | 49.989
2024-03-04 | 14:08 | 49.987
2024-03-04 | 14:08 | 49.985
2024-03-04 | 14:08 | 49.982
2024-03-04 | 14:08 | 49.978
2024-03-04 | 14:08 | 49.974
2024-03-04 | 14:08 | 49.973
2024-03-04 | 14:08 | 49.973
2024-03-04 | 14:08 | 49.972
2024-03-04 | 14:09 | 49.97
2024-03-04 | 14:09 | 49.971
2024-03-04 | 14:09 | 49.971
2024-03-04 | 14:09 | 49.973
2024-03-04 | 14:09 | 49.974
2024-03-04 | 14:09 | 49.975
2024-03-04 | 14:09 | 49.978
2024-03-04 | 14:09 | 49.98
2024-03-04 | 14:09 | 49.981
2024-03-04 | 14:09 | 49.983
2024-03-04 | 14:09 | 49.985
2024-03-04 | 14:09 | 49.984
2024-03-04 | 14:09 | 49.985
2024-03-04 | 14:09 | 49.983
2024-03-04 | 14:09 | 49.981
2024-03-04 | 14:09 | 49.979
2024-03-04 | 14:09 | 49.976
2024-03-04 | 14:09 | 49.977
2024-03-04 | 14:09 | 49.979
2024-03-04 | 14:09 | 49.981
2024-03-04 | 14:09 | 49.981
2024-03-04 | 14:09 | 49.977
2024-03-04 | 14:09 | 49.975
2024-03-04 | 14:09 | 49.973
2024-03-04 | 14:09 | 49.97
2024-03-04 | 14:09 | 49.969
2024-03-04 | 14:09 | 49.967
2024-03-04 | 14:09 | 49.967
2024-03-04 | 14:09 | 49.968
2024-03-04 | 14:09 | 49.967
2024-03-04 | 14:09 | 49.969
2024-03-04 | 14:09 | 49.967
2024-03-04 | 14:09 | 49.967
2024-03-04 | 14:09 | 49.966
2024-03-04 | 14:09 | 49.962
2024-03-04 | 14:09 | 49.962
2024-03-04 | 14:09 | 49.963
2024-03-04 | 14:09 | 49.964
2024-03-04 | 14:09 | 49.963
2024-03-04 | 14:09 | 49.964
2024-03-04 | 14:09 | 49.964
2024-03-04 | 14:09 | 49.964
2024-03-04 | 14:09 | 49.962
2024-03-04 | 14:09 | 49.96
2024-03-04 | 14:09 | 49.958
2024-03-04 | 14:09 | 49.958
2024-03-04 | 14:09 | 49.96
2024-03-04 | 14:09 | 49.959
2024-03-04 | 14:09 | 49.96
2024-03-04 | 14:09 | 49.957
2024-03-04 | 14:09 | 49.956
2024-03-04 | 14:09 | 49.956
2024-03-04 | 14:09 | 49.956
2024-03-04 | 14:09 | 49.963
2024-03-04 | 14:09 | 49.964
2024-03-04 | 14:09 | 49.963
2024-03-04 | 14:09 | 49.961
2024-03-04 | 14:09 | 49.962
2024-03-04 | 14:09 | 49.963
2024-03-04 | 14:09 | 49.965
2024-03-04 | 14:09 | 49.966
2024-03-04 | 14:10 | 49.969
2024-03-04 | 14:10 | 49.971
2024-03-04 | 14:10 | 49.971
2024-03-04 | 14:10 | 49.971
2024-03-04 | 14:10 | 49.969
2024-03-04 | 14:10 | 49.968
2024-03-04 | 14:10 | 49.965
2024-03-04 | 14:10 | 49.963
2024-03-04 | 14:10 | 49.962
2024-03-04 | 14:10 | 49.962
2024-03-04 | 14:10 | 49.961
2024-03-04 | 14:10 | 49.961
2024-03-04 | 14:10 | 49.964
2024-03-04 | 14:10 | 49.967
2024-03-04 | 14:10 | 49.968
2024-03-04 | 14:10 | 49.971
2024-03-04 | 14:10 | 49.969
2024-03-04 | 14:10 | 49.967
2024-03-04 | 14:10 | 49.964
2024-03-04 | 14:10 | 49.962
2024-03-04 | 14:10 | 49.962
2024-03-04 | 14:10 | 49.964
2024-03-04 | 14:10 | 49.967
2024-03-04 | 14:10 | 49.972
2024-03-04 | 14:10 | 49.974
2024-03-04 | 14:10 | 49.975
2024-03-04 | 14:10 | 49.973
2024-03-04 | 14:10 | 49.973
2024-03-04 | 14:10 | 49.971
2024-03-04 | 14:10 | 49.972
2024-03-04 | 14:10 | 49.974
2024-03-04 | 14:10 | 49.974
2024-03-04 | 14:10 | 49.973
2024-03-04 | 14:10 | 49.974
2024-03-04 | 14:10 | 49.97
2024-03-04 | 14:10 | 49.968
2024-03-04 | 14:10 | 49.962
2024-03-04 | 14:10 | 49.961
2024-03-04 | 14:10 | 49.96
2024-03-04 | 14:10 | 49.959
2024-03-04 | 14:10 | 49.962
2024-03-04 | 14:10 | 49.961
2024-03-04 | 14:10 | 49.961
2024-03-04 | 14:10 | 49.961
2024-03-04 | 14:10 | 49.963
2024-03-04 | 14:10 | 49.966
2024-03-04 | 14:10 | 49.973
2024-03-04 | 14:10 | 49.979
2024-03-04 | 14:10 | 49.982
2024-03-04 | 14:10 | 49.981
2024-03-04 | 14:10 | 49.981
2024-03-04 | 14:10 | 49.982
2024-03-04 | 14:10 | 49.98
2024-03-04 | 14:10 | 49.978
2024-03-04 | 14:10 | 49.974
2024-03-04 | 14:10 | 49.976
2024-03-04 | 14:10 | 49.976
2024-03-04 | 14:10 | 49.978
2024-03-04 | 14:10 | 49.982
2024-03-04 | 14:11 | 49.984
2024-03-04 | 14:11 | 49.985
2024-03-04 | 14:11 | 49.987
2024-03-04 | 14:11 | 49.993
2024-03-04 | 14:11 | 49.996
2024-03-04 | 14:11 | 50.002
2024-03-04 | 14:11 | 50.008
2024-03-04 | 14:11 | 50.013
2024-03-04 | 14:11 | 50.018
2024-03-04 | 14:11 | 50.022
2024-03-04 | 14:11 | 50.024
2024-03-04 | 14:11 | 50.027
2024-03-04 | 14:11 | 50.029
2024-03-04 | 14:11 | 50.026
2024-03-04 | 14:11 | 50.023
2024-03-04 | 14:11 | 50.024
2024-03-04 | 14:11 | 50.023
2024-03-04 | 14:11 | 50.022
2024-03-04 | 14:11 | 50.02
2024-03-04 | 14:11 | 50.022
2024-03-04 | 14:11 | 50.026
2024-03-04 | 14:11 | 50.028
2024-03-04 | 14:11 | 50.027
2024-03-04 | 14:11 | 50.028
2024-03-04 | 14:11 | 50.029
2024-03-04 | 14:11 | 50.03
2024-03-04 | 14:11 | 50.031
2024-03-04 | 14:11 | 50.032
2024-03-04 | 14:11 | 50.035
2024-03-04 | 14:11 | 50.033
2024-03-04 | 14:11 | 50.032
2024-03-04 | 14:11 | 50.029
2024-03-04 | 14:11 | 50.027
2024-03-04 | 14:11 | 50.028
2024-03-04 | 14:11 | 50.028
2024-03-04 | 14:11 | 50.03
2024-03-04 | 14:11 | 50.033
2024-03-04 | 14:11 | 50.038
2024-03-04 | 14:11 | 50.04
2024-03-04 | 14:11 | 50.038
2024-03-04 | 14:11 | 50.032
2024-03-04 | 14:11 | 50.025
2024-03-04 | 14:11 | 50.022
2024-03-04 | 14:11 | 50.021
2024-03-04 | 14:11 | 50.023
2024-03-04 | 14:11 | 50.022
2024-03-04 | 14:11 | 50.023
2024-03-04 | 14:11 | 50.02
2024-03-04 | 14:11 | 50.018
2024-03-04 | 14:11 | 50.016
2024-03-04 | 14:11 | 50.016
2024-03-04 | 14:11 | 50.015
2024-03-04 | 14:11 | 50.016
2024-03-04 | 14:11 | 50.018
2024-03-04 | 14:11 | 50.021
2024-03-04 | 14:11 | 50.027
2024-03-04 | 14:11 | 50.029
2024-03-04 | 14:11 | 50.029
2024-03-04 | 14:11 | 50.03
2024-03-04 | 14:11 | 50.032
2024-03-04 | 14:11 | 50.037
2024-03-04 | 14:12 | 50.037
2024-03-04 | 14:12 | 50.032
2024-03-04 | 14:12 | 50.027
2024-03-04 | 14:12 | 50.022
2024-03-04 | 14:12 | 50.019
2024-03-04 | 14:12 | 50.018
2024-03-04 | 14:12 | 50.017
2024-03-04 | 14:12 | 50.018
2024-03-04 | 14:12 | 50.015
2024-03-04 | 14:12 | 50.012
2024-03-04 | 14:12 | 50.01
2024-03-04 | 14:12 | 50.01
2024-03-04 | 14:12 | 50.014
2024-03-04 | 14:12 | 50.015
2024-03-04 | 14:12 | 50.015
2024-03-04 | 14:12 | 50.015
2024-03-04 | 14:12 | 50.016
2024-03-04 | 14:12 | 50.021
2024-03-04 | 14:12 | 50.025
2024-03-04 | 14:12 | 50.031
2024-03-04 | 14:12 | 50.032
2024-03-04 | 14:12 | 50.034
2024-03-04 | 14:12 | 50.036
2024-03-04 | 14:12 | 50.038
2024-03-04 | 14:12 | 50.037
2024-03-04 | 14:12 | 50.036
2024-03-04 | 14:12 | 50.038
2024-03-04 | 14:12 | 50.04
2024-03-04 | 14:12 | 50.038

## 20240306-1
In GMT
Date | Time | Freq
2024-03-06 | 7:45 | 50.044 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-06 | 7:45 | 50.043 | 222 | BRITNED | 676.211
2024-03-06 | 7:45 | 50.039 | 268 | WBURB-2 | 428.156
2024-03-06 | 7:45 | 50.034 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-06 | 7:45 | 50.033 |  | Viking Link | -648.9
2024-03-06 | 7:45 | 50.032 |  | Viking Link | 1398.96
2024-03-06 | 7:45 | 50.03 | 209 | DRAXX-3 | 626.95
2024-03-06 | 7:45 | 50.027 | 154 | CDCL-1 | 391.57
2024-03-06 | 7:45 | 50.023 | 268 | ROCK-1 | 468.495
2024-03-06 | 7:45 | 50.021 | 148 | IFA Bipole1 | 945.473
2024-03-06 | 7:45 | 50.018 | 132 | IFA Bipole1 | 999.1
2024-03-06 | 7:45 | 50.015 | 141 | IFA Bipole2 | 1000
2024-03-06 | 7:45 | 50.013 | 135 | IFA Bipole1 | 996.75
2024-03-06 | 7:45 | 50.01 |  | Viking Link | -780.3
2024-03-06 | 7:45 | 50.009
2024-03-06 | 7:45 | 50.008
2024-03-06 | 7:45 | 50.008
2024-03-06 | 7:45 | 50.011
2024-03-06 | 7:45 | 50.012
2024-03-06 | 7:45 | 50.014 | 130 | HEYM12 | 271.908
2024-03-06 | 7:45 | 50.016 | 228 | HUMR-1 | 303.75
2024-03-06 | 7:45 | 50.019
2024-03-06 | 7:45 | 50.023
2024-03-06 | 7:45 | 50.03
2024-03-06 | 7:45 | 50.033
2024-03-06 | 7:45 | 50.033
2024-03-06 | 7:45 | 50.035
2024-03-06 | 7:45 | 50.035
2024-03-06 | 7:45 | 50.033
2024-03-06 | 7:45 | 50.029
2024-03-06 | 7:45 | 50.024 | 211 | CDCL-1 | 291.5
2024-03-06 | 7:46 | 50.021 | 199 | STAY-2 | 413.125
2024-03-06 | 7:46 | 50.018 | 173 | CDCL-1 | 397.375
2024-03-06 | 7:46 | 50.017 | 248 | SEAB-2 | 361.25
2024-03-06 | 7:46 | 50.016 | 255 | FRANCE | 995.65
2024-03-06 | 7:46 | 50.015 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-06 | 7:46 | 50.011
2024-03-06 | 7:46 | 50.012
2024-03-06 | 7:46 | 50.011
2024-03-06 | 7:46 | 50.014
2024-03-06 | 7:46 | 50.016
2024-03-06 | 7:46 | 50.017
2024-03-06 | 7:46 | 50.022
2024-03-06 | 7:46 | 50.024
2024-03-06 | 7:46 | 50.027
2024-03-06 | 7:46 | 50.029
2024-03-06 | 7:46 | 50.032
2024-03-06 | 7:46 | 50.037
2024-03-06 | 7:46 | 50.039
2024-03-06 | 7:46 | 50.039
2024-03-06 | 7:46 | 50.039
2024-03-06 | 7:46 | 50.041
2024-03-06 | 7:46 | 50.039
2024-03-06 | 7:46 | 50.039
2024-03-06 | 7:46 | 50.04
2024-03-06 | 7:46 | 50.043
2024-03-06 | 7:46 | 50.043
2024-03-06 | 7:46 | 50.042
2024-03-06 | 7:46 | 50.041
2024-03-06 | 7:46 | 50.039
2024-03-06 | 7:46 | 50.037
2024-03-06 | 7:46 | 50.034
2024-03-06 | 7:46 | 50.031
2024-03-06 | 7:46 | 50.029
2024-03-06 | 7:46 | 50.026
2024-03-06 | 7:46 | 50.026
2024-03-06 | 7:46 | 50.028
2024-03-06 | 7:46 | 50.031
2024-03-06 | 7:46 | 50.033
2024-03-06 | 7:46 | 50.036
2024-03-06 | 7:46 | 50.036
2024-03-06 | 7:46 | 50.037
2024-03-06 | 7:46 | 50.037
2024-03-06 | 7:46 | 50.036
2024-03-06 | 7:46 | 50.036
2024-03-06 | 7:46 | 50.039
2024-03-06 | 7:46 | 50.04
2024-03-06 | 7:46 | 50.039
2024-03-06 | 7:46 | 50.016
2024-03-06 | 7:46 | 49.997
2024-03-06 | 7:46 | 49.974
2024-03-06 | 7:46 | 49.948
2024-03-06 | 7:46 | 49.926
2024-03-06 | 7:46 | 49.909
2024-03-06 | 7:46 | 49.897
2024-03-06 | 7:46 | 49.887
2024-03-06 | 7:46 | 49.881
2024-03-06 | 7:46 | 49.878
2024-03-06 | 7:46 | 49.878
2024-03-06 | 7:46 | 49.879
2024-03-06 | 7:46 | 49.878
2024-03-06 | 7:47 | 49.878
2024-03-06 | 7:47 | 49.879
2024-03-06 | 7:47 | 49.881
2024-03-06 | 7:47 | 49.883
2024-03-06 | 7:47 | 49.883
2024-03-06 | 7:47 | 49.882
2024-03-06 | 7:47 | 49.882
2024-03-06 | 7:47 | 49.883
2024-03-06 | 7:47 | 49.882
2024-03-06 | 7:47 | 49.881
2024-03-06 | 7:47 | 49.88
2024-03-06 | 7:47 | 49.879
2024-03-06 | 7:47 | 49.878
2024-03-06 | 7:47 | 49.878
2024-03-06 | 7:47 | 49.877
2024-03-06 | 7:47 | 49.881
2024-03-06 | 7:47 | 49.881
2024-03-06 | 7:47 | 49.884
2024-03-06 | 7:47 | 49.884
2024-03-06 | 7:47 | 49.885
2024-03-06 | 7:47 | 49.886
2024-03-06 | 7:47 | 49.889
2024-03-06 | 7:47 | 49.893
2024-03-06 | 7:47 | 49.898
2024-03-06 | 7:47 | 49.9
2024-03-06 | 7:47 | 49.9
2024-03-06 | 7:47 | 49.901
2024-03-06 | 7:47 | 49.898
2024-03-06 | 7:47 | 49.898
2024-03-06 | 7:47 | 49.899
2024-03-06 | 7:47 | 49.896
2024-03-06 | 7:47 | 49.894
2024-03-06 | 7:47 | 49.892
2024-03-06 | 7:47 | 49.89
2024-03-06 | 7:47 | 49.888
2024-03-06 | 7:47 | 49.885
2024-03-06 | 7:47 | 49.885
2024-03-06 | 7:47 | 49.883
2024-03-06 | 7:47 | 49.882
2024-03-06 | 7:47 | 49.88
2024-03-06 | 7:47 | 49.879
2024-03-06 | 7:47 | 49.88
2024-03-06 | 7:47 | 49.88
2024-03-06 | 7:47 | 49.884
2024-03-06 | 7:47 | 49.886
2024-03-06 | 7:47 | 49.889
2024-03-06 | 7:47 | 49.889
2024-03-06 | 7:47 | 49.891
2024-03-06 | 7:47 | 49.892
2024-03-06 | 7:47 | 49.896
2024-03-06 | 7:47 | 49.898
2024-03-06 | 7:47 | 49.899
2024-03-06 | 7:47 | 49.899
2024-03-06 | 7:47 | 49.9
2024-03-06 | 7:47 | 49.901
2024-03-06 | 7:47 | 49.902
2024-03-06 | 7:47 | 49.904
2024-03-06 | 7:47 | 49.908
2024-03-06 | 7:47 | 49.91
2024-03-06 | 7:48 | 49.908
2024-03-06 | 7:48 | 49.908
2024-03-06 | 7:48 | 49.909
2024-03-06 | 7:48 | 49.909
2024-03-06 | 7:48 | 49.912
2024-03-06 | 7:48 | 49.913
2024-03-06 | 7:48 | 49.917
2024-03-06 | 7:48 | 49.918
2024-03-06 | 7:48 | 49.918
2024-03-06 | 7:48 | 49.918
2024-03-06 | 7:48 | 49.919
2024-03-06 | 7:48 | 49.919
2024-03-06 | 7:48 | 49.914
2024-03-06 | 7:48 | 49.912
2024-03-06 | 7:48 | 49.91
2024-03-06 | 7:48 | 49.906
2024-03-06 | 7:48 | 49.899
2024-03-06 | 7:48 | 49.896
2024-03-06 | 7:48 | 49.893
2024-03-06 | 7:48 | 49.894
2024-03-06 | 7:48 | 49.894
2024-03-06 | 7:48 | 49.894
2024-03-06 | 7:48 | 49.896
2024-03-06 | 7:48 | 49.899
2024-03-06 | 7:48 | 49.902
2024-03-06 | 7:48 | 49.903
2024-03-06 | 7:48 | 49.902
2024-03-06 | 7:48 | 49.9
2024-03-06 | 7:48 | 49.899
2024-03-06 | 7:48 | 49.897
2024-03-06 | 7:48 | 49.897
2024-03-06 | 7:48 | 49.895
2024-03-06 | 7:48 | 49.893
2024-03-06 | 7:48 | 49.896
2024-03-06 | 7:48 | 49.895
2024-03-06 | 7:48 | 49.894
2024-03-06 | 7:48 | 49.892
2024-03-06 | 7:48 | 49.892
2024-03-06 | 7:48 | 49.894
2024-03-06 | 7:48 | 49.894
2024-03-06 | 7:48 | 49.894
2024-03-06 | 7:48 | 49.894
2024-03-06 | 7:48 | 49.895
2024-03-06 | 7:48 | 49.898
2024-03-06 | 7:48 | 49.902
2024-03-06 | 7:48 | 49.901
2024-03-06 | 7:48 | 49.902
2024-03-06 | 7:48 | 49.901
2024-03-06 | 7:48 | 49.896
2024-03-06 | 7:48 | 49.893
2024-03-06 | 7:48 | 49.89
2024-03-06 | 7:48 | 49.886
2024-03-06 | 7:48 | 49.886
2024-03-06 | 7:48 | 49.885
2024-03-06 | 7:48 | 49.883
2024-03-06 | 7:48 | 49.88
2024-03-06 | 7:48 | 49.879
2024-03-06 | 7:48 | 49.881
2024-03-06 | 7:48 | 49.879
2024-03-06 | 7:48 | 49.881
2024-03-06 | 7:48 | 49.88
2024-03-06 | 7:49 | 49.879
2024-03-06 | 7:49 | 49.88
2024-03-06 | 7:49 | 49.882
2024-03-06 | 7:49 | 49.881
2024-03-06 | 7:49 | 49.88
2024-03-06 | 7:49 | 49.88
2024-03-06 | 7:49 | 49.881
2024-03-06 | 7:49 | 49.885
2024-03-06 | 7:49 | 49.885
2024-03-06 | 7:49 | 49.885
2024-03-06 | 7:49 | 49.884
2024-03-06 | 7:49 | 49.883
2024-03-06 | 7:49 | 49.885
2024-03-06 | 7:49 | 49.885
2024-03-06 | 7:49 | 49.884
2024-03-06 | 7:49 | 49.884
2024-03-06 | 7:49 | 49.882
2024-03-06 | 7:49 | 49.882
2024-03-06 | 7:49 | 49.881
2024-03-06 | 7:49 | 49.879
2024-03-06 | 7:49 | 49.88
2024-03-06 | 7:49 | 49.881
2024-03-06 | 7:49 | 49.881
2024-03-06 | 7:49 | 49.88
2024-03-06 | 7:49 | 49.882
2024-03-06 | 7:49 | 49.884
2024-03-06 | 7:49 | 49.883
2024-03-06 | 7:49 | 49.884
2024-03-06 | 7:49 | 49.883
2024-03-06 | 7:49 | 49.881
2024-03-06 | 7:49 | 49.878
2024-03-06 | 7:49 | 49.877
2024-03-06 | 7:49 | 49.876
2024-03-06 | 7:49 | 49.876
2024-03-06 | 7:49 | 49.874
2024-03-06 | 7:49 | 49.872
2024-03-06 | 7:49 | 49.872
2024-03-06 | 7:49 | 49.87
2024-03-06 | 7:49 | 49.866
2024-03-06 | 7:49 | 49.865
2024-03-06 | 7:49 | 49.863
2024-03-06 | 7:49 | 49.863
2024-03-06 | 7:49 | 49.863
2024-03-06 | 7:49 | 49.863
2024-03-06 | 7:49 | 49.865
2024-03-06 | 7:49 | 49.866
2024-03-06 | 7:49 | 49.865
2024-03-06 | 7:49 | 49.864
2024-03-06 | 7:49 | 49.864
2024-03-06 | 7:49 | 49.864
2024-03-06 | 7:49 | 49.863
2024-03-06 | 7:49 | 49.863
2024-03-06 | 7:49 | 49.862
2024-03-06 | 7:49 | 49.863
2024-03-06 | 7:49 | 49.864
2024-03-06 | 7:49 | 49.865
2024-03-06 | 7:49 | 49.861
2024-03-06 | 7:49 | 49.857
2024-03-06 | 7:49 | 49.856
2024-03-06 | 7:50 | 49.855
2024-03-06 | 7:50 | 49.855
2024-03-06 | 7:50 | 49.855
2024-03-06 | 7:50 | 49.855
2024-03-06 | 7:50 | 49.857
2024-03-06 | 7:50 | 49.859
2024-03-06 | 7:50 | 49.862
2024-03-06 | 7:50 | 49.865
2024-03-06 | 7:50 | 49.87
2024-03-06 | 7:50 | 49.87
2024-03-06 | 7:50 | 49.872
2024-03-06 | 7:50 | 49.871
2024-03-06 | 7:50 | 49.872
2024-03-06 | 7:50 | 49.869
2024-03-06 | 7:50 | 49.865
2024-03-06 | 7:50 | 49.863
2024-03-06 | 7:50 | 49.86
2024-03-06 | 7:50 | 49.859
2024-03-06 | 7:50 | 49.861
2024-03-06 | 7:50 | 49.86
2024-03-06 | 7:50 | 49.858
2024-03-06 | 7:50 | 49.856
2024-03-06 | 7:50 | 49.856
2024-03-06 | 7:50 | 49.854
2024-03-06 | 7:50 | 49.854
2024-03-06 | 7:50 | 49.853
2024-03-06 | 7:50 | 49.853
2024-03-06 | 7:50 | 49.855
2024-03-06 | 7:50 | 49.856
2024-03-06 | 7:50 | 49.86
2024-03-06 | 7:50 | 49.861
2024-03-06 | 7:50 | 49.86
2024-03-06 | 7:50 | 49.858
2024-03-06 | 7:50 | 49.857
2024-03-06 | 7:50 | 49.856
2024-03-06 | 7:50 | 49.855
2024-03-06 | 7:50 | 49.856
2024-03-06 | 7:50 | 49.856
2024-03-06 | 7:50 | 49.856
2024-03-06 | 7:50 | 49.857
2024-03-06 | 7:50 | 49.858
2024-03-06 | 7:50 | 49.859
2024-03-06 | 7:50 | 49.859
2024-03-06 | 7:50 | 49.861
2024-03-06 | 7:50 | 49.862
2024-03-06 | 7:50 | 49.863
2024-03-06 | 7:50 | 49.862
2024-03-06 | 7:50 | 49.86
2024-03-06 | 7:50 | 49.86
2024-03-06 | 7:50 | 49.862
2024-03-06 | 7:50 | 49.863
2024-03-06 | 7:50 | 49.863
2024-03-06 | 7:50 | 49.864
2024-03-06 | 7:50 | 49.862
2024-03-06 | 7:50 | 49.862
2024-03-06 | 7:50 | 49.86
2024-03-06 | 7:50 | 49.859
2024-03-06 | 7:50 | 49.859
2024-03-06 | 7:50 | 49.86
2024-03-06 | 7:50 | 49.859
2024-03-06 | 7:50 | 49.857
2024-03-06 | 7:51 | 49.853
2024-03-06 | 7:51 | 49.852
2024-03-06 | 7:51 | 49.851
2024-03-06 | 7:51 | 49.849
2024-03-06 | 7:51 | 49.846
2024-03-06 | 7:51 | 49.846
2024-03-06 | 7:51 | 49.844
2024-03-06 | 7:51 | 49.844
2024-03-06 | 7:51 | 49.845
2024-03-06 | 7:51 | 49.843
2024-03-06 | 7:51 | 49.843
2024-03-06 | 7:51 | 49.843
2024-03-06 | 7:51 | 49.842
2024-03-06 | 7:51 | 49.842
2024-03-06 | 7:51 | 49.84
2024-03-06 | 7:51 | 49.839
2024-03-06 | 7:51 | 49.836
2024-03-06 | 7:51 | 49.835
2024-03-06 | 7:51 | 49.834
2024-03-06 | 7:51 | 49.835
2024-03-06 | 7:51 | 49.837
2024-03-06 | 7:51 | 49.839
2024-03-06 | 7:51 | 49.84
2024-03-06 | 7:51 | 49.84
2024-03-06 | 7:51 | 49.838
2024-03-06 | 7:51 | 49.835
2024-03-06 | 7:51 | 49.832
2024-03-06 | 7:51 | 49.832
2024-03-06 | 7:51 | 49.833
2024-03-06 | 7:51 | 49.833
2024-03-06 | 7:51 | 49.834
2024-03-06 | 7:51 | 49.835
2024-03-06 | 7:51 | 49.836
2024-03-06 | 7:51 | 49.839
2024-03-06 | 7:51 | 49.84
2024-03-06 | 7:51 | 49.84
2024-03-06 | 7:51 | 49.839
2024-03-06 | 7:51 | 49.838
2024-03-06 | 7:51 | 49.836
2024-03-06 | 7:51 | 49.834
2024-03-06 | 7:51 | 49.832
2024-03-06 | 7:51 | 49.833
2024-03-06 | 7:51 | 49.832
2024-03-06 | 7:51 | 49.831
2024-03-06 | 7:51 | 49.831
2024-03-06 | 7:51 | 49.829
2024-03-06 | 7:51 | 49.832
2024-03-06 | 7:51 | 49.834
2024-03-06 | 7:51 | 49.835
2024-03-06 | 7:51 | 49.835
2024-03-06 | 7:51 | 49.837
2024-03-06 | 7:51 | 49.837
2024-03-06 | 7:51 | 49.838
2024-03-06 | 7:51 | 49.837
2024-03-06 | 7:51 | 49.836
2024-03-06 | 7:51 | 49.834
2024-03-06 | 7:51 | 49.833
2024-03-06 | 7:51 | 49.832
2024-03-06 | 7:51 | 49.828
2024-03-06 | 7:52 | 49.827
2024-03-06 | 7:52 | 49.827
2024-03-06 | 7:52 | 49.829
2024-03-06 | 7:52 | 49.83
2024-03-06 | 7:52 | 49.83
2024-03-06 | 7:52 | 49.831
2024-03-06 | 7:52 | 49.831
2024-03-06 | 7:52 | 49.832
2024-03-06 | 7:52 | 49.835
2024-03-06 | 7:52 | 49.838
2024-03-06 | 7:52 | 49.841
2024-03-06 | 7:52 | 49.847
2024-03-06 | 7:52 | 49.851
2024-03-06 | 7:52 | 49.855
2024-03-06 | 7:52 | 49.859
2024-03-06 | 7:52 | 49.861
2024-03-06 | 7:52 | 49.865
2024-03-06 | 7:52 | 49.867
2024-03-06 | 7:52 | 49.872
2024-03-06 | 7:52 | 49.874
2024-03-06 | 7:52 | 49.874
2024-03-06 | 7:52 | 49.874
2024-03-06 | 7:52 | 49.873
2024-03-06 | 7:52 | 49.874
2024-03-06 | 7:52 | 49.873
2024-03-06 | 7:52 | 49.871
2024-03-06 | 7:52 | 49.869
2024-03-06 | 7:52 | 49.868
2024-03-06 | 7:52 | 49.867
2024-03-06 | 7:52 | 49.866
2024-03-06 | 7:52 | 49.867
2024-03-06 | 7:52 | 49.866
2024-03-06 | 7:52 | 49.867
2024-03-06 | 7:52 | 49.869
2024-03-06 | 7:52 | 49.869
2024-03-06 | 7:52 | 49.871
2024-03-06 | 7:52 | 49.872
2024-03-06 | 7:52 | 49.874
2024-03-06 | 7:52 | 49.874
2024-03-06 | 7:52 | 49.873
2024-03-06 | 7:52 | 49.871
2024-03-06 | 7:52 | 49.869
2024-03-06 | 7:52 | 49.868
2024-03-06 | 7:52 | 49.869
2024-03-06 | 7:52 | 49.869
2024-03-06 | 7:52 | 49.867
2024-03-06 | 7:52 | 49.866
2024-03-06 | 7:52 | 49.865
2024-03-06 | 7:52 | 49.864
2024-03-06 | 7:52 | 49.861
2024-03-06 | 7:52 | 49.861
2024-03-06 | 7:52 | 49.861
2024-03-06 | 7:52 | 49.863
2024-03-06 | 7:52 | 49.866
2024-03-06 | 7:52 | 49.866
2024-03-06 | 7:52 | 49.866
2024-03-06 | 7:52 | 49.865
2024-03-06 | 7:52 | 49.864
2024-03-06 | 7:52 | 49.865
2024-03-06 | 7:52 | 49.866
2024-03-06 | 7:52 | 49.868
2024-03-06 | 7:53 | 49.871
2024-03-06 | 7:53 | 49.874
2024-03-06 | 7:53 | 49.876
2024-03-06 | 7:53 | 49.875
2024-03-06 | 7:53 | 49.875
2024-03-06 | 7:53 | 49.874
2024-03-06 | 7:53 | 49.872
2024-03-06 | 7:53 | 49.873
2024-03-06 | 7:53 | 49.873
2024-03-06 | 7:53 | 49.874
2024-03-06 | 7:53 | 49.874
2024-03-06 | 7:53 | 49.874
2024-03-06 | 7:53 | 49.874
2024-03-06 | 7:53 | 49.875
2024-03-06 | 7:53 | 49.875
2024-03-06 | 7:53 | 49.874
2024-03-06 | 7:53 | 49.872
2024-03-06 | 7:53 | 49.873
2024-03-06 | 7:53 | 49.872
2024-03-06 | 7:53 | 49.872
2024-03-06 | 7:53 | 49.873
2024-03-06 | 7:53 | 49.873
2024-03-06 | 7:53 | 49.874
2024-03-06 | 7:53 | 49.873
2024-03-06 | 7:53 | 49.871
2024-03-06 | 7:53 | 49.87
2024-03-06 | 7:53 | 49.872
2024-03-06 | 7:53 | 49.87
2024-03-06 | 7:53 | 49.87
2024-03-06 | 7:53 | 49.869
2024-03-06 | 7:53 | 49.869
2024-03-06 | 7:53 | 49.867
2024-03-06 | 7:53 | 49.867
2024-03-06 | 7:53 | 49.866
2024-03-06 | 7:53 | 49.867
2024-03-06 | 7:53 | 49.865
2024-03-06 | 7:53 | 49.864
2024-03-06 | 7:53 | 49.864
2024-03-06 | 7:53 | 49.863
2024-03-06 | 7:53 | 49.862
2024-03-06 | 7:53 | 49.862
2024-03-06 | 7:53 | 49.862
2024-03-06 | 7:53 | 49.862
2024-03-06 | 7:53 | 49.863
2024-03-06 | 7:53 | 49.862
2024-03-06 | 7:53 | 49.862
2024-03-06 | 7:53 | 49.866
2024-03-06 | 7:53 | 49.867
2024-03-06 | 7:53 | 49.866
2024-03-06 | 7:53 | 49.865
2024-03-06 | 7:53 | 49.863
2024-03-06 | 7:53 | 49.862
2024-03-06 | 7:53 | 49.861
2024-03-06 | 7:53 | 49.861
2024-03-06 | 7:53 | 49.857
2024-03-06 | 7:53 | 49.855
2024-03-06 | 7:53 | 49.854
2024-03-06 | 7:53 | 49.852
2024-03-06 | 7:53 | 49.852
2024-03-06 | 7:54 | 49.851
2024-03-06 | 7:54 | 49.851
2024-03-06 | 7:54 | 49.85
2024-03-06 | 7:54 | 49.849
2024-03-06 | 7:54 | 49.849
2024-03-06 | 7:54 | 49.85
2024-03-06 | 7:54 | 49.852
2024-03-06 | 7:54 | 49.852
2024-03-06 | 7:54 | 49.854
2024-03-06 | 7:54 | 49.854
2024-03-06 | 7:54 | 49.853
2024-03-06 | 7:54 | 49.852
2024-03-06 | 7:54 | 49.85
2024-03-06 | 7:54 | 49.848
2024-03-06 | 7:54 | 49.847
2024-03-06 | 7:54 | 49.846
2024-03-06 | 7:54 | 49.844
2024-03-06 | 7:54 | 49.841
2024-03-06 | 7:54 | 49.841
2024-03-06 | 7:54 | 49.84
2024-03-06 | 7:54 | 49.838
2024-03-06 | 7:54 | 49.836
2024-03-06 | 7:54 | 49.837
2024-03-06 | 7:54 | 49.84
2024-03-06 | 7:54 | 49.841
2024-03-06 | 7:54 | 49.839
2024-03-06 | 7:54 | 49.839
2024-03-06 | 7:54 | 49.838
2024-03-06 | 7:54 | 49.837
2024-03-06 | 7:54 | 49.837
2024-03-06 | 7:54 | 49.839
2024-03-06 | 7:54 | 49.836
2024-03-06 | 7:54 | 49.836
2024-03-06 | 7:54 | 49.837
2024-03-06 | 7:54 | 49.837
2024-03-06 | 7:54 | 49.838
2024-03-06 | 7:54 | 49.837
2024-03-06 | 7:54 | 49.84
2024-03-06 | 7:54 | 49.839
2024-03-06 | 7:54 | 49.837
2024-03-06 | 7:54 | 49.836
2024-03-06 | 7:54 | 49.835
2024-03-06 | 7:54 | 49.836
2024-03-06 | 7:54 | 49.836
2024-03-06 | 7:54 | 49.838
2024-03-06 | 7:54 | 49.838
2024-03-06 | 7:54 | 49.838
2024-03-06 | 7:54 | 49.837
2024-03-06 | 7:54 | 49.837
2024-03-06 | 7:54 | 49.836
2024-03-06 | 7:54 | 49.836
2024-03-06 | 7:54 | 49.833
2024-03-06 | 7:54 | 49.832
2024-03-06 | 7:54 | 49.829
2024-03-06 | 7:54 | 49.828
2024-03-06 | 7:54 | 49.829
2024-03-06 | 7:54 | 49.83
2024-03-06 | 7:54 | 49.829
2024-03-06 | 7:54 | 49.828
2024-03-06 | 7:54 | 49.827
2024-03-06 | 7:54 | 49.828
2024-03-06 | 7:55 | 49.83
2024-03-06 | 7:55 | 49.832
2024-03-06 | 7:55 | 49.831
2024-03-06 | 7:55 | 49.833
2024-03-06 | 7:55 | 49.832
2024-03-06 | 7:55 | 49.836
2024-03-06 | 7:55 | 49.837
2024-03-06 | 7:55 | 49.837
2024-03-06 | 7:55 | 49.837
2024-03-06 | 7:55 | 49.838
2024-03-06 | 7:55 | 49.838
2024-03-06 | 7:55 | 49.837
2024-03-06 | 7:55 | 49.838
2024-03-06 | 7:55 | 49.839
2024-03-06 | 7:55 | 49.84
2024-03-06 | 7:55 | 49.843
2024-03-06 | 7:55 | 49.846
2024-03-06 | 7:55 | 49.851
2024-03-06 | 7:55 | 49.852
2024-03-06 | 7:55 | 49.853
2024-03-06 | 7:55 | 49.853
2024-03-06 | 7:55 | 49.852
2024-03-06 | 7:55 | 49.85
2024-03-06 | 7:55 | 49.847
2024-03-06 | 7:55 | 49.846
2024-03-06 | 7:55 | 49.844
2024-03-06 | 7:55 | 49.843
2024-03-06 | 7:55 | 49.843
2024-03-06 | 7:55 | 49.843
2024-03-06 | 7:55 | 49.843
2024-03-06 | 7:55 | 49.841
2024-03-06 | 7:55 | 49.838
2024-03-06 | 7:55 | 49.837
2024-03-06 | 7:55 | 49.835
2024-03-06 | 7:55 | 49.833
2024-03-06 | 7:55 | 49.832
2024-03-06 | 7:55 | 49.831
2024-03-06 | 7:55 | 49.831
2024-03-06 | 7:55 | 49.826
2024-03-06 | 7:55 | 49.827
2024-03-06 | 7:55 | 49.827
2024-03-06 | 7:55 | 49.829
2024-03-06 | 7:55 | 49.83
2024-03-06 | 7:55 | 49.829
2024-03-06 | 7:55 | 49.829
2024-03-06 | 7:55 | 49.828
2024-03-06 | 7:55 | 49.828
2024-03-06 | 7:55 | 49.827
2024-03-06 | 7:55 | 49.826
2024-03-06 | 7:55 | 49.826
2024-03-06 | 7:55 | 49.824
2024-03-06 | 7:55 | 49.821
2024-03-06 | 7:55 | 49.821
2024-03-06 | 7:55 | 49.822
2024-03-06 | 7:55 | 49.825
2024-03-06 | 7:55 | 49.827
2024-03-06 | 7:55 | 49.828
2024-03-06 | 7:55 | 49.828
2024-03-06 | 7:55 | 49.829
2024-03-06 | 7:56 | 49.831
2024-03-06 | 7:56 | 49.834
2024-03-06 | 7:56 | 49.836
2024-03-06 | 7:56 | 49.838
2024-03-06 | 7:56 | 49.839
2024-03-06 | 7:56 | 49.839
2024-03-06 | 7:56 | 49.84
2024-03-06 | 7:56 | 49.843
2024-03-06 | 7:56 | 49.845
2024-03-06 | 7:56 | 49.846
2024-03-06 | 7:56 | 49.848
2024-03-06 | 7:56 | 49.848
2024-03-06 | 7:56 | 49.85
2024-03-06 | 7:56 | 49.852
2024-03-06 | 7:56 | 49.855
2024-03-06 | 7:56 | 49.858
2024-03-06 | 7:56 | 49.86
2024-03-06 | 7:56 | 49.861
2024-03-06 | 7:56 | 49.864
2024-03-06 | 7:56 | 49.865
2024-03-06 | 7:56 | 49.867
2024-03-06 | 7:56 | 49.867
2024-03-06 | 7:56 | 49.867
2024-03-06 | 7:56 | 49.865
2024-03-06 | 7:56 | 49.866
2024-03-06 | 7:56 | 49.865
2024-03-06 | 7:56 | 49.864
2024-03-06 | 7:56 | 49.862
2024-03-06 | 7:56 | 49.862
2024-03-06 | 7:56 | 49.861
2024-03-06 | 7:56 | 49.86
2024-03-06 | 7:56 | 49.856
2024-03-06 | 7:56 | 49.853
2024-03-06 | 7:56 | 49.852
2024-03-06 | 7:56 | 49.853
2024-03-06 | 7:56 | 49.855
2024-03-06 | 7:56 | 49.854
2024-03-06 | 7:56 | 49.855
2024-03-06 | 7:56 | 49.853
2024-03-06 | 7:56 | 49.851
2024-03-06 | 7:56 | 49.849
2024-03-06 | 7:56 | 49.848
2024-03-06 | 7:56 | 49.847
2024-03-06 | 7:56 | 49.847
2024-03-06 | 7:56 | 49.847
2024-03-06 | 7:56 | 49.847
2024-03-06 | 7:56 | 49.848
2024-03-06 | 7:56 | 49.85
2024-03-06 | 7:56 | 49.849
2024-03-06 | 7:56 | 49.851
2024-03-06 | 7:56 | 49.851
2024-03-06 | 7:56 | 49.852
2024-03-06 | 7:56 | 49.854
2024-03-06 | 7:56 | 49.853
2024-03-06 | 7:56 | 49.856
2024-03-06 | 7:56 | 49.857
2024-03-06 | 7:56 | 49.859
2024-03-06 | 7:56 | 49.861
2024-03-06 | 7:56 | 49.862
2024-03-06 | 7:56 | 49.861
2024-03-06 | 7:56 | 49.86
2024-03-06 | 7:57 | 49.861
2024-03-06 | 7:57 | 49.861
2024-03-06 | 7:57 | 49.859
2024-03-06 | 7:57 | 49.862
2024-03-06 | 7:57 | 49.866
2024-03-06 | 7:57 | 49.866
2024-03-06 | 7:57 | 49.867
2024-03-06 | 7:57 | 49.868
2024-03-06 | 7:57 | 49.868
2024-03-06 | 7:57 | 49.868
2024-03-06 | 7:57 | 49.867
2024-03-06 | 7:57 | 49.868
2024-03-06 | 7:57 | 49.868
2024-03-06 | 7:57 | 49.87
2024-03-06 | 7:57 | 49.869
2024-03-06 | 7:57 | 49.868
2024-03-06 | 7:57 | 49.868
2024-03-06 | 7:57 | 49.868
2024-03-06 | 7:57 | 49.869
2024-03-06 | 7:57 | 49.868
2024-03-06 | 7:57 | 49.868
2024-03-06 | 7:57 | 49.869
2024-03-06 | 7:57 | 49.87
2024-03-06 | 7:57 | 49.874
2024-03-06 | 7:57 | 49.877
2024-03-06 | 7:57 | 49.88
2024-03-06 | 7:57 | 49.882
2024-03-06 | 7:57 | 49.884
2024-03-06 | 7:57 | 49.887
2024-03-06 | 7:57 | 49.89
2024-03-06 | 7:57 | 49.89
2024-03-06 | 7:57 | 49.89
2024-03-06 | 7:57 | 49.891
2024-03-06 | 7:57 | 49.893
2024-03-06 | 7:57 | 49.893
2024-03-06 | 7:57 | 49.89
2024-03-06 | 7:57 | 49.89
2024-03-06 | 7:57 | 49.892
2024-03-06 | 7:57 | 49.893
2024-03-06 | 7:57 | 49.894
2024-03-06 | 7:57 | 49.895
2024-03-06 | 7:57 | 49.896
2024-03-06 | 7:57 | 49.899
2024-03-06 | 7:57 | 49.902
2024-03-06 | 7:57 | 49.904
2024-03-06 | 7:57 | 49.905
2024-03-06 | 7:57 | 49.906
2024-03-06 | 7:57 | 49.908
2024-03-06 | 7:57 | 49.909
2024-03-06 | 7:57 | 49.911
2024-03-06 | 7:57 | 49.911
2024-03-06 | 7:57 | 49.909
2024-03-06 | 7:57 | 49.905
2024-03-06 | 7:57 | 49.906
2024-03-06 | 7:57 | 49.904
2024-03-06 | 7:57 | 49.903
2024-03-06 | 7:57 | 49.901
2024-03-06 | 7:57 | 49.9
2024-03-06 | 7:57 | 49.901
2024-03-06 | 7:58 | 49.902
2024-03-06 | 7:58 | 49.903
2024-03-06 | 7:58 | 49.902
2024-03-06 | 7:58 | 49.9
2024-03-06 | 7:58 | 49.898
2024-03-06 | 7:58 | 49.898
2024-03-06 | 7:58 | 49.9
2024-03-06 | 7:58 | 49.901
2024-03-06 | 7:58 | 49.903
2024-03-06 | 7:58 | 49.902
2024-03-06 | 7:58 | 49.902
2024-03-06 | 7:58 | 49.901
2024-03-06 | 7:58 | 49.898
2024-03-06 | 7:58 | 49.897
2024-03-06 | 7:58 | 49.899
2024-03-06 | 7:58 | 49.899
2024-03-06 | 7:58 | 49.9
2024-03-06 | 7:58 | 49.902
2024-03-06 | 7:58 | 49.904
2024-03-06 | 7:58 | 49.905
2024-03-06 | 7:58 | 49.905
2024-03-06 | 7:58 | 49.904
2024-03-06 | 7:58 | 49.903
2024-03-06 | 7:58 | 49.902
2024-03-06 | 7:58 | 49.904
2024-03-06 | 7:58 | 49.904
2024-03-06 | 7:58 | 49.906
2024-03-06 | 7:58 | 49.909
2024-03-06 | 7:58 | 49.912
2024-03-06 | 7:58 | 49.913
2024-03-06 | 7:58 | 49.915
2024-03-06 | 7:58 | 49.916
2024-03-06 | 7:58 | 49.917
2024-03-06 | 7:58 | 49.918
2024-03-06 | 7:58 | 49.919
2024-03-06 | 7:58 | 49.923
2024-03-06 | 7:58 | 49.925
2024-03-06 | 7:58 | 49.926
2024-03-06 | 7:58 | 49.927
2024-03-06 | 7:58 | 49.925
2024-03-06 | 7:58 | 49.924
2024-03-06 | 7:58 | 49.922
2024-03-06 | 7:58 | 49.921
2024-03-06 | 7:58 | 49.92
2024-03-06 | 7:58 | 49.921
2024-03-06 | 7:58 | 49.921
2024-03-06 | 7:58 | 49.922
2024-03-06 | 7:58 | 49.923
2024-03-06 | 7:58 | 49.923
2024-03-06 | 7:58 | 49.926
2024-03-06 | 7:58 | 49.928
2024-03-06 | 7:58 | 49.927
2024-03-06 | 7:58 | 49.929
2024-03-06 | 7:58 | 49.93
2024-03-06 | 7:58 | 49.932
2024-03-06 | 7:58 | 49.936
2024-03-06 | 7:58 | 49.941
2024-03-06 | 7:58 | 49.948
2024-03-06 | 7:58 | 49.952
2024-03-06 | 7:58 | 49.96
2024-03-06 | 7:58 | 49.965
2024-03-06 | 7:59 | 49.972
2024-03-06 | 7:59 | 49.98
2024-03-06 | 7:59 | 49.988
2024-03-06 | 7:59 | 49.997
2024-03-06 | 7:59 | 50.008
2024-03-06 | 7:59 | 50.018
2024-03-06 | 7:59 | 50.031
2024-03-06 | 7:59 | 50.041
2024-03-06 | 7:59 | 50.051
2024-03-06 | 7:59 | 50.056
2024-03-06 | 7:59 | 50.06
2024-03-06 | 7:59 | 50.063
2024-03-06 | 7:59 | 50.063
2024-03-06 | 7:59 | 50.062
2024-03-06 | 7:59 | 50.06
2024-03-06 | 7:59 | 50.058
2024-03-06 | 7:59 | 50.054
2024-03-06 | 7:59 | 50.051
2024-03-06 | 7:59 | 50.05
2024-03-06 | 7:59 | 50.051
2024-03-06 | 7:59 | 50.048
2024-03-06 | 7:59 | 50.048
2024-03-06 | 7:59 | 50.046
2024-03-06 | 7:59 | 50.047
2024-03-06 | 7:59 | 50.049
2024-03-06 | 7:59 | 50.05
2024-03-06 | 7:59 | 50.054
2024-03-06 | 7:59 | 50.056
2024-03-06 | 7:59 | 50.06
2024-03-06 | 7:59 | 50.063
2024-03-06 | 7:59 | 50.066
2024-03-06 | 7:59 | 50.066
2024-03-06 | 7:59 | 50.07
2024-03-06 | 7:59 | 50.074
2024-03-06 | 7:59 | 50.075
2024-03-06 | 7:59 | 50.073
2024-03-06 | 7:59 | 50.074
2024-03-06 | 7:59 | 50.076
2024-03-06 | 7:59 | 50.079
2024-03-06 | 7:59 | 50.081
2024-03-06 | 7:59 | 50.084
2024-03-06 | 7:59 | 50.086
2024-03-06 | 7:59 | 50.087
2024-03-06 | 7:59 | 50.089
2024-03-06 | 7:59 | 50.091
2024-03-06 | 7:59 | 50.092
2024-03-06 | 7:59 | 50.096
2024-03-06 | 7:59 | 50.1
2024-03-06 | 7:59 | 50.103
2024-03-06 | 7:59 | 50.104
2024-03-06 | 7:59 | 50.104
2024-03-06 | 7:59 | 50.106
2024-03-06 | 7:59 | 50.105
2024-03-06 | 7:59 | 50.105
2024-03-06 | 7:59 | 50.102
2024-03-06 | 7:59 | 50.101
2024-03-06 | 7:59 | 50.1
2024-03-06 | 7:59 | 50.101
2024-03-06 | 7:59 | 50.103
2024-03-06 | 8:00 | 50.104
2024-03-06 | 8:00 | 50.106
2024-03-06 | 8:00 | 50.107
2024-03-06 | 8:00 | 50.107
2024-03-06 | 8:00 | 50.106
2024-03-06 | 8:00 | 50.105
2024-03-06 | 8:00 | 50.102
2024-03-06 | 8:00 | 50.102
2024-03-06 | 8:00 | 50.101
2024-03-06 | 8:00 | 50.102
2024-03-06 | 8:00 | 50.102
2024-03-06 | 8:00 | 50.104
2024-03-06 | 8:00 | 50.105
2024-03-06 | 8:00 | 50.104
2024-03-06 | 8:00 | 50.104
2024-03-06 | 8:00 | 50.105
2024-03-06 | 8:00 | 50.106
2024-03-06 | 8:00 | 50.107
2024-03-06 | 8:00 | 50.108
2024-03-06 | 8:00 | 50.109
2024-03-06 | 8:00 | 50.109
2024-03-06 | 8:00 | 50.11
2024-03-06 | 8:00 | 50.112
2024-03-06 | 8:00 | 50.113
2024-03-06 | 8:00 | 50.113
2024-03-06 | 8:00 | 50.114
2024-03-06 | 8:00 | 50.111
2024-03-06 | 8:00 | 50.109
2024-03-06 | 8:00 | 50.109
2024-03-06 | 8:00 | 50.109

## 20240307-1
In GMT
Date | Time | Freq
2024-03-07 | 2:54 | 49.978 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-07 | 2:54 | 49.976 | 222 | BRITNED | 676.211
2024-03-07 | 2:54 | 49.977 | 268 | WBURB-2 | 428.156
2024-03-07 | 2:54 | 49.979 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-07 | 2:54 | 49.98 |  | Viking Link | -648.9
2024-03-07 | 2:54 | 49.982 |  | Viking Link | 1398.96
2024-03-07 | 2:54 | 49.983 | 209 | DRAXX-3 | 626.95
2024-03-07 | 2:54 | 49.982 | 154 | CDCL-1 | 391.57
2024-03-07 | 2:54 | 49.982 | 268 | ROCK-1 | 468.495
2024-03-07 | 2:54 | 49.982 | 148 | IFA Bipole1 | 945.473
2024-03-07 | 2:54 | 49.981 | 132 | IFA Bipole1 | 999.1
2024-03-07 | 2:54 | 49.979 | 141 | IFA Bipole2 | 1000
2024-03-07 | 2:54 | 49.98 | 135 | IFA Bipole1 | 996.75
2024-03-07 | 2:54 | 49.98 |  | Viking Link | -780.3
2024-03-07 | 2:54 | 49.981
2024-03-07 | 2:54 | 49.982
2024-03-07 | 2:54 | 49.982
2024-03-07 | 2:54 | 49.983
2024-03-07 | 2:54 | 49.981
2024-03-07 | 2:54 | 49.98 | 130 | HEYM12 | 271.908
2024-03-07 | 2:54 | 49.979 | 228 | HUMR-1 | 303.75
2024-03-07 | 2:54 | 49.978
2024-03-07 | 2:54 | 49.98
2024-03-07 | 2:54 | 49.98
2024-03-07 | 2:54 | 49.979
2024-03-07 | 2:54 | 49.98
2024-03-07 | 2:54 | 49.98
2024-03-07 | 2:54 | 49.978
2024-03-07 | 2:54 | 49.978
2024-03-07 | 2:54 | 49.977
2024-03-07 | 2:54 | 49.977 | 211 | CDCL-1 | 291.5
2024-03-07 | 2:55 | 49.976 | 199 | STAY-2 | 413.125
2024-03-07 | 2:55 | 49.976 | 173 | CDCL-1 | 397.375
2024-03-07 | 2:55 | 49.975 | 248 | SEAB-2 | 361.25
2024-03-07 | 2:55 | 49.976 | 255 | FRANCE | 995.65
2024-03-07 | 2:55 | 49.978 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-07 | 2:55 | 49.978
2024-03-07 | 2:55 | 49.978
2024-03-07 | 2:55 | 49.979
2024-03-07 | 2:55 | 49.978
2024-03-07 | 2:55 | 49.976
2024-03-07 | 2:55 | 49.976
2024-03-07 | 2:55 | 49.975
2024-03-07 | 2:55 | 49.975
2024-03-07 | 2:55 | 49.976
2024-03-07 | 2:55 | 49.974
2024-03-07 | 2:55 | 49.973
2024-03-07 | 2:55 | 49.972
2024-03-07 | 2:55 | 49.973
2024-03-07 | 2:55 | 49.97
2024-03-07 | 2:55 | 49.97
2024-03-07 | 2:55 | 49.97
2024-03-07 | 2:55 | 49.971
2024-03-07 | 2:55 | 49.968
2024-03-07 | 2:55 | 49.969
2024-03-07 | 2:55 | 49.968
2024-03-07 | 2:55 | 49.967
2024-03-07 | 2:55 | 49.968
2024-03-07 | 2:55 | 49.969
2024-03-07 | 2:55 | 49.969
2024-03-07 | 2:55 | 49.969
2024-03-07 | 2:55 | 49.967
2024-03-07 | 2:55 | 49.968
2024-03-07 | 2:55 | 49.967
2024-03-07 | 2:55 | 49.969
2024-03-07 | 2:55 | 49.966
2024-03-07 | 2:55 | 49.966
2024-03-07 | 2:55 | 49.966
2024-03-07 | 2:55 | 49.965
2024-03-07 | 2:55 | 49.967
2024-03-07 | 2:55 | 49.967
2024-03-07 | 2:55 | 49.969
2024-03-07 | 2:55 | 49.969
2024-03-07 | 2:55 | 49.97
2024-03-07 | 2:55 | 49.969
2024-03-07 | 2:55 | 49.969
2024-03-07 | 2:55 | 49.966
2024-03-07 | 2:55 | 49.962
2024-03-07 | 2:55 | 49.958
2024-03-07 | 2:55 | 49.957
2024-03-07 | 2:55 | 49.959
2024-03-07 | 2:55 | 49.961
2024-03-07 | 2:55 | 49.962
2024-03-07 | 2:55 | 49.962
2024-03-07 | 2:55 | 49.963
2024-03-07 | 2:55 | 49.963
2024-03-07 | 2:55 | 49.964
2024-03-07 | 2:55 | 49.962
2024-03-07 | 2:55 | 49.96
2024-03-07 | 2:55 | 49.961
2024-03-07 | 2:56 | 49.962
2024-03-07 | 2:56 | 49.961
2024-03-07 | 2:56 | 49.962
2024-03-07 | 2:56 | 49.962
2024-03-07 | 2:56 | 49.962
2024-03-07 | 2:56 | 49.961
2024-03-07 | 2:56 | 49.96
2024-03-07 | 2:56 | 49.957
2024-03-07 | 2:56 | 49.956
2024-03-07 | 2:56 | 49.954
2024-03-07 | 2:56 | 49.954
2024-03-07 | 2:56 | 49.955
2024-03-07 | 2:56 | 49.953
2024-03-07 | 2:56 | 49.953
2024-03-07 | 2:56 | 49.955
2024-03-07 | 2:56 | 49.955
2024-03-07 | 2:56 | 49.955
2024-03-07 | 2:56 | 49.954
2024-03-07 | 2:56 | 49.954
2024-03-07 | 2:56 | 49.954
2024-03-07 | 2:56 | 49.954
2024-03-07 | 2:56 | 49.952
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.949
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.948
2024-03-07 | 2:56 | 49.946
2024-03-07 | 2:56 | 49.943
2024-03-07 | 2:56 | 49.944
2024-03-07 | 2:56 | 49.945
2024-03-07 | 2:56 | 49.947
2024-03-07 | 2:56 | 49.949
2024-03-07 | 2:56 | 49.951
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.953
2024-03-07 | 2:56 | 49.953
2024-03-07 | 2:56 | 49.953
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.947
2024-03-07 | 2:56 | 49.945
2024-03-07 | 2:56 | 49.946
2024-03-07 | 2:56 | 49.948
2024-03-07 | 2:56 | 49.948
2024-03-07 | 2:56 | 49.951
2024-03-07 | 2:56 | 49.953
2024-03-07 | 2:56 | 49.954
2024-03-07 | 2:56 | 49.953
2024-03-07 | 2:56 | 49.953
2024-03-07 | 2:56 | 49.953
2024-03-07 | 2:56 | 49.949
2024-03-07 | 2:56 | 49.949
2024-03-07 | 2:56 | 49.949
2024-03-07 | 2:56 | 49.95
2024-03-07 | 2:56 | 49.952
2024-03-07 | 2:56 | 49.952
2024-03-07 | 2:57 | 49.952
2024-03-07 | 2:57 | 49.951
2024-03-07 | 2:57 | 49.949
2024-03-07 | 2:57 | 49.951
2024-03-07 | 2:57 | 49.95
2024-03-07 | 2:57 | 49.948
2024-03-07 | 2:57 | 49.948
2024-03-07 | 2:57 | 49.947
2024-03-07 | 2:57 | 49.948
2024-03-07 | 2:57 | 49.95
2024-03-07 | 2:57 | 49.95
2024-03-07 | 2:57 | 49.95
2024-03-07 | 2:57 | 49.95
2024-03-07 | 2:57 | 49.949
2024-03-07 | 2:57 | 49.948
2024-03-07 | 2:57 | 49.948
2024-03-07 | 2:57 | 49.947
2024-03-07 | 2:57 | 49.948
2024-03-07 | 2:57 | 49.948
2024-03-07 | 2:57 | 49.949
2024-03-07 | 2:57 | 49.948
2024-03-07 | 2:57 | 49.949
2024-03-07 | 2:57 | 49.949
2024-03-07 | 2:57 | 49.949
2024-03-07 | 2:57 | 49.949
2024-03-07 | 2:57 | 49.953
2024-03-07 | 2:57 | 49.954
2024-03-07 | 2:57 | 49.954
2024-03-07 | 2:57 | 49.954
2024-03-07 | 2:57 | 49.953
2024-03-07 | 2:57 | 49.949
2024-03-07 | 2:57 | 49.946
2024-03-07 | 2:57 | 49.945
2024-03-07 | 2:57 | 49.945
2024-03-07 | 2:57 | 49.945
2024-03-07 | 2:57 | 49.946
2024-03-07 | 2:57 | 49.945
2024-03-07 | 2:57 | 49.945
2024-03-07 | 2:57 | 49.945
2024-03-07 | 2:57 | 49.945
2024-03-07 | 2:57 | 49.945
2024-03-07 | 2:57 | 49.943
2024-03-07 | 2:57 | 49.943
2024-03-07 | 2:57 | 49.941
2024-03-07 | 2:57 | 49.941
2024-03-07 | 2:57 | 49.941
2024-03-07 | 2:57 | 49.94
2024-03-07 | 2:57 | 49.94
2024-03-07 | 2:57 | 49.941
2024-03-07 | 2:57 | 49.943
2024-03-07 | 2:57 | 49.94
2024-03-07 | 2:57 | 49.941
2024-03-07 | 2:57 | 49.941
2024-03-07 | 2:57 | 49.94
2024-03-07 | 2:57 | 49.94
2024-03-07 | 2:57 | 49.939
2024-03-07 | 2:57 | 49.942
2024-03-07 | 2:57 | 49.94
2024-03-07 | 2:57 | 49.94
2024-03-07 | 2:58 | 49.94
2024-03-07 | 2:58 | 49.937
2024-03-07 | 2:58 | 49.936
2024-03-07 | 2:58 | 49.935
2024-03-07 | 2:58 | 49.935
2024-03-07 | 2:58 | 49.934
2024-03-07 | 2:58 | 49.933
2024-03-07 | 2:58 | 49.934
2024-03-07 | 2:58 | 49.932
2024-03-07 | 2:58 | 49.93
2024-03-07 | 2:58 | 49.928
2024-03-07 | 2:58 | 49.928
2024-03-07 | 2:58 | 49.927
2024-03-07 | 2:58 | 49.926
2024-03-07 | 2:58 | 49.926
2024-03-07 | 2:58 | 49.926
2024-03-07 | 2:58 | 49.925
2024-03-07 | 2:58 | 49.924
2024-03-07 | 2:58 | 49.923
2024-03-07 | 2:58 | 49.924
2024-03-07 | 2:58 | 49.924
2024-03-07 | 2:58 | 49.925
2024-03-07 | 2:58 | 49.925
2024-03-07 | 2:58 | 49.925
2024-03-07 | 2:58 | 49.928
2024-03-07 | 2:58 | 49.927
2024-03-07 | 2:58 | 49.928
2024-03-07 | 2:58 | 49.928
2024-03-07 | 2:58 | 49.929
2024-03-07 | 2:58 | 49.93
2024-03-07 | 2:58 | 49.931
2024-03-07 | 2:58 | 49.929
2024-03-07 | 2:58 | 49.928
2024-03-07 | 2:58 | 49.928
2024-03-07 | 2:58 | 49.927
2024-03-07 | 2:58 | 49.926
2024-03-07 | 2:58 | 49.926
2024-03-07 | 2:58 | 49.925
2024-03-07 | 2:58 | 49.926
2024-03-07 | 2:58 | 49.926
2024-03-07 | 2:58 | 49.926
2024-03-07 | 2:58 | 49.929
2024-03-07 | 2:58 | 49.929
2024-03-07 | 2:58 | 49.929
2024-03-07 | 2:58 | 49.932
2024-03-07 | 2:58 | 49.931
2024-03-07 | 2:58 | 49.931
2024-03-07 | 2:58 | 49.934
2024-03-07 | 2:58 | 49.934
2024-03-07 | 2:58 | 49.935
2024-03-07 | 2:58 | 49.935
2024-03-07 | 2:58 | 49.936
2024-03-07 | 2:58 | 49.935
2024-03-07 | 2:58 | 49.934
2024-03-07 | 2:58 | 49.934
2024-03-07 | 2:58 | 49.935
2024-03-07 | 2:58 | 49.936
2024-03-07 | 2:58 | 49.936
2024-03-07 | 2:58 | 49.937
2024-03-07 | 2:58 | 49.937
2024-03-07 | 2:58 | 49.938
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.94
2024-03-07 | 2:59 | 49.94
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.942
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.943
2024-03-07 | 2:59 | 49.943
2024-03-07 | 2:59 | 49.942
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.942
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.943
2024-03-07 | 2:59 | 49.942
2024-03-07 | 2:59 | 49.94
2024-03-07 | 2:59 | 49.94
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.94
2024-03-07 | 2:59 | 49.938
2024-03-07 | 2:59 | 49.934
2024-03-07 | 2:59 | 49.935
2024-03-07 | 2:59 | 49.932
2024-03-07 | 2:59 | 49.928
2024-03-07 | 2:59 | 49.926
2024-03-07 | 2:59 | 49.923
2024-03-07 | 2:59 | 49.923
2024-03-07 | 2:59 | 49.923
2024-03-07 | 2:59 | 49.924
2024-03-07 | 2:59 | 49.924
2024-03-07 | 2:59 | 49.927
2024-03-07 | 2:59 | 49.929
2024-03-07 | 2:59 | 49.93
2024-03-07 | 2:59 | 49.93
2024-03-07 | 2:59 | 49.932
2024-03-07 | 2:59 | 49.933
2024-03-07 | 2:59 | 49.933
2024-03-07 | 2:59 | 49.934
2024-03-07 | 2:59 | 49.934
2024-03-07 | 2:59 | 49.934
2024-03-07 | 2:59 | 49.935
2024-03-07 | 2:59 | 49.935
2024-03-07 | 2:59 | 49.936
2024-03-07 | 2:59 | 49.938
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.942
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.94
2024-03-07 | 2:59 | 49.941
2024-03-07 | 2:59 | 49.942
2024-03-07 | 2:59 | 49.94
2024-03-07 | 2:59 | 49.94
2024-03-07 | 3:00 | 49.941
2024-03-07 | 3:00 | 49.943
2024-03-07 | 3:00 | 49.945
2024-03-07 | 3:00 | 49.948
2024-03-07 | 3:00 | 49.948
2024-03-07 | 3:00 | 49.95
2024-03-07 | 3:00 | 49.95
2024-03-07 | 3:00 | 49.951
2024-03-07 | 3:00 | 49.952
2024-03-07 | 3:00 | 49.951
2024-03-07 | 3:00 | 49.951
2024-03-07 | 3:00 | 49.953
2024-03-07 | 3:00 | 49.952
2024-03-07 | 3:00 | 49.953
2024-03-07 | 3:00 | 49.953
2024-03-07 | 3:00 | 49.952
2024-03-07 | 3:00 | 49.95
2024-03-07 | 3:00 | 49.949
2024-03-07 | 3:00 | 49.948
2024-03-07 | 3:00 | 49.947
2024-03-07 | 3:00 | 49.946
2024-03-07 | 3:00 | 49.946
2024-03-07 | 3:00 | 49.948
2024-03-07 | 3:00 | 49.95
2024-03-07 | 3:00 | 49.952
2024-03-07 | 3:00 | 49.953
2024-03-07 | 3:00 | 49.957
2024-03-07 | 3:00 | 49.956
2024-03-07 | 3:00 | 49.956
2024-03-07 | 3:00 | 49.956
2024-03-07 | 3:00 | 49.955
2024-03-07 | 3:00 | 49.96
2024-03-07 | 3:00 | 49.964
2024-03-07 | 3:00 | 49.964
2024-03-07 | 3:00 | 49.963
2024-03-07 | 3:00 | 49.962
2024-03-07 | 3:00 | 49.962
2024-03-07 | 3:00 | 49.96
2024-03-07 | 3:00 | 49.961
2024-03-07 | 3:00 | 49.96
2024-03-07 | 3:00 | 49.96
2024-03-07 | 3:00 | 49.958
2024-03-07 | 3:00 | 49.959
2024-03-07 | 3:00 | 49.959
2024-03-07 | 3:00 | 49.961
2024-03-07 | 3:00 | 49.962
2024-03-07 | 3:00 | 49.963
2024-03-07 | 3:00 | 49.967
2024-03-07 | 3:00 | 49.972
2024-03-07 | 3:00 | 49.978
2024-03-07 | 3:00 | 49.984
2024-03-07 | 3:00 | 49.99
2024-03-07 | 3:00 | 49.995
2024-03-07 | 3:00 | 50.001
2024-03-07 | 3:00 | 50.006
2024-03-07 | 3:00 | 50.012
2024-03-07 | 3:00 | 50.02
2024-03-07 | 3:00 | 50.026
2024-03-07 | 3:00 | 50.03
2024-03-07 | 3:00 | 50.029
2024-03-07 | 3:00 | 50.031
2024-03-07 | 3:01 | 50.029
2024-03-07 | 3:01 | 50.028
2024-03-07 | 3:01 | 50.027
2024-03-07 | 3:01 | 50.025
2024-03-07 | 3:01 | 50.024
2024-03-07 | 3:01 | 50.023
2024-03-07 | 3:01 | 50.021
2024-03-07 | 3:01 | 50.023
2024-03-07 | 3:01 | 50.026
2024-03-07 | 3:01 | 50.029
2024-03-07 | 3:01 | 50.029
2024-03-07 | 3:01 | 50.031
2024-03-07 | 3:01 | 50.03
2024-03-07 | 3:01 | 50.031
2024-03-07 | 3:01 | 50.03
2024-03-07 | 3:01 | 50.03
2024-03-07 | 3:01 | 50.032
2024-03-07 | 3:01 | 50.029
2024-03-07 | 3:01 | 50.029
2024-03-07 | 3:01 | 50.026
2024-03-07 | 3:01 | 50.025
2024-03-07 | 3:01 | 50.024
2024-03-07 | 3:01 | 50.024
2024-03-07 | 3:01 | 50.025
2024-03-07 | 3:01 | 50.025
2024-03-07 | 3:01 | 50.025
2024-03-07 | 3:01 | 50.024
2024-03-07 | 3:01 | 50.025
2024-03-07 | 3:01 | 50.023

## 20240308-1
In GMT
Date | Time | Freq
2024-03-08 | 4:01 | 50.129 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-08 | 4:01 | 50.127 | 222 | BRITNED | 676.211
2024-03-08 | 4:01 | 50.125 | 268 | WBURB-2 | 428.156
2024-03-08 | 4:01 | 50.127 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-08 | 4:01 | 50.128 |  | Viking Link | -648.9
2024-03-08 | 4:01 | 50.127 |  | Viking Link | 1398.96
2024-03-08 | 4:01 | 50.125 | 209 | DRAXX-3 | 626.95
2024-03-08 | 4:01 | 50.123 | 154 | CDCL-1 | 391.57
2024-03-08 | 4:01 | 50.126 | 268 | ROCK-1 | 468.495
2024-03-08 | 4:01 | 50.126 | 148 | IFA Bipole1 | 945.473
2024-03-08 | 4:01 | 50.128 | 132 | IFA Bipole1 | 999.1
2024-03-08 | 4:01 | 50.129 | 141 | IFA Bipole2 | 1000
2024-03-08 | 4:01 | 50.128 | 135 | IFA Bipole1 | 996.75
2024-03-08 | 4:01 | 50.129 |  | Viking Link | -780.3
2024-03-08 | 4:01 | 50.126
2024-03-08 | 4:01 | 50.124
2024-03-08 | 4:01 | 50.123
2024-03-08 | 4:01 | 50.122
2024-03-08 | 4:01 | 50.122
2024-03-08 | 4:01 | 50.121 | 130 | HEYM12 | 271.908
2024-03-08 | 4:01 | 50.119 | 228 | HUMR-1 | 303.75
2024-03-08 | 4:01 | 50.116
2024-03-08 | 4:01 | 50.116
2024-03-08 | 4:01 | 50.119
2024-03-08 | 4:01 | 50.122
2024-03-08 | 4:01 | 50.123
2024-03-08 | 4:01 | 50.124
2024-03-08 | 4:01 | 50.122
2024-03-08 | 4:01 | 50.121
2024-03-08 | 4:01 | 50.123
2024-03-08 | 4:02 | 50.124 | 211 | CDCL-1 | 291.5
2024-03-08 | 4:02 | 50.124 | 199 | STAY-2 | 413.125
2024-03-08 | 4:02 | 50.124 | 173 | CDCL-1 | 397.375
2024-03-08 | 4:02 | 50.123 | 248 | SEAB-2 | 361.25
2024-03-08 | 4:02 | 50.12 | 255 | FRANCE | 995.65
2024-03-08 | 4:02 | 50.117 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-08 | 4:02 | 50.114
2024-03-08 | 4:02 | 50.114
2024-03-08 | 4:02 | 50.112
2024-03-08 | 4:02 | 50.116
2024-03-08 | 4:02 | 50.116
2024-03-08 | 4:02 | 50.118
2024-03-08 | 4:02 | 50.118
2024-03-08 | 4:02 | 50.119
2024-03-08 | 4:02 | 50.12
2024-03-08 | 4:02 | 50.122
2024-03-08 | 4:02 | 50.122
2024-03-08 | 4:02 | 50.12
2024-03-08 | 4:02 | 50.119
2024-03-08 | 4:02 | 50.116
2024-03-08 | 4:02 | 50.118
2024-03-08 | 4:02 | 50.118
2024-03-08 | 4:02 | 50.117
2024-03-08 | 4:02 | 50.118
2024-03-08 | 4:02 | 50.117
2024-03-08 | 4:02 | 50.117
2024-03-08 | 4:02 | 50.117
2024-03-08 | 4:02 | 50.116
2024-03-08 | 4:02 | 50.14
2024-03-08 | 4:02 | 50.199
2024-03-08 | 4:02 | 50.243
2024-03-08 | 4:02 | 50.202
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.166
2024-03-08 | 4:02 | 50.165
2024-03-08 | 4:02 | 50.167
2024-03-08 | 4:02 | 50.171
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.176
2024-03-08 | 4:02 | 50.178
2024-03-08 | 4:02 | 50.176
2024-03-08 | 4:02 | 50.174
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.176
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.174
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.173
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.176
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.175
2024-03-08 | 4:02 | 50.173
2024-03-08 | 4:02 | 50.171
2024-03-08 | 4:02 | 50.172
2024-03-08 | 4:02 | 50.173
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.173
2024-03-08 | 4:03 | 50.182
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.172
2024-03-08 | 4:03 | 50.173
2024-03-08 | 4:03 | 50.172
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.179
2024-03-08 | 4:03 | 50.182
2024-03-08 | 4:03 | 50.183
2024-03-08 | 4:03 | 50.182
2024-03-08 | 4:03 | 50.179
2024-03-08 | 4:03 | 50.177
2024-03-08 | 4:03 | 50.179
2024-03-08 | 4:03 | 50.181
2024-03-08 | 4:03 | 50.182
2024-03-08 | 4:03 | 50.181
2024-03-08 | 4:03 | 50.179
2024-03-08 | 4:03 | 50.178
2024-03-08 | 4:03 | 50.177
2024-03-08 | 4:03 | 50.177
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.175
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.176
2024-03-08 | 4:03 | 50.174
2024-03-08 | 4:03 | 50.173
2024-03-08 | 4:03 | 50.172
2024-03-08 | 4:03 | 50.17
2024-03-08 | 4:04 | 50.171
2024-03-08 | 4:04 | 50.171
2024-03-08 | 4:04 | 50.169
2024-03-08 | 4:04 | 50.169
2024-03-08 | 4:04 | 50.168
2024-03-08 | 4:04 | 50.165
2024-03-08 | 4:04 | 50.161
2024-03-08 | 4:04 | 50.16
2024-03-08 | 4:04 | 50.158
2024-03-08 | 4:04 | 50.157
2024-03-08 | 4:04 | 50.153
2024-03-08 | 4:04 | 50.151
2024-03-08 | 4:04 | 50.147
2024-03-08 | 4:04 | 50.151
2024-03-08 | 4:04 | 50.15
2024-03-08 | 4:04 | 50.153
2024-03-08 | 4:04 | 50.154
2024-03-08 | 4:04 | 50.152
2024-03-08 | 4:04 | 50.152
2024-03-08 | 4:04 | 50.147
2024-03-08 | 4:04 | 50.135
2024-03-08 | 4:04 | 50.125
2024-03-08 | 4:04 | 50.117
2024-03-08 | 4:04 | 50.113
2024-03-08 | 4:04 | 50.11
2024-03-08 | 4:04 | 50.109
2024-03-08 | 4:04 | 50.109
2024-03-08 | 4:04 | 50.11
2024-03-08 | 4:04 | 50.109
2024-03-08 | 4:04 | 50.11
2024-03-08 | 4:04 | 50.109
2024-03-08 | 4:04 | 50.105
2024-03-08 | 4:04 | 50.104
2024-03-08 | 4:04 | 50.103
2024-03-08 | 4:04 | 50.105
2024-03-08 | 4:04 | 50.109
2024-03-08 | 4:04 | 50.107
2024-03-08 | 4:04 | 50.106
2024-03-08 | 4:04 | 50.109
2024-03-08 | 4:04 | 50.108
2024-03-08 | 4:04 | 50.108
2024-03-08 | 4:04 | 50.108
2024-03-08 | 4:04 | 50.107
2024-03-08 | 4:04 | 50.107
2024-03-08 | 4:04 | 50.105
2024-03-08 | 4:04 | 50.104
2024-03-08 | 4:04 | 50.105
2024-03-08 | 4:04 | 50.105
2024-03-08 | 4:04 | 50.103
2024-03-08 | 4:04 | 50.101
2024-03-08 | 4:04 | 50.101
2024-03-08 | 4:04 | 50.098
2024-03-08 | 4:04 | 50.1
2024-03-08 | 4:04 | 50.101
2024-03-08 | 4:04 | 50.103
2024-03-08 | 4:04 | 50.103
2024-03-08 | 4:04 | 50.103
2024-03-08 | 4:04 | 50.104
2024-03-08 | 4:04 | 50.104
2024-03-08 | 4:04 | 50.106
2024-03-08 | 4:04 | 50.105
2024-03-08 | 4:05 | 50.102
2024-03-08 | 4:05 | 50.102
2024-03-08 | 4:05 | 50.099
2024-03-08 | 4:05 | 50.099
2024-03-08 | 4:05 | 50.095
2024-03-08 | 4:05 | 50.09
2024-03-08 | 4:05 | 50.087
2024-03-08 | 4:05 | 50.086
2024-03-08 | 4:05 | 50.085
2024-03-08 | 4:05 | 50.085
2024-03-08 | 4:05 | 50.089
2024-03-08 | 4:05 | 50.09
2024-03-08 | 4:05 | 50.091
2024-03-08 | 4:05 | 50.09
2024-03-08 | 4:05 | 50.089
2024-03-08 | 4:05 | 50.088
2024-03-08 | 4:05 | 50.085
2024-03-08 | 4:05 | 50.083
2024-03-08 | 4:05 | 50.083
2024-03-08 | 4:05 | 50.082
2024-03-08 | 4:05 | 50.079
2024-03-08 | 4:05 | 50.075
2024-03-08 | 4:05 | 50.076
2024-03-08 | 4:05 | 50.075
2024-03-08 | 4:05 | 50.08
2024-03-08 | 4:05 | 50.082
2024-03-08 | 4:05 | 50.083
2024-03-08 | 4:05 | 50.084
2024-03-08 | 4:05 | 50.084
2024-03-08 | 4:05 | 50.082
2024-03-08 | 4:05 | 50.078
2024-03-08 | 4:05 | 50.074
2024-03-08 | 4:05 | 50.07
2024-03-08 | 4:05 | 50.067
2024-03-08 | 4:05 | 50.065
2024-03-08 | 4:05 | 50.063
2024-03-08 | 4:05 | 50.063
2024-03-08 | 4:05 | 50.063
2024-03-08 | 4:05 | 50.065
2024-03-08 | 4:05 | 50.065
2024-03-08 | 4:05 | 50.067
2024-03-08 | 4:05 | 50.07
2024-03-08 | 4:05 | 50.071
2024-03-08 | 4:05 | 50.074
2024-03-08 | 4:05 | 50.074
2024-03-08 | 4:05 | 50.074
2024-03-08 | 4:05 | 50.076
2024-03-08 | 4:05 | 50.077
2024-03-08 | 4:05 | 50.079
2024-03-08 | 4:05 | 50.08
2024-03-08 | 4:05 | 50.079
2024-03-08 | 4:05 | 50.077
2024-03-08 | 4:05 | 50.075
2024-03-08 | 4:05 | 50.074
2024-03-08 | 4:05 | 50.072
2024-03-08 | 4:05 | 50.07
2024-03-08 | 4:05 | 50.069
2024-03-08 | 4:05 | 50.065
2024-03-08 | 4:05 | 50.064
2024-03-08 | 4:06 | 50.065
2024-03-08 | 4:06 | 50.063
2024-03-08 | 4:06 | 50.061
2024-03-08 | 4:06 | 50.06
2024-03-08 | 4:06 | 50.057
2024-03-08 | 4:06 | 50.054
2024-03-08 | 4:06 | 50.052
2024-03-08 | 4:06 | 50.05
2024-03-08 | 4:06 | 50.05
2024-03-08 | 4:06 | 50.051
2024-03-08 | 4:06 | 50.053
2024-03-08 | 4:06 | 50.057
2024-03-08 | 4:06 | 50.06
2024-03-08 | 4:06 | 50.06
2024-03-08 | 4:06 | 50.061
2024-03-08 | 4:06 | 50.06
2024-03-08 | 4:06 | 50.058
2024-03-08 | 4:06 | 50.057
2024-03-08 | 4:06 | 50.056
2024-03-08 | 4:06 | 50.057
2024-03-08 | 4:06 | 50.057
2024-03-08 | 4:06 | 50.057
2024-03-08 | 4:06 | 50.056
2024-03-08 | 4:06 | 50.057
2024-03-08 | 4:06 | 50.058
2024-03-08 | 4:06 | 50.058
2024-03-08 | 4:06 | 50.058
2024-03-08 | 4:06 | 50.056
2024-03-08 | 4:06 | 50.054
2024-03-08 | 4:06 | 50.053
2024-03-08 | 4:06 | 50.051
2024-03-08 | 4:06 | 50.049
2024-03-08 | 4:06 | 50.047
2024-03-08 | 4:06 | 50.044
2024-03-08 | 4:06 | 50.042
2024-03-08 | 4:06 | 50.043
2024-03-08 | 4:06 | 50.041
2024-03-08 | 4:06 | 50.039
2024-03-08 | 4:06 | 50.037
2024-03-08 | 4:06 | 50.037
2024-03-08 | 4:06 | 50.039
2024-03-08 | 4:06 | 50.039
2024-03-08 | 4:06 | 50.038
2024-03-08 | 4:06 | 50.038
2024-03-08 | 4:06 | 50.035
2024-03-08 | 4:06 | 50.034
2024-03-08 | 4:06 | 50.032
2024-03-08 | 4:06 | 50.03
2024-03-08 | 4:06 | 50.03
2024-03-08 | 4:06 | 50.029
2024-03-08 | 4:06 | 50.03
2024-03-08 | 4:06 | 50.028
2024-03-08 | 4:06 | 50.028
2024-03-08 | 4:06 | 50.026
2024-03-08 | 4:06 | 50.024
2024-03-08 | 4:06 | 50.022
2024-03-08 | 4:06 | 50.023
2024-03-08 | 4:06 | 50.022
2024-03-08 | 4:06 | 50.022
2024-03-08 | 4:06 | 50.02
2024-03-08 | 4:06 | 50.016
2024-03-08 | 4:07 | 50.009
2024-03-08 | 4:07 | 50.006
2024-03-08 | 4:07 | 50.005
2024-03-08 | 4:07 | 50.004
2024-03-08 | 4:07 | 50.005
2024-03-08 | 4:07 | 50.005
2024-03-08 | 4:07 | 50.004
2024-03-08 | 4:07 | 50.007
2024-03-08 | 4:07 | 50.008
2024-03-08 | 4:07 | 50.007
2024-03-08 | 4:07 | 50.005
2024-03-08 | 4:07 | 50.004
2024-03-08 | 4:07 | 50.004
2024-03-08 | 4:07 | 50.005
2024-03-08 | 4:07 | 50.004
2024-03-08 | 4:07 | 50.002
2024-03-08 | 4:07 | 50.003
2024-03-08 | 4:07 | 50.005
2024-03-08 | 4:07 | 50.004
2024-03-08 | 4:07 | 50.005
2024-03-08 | 4:07 | 50.007
2024-03-08 | 4:07 | 50.008
2024-03-08 | 4:07 | 50.01
2024-03-08 | 4:07 | 50.012
2024-03-08 | 4:07 | 50.013
2024-03-08 | 4:07 | 50.013
2024-03-08 | 4:07 | 50.011
2024-03-08 | 4:07 | 50.009
2024-03-08 | 4:07 | 50.004
2024-03-08 | 4:07 | 50.001
2024-03-08 | 4:07 | 49.995
2024-03-08 | 4:07 | 49.99
2024-03-08 | 4:07 | 49.986
2024-03-08 | 4:07 | 49.984
2024-03-08 | 4:07 | 49.981
2024-03-08 | 4:07 | 49.979
2024-03-08 | 4:07 | 49.977
2024-03-08 | 4:07 | 49.979
2024-03-08 | 4:07 | 49.98
2024-03-08 | 4:07 | 49.98
2024-03-08 | 4:07 | 49.981
2024-03-08 | 4:07 | 49.979
2024-03-08 | 4:07 | 49.979
2024-03-08 | 4:07 | 49.976
2024-03-08 | 4:07 | 49.975
2024-03-08 | 4:07 | 49.973
2024-03-08 | 4:07 | 49.972
2024-03-08 | 4:07 | 49.97
2024-03-08 | 4:07 | 49.969
2024-03-08 | 4:07 | 49.967
2024-03-08 | 4:07 | 49.962
2024-03-08 | 4:07 | 49.957
2024-03-08 | 4:07 | 49.958
2024-03-08 | 4:07 | 49.96
2024-03-08 | 4:07 | 49.96
2024-03-08 | 4:07 | 49.961
2024-03-08 | 4:07 | 49.963
2024-03-08 | 4:07 | 49.967
2024-03-08 | 4:07 | 49.974
2024-03-08 | 4:08 | 49.975
2024-03-08 | 4:08 | 49.978
2024-03-08 | 4:08 | 49.979
2024-03-08 | 4:08 | 49.983
2024-03-08 | 4:08 | 49.984
2024-03-08 | 4:08 | 49.988
2024-03-08 | 4:08 | 49.996
2024-03-08 | 4:08 | 50.005
2024-03-08 | 4:08 | 50.02
2024-03-08 | 4:08 | 50.037
2024-03-08 | 4:08 | 50.047
2024-03-08 | 4:08 | 50.051
2024-03-08 | 4:08 | 50.055
2024-03-08 | 4:08 | 50.059
2024-03-08 | 4:08 | 50.062
2024-03-08 | 4:08 | 50.062
2024-03-08 | 4:08 | 50.065
2024-03-08 | 4:08 | 50.069
2024-03-08 | 4:08 | 50.068
2024-03-08 | 4:08 | 50.068
2024-03-08 | 4:08 | 50.069
2024-03-08 | 4:08 | 50.069
2024-03-08 | 4:08 | 50.068
2024-03-08 | 4:08 | 50.069
2024-03-08 | 4:08 | 50.071
2024-03-08 | 4:08 | 50.071
2024-03-08 | 4:08 | 50.07
2024-03-08 | 4:08 | 50.07
2024-03-08 | 4:08 | 50.068
2024-03-08 | 4:08 | 50.067
2024-03-08 | 4:08 | 50.072
2024-03-08 | 4:08 | 50.073
2024-03-08 | 4:08 | 50.073
2024-03-08 | 4:08 | 50.074
2024-03-08 | 4:08 | 50.073
2024-03-08 | 4:08 | 50.072
2024-03-08 | 4:08 | 50.068
2024-03-08 | 4:08 | 50.064
2024-03-08 | 4:08 | 50.06
2024-03-08 | 4:08 | 50.057
2024-03-08 | 4:08 | 50.055
2024-03-08 | 4:08 | 50.057
2024-03-08 | 4:08 | 50.061
2024-03-08 | 4:08 | 50.063
2024-03-08 | 4:08 | 50.062
2024-03-08 | 4:08 | 50.061
2024-03-08 | 4:08 | 50.059
2024-03-08 | 4:08 | 50.056
2024-03-08 | 4:08 | 50.056
2024-03-08 | 4:08 | 50.056
2024-03-08 | 4:08 | 50.06
2024-03-08 | 4:08 | 50.06
2024-03-08 | 4:08 | 50.057
2024-03-08 | 4:08 | 50.054
2024-03-08 | 4:08 | 50.055
2024-03-08 | 4:08 | 50.054
2024-03-08 | 4:08 | 50.056
2024-03-08 | 4:08 | 50.059
2024-03-08 | 4:08 | 50.064
2024-03-08 | 4:08 | 50.066
2024-03-08 | 4:08 | 50.065
2024-03-08 | 4:09 | 50.066
2024-03-08 | 4:09 | 50.066
2024-03-08 | 4:09 | 50.069
2024-03-08 | 4:09 | 50.072
2024-03-08 | 4:09 | 50.072
2024-03-08 | 4:09 | 50.071
2024-03-08 | 4:09 | 50.07
2024-03-08 | 4:09 | 50.065
2024-03-08 | 4:09 | 50.058
2024-03-08 | 4:09 | 50.052
2024-03-08 | 4:09 | 50.051
2024-03-08 | 4:09 | 50.053
2024-03-08 | 4:09 | 50.055
2024-03-08 | 4:09 | 50.055
2024-03-08 | 4:09 | 50.057
2024-03-08 | 4:09 | 50.058
2024-03-08 | 4:09 | 50.062
2024-03-08 | 4:09 | 50.06
2024-03-08 | 4:09 | 50.057
2024-03-08 | 4:09 | 50.054
2024-03-08 | 4:09 | 50.054
2024-03-08 | 4:09 | 50.053
2024-03-08 | 4:09 | 50.051
2024-03-08 | 4:09 | 50.048
2024-03-08 | 4:09 | 50.047
2024-03-08 | 4:09 | 50.046
2024-03-08 | 4:09 | 50.042
2024-03-08 | 4:09 | 50.04
2024-03-08 | 4:09 | 50.039

## 20240311-1
In GMT
Date | Time | Freq
2024-03-11 | 9:55 | 49.883 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-11 | 9:55 | 49.884 | 222 | BRITNED | 676.211
2024-03-11 | 9:55 | 49.886 | 268 | WBURB-2 | 428.156
2024-03-11 | 9:55 | 49.888 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-11 | 9:55 | 49.886 |  | Viking Link | -648.9
2024-03-11 | 9:55 | 49.882 |  | Viking Link | 1398.96
2024-03-11 | 9:55 | 49.88 | 209 | DRAXX-3 | 626.95
2024-03-11 | 9:55 | 49.877 | 154 | CDCL-1 | 391.57
2024-03-11 | 9:55 | 49.876 | 268 | ROCK-1 | 468.495
2024-03-11 | 9:55 | 49.875 | 148 | IFA Bipole1 | 945.473
2024-03-11 | 9:55 | 49.877 | 132 | IFA Bipole1 | 999.1
2024-03-11 | 9:55 | 49.877 | 141 | IFA Bipole2 | 1000
2024-03-11 | 9:55 | 49.878 | 135 | IFA Bipole1 | 996.75
2024-03-11 | 9:55 | 49.879 |  | Viking Link | -780.3
2024-03-11 | 9:55 | 49.881
2024-03-11 | 9:55 | 49.882
2024-03-11 | 9:55 | 49.881
2024-03-11 | 9:55 | 49.881
2024-03-11 | 9:55 | 49.879
2024-03-11 | 9:55 | 49.878 | 130 | HEYM12 | 271.908
2024-03-11 | 9:55 | 49.876 | 228 | HUMR-1 | 303.75
2024-03-11 | 9:55 | 49.875
2024-03-11 | 9:55 | 49.874
2024-03-11 | 9:55 | 49.872
2024-03-11 | 9:55 | 49.873
2024-03-11 | 9:55 | 49.876
2024-03-11 | 9:55 | 49.878
2024-03-11 | 9:55 | 49.875
2024-03-11 | 9:55 | 49.871
2024-03-11 | 9:55 | 49.871
2024-03-11 | 9:56 | 49.87 | 211 | CDCL-1 | 291.5
2024-03-11 | 9:56 | 49.869 | 199 | STAY-2 | 413.125
2024-03-11 | 9:56 | 49.869 | 173 | CDCL-1 | 397.375
2024-03-11 | 9:56 | 49.868 | 248 | SEAB-2 | 361.25
2024-03-11 | 9:56 | 49.867 | 255 | FRANCE | 995.65
2024-03-11 | 9:56 | 49.869 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-11 | 9:56 | 49.872
2024-03-11 | 9:56 | 49.874
2024-03-11 | 9:56 | 49.874
2024-03-11 | 9:56 | 49.876
2024-03-11 | 9:56 | 49.877
2024-03-11 | 9:56 | 49.878
2024-03-11 | 9:56 | 49.879
2024-03-11 | 9:56 | 49.882
2024-03-11 | 9:56 | 49.885
2024-03-11 | 9:56 | 49.887
2024-03-11 | 9:56 | 49.885
2024-03-11 | 9:56 | 49.882
2024-03-11 | 9:56 | 49.881
2024-03-11 | 9:56 | 49.879
2024-03-11 | 9:56 | 49.88
2024-03-11 | 9:56 | 49.881
2024-03-11 | 9:56 | 49.883
2024-03-11 | 9:56 | 49.881
2024-03-11 | 9:56 | 49.879
2024-03-11 | 9:56 | 49.874
2024-03-11 | 9:56 | 49.873
2024-03-11 | 9:56 | 49.871
2024-03-11 | 9:56 | 49.868
2024-03-11 | 9:56 | 49.867
2024-03-11 | 9:56 | 49.869
2024-03-11 | 9:56 | 49.871
2024-03-11 | 9:56 | 49.876
2024-03-11 | 9:56 | 49.883
2024-03-11 | 9:56 | 49.888
2024-03-11 | 9:56 | 49.89
2024-03-11 | 9:56 | 49.888
2024-03-11 | 9:56 | 49.886
2024-03-11 | 9:56 | 49.888
2024-03-11 | 9:56 | 49.891
2024-03-11 | 9:56 | 49.889
2024-03-11 | 9:56 | 49.884
2024-03-11 | 9:56 | 49.855
2024-03-11 | 9:56 | 49.747
2024-03-11 | 9:56 | 49.662
2024-03-11 | 9:56 | 49.638
2024-03-11 | 9:56 | 49.634
2024-03-11 | 9:56 | 49.643
2024-03-11 | 9:56 | 49.647
2024-03-11 | 9:56 | 49.652
2024-03-11 | 9:56 | 49.653
2024-03-11 | 9:56 | 49.649
2024-03-11 | 9:56 | 49.647
2024-03-11 | 9:56 | 49.646
2024-03-11 | 9:56 | 49.645
2024-03-11 | 9:56 | 49.644
2024-03-11 | 9:56 | 49.643
2024-03-11 | 9:56 | 49.645
2024-03-11 | 9:56 | 49.649
2024-03-11 | 9:56 | 49.65
2024-03-11 | 9:56 | 49.651
2024-03-11 | 9:57 | 49.653
2024-03-11 | 9:57 | 49.653
2024-03-11 | 9:57 | 49.653
2024-03-11 | 9:57 | 49.651
2024-03-11 | 9:57 | 49.654
2024-03-11 | 9:57 | 49.659
2024-03-11 | 9:57 | 49.665
2024-03-11 | 9:57 | 49.667
2024-03-11 | 9:57 | 49.669
2024-03-11 | 9:57 | 49.671
2024-03-11 | 9:57 | 49.672
2024-03-11 | 9:57 | 49.669
2024-03-11 | 9:57 | 49.669
2024-03-11 | 9:57 | 49.669
2024-03-11 | 9:57 | 49.667
2024-03-11 | 9:57 | 49.664
2024-03-11 | 9:57 | 49.66
2024-03-11 | 9:57 | 49.661
2024-03-11 | 9:57 | 49.662
2024-03-11 | 9:57 | 49.662
2024-03-11 | 9:57 | 49.657
2024-03-11 | 9:57 | 49.65
2024-03-11 | 9:57 | 49.65
2024-03-11 | 9:57 | 49.648
2024-03-11 | 9:57 | 49.647
2024-03-11 | 9:57 | 49.647
2024-03-11 | 9:57 | 49.645
2024-03-11 | 9:57 | 49.644
2024-03-11 | 9:57 | 49.644
2024-03-11 | 9:57 | 49.645
2024-03-11 | 9:57 | 49.648
2024-03-11 | 9:57 | 49.651
2024-03-11 | 9:57 | 49.651
2024-03-11 | 9:57 | 49.653
2024-03-11 | 9:57 | 49.654
2024-03-11 | 9:57 | 49.659
2024-03-11 | 9:57 | 49.661
2024-03-11 | 9:57 | 49.667
2024-03-11 | 9:57 | 49.672
2024-03-11 | 9:57 | 49.675
2024-03-11 | 9:57 | 49.677
2024-03-11 | 9:57 | 49.679
2024-03-11 | 9:57 | 49.683
2024-03-11 | 9:57 | 49.686
2024-03-11 | 9:57 | 49.691
2024-03-11 | 9:57 | 49.699
2024-03-11 | 9:57 | 49.7
2024-03-11 | 9:57 | 49.704
2024-03-11 | 9:57 | 49.708
2024-03-11 | 9:57 | 49.712
2024-03-11 | 9:57 | 49.718
2024-03-11 | 9:57 | 49.721
2024-03-11 | 9:57 | 49.722
2024-03-11 | 9:57 | 49.725
2024-03-11 | 9:57 | 49.729
2024-03-11 | 9:57 | 49.732
2024-03-11 | 9:57 | 49.736
2024-03-11 | 9:57 | 49.737
2024-03-11 | 9:57 | 49.736
2024-03-11 | 9:58 | 49.735
2024-03-11 | 9:58 | 49.736
2024-03-11 | 9:58 | 49.738
2024-03-11 | 9:58 | 49.739
2024-03-11 | 9:58 | 49.742
2024-03-11 | 9:58 | 49.746
2024-03-11 | 9:58 | 49.749
2024-03-11 | 9:58 | 49.753
2024-03-11 | 9:58 | 49.755
2024-03-11 | 9:58 | 49.759
2024-03-11 | 9:58 | 49.763
2024-03-11 | 9:58 | 49.763
2024-03-11 | 9:58 | 49.767
2024-03-11 | 9:58 | 49.769
2024-03-11 | 9:58 | 49.768
2024-03-11 | 9:58 | 49.767
2024-03-11 | 9:58 | 49.768
2024-03-11 | 9:58 | 49.768
2024-03-11 | 9:58 | 49.769
2024-03-11 | 9:58 | 49.769
2024-03-11 | 9:58 | 49.767
2024-03-11 | 9:58 | 49.77
2024-03-11 | 9:58 | 49.771
2024-03-11 | 9:58 | 49.772
2024-03-11 | 9:58 | 49.775
2024-03-11 | 9:58 | 49.774
2024-03-11 | 9:58 | 49.774
2024-03-11 | 9:58 | 49.772
2024-03-11 | 9:58 | 49.774
2024-03-11 | 9:58 | 49.774
2024-03-11 | 9:58 | 49.772
2024-03-11 | 9:58 | 49.768
2024-03-11 | 9:58 | 49.766
2024-03-11 | 9:58 | 49.767
2024-03-11 | 9:58 | 49.771
2024-03-11 | 9:58 | 49.773
2024-03-11 | 9:58 | 49.777
2024-03-11 | 9:58 | 49.778
2024-03-11 | 9:58 | 49.777
2024-03-11 | 9:58 | 49.777
2024-03-11 | 9:58 | 49.777
2024-03-11 | 9:58 | 49.778
2024-03-11 | 9:58 | 49.779
2024-03-11 | 9:58 | 49.781
2024-03-11 | 9:58 | 49.784
2024-03-11 | 9:58 | 49.786
2024-03-11 | 9:58 | 49.791
2024-03-11 | 9:58 | 49.795
2024-03-11 | 9:58 | 49.8
2024-03-11 | 9:58 | 49.809
2024-03-11 | 9:58 | 49.815
2024-03-11 | 9:58 | 49.823
2024-03-11 | 9:58 | 49.83
2024-03-11 | 9:58 | 49.838
2024-03-11 | 9:58 | 49.841
2024-03-11 | 9:58 | 49.847
2024-03-11 | 9:58 | 49.851
2024-03-11 | 9:58 | 49.855
2024-03-11 | 9:58 | 49.859
2024-03-11 | 9:58 | 49.864
2024-03-11 | 9:58 | 49.869
2024-03-11 | 9:59 | 49.872
2024-03-11 | 9:59 | 49.875
2024-03-11 | 9:59 | 49.877
2024-03-11 | 9:59 | 49.878
2024-03-11 | 9:59 | 49.882
2024-03-11 | 9:59 | 49.884
2024-03-11 | 9:59 | 49.885
2024-03-11 | 9:59 | 49.885
2024-03-11 | 9:59 | 49.887
2024-03-11 | 9:59 | 49.889
2024-03-11 | 9:59 | 49.89
2024-03-11 | 9:59 | 49.894
2024-03-11 | 9:59 | 49.895
2024-03-11 | 9:59 | 49.897
2024-03-11 | 9:59 | 49.897
2024-03-11 | 9:59 | 49.897
2024-03-11 | 9:59 | 49.896
2024-03-11 | 9:59 | 49.898
2024-03-11 | 9:59 | 49.897
2024-03-11 | 9:59 | 49.896
2024-03-11 | 9:59 | 49.896
2024-03-11 | 9:59 | 49.895
2024-03-11 | 9:59 | 49.894
2024-03-11 | 9:59 | 49.894
2024-03-11 | 9:59 | 49.896
2024-03-11 | 9:59 | 49.898
2024-03-11 | 9:59 | 49.899
2024-03-11 | 9:59 | 49.901
2024-03-11 | 9:59 | 49.902
2024-03-11 | 9:59 | 49.902
2024-03-11 | 9:59 | 49.901
2024-03-11 | 9:59 | 49.901
2024-03-11 | 9:59 | 49.9
2024-03-11 | 9:59 | 49.898
2024-03-11 | 9:59 | 49.9
2024-03-11 | 9:59 | 49.899
2024-03-11 | 9:59 | 49.899
2024-03-11 | 9:59 | 49.898
2024-03-11 | 9:59 | 49.899
2024-03-11 | 9:59 | 49.899
2024-03-11 | 9:59 | 49.899
2024-03-11 | 9:59 | 49.9
2024-03-11 | 9:59 | 49.901
2024-03-11 | 9:59 | 49.902
2024-03-11 | 9:59 | 49.903
2024-03-11 | 9:59 | 49.903
2024-03-11 | 9:59 | 49.905
2024-03-11 | 9:59 | 49.905
2024-03-11 | 9:59 | 49.907
2024-03-11 | 9:59 | 49.909
2024-03-11 | 9:59 | 49.911
2024-03-11 | 9:59 | 49.912
2024-03-11 | 9:59 | 49.912
2024-03-11 | 9:59 | 49.913
2024-03-11 | 9:59 | 49.915
2024-03-11 | 9:59 | 49.916
2024-03-11 | 9:59 | 49.917
2024-03-11 | 9:59 | 49.918
2024-03-11 | 9:59 | 49.918
2024-03-11 | 10:00 | 49.919
2024-03-11 | 10:00 | 49.92
2024-03-11 | 10:00 | 49.922
2024-03-11 | 10:00 | 49.924
2024-03-11 | 10:00 | 49.927
2024-03-11 | 10:00 | 49.928
2024-03-11 | 10:00 | 49.929
2024-03-11 | 10:00 | 49.928
2024-03-11 | 10:00 | 49.927
2024-03-11 | 10:00 | 49.927
2024-03-11 | 10:00 | 49.928
2024-03-11 | 10:00 | 49.927
2024-03-11 | 10:00 | 49.924
2024-03-11 | 10:00 | 49.922
2024-03-11 | 10:00 | 49.922
2024-03-11 | 10:00 | 49.925
2024-03-11 | 10:00 | 49.925
2024-03-11 | 10:00 | 49.929
2024-03-11 | 10:00 | 49.931
2024-03-11 | 10:00 | 49.935
2024-03-11 | 10:00 | 49.938
2024-03-11 | 10:00 | 49.94
2024-03-11 | 10:00 | 49.942
2024-03-11 | 10:00 | 49.944
2024-03-11 | 10:00 | 49.946
2024-03-11 | 10:00 | 49.947
2024-03-11 | 10:00 | 49.947
2024-03-11 | 10:00 | 49.948
2024-03-11 | 10:00 | 49.948
2024-03-11 | 10:00 | 49.951
2024-03-11 | 10:00 | 49.951
2024-03-11 | 10:00 | 49.946
2024-03-11 | 10:00 | 49.941
2024-03-11 | 10:00 | 49.936
2024-03-11 | 10:00 | 49.934
2024-03-11 | 10:00 | 49.931
2024-03-11 | 10:00 | 49.931
2024-03-11 | 10:00 | 49.933
2024-03-11 | 10:00 | 49.936
2024-03-11 | 10:00 | 49.938
2024-03-11 | 10:00 | 49.936
2024-03-11 | 10:00 | 49.935
2024-03-11 | 10:00 | 49.933
2024-03-11 | 10:00 | 49.931
2024-03-11 | 10:00 | 49.93
2024-03-11 | 10:00 | 49.93
2024-03-11 | 10:00 | 49.931
2024-03-11 | 10:00 | 49.93
2024-03-11 | 10:00 | 49.931
2024-03-11 | 10:00 | 49.931
2024-03-11 | 10:00 | 49.93
2024-03-11 | 10:00 | 49.93
2024-03-11 | 10:00 | 49.932
2024-03-11 | 10:00 | 49.931
2024-03-11 | 10:00 | 49.931
2024-03-11 | 10:00 | 49.935
2024-03-11 | 10:00 | 49.936
2024-03-11 | 10:00 | 49.935
2024-03-11 | 10:00 | 49.934
2024-03-11 | 10:00 | 49.935
2024-03-11 | 10:00 | 49.935
2024-03-11 | 10:01 | 49.937
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.938
2024-03-11 | 10:01 | 49.938
2024-03-11 | 10:01 | 49.939
2024-03-11 | 10:01 | 49.938
2024-03-11 | 10:01 | 49.937
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.935
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.938
2024-03-11 | 10:01 | 49.938
2024-03-11 | 10:01 | 49.938
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.934
2024-03-11 | 10:01 | 49.933
2024-03-11 | 10:01 | 49.933
2024-03-11 | 10:01 | 49.934
2024-03-11 | 10:01 | 49.934
2024-03-11 | 10:01 | 49.932
2024-03-11 | 10:01 | 49.93
2024-03-11 | 10:01 | 49.928
2024-03-11 | 10:01 | 49.926
2024-03-11 | 10:01 | 49.924
2024-03-11 | 10:01 | 49.925
2024-03-11 | 10:01 | 49.925
2024-03-11 | 10:01 | 49.925
2024-03-11 | 10:01 | 49.927
2024-03-11 | 10:01 | 49.928
2024-03-11 | 10:01 | 49.93
2024-03-11 | 10:01 | 49.933
2024-03-11 | 10:01 | 49.933
2024-03-11 | 10:01 | 49.934
2024-03-11 | 10:01 | 49.934
2024-03-11 | 10:01 | 49.935
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.937
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.937
2024-03-11 | 10:01 | 49.938
2024-03-11 | 10:01 | 49.936
2024-03-11 | 10:01 | 49.934
2024-03-11 | 10:01 | 49.934
2024-03-11 | 10:01 | 49.931
2024-03-11 | 10:01 | 49.931
2024-03-11 | 10:01 | 49.929
2024-03-11 | 10:01 | 49.93
2024-03-11 | 10:01 | 49.93
2024-03-11 | 10:01 | 49.932
2024-03-11 | 10:01 | 49.934
2024-03-11 | 10:01 | 49.933
2024-03-11 | 10:01 | 49.934
2024-03-11 | 10:01 | 49.935
2024-03-11 | 10:01 | 49.937
2024-03-11 | 10:01 | 49.939
2024-03-11 | 10:02 | 49.939
2024-03-11 | 10:02 | 49.939
2024-03-11 | 10:02 | 49.938
2024-03-11 | 10:02 | 49.934
2024-03-11 | 10:02 | 49.931
2024-03-11 | 10:02 | 49.928
2024-03-11 | 10:02 | 49.927
2024-03-11 | 10:02 | 49.926
2024-03-11 | 10:02 | 49.928
2024-03-11 | 10:02 | 49.928
2024-03-11 | 10:02 | 49.931
2024-03-11 | 10:02 | 49.935
2024-03-11 | 10:02 | 49.939
2024-03-11 | 10:02 | 49.945
2024-03-11 | 10:02 | 49.95
2024-03-11 | 10:02 | 49.953
2024-03-11 | 10:02 | 49.954
2024-03-11 | 10:02 | 49.953
2024-03-11 | 10:02 | 49.952
2024-03-11 | 10:02 | 49.952
2024-03-11 | 10:02 | 49.95
2024-03-11 | 10:02 | 49.949
2024-03-11 | 10:02 | 49.946
2024-03-11 | 10:02 | 49.941
2024-03-11 | 10:02 | 49.939
2024-03-11 | 10:02 | 49.938
2024-03-11 | 10:02 | 49.935
2024-03-11 | 10:02 | 49.933
2024-03-11 | 10:02 | 49.933
2024-03-11 | 10:02 | 49.93
2024-03-11 | 10:02 | 49.929
2024-03-11 | 10:02 | 49.929
2024-03-11 | 10:02 | 49.931
2024-03-11 | 10:02 | 49.93
2024-03-11 | 10:02 | 49.934
2024-03-11 | 10:02 | 49.937
2024-03-11 | 10:02 | 49.939
2024-03-11 | 10:02 | 49.939
2024-03-11 | 10:02 | 49.94
2024-03-11 | 10:02 | 49.942
2024-03-11 | 10:02 | 49.945
2024-03-11 | 10:02 | 49.948
2024-03-11 | 10:02 | 49.95
2024-03-11 | 10:02 | 49.951
2024-03-11 | 10:02 | 49.95
2024-03-11 | 10:02 | 49.952
2024-03-11 | 10:02 | 49.955
2024-03-11 | 10:02 | 49.958
2024-03-11 | 10:02 | 49.962
2024-03-11 | 10:02 | 49.962
2024-03-11 | 10:02 | 49.965
2024-03-11 | 10:02 | 49.964
2024-03-11 | 10:02 | 49.966
2024-03-11 | 10:02 | 49.968
2024-03-11 | 10:02 | 49.966
2024-03-11 | 10:02 | 49.964
2024-03-11 | 10:02 | 49.96
2024-03-11 | 10:02 | 49.96
2024-03-11 | 10:02 | 49.959
2024-03-11 | 10:02 | 49.957
2024-03-11 | 10:02 | 49.955
2024-03-11 | 10:03 | 49.955
2024-03-11 | 10:03 | 49.954
2024-03-11 | 10:03 | 49.956
2024-03-11 | 10:03 | 49.958
2024-03-11 | 10:03 | 49.96
2024-03-11 | 10:03 | 49.964
2024-03-11 | 10:03 | 49.967
2024-03-11 | 10:03 | 49.968
2024-03-11 | 10:03 | 49.97
2024-03-11 | 10:03 | 49.974
2024-03-11 | 10:03 | 49.976
2024-03-11 | 10:03 | 49.979
2024-03-11 | 10:03 | 49.98
2024-03-11 | 10:03 | 49.982
2024-03-11 | 10:03 | 49.982
2024-03-11 | 10:03 | 49.984
2024-03-11 | 10:03 | 49.984
2024-03-11 | 10:03 | 49.985
2024-03-11 | 10:03 | 49.987
2024-03-11 | 10:03 | 49.986
2024-03-11 | 10:03 | 49.983
2024-03-11 | 10:03 | 49.983
2024-03-11 | 10:03 | 49.982
2024-03-11 | 10:03 | 49.982
2024-03-11 | 10:03 | 49.98
2024-03-11 | 10:03 | 49.978
2024-03-11 | 10:03 | 49.978
2024-03-11 | 10:03 | 49.977
2024-03-11 | 10:03 | 49.977
2024-03-11 | 10:03 | 49.976
2024-03-11 | 10:03 | 49.974
2024-03-11 | 10:03 | 49.977
2024-03-11 | 10:03 | 49.981
2024-03-11 | 10:03 | 49.984
2024-03-11 | 10:03 | 49.988
2024-03-11 | 10:03 | 49.991
2024-03-11 | 10:03 | 49.995
2024-03-11 | 10:03 | 49.996
2024-03-11 | 10:03 | 49.995
2024-03-11 | 10:03 | 49.997
2024-03-11 | 10:03 | 49.997
2024-03-11 | 10:03 | 49.997
2024-03-11 | 10:03 | 49.997
2024-03-11 | 10:03 | 49.997
2024-03-11 | 10:03 | 49.998
2024-03-11 | 10:03 | 49.999
2024-03-11 | 10:03 | 50.001
2024-03-11 | 10:03 | 50
2024-03-11 | 10:03 | 49.998
2024-03-11 | 10:03 | 49.997
2024-03-11 | 10:03 | 49.996
2024-03-11 | 10:03 | 49.996
2024-03-11 | 10:03 | 49.996
2024-03-11 | 10:03 | 49.998
2024-03-11 | 10:03 | 50.001
2024-03-11 | 10:03 | 50.002
2024-03-11 | 10:03 | 50.005
2024-03-11 | 10:03 | 50.007
2024-03-11 | 10:03 | 50.009
2024-03-11 | 10:04 | 50.012
2024-03-11 | 10:04 | 50.014
2024-03-11 | 10:04 | 50.017
2024-03-11 | 10:04 | 50.02
2024-03-11 | 10:04 | 50.024
2024-03-11 | 10:04 | 50.026
2024-03-11 | 10:04 | 50.025
2024-03-11 | 10:04 | 50.025
2024-03-11 | 10:04 | 50.026
2024-03-11 | 10:04 | 50.026
2024-03-11 | 10:04 | 50.026
2024-03-11 | 10:04 | 50.028
2024-03-11 | 10:04 | 50.031
2024-03-11 | 10:04 | 50.033
2024-03-11 | 10:04 | 50.034
2024-03-11 | 10:04 | 50.034
2024-03-11 | 10:04 | 50.032
2024-03-11 | 10:04 | 50.031
2024-03-11 | 10:04 | 50.028
2024-03-11 | 10:04 | 50.026
2024-03-11 | 10:04 | 50.025
2024-03-11 | 10:04 | 50.025
2024-03-11 | 10:04 | 50.025
2024-03-11 | 10:04 | 50.025
2024-03-11 | 10:04 | 50.023
2024-03-11 | 10:04 | 50.022
2024-03-11 | 10:04 | 50.023
2024-03-11 | 10:04 | 50.024
2024-03-11 | 10:04 | 50.026
2024-03-11 | 10:04 | 50.027
2024-03-11 | 10:04 | 50.027
2024-03-11 | 10:04 | 50.028
2024-03-11 | 10:04 | 50.028
2024-03-11 | 10:04 | 50.029
2024-03-11 | 10:04 | 50.029
2024-03-11 | 10:04 | 50.031
2024-03-11 | 10:04 | 50.033
2024-03-11 | 10:04 | 50.035
2024-03-11 | 10:04 | 50.037
2024-03-11 | 10:04 | 50.036
2024-03-11 | 10:04 | 50.035
2024-03-11 | 10:04 | 50.034
2024-03-11 | 10:04 | 50.03
2024-03-11 | 10:04 | 50.028
2024-03-11 | 10:04 | 50.026
2024-03-11 | 10:04 | 50.021
2024-03-11 | 10:04 | 50.018
2024-03-11 | 10:04 | 50.015
2024-03-11 | 10:04 | 50.014
2024-03-11 | 10:04 | 50.012
2024-03-11 | 10:04 | 50.012
2024-03-11 | 10:04 | 50.012
2024-03-11 | 10:04 | 50.014
2024-03-11 | 10:04 | 50.012
2024-03-11 | 10:04 | 50.015
2024-03-11 | 10:04 | 50.015
2024-03-11 | 10:04 | 50.02
2024-03-11 | 10:04 | 50.021
2024-03-11 | 10:04 | 50.021
2024-03-11 | 10:04 | 50.018
2024-03-11 | 10:04 | 50.015
2024-03-11 | 10:05 | 50.013
2024-03-11 | 10:05 | 50.008
2024-03-11 | 10:05 | 50.005
2024-03-11 | 10:05 | 50.001
2024-03-11 | 10:05 | 49.998
2024-03-11 | 10:05 | 49.995
2024-03-11 | 10:05 | 49.99
2024-03-11 | 10:05 | 49.988
2024-03-11 | 10:05 | 49.985
2024-03-11 | 10:05 | 49.986
2024-03-11 | 10:05 | 49.986
2024-03-11 | 10:05 | 49.988
2024-03-11 | 10:05 | 49.988
2024-03-11 | 10:05 | 49.99
2024-03-11 | 10:05 | 49.992
2024-03-11 | 10:05 | 49.997
2024-03-11 | 10:05 | 50.002
2024-03-11 | 10:05 | 50.01
2024-03-11 | 10:05 | 50.017
2024-03-11 | 10:05 | 50.027
2024-03-11 | 10:05 | 50.036
2024-03-11 | 10:05 | 50.041
2024-03-11 | 10:05 | 50.047
2024-03-11 | 10:05 | 50.052
2024-03-11 | 10:05 | 50.054
2024-03-11 | 10:05 | 50.053
2024-03-11 | 10:05 | 50.053
2024-03-11 | 10:05 | 50.053
2024-03-11 | 10:05 | 50.054

## 20240313-1
In GMT
Date | Time | Freq
2024-03-13 | 15:29 | 50.108 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-13 | 15:29 | 50.104 | 222 | BRITNED | 676.211
2024-03-13 | 15:29 | 50.101 | 268 | WBURB-2 | 428.156
2024-03-13 | 15:29 | 50.103 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-13 | 15:29 | 50.104 |  | Viking Link | -648.9
2024-03-13 | 15:29 | 50.104 |  | Viking Link | 1398.96
2024-03-13 | 15:29 | 50.101 | 209 | DRAXX-3 | 626.95
2024-03-13 | 15:29 | 50.098 | 154 | CDCL-1 | 391.57
2024-03-13 | 15:29 | 50.098 | 268 | ROCK-1 | 468.495
2024-03-13 | 15:29 | 50.097 | 148 | IFA Bipole1 | 945.473
2024-03-13 | 15:29 | 50.096 | 132 | IFA Bipole1 | 999.1
2024-03-13 | 15:29 | 50.097 | 141 | IFA Bipole2 | 1000
2024-03-13 | 15:29 | 50.098 | 135 | IFA Bipole1 | 996.75
2024-03-13 | 15:29 | 50.098 |  | Viking Link | -780.3
2024-03-13 | 15:29 | 50.099
2024-03-13 | 15:29 | 50.098
2024-03-13 | 15:29 | 50.099
2024-03-13 | 15:29 | 50.102
2024-03-13 | 15:29 | 50.102
2024-03-13 | 15:29 | 50.107 | 130 | HEYM12 | 271.908
2024-03-13 | 15:29 | 50.11 | 228 | HUMR-1 | 303.75
2024-03-13 | 15:29 | 50.113
2024-03-13 | 15:29 | 50.115
2024-03-13 | 15:29 | 50.116
2024-03-13 | 15:29 | 50.114
2024-03-13 | 15:29 | 50.114
2024-03-13 | 15:29 | 50.115
2024-03-13 | 15:29 | 50.115
2024-03-13 | 15:29 | 50.115
2024-03-13 | 15:29 | 50.116
2024-03-13 | 15:30 | 50.117 | 211 | CDCL-1 | 291.5
2024-03-13 | 15:30 | 50.12 | 199 | STAY-2 | 413.125
2024-03-13 | 15:30 | 50.123 | 173 | CDCL-1 | 397.375
2024-03-13 | 15:30 | 50.124 | 248 | SEAB-2 | 361.25
2024-03-13 | 15:30 | 50.123 | 255 | FRANCE | 995.65
2024-03-13 | 15:30 | 50.125 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-13 | 15:30 | 50.124
2024-03-13 | 15:30 | 50.124
2024-03-13 | 15:30 | 50.124
2024-03-13 | 15:30 | 50.126
2024-03-13 | 15:30 | 50.125
2024-03-13 | 15:30 | 50.127
2024-03-13 | 15:30 | 50.127
2024-03-13 | 15:30 | 50.13
2024-03-13 | 15:30 | 50.13
2024-03-13 | 15:30 | 50.13
2024-03-13 | 15:30 | 50.129
2024-03-13 | 15:30 | 50.129
2024-03-13 | 15:30 | 50.13
2024-03-13 | 15:30 | 50.13
2024-03-13 | 15:30 | 50.132
2024-03-13 | 15:30 | 50.134
2024-03-13 | 15:30 | 50.136
2024-03-13 | 15:30 | 50.136
2024-03-13 | 15:30 | 50.135
2024-03-13 | 15:30 | 50.135
2024-03-13 | 15:30 | 50.132
2024-03-13 | 15:30 | 50.13
2024-03-13 | 15:30 | 50.127
2024-03-13 | 15:30 | 50.126
2024-03-13 | 15:30 | 50.127
2024-03-13 | 15:30 | 50.134
2024-03-13 | 15:30 | 50.136
2024-03-13 | 15:30 | 50.137
2024-03-13 | 15:30 | 50.138
2024-03-13 | 15:30 | 50.136
2024-03-13 | 15:30 | 50.132
2024-03-13 | 15:30 | 50.131
2024-03-13 | 15:30 | 50.13
2024-03-13 | 15:30 | 50.126
2024-03-13 | 15:30 | 50.126
2024-03-13 | 15:30 | 50.123
2024-03-13 | 15:30 | 50.122
2024-03-13 | 15:30 | 50.12
2024-03-13 | 15:30 | 50.117
2024-03-13 | 15:30 | 50.114
2024-03-13 | 15:30 | 50.114
2024-03-13 | 15:30 | 50.115
2024-03-13 | 15:30 | 50.115
2024-03-13 | 15:30 | 50.118
2024-03-13 | 15:30 | 50.104
2024-03-13 | 15:30 | 50.033
2024-03-13 | 15:30 | 49.988
2024-03-13 | 15:30 | 49.956
2024-03-13 | 15:30 | 49.936
2024-03-13 | 15:30 | 49.924
2024-03-13 | 15:30 | 49.919
2024-03-13 | 15:30 | 49.914
2024-03-13 | 15:30 | 49.916
2024-03-13 | 15:30 | 49.918
2024-03-13 | 15:30 | 49.918
2024-03-13 | 15:31 | 49.919
2024-03-13 | 15:31 | 49.918
2024-03-13 | 15:31 | 49.918
2024-03-13 | 15:31 | 49.915
2024-03-13 | 15:31 | 49.916
2024-03-13 | 15:31 | 49.918
2024-03-13 | 15:31 | 49.92
2024-03-13 | 15:31 | 49.922
2024-03-13 | 15:31 | 49.921
2024-03-13 | 15:31 | 49.92
2024-03-13 | 15:31 | 49.916
2024-03-13 | 15:31 | 49.918
2024-03-13 | 15:31 | 49.918
2024-03-13 | 15:31 | 49.921
2024-03-13 | 15:31 | 49.923
2024-03-13 | 15:31 | 49.922
2024-03-13 | 15:31 | 49.922
2024-03-13 | 15:31 | 49.921
2024-03-13 | 15:31 | 49.918
2024-03-13 | 15:31 | 49.917
2024-03-13 | 15:31 | 49.915
2024-03-13 | 15:31 | 49.913
2024-03-13 | 15:31 | 49.91
2024-03-13 | 15:31 | 49.906
2024-03-13 | 15:31 | 49.901
2024-03-13 | 15:31 | 49.895
2024-03-13 | 15:31 | 49.891
2024-03-13 | 15:31 | 49.889
2024-03-13 | 15:31 | 49.889
2024-03-13 | 15:31 | 49.889
2024-03-13 | 15:31 | 49.887
2024-03-13 | 15:31 | 49.888
2024-03-13 | 15:31 | 49.889
2024-03-13 | 15:31 | 49.89
2024-03-13 | 15:31 | 49.892
2024-03-13 | 15:31 | 49.893
2024-03-13 | 15:31 | 49.892
2024-03-13 | 15:31 | 49.888
2024-03-13 | 15:31 | 49.885
2024-03-13 | 15:31 | 49.883
2024-03-13 | 15:31 | 49.879
2024-03-13 | 15:31 | 49.878
2024-03-13 | 15:31 | 49.877
2024-03-13 | 15:31 | 49.875
2024-03-13 | 15:31 | 49.872
2024-03-13 | 15:31 | 49.873
2024-03-13 | 15:31 | 49.873
2024-03-13 | 15:31 | 49.877
2024-03-13 | 15:31 | 49.878
2024-03-13 | 15:31 | 49.879
2024-03-13 | 15:31 | 49.881
2024-03-13 | 15:31 | 49.881
2024-03-13 | 15:31 | 49.884
2024-03-13 | 15:31 | 49.885
2024-03-13 | 15:31 | 49.885
2024-03-13 | 15:31 | 49.887
2024-03-13 | 15:31 | 49.889
2024-03-13 | 15:31 | 49.89
2024-03-13 | 15:31 | 49.892
2024-03-13 | 15:32 | 49.892
2024-03-13 | 15:32 | 49.89
2024-03-13 | 15:32 | 49.89
2024-03-13 | 15:32 | 49.89
2024-03-13 | 15:32 | 49.889
2024-03-13 | 15:32 | 49.888
2024-03-13 | 15:32 | 49.887
2024-03-13 | 15:32 | 49.885
2024-03-13 | 15:32 | 49.882
2024-03-13 | 15:32 | 49.878
2024-03-13 | 15:32 | 49.875
2024-03-13 | 15:32 | 49.873
2024-03-13 | 15:32 | 49.87
2024-03-13 | 15:32 | 49.867
2024-03-13 | 15:32 | 49.865
2024-03-13 | 15:32 | 49.866
2024-03-13 | 15:32 | 49.867
2024-03-13 | 15:32 | 49.871
2024-03-13 | 15:32 | 49.874
2024-03-13 | 15:32 | 49.874
2024-03-13 | 15:32 | 49.877
2024-03-13 | 15:32 | 49.879
2024-03-13 | 15:32 | 49.881
2024-03-13 | 15:32 | 49.884
2024-03-13 | 15:32 | 49.885
2024-03-13 | 15:32 | 49.885
2024-03-13 | 15:32 | 49.887
2024-03-13 | 15:32 | 49.887
2024-03-13 | 15:32 | 49.887
2024-03-13 | 15:32 | 49.881
2024-03-13 | 15:32 | 49.877
2024-03-13 | 15:32 | 49.872
2024-03-13 | 15:32 | 49.87
2024-03-13 | 15:32 | 49.872
2024-03-13 | 15:32 | 49.872
2024-03-13 | 15:32 | 49.871
2024-03-13 | 15:32 | 49.87
2024-03-13 | 15:32 | 49.872
2024-03-13 | 15:32 | 49.873
2024-03-13 | 15:32 | 49.871
2024-03-13 | 15:32 | 49.874
2024-03-13 | 15:32 | 49.874
2024-03-13 | 15:32 | 49.878
2024-03-13 | 15:32 | 49.88
2024-03-13 | 15:32 | 49.884
2024-03-13 | 15:32 | 49.884
2024-03-13 | 15:32 | 49.883
2024-03-13 | 15:32 | 49.885
2024-03-13 | 15:32 | 49.888
2024-03-13 | 15:32 | 49.89
2024-03-13 | 15:32 | 49.894
2024-03-13 | 15:32 | 49.894
2024-03-13 | 15:32 | 49.896
2024-03-13 | 15:32 | 49.896
2024-03-13 | 15:32 | 49.897
2024-03-13 | 15:32 | 49.898
2024-03-13 | 15:32 | 49.903
2024-03-13 | 15:32 | 49.903
2024-03-13 | 15:32 | 49.902
2024-03-13 | 15:32 | 49.902
2024-03-13 | 15:32 | 49.902
2024-03-13 | 15:33 | 49.903
2024-03-13 | 15:33 | 49.901
2024-03-13 | 15:33 | 49.898
2024-03-13 | 15:33 | 49.897
2024-03-13 | 15:33 | 49.895
2024-03-13 | 15:33 | 49.895
2024-03-13 | 15:33 | 49.897
2024-03-13 | 15:33 | 49.899
2024-03-13 | 15:33 | 49.898
2024-03-13 | 15:33 | 49.899
2024-03-13 | 15:33 | 49.9
2024-03-13 | 15:33 | 49.9
2024-03-13 | 15:33 | 49.901
2024-03-13 | 15:33 | 49.902
2024-03-13 | 15:33 | 49.902
2024-03-13 | 15:33 | 49.901
2024-03-13 | 15:33 | 49.9
2024-03-13 | 15:33 | 49.896
2024-03-13 | 15:33 | 49.892
2024-03-13 | 15:33 | 49.89
2024-03-13 | 15:33 | 49.887
2024-03-13 | 15:33 | 49.89
2024-03-13 | 15:33 | 49.893
2024-03-13 | 15:33 | 49.897
2024-03-13 | 15:33 | 49.9
2024-03-13 | 15:33 | 49.905
2024-03-13 | 15:33 | 49.904
2024-03-13 | 15:33 | 49.906
2024-03-13 | 15:33 | 49.907
2024-03-13 | 15:33 | 49.906
2024-03-13 | 15:33 | 49.901
2024-03-13 | 15:33 | 49.9
2024-03-13 | 15:33 | 49.896
2024-03-13 | 15:33 | 49.895
2024-03-13 | 15:33 | 49.897
2024-03-13 | 15:33 | 49.895
2024-03-13 | 15:33 | 49.897
2024-03-13 | 15:33 | 49.897
2024-03-13 | 15:33 | 49.897
2024-03-13 | 15:33 | 49.901
2024-03-13 | 15:33 | 49.904
2024-03-13 | 15:33 | 49.904
2024-03-13 | 15:33 | 49.906
2024-03-13 | 15:33 | 49.908
2024-03-13 | 15:33 | 49.908
2024-03-13 | 15:33 | 49.909
2024-03-13 | 15:33 | 49.908
2024-03-13 | 15:33 | 49.907
2024-03-13 | 15:33 | 49.906
2024-03-13 | 15:33 | 49.906
2024-03-13 | 15:33 | 49.909
2024-03-13 | 15:33 | 49.912
2024-03-13 | 15:33 | 49.913
2024-03-13 | 15:33 | 49.913
2024-03-13 | 15:33 | 49.915
2024-03-13 | 15:33 | 49.915
2024-03-13 | 15:33 | 49.916
2024-03-13 | 15:33 | 49.911
2024-03-13 | 15:33 | 49.909
2024-03-13 | 15:34 | 49.907
2024-03-13 | 15:34 | 49.905
2024-03-13 | 15:34 | 49.906
2024-03-13 | 15:34 | 49.91
2024-03-13 | 15:34 | 49.912
2024-03-13 | 15:34 | 49.915
2024-03-13 | 15:34 | 49.918
2024-03-13 | 15:34 | 49.918
2024-03-13 | 15:34 | 49.92
2024-03-13 | 15:34 | 49.916
2024-03-13 | 15:34 | 49.916
2024-03-13 | 15:34 | 49.917
2024-03-13 | 15:34 | 49.919
2024-03-13 | 15:34 | 49.921
2024-03-13 | 15:34 | 49.922
2024-03-13 | 15:34 | 49.925
2024-03-13 | 15:34 | 49.926
2024-03-13 | 15:34 | 49.928
2024-03-13 | 15:34 | 49.93
2024-03-13 | 15:34 | 49.931
2024-03-13 | 15:34 | 49.932
2024-03-13 | 15:34 | 49.935
2024-03-13 | 15:34 | 49.937
2024-03-13 | 15:34 | 49.937
2024-03-13 | 15:34 | 49.937
2024-03-13 | 15:34 | 49.936
2024-03-13 | 15:34 | 49.934
2024-03-13 | 15:34 | 49.931
2024-03-13 | 15:34 | 49.926
2024-03-13 | 15:34 | 49.924
2024-03-13 | 15:34 | 49.921
2024-03-13 | 15:34 | 49.919
2024-03-13 | 15:34 | 49.918
2024-03-13 | 15:34 | 49.918
2024-03-13 | 15:34 | 49.918
2024-03-13 | 15:34 | 49.918
2024-03-13 | 15:34 | 49.919
2024-03-13 | 15:34 | 49.919
2024-03-13 | 15:34 | 49.92
2024-03-13 | 15:34 | 49.92
2024-03-13 | 15:34 | 49.92
2024-03-13 | 15:34 | 49.92
2024-03-13 | 15:34 | 49.922
2024-03-13 | 15:34 | 49.924
2024-03-13 | 15:34 | 49.927
2024-03-13 | 15:34 | 49.925
2024-03-13 | 15:34 | 49.923
2024-03-13 | 15:34 | 49.924
2024-03-13 | 15:34 | 49.922
2024-03-13 | 15:34 | 49.919
2024-03-13 | 15:34 | 49.917
2024-03-13 | 15:34 | 49.919
2024-03-13 | 15:34 | 49.923
2024-03-13 | 15:34 | 49.922
2024-03-13 | 15:34 | 49.923
2024-03-13 | 15:34 | 49.922
2024-03-13 | 15:34 | 49.921
2024-03-13 | 15:34 | 49.918
2024-03-13 | 15:34 | 49.919
2024-03-13 | 15:34 | 49.92
2024-03-13 | 15:34 | 49.924
2024-03-13 | 15:35 | 49.925
2024-03-13 | 15:35 | 49.926
2024-03-13 | 15:35 | 49.929
2024-03-13 | 15:35 | 49.93
2024-03-13 | 15:35 | 49.929
2024-03-13 | 15:35 | 49.93
2024-03-13 | 15:35 | 49.933
2024-03-13 | 15:35 | 49.935
2024-03-13 | 15:35 | 49.938
2024-03-13 | 15:35 | 49.936
2024-03-13 | 15:35 | 49.932
2024-03-13 | 15:35 | 49.932
2024-03-13 | 15:35 | 49.932
2024-03-13 | 15:35 | 49.932
2024-03-13 | 15:35 | 49.933
2024-03-13 | 15:35 | 49.936
2024-03-13 | 15:35 | 49.937
2024-03-13 | 15:35 | 49.935
2024-03-13 | 15:35 | 49.936
2024-03-13 | 15:35 | 49.935
2024-03-13 | 15:35 | 49.936
2024-03-13 | 15:35 | 49.94
2024-03-13 | 15:35 | 49.941
2024-03-13 | 15:35 | 49.94
2024-03-13 | 15:35 | 49.942
2024-03-13 | 15:35 | 49.939
2024-03-13 | 15:35 | 49.938
2024-03-13 | 15:35 | 49.937
2024-03-13 | 15:35 | 49.938
2024-03-13 | 15:35 | 49.943
2024-03-13 | 15:35 | 49.943
2024-03-13 | 15:35 | 49.944
2024-03-13 | 15:35 | 49.945
2024-03-13 | 15:35 | 49.946
2024-03-13 | 15:35 | 49.944
2024-03-13 | 15:35 | 49.941
2024-03-13 | 15:35 | 49.937
2024-03-13 | 15:35 | 49.936
2024-03-13 | 15:35 | 49.931
2024-03-13 | 15:35 | 49.928
2024-03-13 | 15:35 | 49.927
2024-03-13 | 15:35 | 49.926
2024-03-13 | 15:35 | 49.923
2024-03-13 | 15:35 | 49.923
2024-03-13 | 15:35 | 49.921
2024-03-13 | 15:35 | 49.92
2024-03-13 | 15:35 | 49.921
2024-03-13 | 15:35 | 49.924
2024-03-13 | 15:35 | 49.927
2024-03-13 | 15:35 | 49.927
2024-03-13 | 15:35 | 49.926
2024-03-13 | 15:35 | 49.925
2024-03-13 | 15:35 | 49.919
2024-03-13 | 15:35 | 49.914
2024-03-13 | 15:35 | 49.91
2024-03-13 | 15:35 | 49.903
2024-03-13 | 15:35 | 49.898
2024-03-13 | 15:35 | 49.894
2024-03-13 | 15:35 | 49.891
2024-03-13 | 15:36 | 49.891
2024-03-13 | 15:36 | 49.892
2024-03-13 | 15:36 | 49.891
2024-03-13 | 15:36 | 49.892
2024-03-13 | 15:36 | 49.894
2024-03-13 | 15:36 | 49.898
2024-03-13 | 15:36 | 49.902
2024-03-13 | 15:36 | 49.902
2024-03-13 | 15:36 | 49.905
2024-03-13 | 15:36 | 49.908
2024-03-13 | 15:36 | 49.91
2024-03-13 | 15:36 | 49.912
2024-03-13 | 15:36 | 49.917
2024-03-13 | 15:36 | 49.918
2024-03-13 | 15:36 | 49.917
2024-03-13 | 15:36 | 49.917
2024-03-13 | 15:36 | 49.916
2024-03-13 | 15:36 | 49.914
2024-03-13 | 15:36 | 49.911
2024-03-13 | 15:36 | 49.909
2024-03-13 | 15:36 | 49.91
2024-03-13 | 15:36 | 49.91
2024-03-13 | 15:36 | 49.914
2024-03-13 | 15:36 | 49.917
2024-03-13 | 15:36 | 49.917
2024-03-13 | 15:36 | 49.919
2024-03-13 | 15:36 | 49.921
2024-03-13 | 15:36 | 49.919
2024-03-13 | 15:36 | 49.916
2024-03-13 | 15:36 | 49.916
2024-03-13 | 15:36 | 49.917
2024-03-13 | 15:36 | 49.909
2024-03-13 | 15:36 | 49.904
2024-03-13 | 15:36 | 49.901
2024-03-13 | 15:36 | 49.895
2024-03-13 | 15:36 | 49.894
2024-03-13 | 15:36 | 49.894
2024-03-13 | 15:36 | 49.894
2024-03-13 | 15:36 | 49.895
2024-03-13 | 15:36 | 49.894
2024-03-13 | 15:36 | 49.892
2024-03-13 | 15:36 | 49.894
2024-03-13 | 15:36 | 49.894
2024-03-13 | 15:36 | 49.894
2024-03-13 | 15:36 | 49.898
2024-03-13 | 15:36 | 49.896
2024-03-13 | 15:36 | 49.898
2024-03-13 | 15:36 | 49.899
2024-03-13 | 15:36 | 49.9
2024-03-13 | 15:36 | 49.9
2024-03-13 | 15:36 | 49.901
2024-03-13 | 15:36 | 49.902
2024-03-13 | 15:36 | 49.901
2024-03-13 | 15:36 | 49.899
2024-03-13 | 15:36 | 49.895
2024-03-13 | 15:36 | 49.896
2024-03-13 | 15:36 | 49.896
2024-03-13 | 15:36 | 49.896
2024-03-13 | 15:36 | 49.893
2024-03-13 | 15:36 | 49.895
2024-03-13 | 15:36 | 49.893
2024-03-13 | 15:37 | 49.895
2024-03-13 | 15:37 | 49.894
2024-03-13 | 15:37 | 49.893
2024-03-13 | 15:37 | 49.891
2024-03-13 | 15:37 | 49.893
2024-03-13 | 15:37 | 49.894
2024-03-13 | 15:37 | 49.895
2024-03-13 | 15:37 | 49.894
2024-03-13 | 15:37 | 49.898
2024-03-13 | 15:37 | 49.898
2024-03-13 | 15:37 | 49.895
2024-03-13 | 15:37 | 49.894
2024-03-13 | 15:37 | 49.892
2024-03-13 | 15:37 | 49.895
2024-03-13 | 15:37 | 49.898
2024-03-13 | 15:37 | 49.896
2024-03-13 | 15:37 | 49.895
2024-03-13 | 15:37 | 49.896
2024-03-13 | 15:37 | 49.895
2024-03-13 | 15:37 | 49.894
2024-03-13 | 15:37 | 49.894
2024-03-13 | 15:37 | 49.892
2024-03-13 | 15:37 | 49.891
2024-03-13 | 15:37 | 49.89
2024-03-13 | 15:37 | 49.89
2024-03-13 | 15:37 | 49.893
2024-03-13 | 15:37 | 49.895
2024-03-13 | 15:37 | 49.894
2024-03-13 | 15:37 | 49.895
2024-03-13 | 15:37 | 49.895
2024-03-13 | 15:37 | 49.896
2024-03-13 | 15:37 | 49.892
2024-03-13 | 15:37 | 49.893
2024-03-13 | 15:37 | 49.894
2024-03-13 | 15:37 | 49.892
2024-03-13 | 15:37 | 49.894
2024-03-13 | 15:37 | 49.894
2024-03-13 | 15:37 | 49.893
2024-03-13 | 15:37 | 49.888
2024-03-13 | 15:37 | 49.887
2024-03-13 | 15:37 | 49.89
2024-03-13 | 15:37 | 49.891
2024-03-13 | 15:37 | 49.891
2024-03-13 | 15:37 | 49.891
2024-03-13 | 15:37 | 49.887
2024-03-13 | 15:37 | 49.882
2024-03-13 | 15:37 | 49.876
2024-03-13 | 15:37 | 49.875
2024-03-13 | 15:37 | 49.875
2024-03-13 | 15:37 | 49.876
2024-03-13 | 15:37 | 49.875
2024-03-13 | 15:37 | 49.881
2024-03-13 | 15:37 | 49.882
2024-03-13 | 15:37 | 49.885
2024-03-13 | 15:37 | 49.886
2024-03-13 | 15:37 | 49.887
2024-03-13 | 15:37 | 49.886
2024-03-13 | 15:37 | 49.886
2024-03-13 | 15:37 | 49.889
2024-03-13 | 15:38 | 49.89
2024-03-13 | 15:38 | 49.89
2024-03-13 | 15:38 | 49.886
2024-03-13 | 15:38 | 49.885
2024-03-13 | 15:38 | 49.882
2024-03-13 | 15:38 | 49.882
2024-03-13 | 15:38 | 49.88
2024-03-13 | 15:38 | 49.879
2024-03-13 | 15:38 | 49.876
2024-03-13 | 15:38 | 49.876
2024-03-13 | 15:38 | 49.88
2024-03-13 | 15:38 | 49.881
2024-03-13 | 15:38 | 49.885
2024-03-13 | 15:38 | 49.882
2024-03-13 | 15:38 | 49.88
2024-03-13 | 15:38 | 49.88
2024-03-13 | 15:38 | 49.878
2024-03-13 | 15:38 | 49.877
2024-03-13 | 15:38 | 49.877
2024-03-13 | 15:38 | 49.878
2024-03-13 | 15:38 | 49.879
2024-03-13 | 15:38 | 49.875
2024-03-13 | 15:38 | 49.874
2024-03-13 | 15:38 | 49.873
2024-03-13 | 15:38 | 49.872
2024-03-13 | 15:38 | 49.87
2024-03-13 | 15:38 | 49.87
2024-03-13 | 15:38 | 49.871
2024-03-13 | 15:38 | 49.872
2024-03-13 | 15:38 | 49.87
2024-03-13 | 15:38 | 49.87
2024-03-13 | 15:38 | 49.864
2024-03-13 | 15:38 | 49.863
2024-03-13 | 15:38 | 49.861
2024-03-13 | 15:38 | 49.859
2024-03-13 | 15:38 | 49.856
2024-03-13 | 15:38 | 49.856
2024-03-13 | 15:38 | 49.857
2024-03-13 | 15:38 | 49.858
2024-03-13 | 15:38 | 49.86
2024-03-13 | 15:38 | 49.861
2024-03-13 | 15:38 | 49.866
2024-03-13 | 15:38 | 49.869
2024-03-13 | 15:38 | 49.87
2024-03-13 | 15:38 | 49.869
2024-03-13 | 15:38 | 49.867
2024-03-13 | 15:38 | 49.866
2024-03-13 | 15:38 | 49.869
2024-03-13 | 15:38 | 49.869
2024-03-13 | 15:38 | 49.868
2024-03-13 | 15:38 | 49.866
2024-03-13 | 15:38 | 49.865
2024-03-13 | 15:38 | 49.867
2024-03-13 | 15:38 | 49.87
2024-03-13 | 15:38 | 49.868
2024-03-13 | 15:38 | 49.865
2024-03-13 | 15:38 | 49.865
2024-03-13 | 15:38 | 49.867
2024-03-13 | 15:38 | 49.866
2024-03-13 | 15:38 | 49.867
2024-03-13 | 15:39 | 49.866
2024-03-13 | 15:39 | 49.864
2024-03-13 | 15:39 | 49.863
2024-03-13 | 15:39 | 49.862
2024-03-13 | 15:39 | 49.863
2024-03-13 | 15:39 | 49.862
2024-03-13 | 15:39 | 49.86
2024-03-13 | 15:39 | 49.858
2024-03-13 | 15:39 | 49.858
2024-03-13 | 15:39 | 49.857
2024-03-13 | 15:39 | 49.856
2024-03-13 | 15:39 | 49.858
2024-03-13 | 15:39 | 49.86
2024-03-13 | 15:39 | 49.863
2024-03-13 | 15:39 | 49.862
2024-03-13 | 15:39 | 49.86
2024-03-13 | 15:39 | 49.857
2024-03-13 | 15:39 | 49.856
2024-03-13 | 15:39 | 49.86
2024-03-13 | 15:39 | 49.861
2024-03-13 | 15:39 | 49.862
2024-03-13 | 15:39 | 49.865
2024-03-13 | 15:39 | 49.866
2024-03-13 | 15:39 | 49.866
2024-03-13 | 15:39 | 49.868
2024-03-13 | 15:39 | 49.869
2024-03-13 | 15:39 | 49.872
2024-03-13 | 15:39 | 49.872
2024-03-13 | 15:39 | 49.875
2024-03-13 | 15:39 | 49.871
2024-03-13 | 15:39 | 49.867
2024-03-13 | 15:39 | 49.864
2024-03-13 | 15:39 | 49.857
2024-03-13 | 15:39 | 49.856
2024-03-13 | 15:39 | 49.857
2024-03-13 | 15:39 | 49.856
2024-03-13 | 15:39 | 49.854
2024-03-13 | 15:39 | 49.85
2024-03-13 | 15:39 | 49.852
2024-03-13 | 15:39 | 49.852
2024-03-13 | 15:39 | 49.854
2024-03-13 | 15:39 | 49.849
2024-03-13 | 15:39 | 49.847
2024-03-13 | 15:39 | 49.845
2024-03-13 | 15:39 | 49.844
2024-03-13 | 15:39 | 49.845
2024-03-13 | 15:39 | 49.845
2024-03-13 | 15:39 | 49.846
2024-03-13 | 15:39 | 49.845
2024-03-13 | 15:39 | 49.845
2024-03-13 | 15:39 | 49.841
2024-03-13 | 15:39 | 49.837
2024-03-13 | 15:39 | 49.834
2024-03-13 | 15:39 | 49.834
2024-03-13 | 15:39 | 49.834
2024-03-13 | 15:39 | 49.836
2024-03-13 | 15:39 | 49.836
2024-03-13 | 15:39 | 49.839
2024-03-13 | 15:39 | 49.84
2024-03-13 | 15:39 | 49.842
2024-03-13 | 15:39 | 49.844
2024-03-13 | 15:40 | 49.844
2024-03-13 | 15:40 | 49.845
2024-03-13 | 15:40 | 49.843
2024-03-13 | 15:40 | 49.845
2024-03-13 | 15:40 | 49.844
2024-03-13 | 15:40 | 49.841
2024-03-13 | 15:40 | 49.841
2024-03-13 | 15:40 | 49.838
2024-03-13 | 15:40 | 49.835
2024-03-13 | 15:40 | 49.834
2024-03-13 | 15:40 | 49.837
2024-03-13 | 15:40 | 49.842
2024-03-13 | 15:40 | 49.849
2024-03-13 | 15:40 | 49.852
2024-03-13 | 15:40 | 49.858
2024-03-13 | 15:40 | 49.862
2024-03-13 | 15:40 | 49.865
2024-03-13 | 15:40 | 49.864
2024-03-13 | 15:40 | 49.864
2024-03-13 | 15:40 | 49.86
2024-03-13 | 15:40 | 49.86
2024-03-13 | 15:40 | 49.857
2024-03-13 | 15:40 | 49.856
2024-03-13 | 15:40 | 49.855
2024-03-13 | 15:40 | 49.854
2024-03-13 | 15:40 | 49.852
2024-03-13 | 15:40 | 49.848
2024-03-13 | 15:40 | 49.847
2024-03-13 | 15:40 | 49.844
2024-03-13 | 15:40 | 49.842
2024-03-13 | 15:40 | 49.838
2024-03-13 | 15:40 | 49.839
2024-03-13 | 15:40 | 49.837
2024-03-13 | 15:40 | 49.835
2024-03-13 | 15:40 | 49.833
2024-03-13 | 15:40 | 49.836
2024-03-13 | 15:40 | 49.837
2024-03-13 | 15:40 | 49.84
2024-03-13 | 15:40 | 49.842
2024-03-13 | 15:40 | 49.845
2024-03-13 | 15:40 | 49.848
2024-03-13 | 15:40 | 49.849
2024-03-13 | 15:40 | 49.847
2024-03-13 | 15:40 | 49.847
2024-03-13 | 15:40 | 49.846
2024-03-13 | 15:40 | 49.842
2024-03-13 | 15:40 | 49.841
2024-03-13 | 15:40 | 49.843
2024-03-13 | 15:40 | 49.842
2024-03-13 | 15:40 | 49.841
2024-03-13 | 15:40 | 49.843
2024-03-13 | 15:40 | 49.845
2024-03-13 | 15:40 | 49.842
2024-03-13 | 15:40 | 49.845
2024-03-13 | 15:40 | 49.846
2024-03-13 | 15:40 | 49.846
2024-03-13 | 15:40 | 49.842
2024-03-13 | 15:40 | 49.842
2024-03-13 | 15:40 | 49.841
2024-03-13 | 15:41 | 49.836
2024-03-13 | 15:41 | 49.835
2024-03-13 | 15:41 | 49.836
2024-03-13 | 15:41 | 49.833
2024-03-13 | 15:41 | 49.833
2024-03-13 | 15:41 | 49.838
2024-03-13 | 15:41 | 49.842
2024-03-13 | 15:41 | 49.844
2024-03-13 | 15:41 | 49.848
2024-03-13 | 15:41 | 49.853
2024-03-13 | 15:41 | 49.859
2024-03-13 | 15:41 | 49.861
2024-03-13 | 15:41 | 49.863
2024-03-13 | 15:41 | 49.861
2024-03-13 | 15:41 | 49.859
2024-03-13 | 15:41 | 49.86
2024-03-13 | 15:41 | 49.86
2024-03-13 | 15:41 | 49.865
2024-03-13 | 15:41 | 49.869
2024-03-13 | 15:41 | 49.868
2024-03-13 | 15:41 | 49.865
2024-03-13 | 15:41 | 49.864
2024-03-13 | 15:41 | 49.863
2024-03-13 | 15:41 | 49.864
2024-03-13 | 15:41 | 49.863
2024-03-13 | 15:41 | 49.861
2024-03-13 | 15:41 | 49.858
2024-03-13 | 15:41 | 49.855
2024-03-13 | 15:41 | 49.854
2024-03-13 | 15:41 | 49.852
2024-03-13 | 15:41 | 49.851
2024-03-13 | 15:41 | 49.848
2024-03-13 | 15:41 | 49.85
2024-03-13 | 15:41 | 49.85
2024-03-13 | 15:41 | 49.849
2024-03-13 | 15:41 | 49.848
2024-03-13 | 15:41 | 49.846
2024-03-13 | 15:41 | 49.845
2024-03-13 | 15:41 | 49.842
2024-03-13 | 15:41 | 49.841
2024-03-13 | 15:41 | 49.839
2024-03-13 | 15:41 | 49.841
2024-03-13 | 15:41 | 49.844
2024-03-13 | 15:41 | 49.849
2024-03-13 | 15:41 | 49.853
2024-03-13 | 15:41 | 49.855
2024-03-13 | 15:41 | 49.857
2024-03-13 | 15:41 | 49.861
2024-03-13 | 15:41 | 49.867
2024-03-13 | 15:41 | 49.867
2024-03-13 | 15:41 | 49.867
2024-03-13 | 15:41 | 49.87
2024-03-13 | 15:41 | 49.869
2024-03-13 | 15:41 | 49.87
2024-03-13 | 15:41 | 49.868
2024-03-13 | 15:41 | 49.868
2024-03-13 | 15:41 | 49.87
2024-03-13 | 15:41 | 49.872
2024-03-13 | 15:41 | 49.874
2024-03-13 | 15:41 | 49.874
2024-03-13 | 15:41 | 49.874
2024-03-13 | 15:42 | 49.874
2024-03-13 | 15:42 | 49.873
2024-03-13 | 15:42 | 49.869
2024-03-13 | 15:42 | 49.869
2024-03-13 | 15:42 | 49.868
2024-03-13 | 15:42 | 49.869
2024-03-13 | 15:42 | 49.868
2024-03-13 | 15:42 | 49.87
2024-03-13 | 15:42 | 49.869
2024-03-13 | 15:42 | 49.875
2024-03-13 | 15:42 | 49.875
2024-03-13 | 15:42 | 49.873
2024-03-13 | 15:42 | 49.871
2024-03-13 | 15:42 | 49.871
2024-03-13 | 15:42 | 49.875
2024-03-13 | 15:42 | 49.872
2024-03-13 | 15:42 | 49.871
2024-03-13 | 15:42 | 49.867
2024-03-13 | 15:42 | 49.866
2024-03-13 | 15:42 | 49.861
2024-03-13 | 15:42 | 49.855
2024-03-13 | 15:42 | 49.854
2024-03-13 | 15:42 | 49.854
2024-03-13 | 15:42 | 49.859
2024-03-13 | 15:42 | 49.857
2024-03-13 | 15:42 | 49.856
2024-03-13 | 15:42 | 49.853
2024-03-13 | 15:42 | 49.854
2024-03-13 | 15:42 | 49.853
2024-03-13 | 15:42 | 49.856
2024-03-13 | 15:42 | 49.852
2024-03-13 | 15:42 | 49.85
2024-03-13 | 15:42 | 49.851
2024-03-13 | 15:42 | 49.851
2024-03-13 | 15:42 | 49.855
2024-03-13 | 15:42 | 49.86
2024-03-13 | 15:42 | 49.863
2024-03-13 | 15:42 | 49.867
2024-03-13 | 15:42 | 49.87
2024-03-13 | 15:42 | 49.871
2024-03-13 | 15:42 | 49.87
2024-03-13 | 15:42 | 49.868
2024-03-13 | 15:42 | 49.867
2024-03-13 | 15:42 | 49.867
2024-03-13 | 15:42 | 49.868
2024-03-13 | 15:42 | 49.871
2024-03-13 | 15:42 | 49.871
2024-03-13 | 15:42 | 49.872
2024-03-13 | 15:42 | 49.871
2024-03-13 | 15:42 | 49.872
2024-03-13 | 15:42 | 49.87
2024-03-13 | 15:42 | 49.871
2024-03-13 | 15:42 | 49.869
2024-03-13 | 15:42 | 49.865
2024-03-13 | 15:42 | 49.862
2024-03-13 | 15:42 | 49.865
2024-03-13 | 15:42 | 49.867
2024-03-13 | 15:42 | 49.867
2024-03-13 | 15:42 | 49.868
2024-03-13 | 15:43 | 49.869
2024-03-13 | 15:43 | 49.867
2024-03-13 | 15:43 | 49.866
2024-03-13 | 15:43 | 49.862
2024-03-13 | 15:43 | 49.859
2024-03-13 | 15:43 | 49.86
2024-03-13 | 15:43 | 49.863
2024-03-13 | 15:43 | 49.865
2024-03-13 | 15:43 | 49.869
2024-03-13 | 15:43 | 49.869
2024-03-13 | 15:43 | 49.869
2024-03-13 | 15:43 | 49.865
2024-03-13 | 15:43 | 49.865
2024-03-13 | 15:43 | 49.864
2024-03-13 | 15:43 | 49.862
2024-03-13 | 15:43 | 49.861
2024-03-13 | 15:43 | 49.861
2024-03-13 | 15:43 | 49.863
2024-03-13 | 15:43 | 49.861
2024-03-13 | 15:43 | 49.86
2024-03-13 | 15:43 | 49.862
2024-03-13 | 15:43 | 49.861
2024-03-13 | 15:43 | 49.859
2024-03-13 | 15:43 | 49.86
2024-03-13 | 15:43 | 49.86
2024-03-13 | 15:43 | 49.863
2024-03-13 | 15:43 | 49.864
2024-03-13 | 15:43 | 49.866
2024-03-13 | 15:43 | 49.867
2024-03-13 | 15:43 | 49.87
2024-03-13 | 15:43 | 49.87
2024-03-13 | 15:43 | 49.864
2024-03-13 | 15:43 | 49.857
2024-03-13 | 15:43 | 49.852
2024-03-13 | 15:43 | 49.85
2024-03-13 | 15:43 | 49.85
2024-03-13 | 15:43 | 49.853
2024-03-13 | 15:43 | 49.853
2024-03-13 | 15:43 | 49.854
2024-03-13 | 15:43 | 49.853
2024-03-13 | 15:43 | 49.849
2024-03-13 | 15:43 | 49.851
2024-03-13 | 15:43 | 49.851
2024-03-13 | 15:43 | 49.851
2024-03-13 | 15:43 | 49.851
2024-03-13 | 15:43 | 49.853
2024-03-13 | 15:43 | 49.854
2024-03-13 | 15:43 | 49.854
2024-03-13 | 15:43 | 49.856
2024-03-13 | 15:43 | 49.858
2024-03-13 | 15:43 | 49.859
2024-03-13 | 15:43 | 49.863
2024-03-13 | 15:43 | 49.86
2024-03-13 | 15:43 | 49.859
2024-03-13 | 15:43 | 49.855
2024-03-13 | 15:43 | 49.853
2024-03-13 | 15:43 | 49.851
2024-03-13 | 15:43 | 49.85
2024-03-13 | 15:43 | 49.853
2024-03-13 | 15:43 | 49.857
2024-03-13 | 15:43 | 49.86
2024-03-13 | 15:44 | 49.861
2024-03-13 | 15:44 | 49.866
2024-03-13 | 15:44 | 49.868
2024-03-13 | 15:44 | 49.871
2024-03-13 | 15:44 | 49.873
2024-03-13 | 15:44 | 49.878
2024-03-13 | 15:44 | 49.88
2024-03-13 | 15:44 | 49.878
2024-03-13 | 15:44 | 49.877
2024-03-13 | 15:44 | 49.874
2024-03-13 | 15:44 | 49.872
2024-03-13 | 15:44 | 49.868
2024-03-13 | 15:44 | 49.871
2024-03-13 | 15:44 | 49.874
2024-03-13 | 15:44 | 49.876
2024-03-13 | 15:44 | 49.875
2024-03-13 | 15:44 | 49.874
2024-03-13 | 15:44 | 49.874
2024-03-13 | 15:44 | 49.872
2024-03-13 | 15:44 | 49.873
2024-03-13 | 15:44 | 49.875
2024-03-13 | 15:44 | 49.878
2024-03-13 | 15:44 | 49.874
2024-03-13 | 15:44 | 49.87
2024-03-13 | 15:44 | 49.864
2024-03-13 | 15:44 | 49.861
2024-03-13 | 15:44 | 49.86
2024-03-13 | 15:44 | 49.858
2024-03-13 | 15:44 | 49.856
2024-03-13 | 15:44 | 49.86
2024-03-13 | 15:44 | 49.862
2024-03-13 | 15:44 | 49.864
2024-03-13 | 15:44 | 49.866
2024-03-13 | 15:44 | 49.871
2024-03-13 | 15:44 | 49.873
2024-03-13 | 15:44 | 49.871
2024-03-13 | 15:44 | 49.87
2024-03-13 | 15:44 | 49.872
2024-03-13 | 15:44 | 49.876
2024-03-13 | 15:44 | 49.879
2024-03-13 | 15:44 | 49.882
2024-03-13 | 15:44 | 49.885
2024-03-13 | 15:44 | 49.886
2024-03-13 | 15:44 | 49.888
2024-03-13 | 15:44 | 49.892
2024-03-13 | 15:44 | 49.893
2024-03-13 | 15:44 | 49.892
2024-03-13 | 15:44 | 49.892
2024-03-13 | 15:44 | 49.89
2024-03-13 | 15:44 | 49.887
2024-03-13 | 15:44 | 49.886
2024-03-13 | 15:44 | 49.887
2024-03-13 | 15:44 | 49.891
2024-03-13 | 15:44 | 49.892
2024-03-13 | 15:44 | 49.891
2024-03-13 | 15:44 | 49.894
2024-03-13 | 15:44 | 49.896
2024-03-13 | 15:44 | 49.897
2024-03-13 | 15:44 | 49.897
2024-03-13 | 15:45 | 49.898
2024-03-13 | 15:45 | 49.9
2024-03-13 | 15:45 | 49.9
2024-03-13 | 15:45 | 49.897
2024-03-13 | 15:45 | 49.896
2024-03-13 | 15:45 | 49.895
2024-03-13 | 15:45 | 49.897
2024-03-13 | 15:45 | 49.899
2024-03-13 | 15:45 | 49.899
2024-03-13 | 15:45 | 49.898
2024-03-13 | 15:45 | 49.899
2024-03-13 | 15:45 | 49.9
2024-03-13 | 15:45 | 49.9
2024-03-13 | 15:45 | 49.9
2024-03-13 | 15:45 | 49.902
2024-03-13 | 15:45 | 49.904
2024-03-13 | 15:45 | 49.904
2024-03-13 | 15:45 | 49.898
2024-03-13 | 15:45 | 49.895
2024-03-13 | 15:45 | 49.892
2024-03-13 | 15:45 | 49.894
2024-03-13 | 15:45 | 49.897
2024-03-13 | 15:45 | 49.901
2024-03-13 | 15:45 | 49.903
2024-03-13 | 15:45 | 49.906
2024-03-13 | 15:45 | 49.907
2024-03-13 | 15:45 | 49.907
2024-03-13 | 15:45 | 49.905
2024-03-13 | 15:45 | 49.906
2024-03-13 | 15:45 | 49.908
2024-03-13 | 15:45 | 49.911
2024-03-13 | 15:45 | 49.91
2024-03-13 | 15:45 | 49.908
2024-03-13 | 15:45 | 49.905
2024-03-13 | 15:45 | 49.904
2024-03-13 | 15:45 | 49.906
2024-03-13 | 15:45 | 49.909
2024-03-13 | 15:45 | 49.909
2024-03-13 | 15:45 | 49.909
2024-03-13 | 15:45 | 49.911
2024-03-13 | 15:45 | 49.913
2024-03-13 | 15:45 | 49.915
2024-03-13 | 15:45 | 49.918
2024-03-13 | 15:45 | 49.919
2024-03-13 | 15:45 | 49.921
2024-03-13 | 15:45 | 49.924
2024-03-13 | 15:45 | 49.925
2024-03-13 | 15:45 | 49.926
2024-03-13 | 15:45 | 49.927
2024-03-13 | 15:45 | 49.925
2024-03-13 | 15:45 | 49.921
2024-03-13 | 15:45 | 49.915
2024-03-13 | 15:45 | 49.913
2024-03-13 | 15:45 | 49.908
2024-03-13 | 15:45 | 49.903
2024-03-13 | 15:45 | 49.9
2024-03-13 | 15:45 | 49.898
2024-03-13 | 15:45 | 49.899
2024-03-13 | 15:45 | 49.903
2024-03-13 | 15:45 | 49.904
2024-03-13 | 15:45 | 49.905
2024-03-13 | 15:46 | 49.906
2024-03-13 | 15:46 | 49.903
2024-03-13 | 15:46 | 49.901
2024-03-13 | 15:46 | 49.902
2024-03-13 | 15:46 | 49.9
2024-03-13 | 15:46 | 49.901
2024-03-13 | 15:46 | 49.897
2024-03-13 | 15:46 | 49.895
2024-03-13 | 15:46 | 49.896
2024-03-13 | 15:46 | 49.894
2024-03-13 | 15:46 | 49.892
2024-03-13 | 15:46 | 49.894
2024-03-13 | 15:46 | 49.898
2024-03-13 | 15:46 | 49.898
2024-03-13 | 15:46 | 49.901
2024-03-13 | 15:46 | 49.904
2024-03-13 | 15:46 | 49.906
2024-03-13 | 15:46 | 49.907
2024-03-13 | 15:46 | 49.91
2024-03-13 | 15:46 | 49.913
2024-03-13 | 15:46 | 49.917
2024-03-13 | 15:46 | 49.919
2024-03-13 | 15:46 | 49.92
2024-03-13 | 15:46 | 49.92
2024-03-13 | 15:46 | 49.921
2024-03-13 | 15:46 | 49.92
2024-03-13 | 15:46 | 49.92
2024-03-13 | 15:46 | 49.919
2024-03-13 | 15:46 | 49.919
2024-03-13 | 15:46 | 49.919
2024-03-13 | 15:46 | 49.922
2024-03-13 | 15:46 | 49.927
2024-03-13 | 15:46 | 49.929
2024-03-13 | 15:46 | 49.933
2024-03-13 | 15:46 | 49.937
2024-03-13 | 15:46 | 49.94
2024-03-13 | 15:46 | 49.939
2024-03-13 | 15:46 | 49.939
2024-03-13 | 15:46 | 49.936
2024-03-13 | 15:46 | 49.934
2024-03-13 | 15:46 | 49.933
2024-03-13 | 15:46 | 49.932
2024-03-13 | 15:46 | 49.931
2024-03-13 | 15:46 | 49.93
2024-03-13 | 15:46 | 49.931
2024-03-13 | 15:46 | 49.929
2024-03-13 | 15:46 | 49.93
2024-03-13 | 15:46 | 49.933
2024-03-13 | 15:46 | 49.934
2024-03-13 | 15:46 | 49.936
2024-03-13 | 15:46 | 49.937
2024-03-13 | 15:46 | 49.941
2024-03-13 | 15:46 | 49.945
2024-03-13 | 15:46 | 49.948
2024-03-13 | 15:46 | 49.953
2024-03-13 | 15:46 | 49.955
2024-03-13 | 15:46 | 49.958
2024-03-13 | 15:46 | 49.962
2024-03-13 | 15:46 | 49.965
2024-03-13 | 15:47 | 49.964
2024-03-13 | 15:47 | 49.964
2024-03-13 | 15:47 | 49.963
2024-03-13 | 15:47 | 49.962
2024-03-13 | 15:47 | 49.963
2024-03-13 | 15:47 | 49.965
2024-03-13 | 15:47 | 49.969
2024-03-13 | 15:47 | 49.97
2024-03-13 | 15:47 | 49.968
2024-03-13 | 15:47 | 49.968
2024-03-13 | 15:47 | 49.966
2024-03-13 | 15:47 | 49.964
2024-03-13 | 15:47 | 49.964
2024-03-13 | 15:47 | 49.96
2024-03-13 | 15:47 | 49.958
2024-03-13 | 15:47 | 49.955
2024-03-13 | 15:47 | 49.952
2024-03-13 | 15:47 | 49.953
2024-03-13 | 15:47 | 49.95
2024-03-13 | 15:47 | 49.95
2024-03-13 | 15:47 | 49.951
2024-03-13 | 15:47 | 49.956
2024-03-13 | 15:47 | 49.959
2024-03-13 | 15:47 | 49.966
2024-03-13 | 15:47 | 49.971
2024-03-13 | 15:47 | 49.975
2024-03-13 | 15:47 | 49.981
2024-03-13 | 15:47 | 49.985
2024-03-13 | 15:47 | 49.989
2024-03-13 | 15:47 | 49.991
2024-03-13 | 15:47 | 49.993
2024-03-13 | 15:47 | 49.993
2024-03-13 | 15:47 | 49.994
2024-03-13 | 15:47 | 49.995
2024-03-13 | 15:47 | 49.998
2024-03-13 | 15:47 | 50.002
2024-03-13 | 15:47 | 50.005
2024-03-13 | 15:47 | 50.005
2024-03-13 | 15:47 | 50.007
2024-03-13 | 15:47 | 50.007
2024-03-13 | 15:47 | 50.004
2024-03-13 | 15:47 | 50.002
2024-03-13 | 15:47 | 49.999
2024-03-13 | 15:47 | 49.995
2024-03-13 | 15:47 | 49.991
2024-03-13 | 15:47 | 49.984
2024-03-13 | 15:47 | 49.979
2024-03-13 | 15:47 | 49.974
2024-03-13 | 15:47 | 49.972
2024-03-13 | 15:47 | 49.969
2024-03-13 | 15:47 | 49.969
2024-03-13 | 15:47 | 49.965
2024-03-13 | 15:47 | 49.961
2024-03-13 | 15:47 | 49.954
2024-03-13 | 15:47 | 49.952
2024-03-13 | 15:47 | 49.944
2024-03-13 | 15:47 | 49.939
2024-03-13 | 15:47 | 49.934
2024-03-13 | 15:47 | 49.935
2024-03-13 | 15:47 | 49.933
2024-03-13 | 15:47 | 49.935
2024-03-13 | 15:48 | 49.937
2024-03-13 | 15:48 | 49.936
2024-03-13 | 15:48 | 49.937
2024-03-13 | 15:48 | 49.94
2024-03-13 | 15:48 | 49.942
2024-03-13 | 15:48 | 49.944
2024-03-13 | 15:48 | 49.948
2024-03-13 | 15:48 | 49.949
2024-03-13 | 15:48 | 49.951
2024-03-13 | 15:48 | 49.953
2024-03-13 | 15:48 | 49.957
2024-03-13 | 15:48 | 49.964
2024-03-13 | 15:48 | 49.971
2024-03-13 | 15:48 | 49.977
2024-03-13 | 15:48 | 49.982
2024-03-13 | 15:48 | 49.983
2024-03-13 | 15:48 | 49.983
2024-03-13 | 15:48 | 49.984
2024-03-13 | 15:48 | 49.982
2024-03-13 | 15:48 | 49.977
2024-03-13 | 15:48 | 49.976
2024-03-13 | 15:48 | 49.973
2024-03-13 | 15:48 | 49.971
2024-03-13 | 15:48 | 49.967
2024-03-13 | 15:48 | 49.964
2024-03-13 | 15:48 | 49.959
2024-03-13 | 15:48 | 49.955
2024-03-13 | 15:48 | 49.952
2024-03-13 | 15:48 | 49.952
2024-03-13 | 15:48 | 49.951
2024-03-13 | 15:48 | 49.949
2024-03-13 | 15:48 | 49.951
2024-03-13 | 15:48 | 49.954
2024-03-13 | 15:48 | 49.955
2024-03-13 | 15:48 | 49.957
2024-03-13 | 15:48 | 49.958
2024-03-13 | 15:48 | 49.958
2024-03-13 | 15:48 | 49.96
2024-03-13 | 15:48 | 49.959
2024-03-13 | 15:48 | 49.956
2024-03-13 | 15:48 | 49.956
2024-03-13 | 15:48 | 49.957
2024-03-13 | 15:48 | 49.959
2024-03-13 | 15:48 | 49.962
2024-03-13 | 15:48 | 49.965
2024-03-13 | 15:48 | 49.962
2024-03-13 | 15:48 | 49.956
2024-03-13 | 15:48 | 49.951
2024-03-13 | 15:48 | 49.947
2024-03-13 | 15:48 | 49.944
2024-03-13 | 15:48 | 49.943
2024-03-13 | 15:48 | 49.944
2024-03-13 | 15:48 | 49.946
2024-03-13 | 15:48 | 49.948
2024-03-13 | 15:48 | 49.952
2024-03-13 | 15:48 | 49.958
2024-03-13 | 15:48 | 49.965
2024-03-13 | 15:48 | 49.97
2024-03-13 | 15:48 | 49.977
2024-03-13 | 15:49 | 49.983
2024-03-13 | 15:49 | 49.983
2024-03-13 | 15:49 | 49.983
2024-03-13 | 15:49 | 49.983
2024-03-13 | 15:49 | 49.984
2024-03-13 | 15:49 | 49.988
2024-03-13 | 15:49 | 49.988
2024-03-13 | 15:49 | 49.99
2024-03-13 | 15:49 | 49.993
2024-03-13 | 15:49 | 49.995
2024-03-13 | 15:49 | 49.993
2024-03-13 | 15:49 | 49.994
2024-03-13 | 15:49 | 49.994
2024-03-13 | 15:49 | 49.997
2024-03-13 | 15:49 | 49.999
2024-03-13 | 15:49 | 50.002
2024-03-13 | 15:49 | 50.005
2024-03-13 | 15:49 | 50.007
2024-03-13 | 15:49 | 50.008
2024-03-13 | 15:49 | 50.01
2024-03-13 | 15:49 | 50.013
2024-03-13 | 15:49 | 50.017
2024-03-13 | 15:49 | 50.02
2024-03-13 | 15:49 | 50.019
2024-03-13 | 15:49 | 50.02
2024-03-13 | 15:49 | 50.023
2024-03-13 | 15:49 | 50.024
2024-03-13 | 15:49 | 50.025
2024-03-13 | 15:49 | 50.027
2024-03-13 | 15:49 | 50.027

## 20240319-1
In GMT
Date | Time | Freq
2024-03-19 | 9:27 | 49.876 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-19 | 9:27 | 49.876 | 222 | BRITNED | 676.211
2024-03-19 | 9:27 | 49.878 | 268 | WBURB-2 | 428.156
2024-03-19 | 9:27 | 49.881 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-19 | 9:27 | 49.885 |  | Viking Link | -648.9
2024-03-19 | 9:27 | 49.888 |  | Viking Link | 1398.96
2024-03-19 | 9:27 | 49.889 | 209 | DRAXX-3 | 626.95
2024-03-19 | 9:27 | 49.891 | 154 | CDCL-1 | 391.57
2024-03-19 | 9:27 | 49.889 | 268 | ROCK-1 | 468.495
2024-03-19 | 9:27 | 49.887 | 148 | IFA Bipole1 | 945.473
2024-03-19 | 9:27 | 49.885 | 132 | IFA Bipole1 | 999.1
2024-03-19 | 9:27 | 49.885 | 141 | IFA Bipole2 | 1000
2024-03-19 | 9:27 | 49.887 | 135 | IFA Bipole1 | 996.75
2024-03-19 | 9:27 | 49.886 |  | Viking Link | -780.3
2024-03-19 | 9:27 | 49.887
2024-03-19 | 9:27 | 49.887
2024-03-19 | 9:27 | 49.886
2024-03-19 | 9:27 | 49.884
2024-03-19 | 9:27 | 49.885
2024-03-19 | 9:27 | 49.889 | 130 | HEYM12 | 271.908
2024-03-19 | 9:27 | 49.889 | 228 | HUMR-1 | 303.75
2024-03-19 | 9:27 | 49.888
2024-03-19 | 9:27 | 49.89
2024-03-19 | 9:27 | 49.893
2024-03-19 | 9:27 | 49.893
2024-03-19 | 9:27 | 49.896
2024-03-19 | 9:27 | 49.9
2024-03-19 | 9:27 | 49.898
2024-03-19 | 9:27 | 49.9
2024-03-19 | 9:27 | 49.905
2024-03-19 | 9:28 | 49.91 | 211 | CDCL-1 | 291.5
2024-03-19 | 9:28 | 49.916 | 199 | STAY-2 | 413.125
2024-03-19 | 9:28 | 49.919 | 173 | CDCL-1 | 397.375
2024-03-19 | 9:28 | 49.924 | 248 | SEAB-2 | 361.25
2024-03-19 | 9:28 | 49.923 | 255 | FRANCE | 995.65
2024-03-19 | 9:28 | 49.921 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-19 | 9:28 | 49.918
2024-03-19 | 9:28 | 49.918
2024-03-19 | 9:28 | 49.919
2024-03-19 | 9:28 | 49.92
2024-03-19 | 9:28 | 49.921
2024-03-19 | 9:28 | 49.921
2024-03-19 | 9:28 | 49.921
2024-03-19 | 9:28 | 49.919
2024-03-19 | 9:28 | 49.918
2024-03-19 | 9:28 | 49.913
2024-03-19 | 9:28 | 49.908
2024-03-19 | 9:28 | 49.906
2024-03-19 | 9:28 | 49.903
2024-03-19 | 9:28 | 49.903
2024-03-19 | 9:28 | 49.905
2024-03-19 | 9:28 | 49.904
2024-03-19 | 9:28 | 49.903
2024-03-19 | 9:28 | 49.903
2024-03-19 | 9:28 | 49.905
2024-03-19 | 9:28 | 49.905
2024-03-19 | 9:28 | 49.901
2024-03-19 | 9:28 | 49.897
2024-03-19 | 9:28 | 49.895
2024-03-19 | 9:28 | 49.892
2024-03-19 | 9:28 | 49.891
2024-03-19 | 9:28 | 49.887
2024-03-19 | 9:28 | 49.888
2024-03-19 | 9:28 | 49.891
2024-03-19 | 9:28 | 49.89
2024-03-19 | 9:28 | 49.891
2024-03-19 | 9:28 | 49.894
2024-03-19 | 9:28 | 49.895
2024-03-19 | 9:28 | 49.897
2024-03-19 | 9:28 | 49.899
2024-03-19 | 9:28 | 49.902
2024-03-19 | 9:28 | 49.903
2024-03-19 | 9:28 | 49.904
2024-03-19 | 9:28 | 49.906
2024-03-19 | 9:28 | 49.906
2024-03-19 | 9:28 | 49.901
2024-03-19 | 9:28 | 49.899
2024-03-19 | 9:28 | 49.896
2024-03-19 | 9:28 | 49.89
2024-03-19 | 9:28 | 49.886
2024-03-19 | 9:28 | 49.887
2024-03-19 | 9:28 | 49.89
2024-03-19 | 9:28 | 49.888
2024-03-19 | 9:28 | 49.894
2024-03-19 | 9:28 | 49.898
2024-03-19 | 9:28 | 49.902
2024-03-19 | 9:28 | 49.907
2024-03-19 | 9:28 | 49.911
2024-03-19 | 9:28 | 49.91
2024-03-19 | 9:28 | 49.911
2024-03-19 | 9:28 | 49.913
2024-03-19 | 9:29 | 49.916
2024-03-19 | 9:29 | 49.913
2024-03-19 | 9:29 | 49.914
2024-03-19 | 9:29 | 49.914
2024-03-19 | 9:29 | 49.913
2024-03-19 | 9:29 | 49.909
2024-03-19 | 9:29 | 49.909
2024-03-19 | 9:29 | 49.913
2024-03-19 | 9:29 | 49.909
2024-03-19 | 9:29 | 49.857
2024-03-19 | 9:29 | 49.825
2024-03-19 | 9:29 | 49.813
2024-03-19 | 9:29 | 49.812
2024-03-19 | 9:29 | 49.812
2024-03-19 | 9:29 | 49.817
2024-03-19 | 9:29 | 49.818
2024-03-19 | 9:29 | 49.818
2024-03-19 | 9:29 | 49.82
2024-03-19 | 9:29 | 49.822
2024-03-19 | 9:29 | 49.826
2024-03-19 | 9:29 | 49.826
2024-03-19 | 9:29 | 49.826
2024-03-19 | 9:29 | 49.826
2024-03-19 | 9:29 | 49.826
2024-03-19 | 9:29 | 49.827
2024-03-19 | 9:29 | 49.827
2024-03-19 | 9:29 | 49.823
2024-03-19 | 9:29 | 49.82
2024-03-19 | 9:29 | 49.818
2024-03-19 | 9:29 | 49.814
2024-03-19 | 9:29 | 49.811
2024-03-19 | 9:29 | 49.809
2024-03-19 | 9:29 | 49.81
2024-03-19 | 9:29 | 49.81
2024-03-19 | 9:29 | 49.81
2024-03-19 | 9:29 | 49.809
2024-03-19 | 9:29 | 49.812
2024-03-19 | 9:29 | 49.819
2024-03-19 | 9:29 | 49.82
2024-03-19 | 9:29 | 49.82
2024-03-19 | 9:29 | 49.818
2024-03-19 | 9:29 | 49.818
2024-03-19 | 9:29 | 49.821
2024-03-19 | 9:29 | 49.818
2024-03-19 | 9:29 | 49.82
2024-03-19 | 9:29 | 49.818
2024-03-19 | 9:29 | 49.814
2024-03-19 | 9:29 | 49.811
2024-03-19 | 9:29 | 49.81
2024-03-19 | 9:29 | 49.808
2024-03-19 | 9:29 | 49.807
2024-03-19 | 9:29 | 49.81
2024-03-19 | 9:29 | 49.808
2024-03-19 | 9:29 | 49.81
2024-03-19 | 9:29 | 49.812
2024-03-19 | 9:29 | 49.81
2024-03-19 | 9:29 | 49.809
2024-03-19 | 9:29 | 49.813
2024-03-19 | 9:29 | 49.814
2024-03-19 | 9:30 | 49.813
2024-03-19 | 9:30 | 49.813
2024-03-19 | 9:30 | 49.811
2024-03-19 | 9:30 | 49.81
2024-03-19 | 9:30 | 49.808
2024-03-19 | 9:30 | 49.808
2024-03-19 | 9:30 | 49.814
2024-03-19 | 9:30 | 49.812
2024-03-19 | 9:30 | 49.81
2024-03-19 | 9:30 | 49.811
2024-03-19 | 9:30 | 49.812
2024-03-19 | 9:30 | 49.817
2024-03-19 | 9:30 | 49.819
2024-03-19 | 9:30 | 49.822
2024-03-19 | 9:30 | 49.821
2024-03-19 | 9:30 | 49.82
2024-03-19 | 9:30 | 49.818
2024-03-19 | 9:30 | 49.819
2024-03-19 | 9:30 | 49.819
2024-03-19 | 9:30 | 49.818
2024-03-19 | 9:30 | 49.823
2024-03-19 | 9:30 | 49.825
2024-03-19 | 9:30 | 49.825
2024-03-19 | 9:30 | 49.826
2024-03-19 | 9:30 | 49.825
2024-03-19 | 9:30 | 49.822
2024-03-19 | 9:30 | 49.823
2024-03-19 | 9:30 | 49.823
2024-03-19 | 9:30 | 49.822
2024-03-19 | 9:30 | 49.824
2024-03-19 | 9:30 | 49.826
2024-03-19 | 9:30 | 49.819
2024-03-19 | 9:30 | 49.818
2024-03-19 | 9:30 | 49.818
2024-03-19 | 9:30 | 49.813
2024-03-19 | 9:30 | 49.812
2024-03-19 | 9:30 | 49.812
2024-03-19 | 9:30 | 49.816
2024-03-19 | 9:30 | 49.815
2024-03-19 | 9:30 | 49.814
2024-03-19 | 9:30 | 49.81
2024-03-19 | 9:30 | 49.811
2024-03-19 | 9:30 | 49.811
2024-03-19 | 9:30 | 49.818
2024-03-19 | 9:30 | 49.823
2024-03-19 | 9:30 | 49.826
2024-03-19 | 9:30 | 49.831
2024-03-19 | 9:30 | 49.833
2024-03-19 | 9:30 | 49.838
2024-03-19 | 9:30 | 49.843
2024-03-19 | 9:30 | 49.85
2024-03-19 | 9:30 | 49.85
2024-03-19 | 9:30 | 49.852
2024-03-19 | 9:30 | 49.851
2024-03-19 | 9:30 | 49.852
2024-03-19 | 9:30 | 49.85
2024-03-19 | 9:30 | 49.856
2024-03-19 | 9:30 | 49.856
2024-03-19 | 9:30 | 49.861
2024-03-19 | 9:30 | 49.857
2024-03-19 | 9:30 | 49.857
2024-03-19 | 9:31 | 49.851
2024-03-19 | 9:31 | 49.851
2024-03-19 | 9:31 | 49.848
2024-03-19 | 9:31 | 49.852
2024-03-19 | 9:31 | 49.852
2024-03-19 | 9:31 | 49.852
2024-03-19 | 9:31 | 49.852
2024-03-19 | 9:31 | 49.852
2024-03-19 | 9:31 | 49.852
2024-03-19 | 9:31 | 49.85
2024-03-19 | 9:31 | 49.849
2024-03-19 | 9:31 | 49.845
2024-03-19 | 9:31 | 49.848
2024-03-19 | 9:31 | 49.847
2024-03-19 | 9:31 | 49.848
2024-03-19 | 9:31 | 49.848
2024-03-19 | 9:31 | 49.849
2024-03-19 | 9:31 | 49.85
2024-03-19 | 9:31 | 49.847
2024-03-19 | 9:31 | 49.848
2024-03-19 | 9:31 | 49.85
2024-03-19 | 9:31 | 49.851
2024-03-19 | 9:31 | 49.846
2024-03-19 | 9:31 | 49.847
2024-03-19 | 9:31 | 49.845
2024-03-19 | 9:31 | 49.847
2024-03-19 | 9:31 | 49.85
2024-03-19 | 9:31 | 49.85
2024-03-19 | 9:31 | 49.852
2024-03-19 | 9:31 | 49.851
2024-03-19 | 9:31 | 49.848
2024-03-19 | 9:31 | 49.843
2024-03-19 | 9:31 | 49.843
2024-03-19 | 9:31 | 49.842
2024-03-19 | 9:31 | 49.845
2024-03-19 | 9:31 | 49.847
2024-03-19 | 9:31 | 49.846
2024-03-19 | 9:31 | 49.845
2024-03-19 | 9:31 | 49.844
2024-03-19 | 9:31 | 49.841
2024-03-19 | 9:31 | 49.841
2024-03-19 | 9:31 | 49.842
2024-03-19 | 9:31 | 49.845
2024-03-19 | 9:31 | 49.844
2024-03-19 | 9:31 | 49.843
2024-03-19 | 9:31 | 49.842
2024-03-19 | 9:31 | 49.847
2024-03-19 | 9:31 | 49.848
2024-03-19 | 9:31 | 49.85
2024-03-19 | 9:31 | 49.852
2024-03-19 | 9:31 | 49.854
2024-03-19 | 9:31 | 49.858
2024-03-19 | 9:31 | 49.858
2024-03-19 | 9:31 | 49.857
2024-03-19 | 9:31 | 49.86
2024-03-19 | 9:31 | 49.857
2024-03-19 | 9:31 | 49.858
2024-03-19 | 9:31 | 49.856
2024-03-19 | 9:31 | 49.858
2024-03-19 | 9:32 | 49.86
2024-03-19 | 9:32 | 49.863
2024-03-19 | 9:32 | 49.863
2024-03-19 | 9:32 | 49.863
2024-03-19 | 9:32 | 49.862
2024-03-19 | 9:32 | 49.864
2024-03-19 | 9:32 | 49.865
2024-03-19 | 9:32 | 49.864
2024-03-19 | 9:32 | 49.863
2024-03-19 | 9:32 | 49.86
2024-03-19 | 9:32 | 49.858
2024-03-19 | 9:32 | 49.857
2024-03-19 | 9:32 | 49.859
2024-03-19 | 9:32 | 49.863
2024-03-19 | 9:32 | 49.864
2024-03-19 | 9:32 | 49.862
2024-03-19 | 9:32 | 49.861
2024-03-19 | 9:32 | 49.86
2024-03-19 | 9:32 | 49.855
2024-03-19 | 9:32 | 49.849
2024-03-19 | 9:32 | 49.846
2024-03-19 | 9:32 | 49.844
2024-03-19 | 9:32 | 49.841
2024-03-19 | 9:32 | 49.839
2024-03-19 | 9:32 | 49.834
2024-03-19 | 9:32 | 49.831
2024-03-19 | 9:32 | 49.834
2024-03-19 | 9:32 | 49.832
2024-03-19 | 9:32 | 49.829
2024-03-19 | 9:32 | 49.832
2024-03-19 | 9:32 | 49.839
2024-03-19 | 9:32 | 49.844
2024-03-19 | 9:32 | 49.843
2024-03-19 | 9:32 | 49.844
2024-03-19 | 9:32 | 49.843
2024-03-19 | 9:32 | 49.842
2024-03-19 | 9:32 | 49.841
2024-03-19 | 9:32 | 49.844
2024-03-19 | 9:32 | 49.842
2024-03-19 | 9:32 | 49.839
2024-03-19 | 9:32 | 49.838
2024-03-19 | 9:32 | 49.842
2024-03-19 | 9:32 | 49.844
2024-03-19 | 9:32 | 49.846
2024-03-19 | 9:32 | 49.848
2024-03-19 | 9:32 | 49.847
2024-03-19 | 9:32 | 49.847
2024-03-19 | 9:32 | 49.845
2024-03-19 | 9:32 | 49.841
2024-03-19 | 9:32 | 49.837
2024-03-19 | 9:32 | 49.835
2024-03-19 | 9:32 | 49.833
2024-03-19 | 9:32 | 49.828
2024-03-19 | 9:32 | 49.825
2024-03-19 | 9:32 | 49.822
2024-03-19 | 9:32 | 49.819
2024-03-19 | 9:32 | 49.823
2024-03-19 | 9:32 | 49.827
2024-03-19 | 9:32 | 49.829
2024-03-19 | 9:32 | 49.825
2024-03-19 | 9:32 | 49.824
2024-03-19 | 9:33 | 49.823
2024-03-19 | 9:33 | 49.818
2024-03-19 | 9:33 | 49.82
2024-03-19 | 9:33 | 49.823
2024-03-19 | 9:33 | 49.82
2024-03-19 | 9:33 | 49.82
2024-03-19 | 9:33 | 49.821
2024-03-19 | 9:33 | 49.825
2024-03-19 | 9:33 | 49.827
2024-03-19 | 9:33 | 49.829
2024-03-19 | 9:33 | 49.83
2024-03-19 | 9:33 | 49.822
2024-03-19 | 9:33 | 49.825
2024-03-19 | 9:33 | 49.829
2024-03-19 | 9:33 | 49.831
2024-03-19 | 9:33 | 49.833
2024-03-19 | 9:33 | 49.833
2024-03-19 | 9:33 | 49.837
2024-03-19 | 9:33 | 49.836
2024-03-19 | 9:33 | 49.837
2024-03-19 | 9:33 | 49.836
2024-03-19 | 9:33 | 49.833
2024-03-19 | 9:33 | 49.833
2024-03-19 | 9:33 | 49.837
2024-03-19 | 9:33 | 49.838
2024-03-19 | 9:33 | 49.84
2024-03-19 | 9:33 | 49.839
2024-03-19 | 9:33 | 49.833
2024-03-19 | 9:33 | 49.833
2024-03-19 | 9:33 | 49.831
2024-03-19 | 9:33 | 49.835
2024-03-19 | 9:33 | 49.838
2024-03-19 | 9:33 | 49.837
2024-03-19 | 9:33 | 49.836
2024-03-19 | 9:33 | 49.828
2024-03-19 | 9:33 | 49.825
2024-03-19 | 9:33 | 49.827
2024-03-19 | 9:33 | 49.829
2024-03-19 | 9:33 | 49.83
2024-03-19 | 9:33 | 49.834
2024-03-19 | 9:33 | 49.841
2024-03-19 | 9:33 | 49.843
2024-03-19 | 9:33 | 49.844
2024-03-19 | 9:33 | 49.842
2024-03-19 | 9:33 | 49.842
2024-03-19 | 9:33 | 49.845
2024-03-19 | 9:33 | 49.847
2024-03-19 | 9:33 | 49.849
2024-03-19 | 9:33 | 49.846
2024-03-19 | 9:33 | 49.844
2024-03-19 | 9:33 | 49.839
2024-03-19 | 9:33 | 49.834
2024-03-19 | 9:33 | 49.833
2024-03-19 | 9:33 | 49.833
2024-03-19 | 9:33 | 49.834
2024-03-19 | 9:33 | 49.834
2024-03-19 | 9:33 | 49.836
2024-03-19 | 9:33 | 49.838
2024-03-19 | 9:33 | 49.837
2024-03-19 | 9:34 | 49.834
2024-03-19 | 9:34 | 49.832
2024-03-19 | 9:34 | 49.831
2024-03-19 | 9:34 | 49.831
2024-03-19 | 9:34 | 49.832
2024-03-19 | 9:34 | 49.836
2024-03-19 | 9:34 | 49.84
2024-03-19 | 9:34 | 49.847
2024-03-19 | 9:34 | 49.849
2024-03-19 | 9:34 | 49.851
2024-03-19 | 9:34 | 49.857
2024-03-19 | 9:34 | 49.863
2024-03-19 | 9:34 | 49.865
2024-03-19 | 9:34 | 49.868
2024-03-19 | 9:34 | 49.868
2024-03-19 | 9:34 | 49.876
2024-03-19 | 9:34 | 49.884
2024-03-19 | 9:34 | 49.883
2024-03-19 | 9:34 | 49.879
2024-03-19 | 9:34 | 49.88
2024-03-19 | 9:34 | 49.879
2024-03-19 | 9:34 | 49.879
2024-03-19 | 9:34 | 49.875
2024-03-19 | 9:34 | 49.873
2024-03-19 | 9:34 | 49.874
2024-03-19 | 9:34 | 49.877
2024-03-19 | 9:34 | 49.879
2024-03-19 | 9:34 | 49.874
2024-03-19 | 9:34 | 49.87
2024-03-19 | 9:34 | 49.87
2024-03-19 | 9:34 | 49.878
2024-03-19 | 9:34 | 49.882
2024-03-19 | 9:34 | 49.883
2024-03-19 | 9:34 | 49.881
2024-03-19 | 9:34 | 49.879
2024-03-19 | 9:34 | 49.881
2024-03-19 | 9:34 | 49.881
2024-03-19 | 9:34 | 49.881
2024-03-19 | 9:34 | 49.883
2024-03-19 | 9:34 | 49.885
2024-03-19 | 9:34 | 49.888
2024-03-19 | 9:34 | 49.89
2024-03-19 | 9:34 | 49.889
2024-03-19 | 9:34 | 49.889
2024-03-19 | 9:34 | 49.889
2024-03-19 | 9:34 | 49.886
2024-03-19 | 9:34 | 49.879
2024-03-19 | 9:34 | 49.877
2024-03-19 | 9:34 | 49.88
2024-03-19 | 9:34 | 49.884
2024-03-19 | 9:34 | 49.885
2024-03-19 | 9:34 | 49.885
2024-03-19 | 9:34 | 49.885
2024-03-19 | 9:34 | 49.886
2024-03-19 | 9:34 | 49.886
2024-03-19 | 9:34 | 49.885
2024-03-19 | 9:34 | 49.888
2024-03-19 | 9:34 | 49.889
2024-03-19 | 9:34 | 49.89
2024-03-19 | 9:34 | 49.892
2024-03-19 | 9:34 | 49.892
2024-03-19 | 9:35 | 49.894
2024-03-19 | 9:35 | 49.895
2024-03-19 | 9:35 | 49.895
2024-03-19 | 9:35 | 49.893
2024-03-19 | 9:35 | 49.892
2024-03-19 | 9:35 | 49.891
2024-03-19 | 9:35 | 49.892
2024-03-19 | 9:35 | 49.892
2024-03-19 | 9:35 | 49.891
2024-03-19 | 9:35 | 49.893
2024-03-19 | 9:35 | 49.896
2024-03-19 | 9:35 | 49.898
2024-03-19 | 9:35 | 49.901
2024-03-19 | 9:35 | 49.902
2024-03-19 | 9:35 | 49.902
2024-03-19 | 9:35 | 49.902
2024-03-19 | 9:35 | 49.9
2024-03-19 | 9:35 | 49.899
2024-03-19 | 9:35 | 49.898
2024-03-19 | 9:35 | 49.893
2024-03-19 | 9:35 | 49.889
2024-03-19 | 9:35 | 49.886
2024-03-19 | 9:35 | 49.881
2024-03-19 | 9:35 | 49.88
2024-03-19 | 9:35 | 49.877
2024-03-19 | 9:35 | 49.874
2024-03-19 | 9:35 | 49.87
2024-03-19 | 9:35 | 49.867
2024-03-19 | 9:35 | 49.867
2024-03-19 | 9:35 | 49.867
2024-03-19 | 9:35 | 49.866
2024-03-19 | 9:35 | 49.866
2024-03-19 | 9:35 | 49.871
2024-03-19 | 9:35 | 49.871
2024-03-19 | 9:35 | 49.869
2024-03-19 | 9:35 | 49.867
2024-03-19 | 9:35 | 49.869
2024-03-19 | 9:35 | 49.869
2024-03-19 | 9:35 | 49.866
2024-03-19 | 9:35 | 49.869
2024-03-19 | 9:35 | 49.869
2024-03-19 | 9:35 | 49.866
2024-03-19 | 9:35 | 49.863
2024-03-19 | 9:35 | 49.863
2024-03-19 | 9:35 | 49.863
2024-03-19 | 9:35 | 49.864
2024-03-19 | 9:35 | 49.864
2024-03-19 | 9:35 | 49.865
2024-03-19 | 9:35 | 49.864
2024-03-19 | 9:35 | 49.86
2024-03-19 | 9:35 | 49.857
2024-03-19 | 9:35 | 49.858
2024-03-19 | 9:35 | 49.861
2024-03-19 | 9:35 | 49.86
2024-03-19 | 9:35 | 49.86
2024-03-19 | 9:35 | 49.859
2024-03-19 | 9:35 | 49.859
2024-03-19 | 9:35 | 49.859
2024-03-19 | 9:35 | 49.862
2024-03-19 | 9:36 | 49.864
2024-03-19 | 9:36 | 49.865
2024-03-19 | 9:36 | 49.869
2024-03-19 | 9:36 | 49.871
2024-03-19 | 9:36 | 49.871
2024-03-19 | 9:36 | 49.875
2024-03-19 | 9:36 | 49.869
2024-03-19 | 9:36 | 49.866
2024-03-19 | 9:36 | 49.869
2024-03-19 | 9:36 | 49.871
2024-03-19 | 9:36 | 49.871
2024-03-19 | 9:36 | 49.87
2024-03-19 | 9:36 | 49.868
2024-03-19 | 9:36 | 49.871
2024-03-19 | 9:36 | 49.878
2024-03-19 | 9:36 | 49.884
2024-03-19 | 9:36 | 49.887
2024-03-19 | 9:36 | 49.889
2024-03-19 | 9:36 | 49.89
2024-03-19 | 9:36 | 49.889
2024-03-19 | 9:36 | 49.887
2024-03-19 | 9:36 | 49.885
2024-03-19 | 9:36 | 49.887
2024-03-19 | 9:36 | 49.889
2024-03-19 | 9:36 | 49.891
2024-03-19 | 9:36 | 49.892
2024-03-19 | 9:36 | 49.894
2024-03-19 | 9:36 | 49.896
2024-03-19 | 9:36 | 49.9
2024-03-19 | 9:36 | 49.899
2024-03-19 | 9:36 | 49.9
2024-03-19 | 9:36 | 49.895
2024-03-19 | 9:36 | 49.893
2024-03-19 | 9:36 | 49.897
2024-03-19 | 9:36 | 49.902
2024-03-19 | 9:36 | 49.901
2024-03-19 | 9:36 | 49.901
2024-03-19 | 9:36 | 49.899
2024-03-19 | 9:36 | 49.898
2024-03-19 | 9:36 | 49.899
2024-03-19 | 9:36 | 49.903
2024-03-19 | 9:36 | 49.906
2024-03-19 | 9:36 | 49.912
2024-03-19 | 9:36 | 49.915
2024-03-19 | 9:36 | 49.919
2024-03-19 | 9:36 | 49.921
2024-03-19 | 9:36 | 49.921
2024-03-19 | 9:36 | 49.917
2024-03-19 | 9:36 | 49.915
2024-03-19 | 9:36 | 49.912
2024-03-19 | 9:36 | 49.911
2024-03-19 | 9:36 | 49.909
2024-03-19 | 9:36 | 49.91
2024-03-19 | 9:36 | 49.907
2024-03-19 | 9:36 | 49.906
2024-03-19 | 9:36 | 49.9
2024-03-19 | 9:36 | 49.894
2024-03-19 | 9:36 | 49.889
2024-03-19 | 9:36 | 49.89
2024-03-19 | 9:36 | 49.888
2024-03-19 | 9:36 | 49.888
2024-03-19 | 9:37 | 49.89
2024-03-19 | 9:37 | 49.896
2024-03-19 | 9:37 | 49.901
2024-03-19 | 9:37 | 49.904
2024-03-19 | 9:37 | 49.907
2024-03-19 | 9:37 | 49.906
2024-03-19 | 9:37 | 49.903
2024-03-19 | 9:37 | 49.903
2024-03-19 | 9:37 | 49.902
2024-03-19 | 9:37 | 49.9
2024-03-19 | 9:37 | 49.898
2024-03-19 | 9:37 | 49.898
2024-03-19 | 9:37 | 49.901
2024-03-19 | 9:37 | 49.901
2024-03-19 | 9:37 | 49.901
2024-03-19 | 9:37 | 49.901
2024-03-19 | 9:37 | 49.903
2024-03-19 | 9:37 | 49.905
2024-03-19 | 9:37 | 49.907
2024-03-19 | 9:37 | 49.905
2024-03-19 | 9:37 | 49.906
2024-03-19 | 9:37 | 49.908
2024-03-19 | 9:37 | 49.91
2024-03-19 | 9:37 | 49.911
2024-03-19 | 9:37 | 49.913
2024-03-19 | 9:37 | 49.913
2024-03-19 | 9:37 | 49.911
2024-03-19 | 9:37 | 49.908
2024-03-19 | 9:37 | 49.908
2024-03-19 | 9:37 | 49.909
2024-03-19 | 9:37 | 49.91
2024-03-19 | 9:37 | 49.914
2024-03-19 | 9:37 | 49.918
2024-03-19 | 9:37 | 49.922
2024-03-19 | 9:37 | 49.929
2024-03-19 | 9:37 | 49.931
2024-03-19 | 9:37 | 49.931
2024-03-19 | 9:37 | 49.931
2024-03-19 | 9:37 | 49.93
2024-03-19 | 9:37 | 49.931
2024-03-19 | 9:37 | 49.929
2024-03-19 | 9:37 | 49.93
2024-03-19 | 9:37 | 49.928
2024-03-19 | 9:37 | 49.929
2024-03-19 | 9:37 | 49.928
2024-03-19 | 9:37 | 49.925
2024-03-19 | 9:37 | 49.919
2024-03-19 | 9:37 | 49.916
2024-03-19 | 9:37 | 49.917
2024-03-19 | 9:37 | 49.918
2024-03-19 | 9:37 | 49.919
2024-03-19 | 9:37 | 49.921
2024-03-19 | 9:37 | 49.924
2024-03-19 | 9:37 | 49.928
2024-03-19 | 9:37 | 49.931
2024-03-19 | 9:37 | 49.932
2024-03-19 | 9:37 | 49.932
2024-03-19 | 9:37 | 49.929
2024-03-19 | 9:37 | 49.93
2024-03-19 | 9:38 | 49.932
2024-03-19 | 9:38 | 49.934
2024-03-19 | 9:38 | 49.934
2024-03-19 | 9:38 | 49.934
2024-03-19 | 9:38 | 49.934
2024-03-19 | 9:38 | 49.936
2024-03-19 | 9:38 | 49.935
2024-03-19 | 9:38 | 49.932
2024-03-19 | 9:38 | 49.933
2024-03-19 | 9:38 | 49.934
2024-03-19 | 9:38 | 49.931
2024-03-19 | 9:38 | 49.921
2024-03-19 | 9:38 | 49.919
2024-03-19 | 9:38 | 49.913
2024-03-19 | 9:38 | 49.905
2024-03-19 | 9:38 | 49.897
2024-03-19 | 9:38 | 49.891
2024-03-19 | 9:38 | 49.89
2024-03-19 | 9:38 | 49.891
2024-03-19 | 9:38 | 49.888
2024-03-19 | 9:38 | 49.89
2024-03-19 | 9:38 | 49.889
2024-03-19 | 9:38 | 49.888
2024-03-19 | 9:38 | 49.888
2024-03-19 | 9:38 | 49.889
2024-03-19 | 9:38 | 49.893
2024-03-19 | 9:38 | 49.899
2024-03-19 | 9:38 | 49.905
2024-03-19 | 9:38 | 49.907
2024-03-19 | 9:38 | 49.905
2024-03-19 | 9:38 | 49.903
2024-03-19 | 9:38 | 49.902
2024-03-19 | 9:38 | 49.898
2024-03-19 | 9:38 | 49.896
2024-03-19 | 9:38 | 49.894
2024-03-19 | 9:38 | 49.892
2024-03-19 | 9:38 | 49.89
2024-03-19 | 9:38 | 49.89
2024-03-19 | 9:38 | 49.89
2024-03-19 | 9:38 | 49.892
2024-03-19 | 9:38 | 49.895
2024-03-19 | 9:38 | 49.892
2024-03-19 | 9:38 | 49.893
2024-03-19 | 9:38 | 49.896
2024-03-19 | 9:38 | 49.896
2024-03-19 | 9:38 | 49.901
2024-03-19 | 9:38 | 49.905
2024-03-19 | 9:38 | 49.906
2024-03-19 | 9:38 | 49.904
2024-03-19 | 9:38 | 49.904
2024-03-19 | 9:38 | 49.906
2024-03-19 | 9:38 | 49.91
2024-03-19 | 9:38 | 49.916
2024-03-19 | 9:38 | 49.92
2024-03-19 | 9:38 | 49.92
2024-03-19 | 9:38 | 49.923
2024-03-19 | 9:38 | 49.922
2024-03-19 | 9:38 | 49.923
2024-03-19 | 9:38 | 49.924
2024-03-19 | 9:38 | 49.921
2024-03-19 | 9:38 | 49.919
2024-03-19 | 9:39 | 49.917
2024-03-19 | 9:39 | 49.923
2024-03-19 | 9:39 | 49.924
2024-03-19 | 9:39 | 49.926
2024-03-19 | 9:39 | 49.929
2024-03-19 | 9:39 | 49.931
2024-03-19 | 9:39 | 49.936
2024-03-19 | 9:39 | 49.937
2024-03-19 | 9:39 | 49.938
2024-03-19 | 9:39 | 49.939
2024-03-19 | 9:39 | 49.935
2024-03-19 | 9:39 | 49.933
2024-03-19 | 9:39 | 49.932
2024-03-19 | 9:39 | 49.934
2024-03-19 | 9:39 | 49.933
2024-03-19 | 9:39 | 49.929
2024-03-19 | 9:39 | 49.924
2024-03-19 | 9:39 | 49.918
2024-03-19 | 9:39 | 49.913
2024-03-19 | 9:39 | 49.911
2024-03-19 | 9:39 | 49.909
2024-03-19 | 9:39 | 49.906
2024-03-19 | 9:39 | 49.905
2024-03-19 | 9:39 | 49.904
2024-03-19 | 9:39 | 49.905
2024-03-19 | 9:39 | 49.907
2024-03-19 | 9:39 | 49.902
2024-03-19 | 9:39 | 49.898
2024-03-19 | 9:39 | 49.898
2024-03-19 | 9:39 | 49.899
2024-03-19 | 9:39 | 49.898
2024-03-19 | 9:39 | 49.9
2024-03-19 | 9:39 | 49.899
2024-03-19 | 9:39 | 49.898
2024-03-19 | 9:39 | 49.896
2024-03-19 | 9:39 | 49.893
2024-03-19 | 9:39 | 49.889
2024-03-19 | 9:39 | 49.885
2024-03-19 | 9:39 | 49.881
2024-03-19 | 9:39 | 49.879
2024-03-19 | 9:39 | 49.881
2024-03-19 | 9:39 | 49.881
2024-03-19 | 9:39 | 49.88
2024-03-19 | 9:39 | 49.88
2024-03-19 | 9:39 | 49.883
2024-03-19 | 9:39 | 49.883
2024-03-19 | 9:39 | 49.887
2024-03-19 | 9:39 | 49.893
2024-03-19 | 9:39 | 49.896
2024-03-19 | 9:39 | 49.893
2024-03-19 | 9:39 | 49.89
2024-03-19 | 9:39 | 49.89
2024-03-19 | 9:39 | 49.889
2024-03-19 | 9:39 | 49.891
2024-03-19 | 9:39 | 49.891
2024-03-19 | 9:39 | 49.893
2024-03-19 | 9:39 | 49.892
2024-03-19 | 9:39 | 49.893
2024-03-19 | 9:39 | 49.892
2024-03-19 | 9:40 | 49.889
2024-03-19 | 9:40 | 49.892
2024-03-19 | 9:40 | 49.888
2024-03-19 | 9:40 | 49.891
2024-03-19 | 9:40 | 49.89
2024-03-19 | 9:40 | 49.89
2024-03-19 | 9:40 | 49.892
2024-03-19 | 9:40 | 49.895
2024-03-19 | 9:40 | 49.898
2024-03-19 | 9:40 | 49.895
2024-03-19 | 9:40 | 49.898
2024-03-19 | 9:40 | 49.906
2024-03-19 | 9:40 | 49.905
2024-03-19 | 9:40 | 49.9
2024-03-19 | 9:40 | 49.897
2024-03-19 | 9:40 | 49.897
2024-03-19 | 9:40 | 49.895
2024-03-19 | 9:40 | 49.891
2024-03-19 | 9:40 | 49.889
2024-03-19 | 9:40 | 49.89
2024-03-19 | 9:40 | 49.886
2024-03-19 | 9:40 | 49.884
2024-03-19 | 9:40 | 49.886
2024-03-19 | 9:40 | 49.892
2024-03-19 | 9:40 | 49.897
2024-03-19 | 9:40 | 49.899
2024-03-19 | 9:40 | 49.899
2024-03-19 | 9:40 | 49.9
2024-03-19 | 9:40 | 49.906
2024-03-19 | 9:40 | 49.906
2024-03-19 | 9:40 | 49.907
2024-03-19 | 9:40 | 49.908
2024-03-19 | 9:40 | 49.911
2024-03-19 | 9:40 | 49.913
2024-03-19 | 9:40 | 49.914
2024-03-19 | 9:40 | 49.915
2024-03-19 | 9:40 | 49.916
2024-03-19 | 9:40 | 49.917
2024-03-19 | 9:40 | 49.923
2024-03-19 | 9:40 | 49.925
2024-03-19 | 9:40 | 49.928
2024-03-19 | 9:40 | 49.926
2024-03-19 | 9:40 | 49.929
2024-03-19 | 9:40 | 49.932
2024-03-19 | 9:40 | 49.932
2024-03-19 | 9:40 | 49.933
2024-03-19 | 9:40 | 49.935
2024-03-19 | 9:40 | 49.936
2024-03-19 | 9:40 | 49.942
2024-03-19 | 9:40 | 49.947
2024-03-19 | 9:40 | 49.949
2024-03-19 | 9:40 | 49.953
2024-03-19 | 9:40 | 49.953
2024-03-19 | 9:40 | 49.952
2024-03-19 | 9:40 | 49.955
2024-03-19 | 9:40 | 49.964
2024-03-19 | 9:40 | 49.971
2024-03-19 | 9:40 | 49.974
2024-03-19 | 9:40 | 49.974
2024-03-19 | 9:40 | 49.974
2024-03-19 | 9:40 | 49.975
2024-03-19 | 9:41 | 49.978
2024-03-19 | 9:41 | 49.978
2024-03-19 | 9:41 | 49.977
2024-03-19 | 9:41 | 49.977
2024-03-19 | 9:41 | 49.977
2024-03-19 | 9:41 | 49.976
2024-03-19 | 9:41 | 49.974
2024-03-19 | 9:41 | 49.972
2024-03-19 | 9:41 | 49.97
2024-03-19 | 9:41 | 49.971
2024-03-19 | 9:41 | 49.969
2024-03-19 | 9:41 | 49.97
2024-03-19 | 9:41 | 49.97
2024-03-19 | 9:41 | 49.967
2024-03-19 | 9:41 | 49.965
2024-03-19 | 9:41 | 49.964
2024-03-19 | 9:41 | 49.963
2024-03-19 | 9:41 | 49.96
2024-03-19 | 9:41 | 49.957
2024-03-19 | 9:41 | 49.955
2024-03-19 | 9:41 | 49.959
2024-03-19 | 9:41 | 49.958
2024-03-19 | 9:41 | 49.959
2024-03-19 | 9:41 | 49.958
2024-03-19 | 9:41 | 49.954
2024-03-19 | 9:41 | 49.948
2024-03-19 | 9:41 | 49.948
2024-03-19 | 9:41 | 49.946
2024-03-19 | 9:41 | 49.943
2024-03-19 | 9:41 | 49.943
2024-03-19 | 9:41 | 49.94
2024-03-19 | 9:41 | 49.94
2024-03-19 | 9:41 | 49.941
2024-03-19 | 9:41 | 49.942
2024-03-19 | 9:41 | 49.945
2024-03-19 | 9:41 | 49.944
2024-03-19 | 9:41 | 49.945
2024-03-19 | 9:41 | 49.948
2024-03-19 | 9:41 | 49.951
2024-03-19 | 9:41 | 49.95
2024-03-19 | 9:41 | 49.945
2024-03-19 | 9:41 | 49.941
2024-03-19 | 9:41 | 49.942
2024-03-19 | 9:41 | 49.942
2024-03-19 | 9:41 | 49.944
2024-03-19 | 9:41 | 49.942
2024-03-19 | 9:41 | 49.94
2024-03-19 | 9:41 | 49.938
2024-03-19 | 9:41 | 49.937
2024-03-19 | 9:41 | 49.932
2024-03-19 | 9:41 | 49.927
2024-03-19 | 9:41 | 49.927
2024-03-19 | 9:41 | 49.928
2024-03-19 | 9:41 | 49.929
2024-03-19 | 9:41 | 49.932
2024-03-19 | 9:41 | 49.933
2024-03-19 | 9:41 | 49.933
2024-03-19 | 9:41 | 49.935
2024-03-19 | 9:41 | 49.936
2024-03-19 | 9:42 | 49.933
2024-03-19 | 9:42 | 49.933
2024-03-19 | 9:42 | 49.933
2024-03-19 | 9:42 | 49.933
2024-03-19 | 9:42 | 49.932
2024-03-19 | 9:42 | 49.932
2024-03-19 | 9:42 | 49.933
2024-03-19 | 9:42 | 49.93
2024-03-19 | 9:42 | 49.928
2024-03-19 | 9:42 | 49.932
2024-03-19 | 9:42 | 49.934
2024-03-19 | 9:42 | 49.935
2024-03-19 | 9:42 | 49.936
2024-03-19 | 9:42 | 49.938
2024-03-19 | 9:42 | 49.938
2024-03-19 | 9:42 | 49.938
2024-03-19 | 9:42 | 49.942
2024-03-19 | 9:42 | 49.945
2024-03-19 | 9:42 | 49.944
2024-03-19 | 9:42 | 49.945
2024-03-19 | 9:42 | 49.943
2024-03-19 | 9:42 | 49.942
2024-03-19 | 9:42 | 49.942
2024-03-19 | 9:42 | 49.94
2024-03-19 | 9:42 | 49.945
2024-03-19 | 9:42 | 49.948
2024-03-19 | 9:42 | 49.946
2024-03-19 | 9:42 | 49.939
2024-03-19 | 9:42 | 49.932
2024-03-19 | 9:42 | 49.927
2024-03-19 | 9:42 | 49.924
2024-03-19 | 9:42 | 49.923
2024-03-19 | 9:42 | 49.919
2024-03-19 | 9:42 | 49.918
2024-03-19 | 9:42 | 49.916
2024-03-19 | 9:42 | 49.918
2024-03-19 | 9:42 | 49.924
2024-03-19 | 9:42 | 49.931
2024-03-19 | 9:42 | 49.938
2024-03-19 | 9:42 | 49.947
2024-03-19 | 9:42 | 49.949
2024-03-19 | 9:42 | 49.946
2024-03-19 | 9:42 | 49.946
2024-03-19 | 9:42 | 49.95
2024-03-19 | 9:42 | 49.956
2024-03-19 | 9:42 | 49.959
2024-03-19 | 9:42 | 49.958
2024-03-19 | 9:42 | 49.956
2024-03-19 | 9:42 | 49.954
2024-03-19 | 9:42 | 49.953
2024-03-19 | 9:42 | 49.955
2024-03-19 | 9:42 | 49.955
2024-03-19 | 9:42 | 49.954
2024-03-19 | 9:42 | 49.953
2024-03-19 | 9:42 | 49.956
2024-03-19 | 9:42 | 49.959
2024-03-19 | 9:42 | 49.958
2024-03-19 | 9:42 | 49.956
2024-03-19 | 9:42 | 49.963
2024-03-19 | 9:42 | 49.964
2024-03-19 | 9:42 | 49.967
2024-03-19 | 9:43 | 49.97
2024-03-19 | 9:43 | 49.971
2024-03-19 | 9:43 | 49.97
2024-03-19 | 9:43 | 49.971
2024-03-19 | 9:43 | 49.976
2024-03-19 | 9:43 | 49.974
2024-03-19 | 9:43 | 49.972
2024-03-19 | 9:43 | 49.967
2024-03-19 | 9:43 | 49.967
2024-03-19 | 9:43 | 49.97
2024-03-19 | 9:43 | 49.973
2024-03-19 | 9:43 | 49.972
2024-03-19 | 9:43 | 49.971
2024-03-19 | 9:43 | 49.975
2024-03-19 | 9:43 | 49.972
2024-03-19 | 9:43 | 49.968
2024-03-19 | 9:43 | 49.962
2024-03-19 | 9:43 | 49.964
2024-03-19 | 9:43 | 49.965
2024-03-19 | 9:43 | 49.961
2024-03-19 | 9:43 | 49.957
2024-03-19 | 9:43 | 49.95
2024-03-19 | 9:43 | 49.95
2024-03-19 | 9:43 | 49.951
2024-03-19 | 9:43 | 49.952
2024-03-19 | 9:43 | 49.953
2024-03-19 | 9:43 | 49.953
2024-03-19 | 9:43 | 49.953
2024-03-19 | 9:43 | 49.956
2024-03-19 | 9:43 | 49.955
2024-03-19 | 9:43 | 49.949
2024-03-19 | 9:43 | 49.947
2024-03-19 | 9:43 | 49.946
2024-03-19 | 9:43 | 49.947
2024-03-19 | 9:43 | 49.95
2024-03-19 | 9:43 | 49.954
2024-03-19 | 9:43 | 49.956
2024-03-19 | 9:43 | 49.955
2024-03-19 | 9:43 | 49.958
2024-03-19 | 9:43 | 49.958
2024-03-19 | 9:43 | 49.961
2024-03-19 | 9:43 | 49.961
2024-03-19 | 9:43 | 49.961
2024-03-19 | 9:43 | 49.964
2024-03-19 | 9:43 | 49.967
2024-03-19 | 9:43 | 49.969
2024-03-19 | 9:43 | 49.971
2024-03-19 | 9:43 | 49.969
2024-03-19 | 9:43 | 49.965
2024-03-19 | 9:43 | 49.968
2024-03-19 | 9:43 | 49.974
2024-03-19 | 9:43 | 49.978
2024-03-19 | 9:43 | 49.977
2024-03-19 | 9:43 | 49.98
2024-03-19 | 9:43 | 49.984
2024-03-19 | 9:43 | 49.988
2024-03-19 | 9:43 | 49.99
2024-03-19 | 9:43 | 49.986
2024-03-19 | 9:43 | 49.978
2024-03-19 | 9:44 | 49.97
2024-03-19 | 9:44 | 49.962
2024-03-19 | 9:44 | 49.963
2024-03-19 | 9:44 | 49.967
2024-03-19 | 9:44 | 49.967
2024-03-19 | 9:44 | 49.966
2024-03-19 | 9:44 | 49.967
2024-03-19 | 9:44 | 49.967
2024-03-19 | 9:44 | 49.972
2024-03-19 | 9:44 | 49.975
2024-03-19 | 9:44 | 49.976
2024-03-19 | 9:44 | 49.978
2024-03-19 | 9:44 | 49.978
2024-03-19 | 9:44 | 49.976
2024-03-19 | 9:44 | 49.974
2024-03-19 | 9:44 | 49.974
2024-03-19 | 9:44 | 49.97
2024-03-19 | 9:44 | 49.971
2024-03-19 | 9:44 | 49.974
2024-03-19 | 9:44 | 49.976
2024-03-19 | 9:44 | 49.974
2024-03-19 | 9:44 | 49.974
2024-03-19 | 9:44 | 49.976
2024-03-19 | 9:44 | 49.979
2024-03-19 | 9:44 | 49.98
2024-03-19 | 9:44 | 49.981
2024-03-19 | 9:44 | 49.982
2024-03-19 | 9:44 | 49.986
2024-03-19 | 9:44 | 49.99
2024-03-19 | 9:44 | 49.994
2024-03-19 | 9:44 | 49.999
2024-03-19 | 9:44 | 50.005
2024-03-19 | 9:44 | 50.007
2024-03-19 | 9:44 | 50.007
2024-03-19 | 9:44 | 50.004
2024-03-19 | 9:44 | 49.999
2024-03-19 | 9:44 | 49.991
2024-03-19 | 9:44 | 49.983
2024-03-19 | 9:44 | 49.977
2024-03-19 | 9:44 | 49.971
2024-03-19 | 9:44 | 49.968
2024-03-19 | 9:44 | 49.968
2024-03-19 | 9:44 | 49.966
2024-03-19 | 9:44 | 49.964
2024-03-19 | 9:44 | 49.967
2024-03-19 | 9:44 | 49.971
2024-03-19 | 9:44 | 49.973
2024-03-19 | 9:44 | 49.971
2024-03-19 | 9:44 | 49.969
2024-03-19 | 9:44 | 49.972
2024-03-19 | 9:44 | 49.974
2024-03-19 | 9:44 | 49.974
2024-03-19 | 9:44 | 49.973
2024-03-19 | 9:44 | 49.973
2024-03-19 | 9:44 | 49.973
2024-03-19 | 9:44 | 49.974
2024-03-19 | 9:44 | 49.974
2024-03-19 | 9:44 | 49.979
2024-03-19 | 9:44 | 49.979
2024-03-19 | 9:44 | 49.979
2024-03-19 | 9:44 | 49.979
2024-03-19 | 9:45 | 49.981
2024-03-19 | 9:45 | 49.98
2024-03-19 | 9:45 | 49.977
2024-03-19 | 9:45 | 49.972
2024-03-19 | 9:45 | 49.969
2024-03-19 | 9:45 | 49.968
2024-03-19 | 9:45 | 49.963
2024-03-19 | 9:45 | 49.963
2024-03-19 | 9:45 | 49.963
2024-03-19 | 9:45 | 49.965
2024-03-19 | 9:45 | 49.965
2024-03-19 | 9:45 | 49.965
2024-03-19 | 9:45 | 49.968
2024-03-19 | 9:45 | 49.97
2024-03-19 | 9:45 | 49.969
2024-03-19 | 9:45 | 49.969
2024-03-19 | 9:45 | 49.974
2024-03-19 | 9:45 | 49.978
2024-03-19 | 9:45 | 49.975
2024-03-19 | 9:45 | 49.971
2024-03-19 | 9:45 | 49.965
2024-03-19 | 9:45 | 49.962
2024-03-19 | 9:45 | 49.96
2024-03-19 | 9:45 | 49.957
2024-03-19 | 9:45 | 49.956
2024-03-19 | 9:45 | 49.955
2024-03-19 | 9:45 | 49.956
2024-03-19 | 9:45 | 49.958
2024-03-19 | 9:45 | 49.96
2024-03-19 | 9:45 | 49.962
2024-03-19 | 9:45 | 49.96
2024-03-19 | 9:45 | 49.963
2024-03-19 | 9:45 | 49.967
2024-03-19 | 9:45 | 49.97
2024-03-19 | 9:45 | 49.972
2024-03-19 | 9:45 | 49.972
2024-03-19 | 9:45 | 49.97
2024-03-19 | 9:45 | 49.969
2024-03-19 | 9:45 | 49.968
2024-03-19 | 9:45 | 49.965
2024-03-19 | 9:45 | 49.957
2024-03-19 | 9:45 | 49.951
2024-03-19 | 9:45 | 49.948
2024-03-19 | 9:45 | 49.947
2024-03-19 | 9:45 | 49.947
2024-03-19 | 9:45 | 49.951
2024-03-19 | 9:45 | 49.953
2024-03-19 | 9:45 | 49.955
2024-03-19 | 9:45 | 49.959
2024-03-19 | 9:45 | 49.964
2024-03-19 | 9:45 | 49.961
2024-03-19 | 9:45 | 49.959
2024-03-19 | 9:45 | 49.961
2024-03-19 | 9:45 | 49.964
2024-03-19 | 9:45 | 49.967
2024-03-19 | 9:45 | 49.971
2024-03-19 | 9:45 | 49.976
2024-03-19 | 9:45 | 49.979
2024-03-19 | 9:45 | 49.98
2024-03-19 | 9:46 | 49.978
2024-03-19 | 9:46 | 49.973
2024-03-19 | 9:46 | 49.972
2024-03-19 | 9:46 | 49.978
2024-03-19 | 9:46 | 49.979
2024-03-19 | 9:46 | 49.977
2024-03-19 | 9:46 | 49.972
2024-03-19 | 9:46 | 49.968
2024-03-19 | 9:46 | 49.964
2024-03-19 | 9:46 | 49.956
2024-03-19 | 9:46 | 49.948
2024-03-19 | 9:46 | 49.939
2024-03-19 | 9:46 | 49.933
2024-03-19 | 9:46 | 49.926
2024-03-19 | 9:46 | 49.919
2024-03-19 | 9:46 | 49.913
2024-03-19 | 9:46 | 49.91
2024-03-19 | 9:46 | 49.907
2024-03-19 | 9:46 | 49.907
2024-03-19 | 9:46 | 49.908
2024-03-19 | 9:46 | 49.91
2024-03-19 | 9:46 | 49.911
2024-03-19 | 9:46 | 49.911
2024-03-19 | 9:46 | 49.909
2024-03-19 | 9:46 | 49.906
2024-03-19 | 9:46 | 49.902
2024-03-19 | 9:46 | 49.902
2024-03-19 | 9:46 | 49.901
2024-03-19 | 9:46 | 49.899
2024-03-19 | 9:46 | 49.895

## 20240326-1
In GMT
Date | Time | Freq
2024-03-26 | 18:33 | 49.982 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-26 | 18:33 | 49.983 | 222 | BRITNED | 676.211
2024-03-26 | 18:33 | 49.983 | 268 | WBURB-2 | 428.156
2024-03-26 | 18:33 | 49.983 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-26 | 18:33 | 49.985 |  | Viking Link | -648.9
2024-03-26 | 18:33 | 49.986 |  | Viking Link | 1398.96
2024-03-26 | 18:33 | 49.988 | 209 | DRAXX-3 | 626.95
2024-03-26 | 18:33 | 49.99 | 154 | CDCL-1 | 391.57
2024-03-26 | 18:33 | 49.993 | 268 | ROCK-1 | 468.495
2024-03-26 | 18:33 | 49.994 | 148 | IFA Bipole1 | 945.473
2024-03-26 | 18:33 | 49.993 | 132 | IFA Bipole1 | 999.1
2024-03-26 | 18:33 | 49.993 | 141 | IFA Bipole2 | 1000
2024-03-26 | 18:33 | 49.995 | 135 | IFA Bipole1 | 996.75
2024-03-26 | 18:33 | 49.996 |  | Viking Link | -780.3
2024-03-26 | 18:33 | 49.999
2024-03-26 | 18:33 | 50
2024-03-26 | 18:33 | 50.001
2024-03-26 | 18:33 | 50.001
2024-03-26 | 18:33 | 50.002
2024-03-26 | 18:33 | 50.005 | 130 | HEYM12 | 271.908
2024-03-26 | 18:33 | 50.005 | 228 | HUMR-1 | 303.75
2024-03-26 | 18:33 | 50.003
2024-03-26 | 18:33 | 50.002
2024-03-26 | 18:33 | 50.002
2024-03-26 | 18:33 | 50.003
2024-03-26 | 18:33 | 50.003
2024-03-26 | 18:33 | 50.006
2024-03-26 | 18:33 | 50.009
2024-03-26 | 18:33 | 50.01
2024-03-26 | 18:33 | 50.012
2024-03-26 | 18:34 | 50.011 | 211 | CDCL-1 | 291.5
2024-03-26 | 18:34 | 50.009 | 199 | STAY-2 | 413.125
2024-03-26 | 18:34 | 50.008 | 173 | CDCL-1 | 397.375
2024-03-26 | 18:34 | 50.003 | 248 | SEAB-2 | 361.25
2024-03-26 | 18:34 | 50.005 | 255 | FRANCE | 995.65
2024-03-26 | 18:34 | 50.002 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-26 | 18:34 | 50.003
2024-03-26 | 18:34 | 50.001
2024-03-26 | 18:34 | 50.001
2024-03-26 | 18:34 | 49.998
2024-03-26 | 18:34 | 49.997
2024-03-26 | 18:34 | 49.992
2024-03-26 | 18:34 | 49.989
2024-03-26 | 18:34 | 49.986
2024-03-26 | 18:34 | 49.982
2024-03-26 | 18:34 | 49.977
2024-03-26 | 18:34 | 49.978
2024-03-26 | 18:34 | 49.976
2024-03-26 | 18:34 | 49.973
2024-03-26 | 18:34 | 49.973
2024-03-26 | 18:34 | 49.972
2024-03-26 | 18:34 | 49.972
2024-03-26 | 18:34 | 49.973
2024-03-26 | 18:34 | 49.969
2024-03-26 | 18:34 | 49.97
2024-03-26 | 18:34 | 49.97
2024-03-26 | 18:34 | 49.955
2024-03-26 | 18:34 | 49.914
2024-03-26 | 18:34 | 49.882
2024-03-26 | 18:34 | 49.86
2024-03-26 | 18:34 | 49.848
2024-03-26 | 18:34 | 49.84
2024-03-26 | 18:34 | 49.833
2024-03-26 | 18:34 | 49.829
2024-03-26 | 18:34 | 49.83
2024-03-26 | 18:34 | 49.831
2024-03-26 | 18:34 | 49.83
2024-03-26 | 18:34 | 49.83
2024-03-26 | 18:34 | 49.83
2024-03-26 | 18:34 | 49.827
2024-03-26 | 18:34 | 49.831
2024-03-26 | 18:34 | 49.828
2024-03-26 | 18:34 | 49.826
2024-03-26 | 18:34 | 49.826
2024-03-26 | 18:34 | 49.823
2024-03-26 | 18:34 | 49.823
2024-03-26 | 18:34 | 49.822
2024-03-26 | 18:34 | 49.819
2024-03-26 | 18:34 | 49.82
2024-03-26 | 18:34 | 49.82
2024-03-26 | 18:34 | 49.821
2024-03-26 | 18:34 | 49.821
2024-03-26 | 18:34 | 49.819
2024-03-26 | 18:34 | 49.821
2024-03-26 | 18:34 | 49.818
2024-03-26 | 18:34 | 49.822
2024-03-26 | 18:34 | 49.821
2024-03-26 | 18:34 | 49.825
2024-03-26 | 18:34 | 49.828
2024-03-26 | 18:34 | 49.83
2024-03-26 | 18:34 | 49.835
2024-03-26 | 18:35 | 49.835
2024-03-26 | 18:35 | 49.837
2024-03-26 | 18:35 | 49.84
2024-03-26 | 18:35 | 49.84
2024-03-26 | 18:35 | 49.844
2024-03-26 | 18:35 | 49.844
2024-03-26 | 18:35 | 49.842
2024-03-26 | 18:35 | 49.844
2024-03-26 | 18:35 | 49.844
2024-03-26 | 18:35 | 49.845
2024-03-26 | 18:35 | 49.847
2024-03-26 | 18:35 | 49.849
2024-03-26 | 18:35 | 49.851
2024-03-26 | 18:35 | 49.855
2024-03-26 | 18:35 | 49.86
2024-03-26 | 18:35 | 49.862
2024-03-26 | 18:35 | 49.865
2024-03-26 | 18:35 | 49.868
2024-03-26 | 18:35 | 49.87
2024-03-26 | 18:35 | 49.869
2024-03-26 | 18:35 | 49.867
2024-03-26 | 18:35 | 49.865
2024-03-26 | 18:35 | 49.867
2024-03-26 | 18:35 | 49.867
2024-03-26 | 18:35 | 49.868
2024-03-26 | 18:35 | 49.869
2024-03-26 | 18:35 | 49.873
2024-03-26 | 18:35 | 49.874
2024-03-26 | 18:35 | 49.874
2024-03-26 | 18:35 | 49.87
2024-03-26 | 18:35 | 49.87
2024-03-26 | 18:35 | 49.869
2024-03-26 | 18:35 | 49.867
2024-03-26 | 18:35 | 49.867
2024-03-26 | 18:35 | 49.866
2024-03-26 | 18:35 | 49.865
2024-03-26 | 18:35 | 49.864
2024-03-26 | 18:35 | 49.864
2024-03-26 | 18:35 | 49.864
2024-03-26 | 18:35 | 49.863
2024-03-26 | 18:35 | 49.862
2024-03-26 | 18:35 | 49.866
2024-03-26 | 18:35 | 49.866
2024-03-26 | 18:35 | 49.867
2024-03-26 | 18:35 | 49.868
2024-03-26 | 18:35 | 49.868
2024-03-26 | 18:35 | 49.87
2024-03-26 | 18:35 | 49.87
2024-03-26 | 18:35 | 49.876
2024-03-26 | 18:35 | 49.875
2024-03-26 | 18:35 | 49.88
2024-03-26 | 18:35 | 49.876
2024-03-26 | 18:35 | 49.879
2024-03-26 | 18:35 | 49.878
2024-03-26 | 18:35 | 49.881
2024-03-26 | 18:35 | 49.879
2024-03-26 | 18:35 | 49.883
2024-03-26 | 18:35 | 49.881
2024-03-26 | 18:35 | 49.886
2024-03-26 | 18:36 | 49.888
2024-03-26 | 18:36 | 49.892
2024-03-26 | 18:36 | 49.891
2024-03-26 | 18:36 | 49.895
2024-03-26 | 18:36 | 49.895
2024-03-26 | 18:36 | 49.897
2024-03-26 | 18:36 | 49.897
2024-03-26 | 18:36 | 49.898
2024-03-26 | 18:36 | 49.9
2024-03-26 | 18:36 | 49.9
2024-03-26 | 18:36 | 49.903
2024-03-26 | 18:36 | 49.906
2024-03-26 | 18:36 | 49.909
2024-03-26 | 18:36 | 49.911
2024-03-26 | 18:36 | 49.91
2024-03-26 | 18:36 | 49.912
2024-03-26 | 18:36 | 49.912
2024-03-26 | 18:36 | 49.912
2024-03-26 | 18:36 | 49.914
2024-03-26 | 18:36 | 49.915
2024-03-26 | 18:36 | 49.916
2024-03-26 | 18:36 | 49.915
2024-03-26 | 18:36 | 49.916
2024-03-26 | 18:36 | 49.915
2024-03-26 | 18:36 | 49.915
2024-03-26 | 18:36 | 49.912
2024-03-26 | 18:36 | 49.911
2024-03-26 | 18:36 | 49.914
2024-03-26 | 18:36 | 49.917
2024-03-26 | 18:36 | 49.92
2024-03-26 | 18:36 | 49.919
2024-03-26 | 18:36 | 49.921
2024-03-26 | 18:36 | 49.924
2024-03-26 | 18:36 | 49.929
2024-03-26 | 18:36 | 49.93
2024-03-26 | 18:36 | 49.93
2024-03-26 | 18:36 | 49.93
2024-03-26 | 18:36 | 49.933
2024-03-26 | 18:36 | 49.934
2024-03-26 | 18:36 | 49.934
2024-03-26 | 18:36 | 49.936
2024-03-26 | 18:36 | 49.938
2024-03-26 | 18:36 | 49.94
2024-03-26 | 18:36 | 49.942
2024-03-26 | 18:36 | 49.942
2024-03-26 | 18:36 | 49.945
2024-03-26 | 18:36 | 49.945
2024-03-26 | 18:36 | 49.947
2024-03-26 | 18:36 | 49.948
2024-03-26 | 18:36 | 49.947
2024-03-26 | 18:36 | 49.947
2024-03-26 | 18:36 | 49.947
2024-03-26 | 18:36 | 49.943
2024-03-26 | 18:36 | 49.944
2024-03-26 | 18:36 | 49.944
2024-03-26 | 18:36 | 49.94
2024-03-26 | 18:36 | 49.94
2024-03-26 | 18:36 | 49.938
2024-03-26 | 18:36 | 49.94
2024-03-26 | 18:36 | 49.944
2024-03-26 | 18:36 | 49.946
2024-03-26 | 18:37 | 49.951
2024-03-26 | 18:37 | 49.952
2024-03-26 | 18:37 | 49.954
2024-03-26 | 18:37 | 49.953
2024-03-26 | 18:37 | 49.955
2024-03-26 | 18:37 | 49.951
2024-03-26 | 18:37 | 49.95
2024-03-26 | 18:37 | 49.947
2024-03-26 | 18:37 | 49.948
2024-03-26 | 18:37 | 49.946
2024-03-26 | 18:37 | 49.947
2024-03-26 | 18:37 | 49.948
2024-03-26 | 18:37 | 49.95
2024-03-26 | 18:37 | 49.952
2024-03-26 | 18:37 | 49.955
2024-03-26 | 18:37 | 49.956
2024-03-26 | 18:37 | 49.963
2024-03-26 | 18:37 | 49.964
2024-03-26 | 18:37 | 49.965
2024-03-26 | 18:37 | 49.965
2024-03-26 | 18:37 | 49.966
2024-03-26 | 18:37 | 49.967
2024-03-26 | 18:37 | 49.97
2024-03-26 | 18:37 | 49.969
2024-03-26 | 18:37 | 49.971
2024-03-26 | 18:37 | 49.97
2024-03-26 | 18:37 | 49.972
2024-03-26 | 18:37 | 49.971
2024-03-26 | 18:37 | 49.974
2024-03-26 | 18:37 | 49.974
2024-03-26 | 18:37 | 49.976
2024-03-26 | 18:37 | 49.974
2024-03-26 | 18:37 | 49.974
2024-03-26 | 18:37 | 49.975
2024-03-26 | 18:37 | 49.979
2024-03-26 | 18:37 | 49.98
2024-03-26 | 18:37 | 49.982
2024-03-26 | 18:37 | 49.98
2024-03-26 | 18:37 | 49.982
2024-03-26 | 18:37 | 49.982
2024-03-26 | 18:37 | 49.982
2024-03-26 | 18:37 | 49.983
2024-03-26 | 18:37 | 49.981
2024-03-26 | 18:37 | 49.981
2024-03-26 | 18:37 | 49.977
2024-03-26 | 18:37 | 49.975
2024-03-26 | 18:37 | 49.97
2024-03-26 | 18:37 | 49.97
2024-03-26 | 18:37 | 49.968
2024-03-26 | 18:37 | 49.97
2024-03-26 | 18:37 | 49.969
2024-03-26 | 18:37 | 49.97
2024-03-26 | 18:37 | 49.972
2024-03-26 | 18:37 | 49.975
2024-03-26 | 18:37 | 49.976
2024-03-26 | 18:37 | 49.978
2024-03-26 | 18:37 | 49.977
2024-03-26 | 18:37 | 49.977
2024-03-26 | 18:37 | 49.976
2024-03-26 | 18:38 | 49.976
2024-03-26 | 18:38 | 49.975
2024-03-26 | 18:38 | 49.974
2024-03-26 | 18:38 | 49.973
2024-03-26 | 18:38 | 49.974
2024-03-26 | 18:38 | 49.974
2024-03-26 | 18:38 | 49.971
2024-03-26 | 18:38 | 49.967
2024-03-26 | 18:38 | 49.964
2024-03-26 | 18:38 | 49.962
2024-03-26 | 18:38 | 49.962
2024-03-26 | 18:38 | 49.958
2024-03-26 | 18:38 | 49.958
2024-03-26 | 18:38 | 49.961
2024-03-26 | 18:38 | 49.962
2024-03-26 | 18:38 | 49.962
2024-03-26 | 18:38 | 49.965
2024-03-26 | 18:38 | 49.963
2024-03-26 | 18:38 | 49.963
2024-03-26 | 18:38 | 49.962
2024-03-26 | 18:38 | 49.961
2024-03-26 | 18:38 | 49.962
2024-03-26 | 18:38 | 49.964
2024-03-26 | 18:38 | 49.963
2024-03-26 | 18:38 | 49.965
2024-03-26 | 18:38 | 49.968
2024-03-26 | 18:38 | 49.969
2024-03-26 | 18:38 | 49.969
2024-03-26 | 18:38 | 49.973
2024-03-26 | 18:38 | 49.975
2024-03-26 | 18:38 | 49.977
2024-03-26 | 18:38 | 49.977
2024-03-26 | 18:38 | 49.973
2024-03-26 | 18:38 | 49.977
2024-03-26 | 18:38 | 49.976
2024-03-26 | 18:38 | 49.975
2024-03-26 | 18:38 | 49.976
2024-03-26 | 18:38 | 49.976
2024-03-26 | 18:38 | 49.977
2024-03-26 | 18:38 | 49.976
2024-03-26 | 18:38 | 49.976
2024-03-26 | 18:38 | 49.976
2024-03-26 | 18:38 | 49.98
2024-03-26 | 18:38 | 49.982
2024-03-26 | 18:38 | 49.987
2024-03-26 | 18:38 | 49.99
2024-03-26 | 18:38 | 49.992
2024-03-26 | 18:38 | 49.994
2024-03-26 | 18:38 | 49.996
2024-03-26 | 18:38 | 49.998
2024-03-26 | 18:38 | 49.998
2024-03-26 | 18:38 | 50.003
2024-03-26 | 18:38 | 50.002
2024-03-26 | 18:38 | 50.005
2024-03-26 | 18:38 | 50.009
2024-03-26 | 18:38 | 50.015
2024-03-26 | 18:38 | 50.022
2024-03-26 | 18:38 | 50.024
2024-03-26 | 18:38 | 50.028
2024-03-26 | 18:38 | 50.033
2024-03-26 | 18:38 | 50.031
2024-03-26 | 18:39 | 50.028
2024-03-26 | 18:39 | 50.028
2024-03-26 | 18:39 | 50.029
2024-03-26 | 18:39 | 50.027
2024-03-26 | 18:39 | 50.023
2024-03-26 | 18:39 | 50.021
2024-03-26 | 18:39 | 50.018
2024-03-26 | 18:39 | 50.016
2024-03-26 | 18:39 | 50.017
2024-03-26 | 18:39 | 50.022
2024-03-26 | 18:39 | 50.024
2024-03-26 | 18:39 | 50.024
2024-03-26 | 18:39 | 50.028
2024-03-26 | 18:39 | 50.026
2024-03-26 | 18:39 | 50.029
2024-03-26 | 18:39 | 50.026
2024-03-26 | 18:39 | 50.025
2024-03-26 | 18:39 | 50.02
2024-03-26 | 18:39 | 50.019
2024-03-26 | 18:39 | 50.017
2024-03-26 | 18:39 | 50.012
2024-03-26 | 18:39 | 50.012
2024-03-26 | 18:39 | 50.011
2024-03-26 | 18:39 | 50.009
2024-03-26 | 18:39 | 50.009
2024-03-26 | 18:39 | 50.011
2024-03-26 | 18:39 | 50.008
2024-03-26 | 18:39 | 50.01
2024-03-26 | 18:39 | 50.009
2024-03-26 | 18:39 | 50.01
2024-03-26 | 18:39 | 50.01
2024-03-26 | 18:39 | 50.007
2024-03-26 | 18:39 | 50.007
2024-03-26 | 18:39 | 50.001
2024-03-26 | 18:39 | 49.999
2024-03-26 | 18:39 | 49.998
2024-03-26 | 18:39 | 50
2024-03-26 | 18:39 | 50.001
2024-03-26 | 18:39 | 50.003
2024-03-26 | 18:39 | 50.004
2024-03-26 | 18:39 | 50.003
2024-03-26 | 18:39 | 50.004
2024-03-26 | 18:39 | 50.004
2024-03-26 | 18:39 | 50.003
2024-03-26 | 18:39 | 50.006
2024-03-26 | 18:39 | 50.011
2024-03-26 | 18:39 | 50.009
2024-03-26 | 18:39 | 50.013
2024-03-26 | 18:39 | 50.013
2024-03-26 | 18:39 | 50.009
2024-03-26 | 18:39 | 50.006
2024-03-26 | 18:39 | 50.003
2024-03-26 | 18:39 | 50.003
2024-03-26 | 18:39 | 50.001
2024-03-26 | 18:39 | 50.003
2024-03-26 | 18:39 | 50.003
2024-03-26 | 18:39 | 50.002
2024-03-26 | 18:39 | 50.003
2024-03-26 | 18:39 | 50.004
2024-03-26 | 18:40 | 50.004
2024-03-26 | 18:40 | 50.007
2024-03-26 | 18:40 | 50.005
2024-03-26 | 18:40 | 50.006
2024-03-26 | 18:40 | 50.005
2024-03-26 | 18:40 | 50.006
2024-03-26 | 18:40 | 50.009
2024-03-26 | 18:40 | 50.011
2024-03-26 | 18:40 | 50.011
2024-03-26 | 18:40 | 50.015
2024-03-26 | 18:40 | 50.016
2024-03-26 | 18:40 | 50.016
2024-03-26 | 18:40 | 50.018
2024-03-26 | 18:40 | 50.019
2024-03-26 | 18:40 | 50.021
2024-03-26 | 18:40 | 50.023
2024-03-26 | 18:40 | 50.023
2024-03-26 | 18:40 | 50.026
2024-03-26 | 18:40 | 50.025
2024-03-26 | 18:40 | 50.028
2024-03-26 | 18:40 | 50.028
2024-03-26 | 18:40 | 50.027
2024-03-26 | 18:40 | 50.027
2024-03-26 | 18:40 | 50.025
2024-03-26 | 18:40 | 50.025
2024-03-26 | 18:40 | 50.022
2024-03-26 | 18:40 | 50.021
2024-03-26 | 18:40 | 50.02
2024-03-26 | 18:40 | 50.018
2024-03-26 | 18:40 | 50.019

## 20240328-1
In GMT
Date | Time | Freq
2024-03-28 | 10:20 | 50.034 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-28 | 10:20 | 50.029 | 222 | BRITNED | 676.211
2024-03-28 | 10:20 | 50.025 | 268 | WBURB-2 | 428.156
2024-03-28 | 10:20 | 50.021 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-28 | 10:20 | 50.019 |  | Viking Link | -648.9
2024-03-28 | 10:20 | 50.019 |  | Viking Link | 1398.96
2024-03-28 | 10:20 | 50.024 | 209 | DRAXX-3 | 626.95
2024-03-28 | 10:20 | 50.026 | 154 | CDCL-1 | 391.57
2024-03-28 | 10:20 | 50.026 | 268 | ROCK-1 | 468.495
2024-03-28 | 10:20 | 50.03 | 148 | IFA Bipole1 | 945.473
2024-03-28 | 10:20 | 50.03 | 132 | IFA Bipole1 | 999.1
2024-03-28 | 10:20 | 50.034 | 141 | IFA Bipole2 | 1000
2024-03-28 | 10:20 | 50.037 | 135 | IFA Bipole1 | 996.75
2024-03-28 | 10:20 | 50.038 |  | Viking Link | -780.3
2024-03-28 | 10:20 | 50.045
2024-03-28 | 10:20 | 50.046
2024-03-28 | 10:20 | 50.046
2024-03-28 | 10:20 | 50.047
2024-03-28 | 10:20 | 50.047
2024-03-28 | 10:20 | 50.046 | 130 | HEYM12 | 271.908
2024-03-28 | 10:20 | 50.047 | 228 | HUMR-1 | 303.75
2024-03-28 | 10:20 | 50.044
2024-03-28 | 10:20 | 50.042
2024-03-28 | 10:20 | 50.042
2024-03-28 | 10:20 | 50.044
2024-03-28 | 10:20 | 50.044
2024-03-28 | 10:20 | 50.04
2024-03-28 | 10:20 | 50.037
2024-03-28 | 10:20 | 50.032
2024-03-28 | 10:20 | 50.03
2024-03-28 | 10:20 | 50.03 | 211 | CDCL-1 | 291.5
2024-03-28 | 10:21 | 50.035 | 199 | STAY-2 | 413.125
2024-03-28 | 10:21 | 50.034 | 173 | CDCL-1 | 397.375
2024-03-28 | 10:21 | 50.031 | 248 | SEAB-2 | 361.25
2024-03-28 | 10:21 | 50.031 | 255 | FRANCE | 995.65
2024-03-28 | 10:21 | 50.034 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-28 | 10:21 | 50.037
2024-03-28 | 10:21 | 50.039
2024-03-28 | 10:21 | 50.037
2024-03-28 | 10:21 | 50.035
2024-03-28 | 10:21 | 50.033
2024-03-28 | 10:21 | 50.032
2024-03-28 | 10:21 | 50.032
2024-03-28 | 10:21 | 50.035
2024-03-28 | 10:21 | 50.036
2024-03-28 | 10:21 | 50.036
2024-03-28 | 10:21 | 50.036
2024-03-28 | 10:21 | 50.036
2024-03-28 | 10:21 | 50.036
2024-03-28 | 10:21 | 50.039
2024-03-28 | 10:21 | 50.039
2024-03-28 | 10:21 | 50.04
2024-03-28 | 10:21 | 50.041
2024-03-28 | 10:21 | 50.041
2024-03-28 | 10:21 | 50.042
2024-03-28 | 10:21 | 50.008
2024-03-28 | 10:21 | 49.892
2024-03-28 | 10:21 | 49.776
2024-03-28 | 10:21 | 49.724
2024-03-28 | 10:21 | 49.714
2024-03-28 | 10:21 | 49.724
2024-03-28 | 10:21 | 49.729
2024-03-28 | 10:21 | 49.733
2024-03-28 | 10:21 | 49.736
2024-03-28 | 10:21 | 49.739
2024-03-28 | 10:21 | 49.739
2024-03-28 | 10:21 | 49.739
2024-03-28 | 10:21 | 49.734
2024-03-28 | 10:21 | 49.732
2024-03-28 | 10:21 | 49.727
2024-03-28 | 10:21 | 49.722
2024-03-28 | 10:21 | 49.72
2024-03-28 | 10:21 | 49.717
2024-03-28 | 10:21 | 49.716
2024-03-28 | 10:21 | 49.711
2024-03-28 | 10:21 | 49.708
2024-03-28 | 10:21 | 49.708
2024-03-28 | 10:21 | 49.706
2024-03-28 | 10:21 | 49.704
2024-03-28 | 10:21 | 49.702
2024-03-28 | 10:21 | 49.701
2024-03-28 | 10:21 | 49.701
2024-03-28 | 10:21 | 49.703
2024-03-28 | 10:21 | 49.702
2024-03-28 | 10:21 | 49.703
2024-03-28 | 10:21 | 49.704
2024-03-28 | 10:21 | 49.708
2024-03-28 | 10:21 | 49.708
2024-03-28 | 10:21 | 49.706
2024-03-28 | 10:21 | 49.707
2024-03-28 | 10:22 | 49.704
2024-03-28 | 10:22 | 49.699
2024-03-28 | 10:22 | 49.695
2024-03-28 | 10:22 | 49.693
2024-03-28 | 10:22 | 49.694
2024-03-28 | 10:22 | 49.695
2024-03-28 | 10:22 | 49.7
2024-03-28 | 10:22 | 49.702
2024-03-28 | 10:22 | 49.705
2024-03-28 | 10:22 | 49.709
2024-03-28 | 10:22 | 49.707
2024-03-28 | 10:22 | 49.71
2024-03-28 | 10:22 | 49.709
2024-03-28 | 10:22 | 49.71
2024-03-28 | 10:22 | 49.713
2024-03-28 | 10:22 | 49.714
2024-03-28 | 10:22 | 49.715
2024-03-28 | 10:22 | 49.716
2024-03-28 | 10:22 | 49.714
2024-03-28 | 10:22 | 49.713
2024-03-28 | 10:22 | 49.715
2024-03-28 | 10:22 | 49.719
2024-03-28 | 10:22 | 49.721
2024-03-28 | 10:22 | 49.721
2024-03-28 | 10:22 | 49.718
2024-03-28 | 10:22 | 49.717
2024-03-28 | 10:22 | 49.715
2024-03-28 | 10:22 | 49.718
2024-03-28 | 10:22 | 49.724
2024-03-28 | 10:22 | 49.729
2024-03-28 | 10:22 | 49.732
2024-03-28 | 10:22 | 49.736
2024-03-28 | 10:22 | 49.739
2024-03-28 | 10:22 | 49.746
2024-03-28 | 10:22 | 49.752
2024-03-28 | 10:22 | 49.76
2024-03-28 | 10:22 | 49.764
2024-03-28 | 10:22 | 49.773
2024-03-28 | 10:22 | 49.781
2024-03-28 | 10:22 | 49.79
2024-03-28 | 10:22 | 49.797
2024-03-28 | 10:22 | 49.807
2024-03-28 | 10:22 | 49.819
2024-03-28 | 10:22 | 49.829
2024-03-28 | 10:22 | 49.839
2024-03-28 | 10:22 | 49.851
2024-03-28 | 10:22 | 49.86
2024-03-28 | 10:22 | 49.868
2024-03-28 | 10:22 | 49.876
2024-03-28 | 10:22 | 49.881
2024-03-28 | 10:22 | 49.883
2024-03-28 | 10:22 | 49.885
2024-03-28 | 10:22 | 49.885
2024-03-28 | 10:22 | 49.889
2024-03-28 | 10:22 | 49.893
2024-03-28 | 10:22 | 49.894
2024-03-28 | 10:22 | 49.895
2024-03-28 | 10:22 | 49.896
2024-03-28 | 10:22 | 49.894
2024-03-28 | 10:22 | 49.893
2024-03-28 | 10:22 | 49.892
2024-03-28 | 10:23 | 49.892
2024-03-28 | 10:23 | 49.894
2024-03-28 | 10:23 | 49.898
2024-03-28 | 10:23 | 49.898
2024-03-28 | 10:23 | 49.895
2024-03-28 | 10:23 | 49.893
2024-03-28 | 10:23 | 49.888
2024-03-28 | 10:23 | 49.888
2024-03-28 | 10:23 | 49.893
2024-03-28 | 10:23 | 49.9
2024-03-28 | 10:23 | 49.906
2024-03-28 | 10:23 | 49.91
2024-03-28 | 10:23 | 49.913
2024-03-28 | 10:23 | 49.914
2024-03-28 | 10:23 | 49.916
2024-03-28 | 10:23 | 49.914
2024-03-28 | 10:23 | 49.914
2024-03-28 | 10:23 | 49.916
2024-03-28 | 10:23 | 49.917
2024-03-28 | 10:23 | 49.915
2024-03-28 | 10:23 | 49.909
2024-03-28 | 10:23 | 49.906
2024-03-28 | 10:23 | 49.904
2024-03-28 | 10:23 | 49.904
2024-03-28 | 10:23 | 49.904
2024-03-28 | 10:23 | 49.902
2024-03-28 | 10:23 | 49.902
2024-03-28 | 10:23 | 49.903
2024-03-28 | 10:23 | 49.908
2024-03-28 | 10:23 | 49.912
2024-03-28 | 10:23 | 49.917
2024-03-28 | 10:23 | 49.918
2024-03-28 | 10:23 | 49.917
2024-03-28 | 10:23 | 49.914
2024-03-28 | 10:23 | 49.915
2024-03-28 | 10:23 | 49.917
2024-03-28 | 10:23 | 49.916
2024-03-28 | 10:23 | 49.916
2024-03-28 | 10:23 | 49.915
2024-03-28 | 10:23 | 49.918
2024-03-28 | 10:23 | 49.921
2024-03-28 | 10:23 | 49.923
2024-03-28 | 10:23 | 49.928
2024-03-28 | 10:23 | 49.931
2024-03-28 | 10:23 | 49.93
2024-03-28 | 10:23 | 49.928
2024-03-28 | 10:23 | 49.927
2024-03-28 | 10:23 | 49.924
2024-03-28 | 10:23 | 49.92
2024-03-28 | 10:23 | 49.917
2024-03-28 | 10:23 | 49.914
2024-03-28 | 10:23 | 49.913
2024-03-28 | 10:23 | 49.912
2024-03-28 | 10:23 | 49.91
2024-03-28 | 10:23 | 49.912
2024-03-28 | 10:23 | 49.915
2024-03-28 | 10:23 | 49.917
2024-03-28 | 10:23 | 49.914
2024-03-28 | 10:23 | 49.912
2024-03-28 | 10:24 | 49.91
2024-03-28 | 10:24 | 49.907
2024-03-28 | 10:24 | 49.903
2024-03-28 | 10:24 | 49.9
2024-03-28 | 10:24 | 49.898
2024-03-28 | 10:24 | 49.899
2024-03-28 | 10:24 | 49.9
2024-03-28 | 10:24 | 49.903
2024-03-28 | 10:24 | 49.905
2024-03-28 | 10:24 | 49.907
2024-03-28 | 10:24 | 49.909
2024-03-28 | 10:24 | 49.909
2024-03-28 | 10:24 | 49.906
2024-03-28 | 10:24 | 49.906
2024-03-28 | 10:24 | 49.906
2024-03-28 | 10:24 | 49.91
2024-03-28 | 10:24 | 49.911
2024-03-28 | 10:24 | 49.911
2024-03-28 | 10:24 | 49.914
2024-03-28 | 10:24 | 49.916
2024-03-28 | 10:24 | 49.918
2024-03-28 | 10:24 | 49.92
2024-03-28 | 10:24 | 49.921
2024-03-28 | 10:24 | 49.923
2024-03-28 | 10:24 | 49.926
2024-03-28 | 10:24 | 49.93
2024-03-28 | 10:24 | 49.931
2024-03-28 | 10:24 | 49.932
2024-03-28 | 10:24 | 49.931
2024-03-28 | 10:24 | 49.933
2024-03-28 | 10:24 | 49.932
2024-03-28 | 10:24 | 49.929
2024-03-28 | 10:24 | 49.93
2024-03-28 | 10:24 | 49.93
2024-03-28 | 10:24 | 49.934
2024-03-28 | 10:24 | 49.938
2024-03-28 | 10:24 | 49.941
2024-03-28 | 10:24 | 49.942
2024-03-28 | 10:24 | 49.943
2024-03-28 | 10:24 | 49.941
2024-03-28 | 10:24 | 49.938
2024-03-28 | 10:24 | 49.935
2024-03-28 | 10:24 | 49.935
2024-03-28 | 10:24 | 49.934
2024-03-28 | 10:24 | 49.932
2024-03-28 | 10:24 | 49.927
2024-03-28 | 10:24 | 49.923
2024-03-28 | 10:24 | 49.92
2024-03-28 | 10:24 | 49.919
2024-03-28 | 10:24 | 49.92
2024-03-28 | 10:24 | 49.923
2024-03-28 | 10:24 | 49.925
2024-03-28 | 10:24 | 49.923
2024-03-28 | 10:24 | 49.923
2024-03-28 | 10:24 | 49.924
2024-03-28 | 10:24 | 49.924
2024-03-28 | 10:24 | 49.928
2024-03-28 | 10:24 | 49.931
2024-03-28 | 10:24 | 49.935
2024-03-28 | 10:24 | 49.937
2024-03-28 | 10:24 | 49.939
2024-03-28 | 10:25 | 49.936
2024-03-28 | 10:25 | 49.935
2024-03-28 | 10:25 | 49.937
2024-03-28 | 10:25 | 49.94
2024-03-28 | 10:25 | 49.942
2024-03-28 | 10:25 | 49.943
2024-03-28 | 10:25 | 49.942
2024-03-28 | 10:25 | 49.941
2024-03-28 | 10:25 | 49.94
2024-03-28 | 10:25 | 49.937
2024-03-28 | 10:25 | 49.936
2024-03-28 | 10:25 | 49.939
2024-03-28 | 10:25 | 49.941
2024-03-28 | 10:25 | 49.944
2024-03-28 | 10:25 | 49.947
2024-03-28 | 10:25 | 49.949
2024-03-28 | 10:25 | 49.953
2024-03-28 | 10:25 | 49.953
2024-03-28 | 10:25 | 49.954
2024-03-28 | 10:25 | 49.95
2024-03-28 | 10:25 | 49.95
2024-03-28 | 10:25 | 49.949
2024-03-28 | 10:25 | 49.949
2024-03-28 | 10:25 | 49.946
2024-03-28 | 10:25 | 49.941
2024-03-28 | 10:25 | 49.936
2024-03-28 | 10:25 | 49.932
2024-03-28 | 10:25 | 49.928
2024-03-28 | 10:25 | 49.924
2024-03-28 | 10:25 | 49.922
2024-03-28 | 10:25 | 49.92
2024-03-28 | 10:25 | 49.922
2024-03-28 | 10:25 | 49.925
2024-03-28 | 10:25 | 49.928
2024-03-28 | 10:25 | 49.934
2024-03-28 | 10:25 | 49.938
2024-03-28 | 10:25 | 49.944
2024-03-28 | 10:25 | 49.946
2024-03-28 | 10:25 | 49.948
2024-03-28 | 10:25 | 49.948
2024-03-28 | 10:25 | 49.951
2024-03-28 | 10:25 | 49.951
2024-03-28 | 10:25 | 49.948
2024-03-28 | 10:25 | 49.946
2024-03-28 | 10:25 | 49.944
2024-03-28 | 10:25 | 49.944
2024-03-28 | 10:25 | 49.942
2024-03-28 | 10:25 | 49.941
2024-03-28 | 10:25 | 49.938
2024-03-28 | 10:25 | 49.934
2024-03-28 | 10:25 | 49.929
2024-03-28 | 10:25 | 49.925
2024-03-28 | 10:25 | 49.923
2024-03-28 | 10:25 | 49.923
2024-03-28 | 10:25 | 49.928
2024-03-28 | 10:25 | 49.929
2024-03-28 | 10:25 | 49.93
2024-03-28 | 10:25 | 49.929
2024-03-28 | 10:25 | 49.93
2024-03-28 | 10:26 | 49.929
2024-03-28 | 10:26 | 49.931
2024-03-28 | 10:26 | 49.933
2024-03-28 | 10:26 | 49.939
2024-03-28 | 10:26 | 49.946
2024-03-28 | 10:26 | 49.954
2024-03-28 | 10:26 | 49.96
2024-03-28 | 10:26 | 49.964
2024-03-28 | 10:26 | 49.969
2024-03-28 | 10:26 | 49.971
2024-03-28 | 10:26 | 49.975
2024-03-28 | 10:26 | 49.98
2024-03-28 | 10:26 | 49.987
2024-03-28 | 10:26 | 49.99
2024-03-28 | 10:26 | 49.992
2024-03-28 | 10:26 | 49.992
2024-03-28 | 10:26 | 49.994
2024-03-28 | 10:26 | 49.993
2024-03-28 | 10:26 | 49.993
2024-03-28 | 10:26 | 49.995
2024-03-28 | 10:26 | 49.999
2024-03-28 | 10:26 | 50.005
2024-03-28 | 10:26 | 50.012
2024-03-28 | 10:26 | 50.022
2024-03-28 | 10:26 | 50.029
2024-03-28 | 10:26 | 50.034
2024-03-28 | 10:26 | 50.04
2024-03-28 | 10:26 | 50.043
2024-03-28 | 10:26 | 50.042
2024-03-28 | 10:26 | 50.042
2024-03-28 | 10:26 | 50.041
2024-03-28 | 10:26 | 50.038
2024-03-28 | 10:26 | 50.033
2024-03-28 | 10:26 | 50.029
2024-03-28 | 10:26 | 50.023
2024-03-28 | 10:26 | 50.021
2024-03-28 | 10:26 | 50.021
2024-03-28 | 10:26 | 50.022
2024-03-28 | 10:26 | 50.025
2024-03-28 | 10:26 | 50.031
2024-03-28 | 10:26 | 50.033
2024-03-28 | 10:26 | 50.035
2024-03-28 | 10:26 | 50.037
2024-03-28 | 10:26 | 50.042
2024-03-28 | 10:26 | 50.044
2024-03-28 | 10:26 | 50.047
2024-03-28 | 10:26 | 50.047
2024-03-28 | 10:26 | 50.048
2024-03-28 | 10:26 | 50.051
2024-03-28 | 10:26 | 50.054
2024-03-28 | 10:26 | 50.054
2024-03-28 | 10:26 | 50.055
2024-03-28 | 10:26 | 50.052
2024-03-28 | 10:26 | 50.05
2024-03-28 | 10:26 | 50.05
2024-03-28 | 10:26 | 50.047
2024-03-28 | 10:26 | 50.046
2024-03-28 | 10:26 | 50.048
2024-03-28 | 10:26 | 50.051
2024-03-28 | 10:26 | 50.052
2024-03-28 | 10:26 | 50.056
2024-03-28 | 10:27 | 50.06
2024-03-28 | 10:27 | 50.063
2024-03-28 | 10:27 | 50.063
2024-03-28 | 10:27 | 50.059
2024-03-28 | 10:27 | 50.053
2024-03-28 | 10:27 | 50.05
2024-03-28 | 10:27 | 50.047
2024-03-28 | 10:27 | 50.045
2024-03-28 | 10:27 | 50.04
2024-03-28 | 10:27 | 50.033
2024-03-28 | 10:27 | 50.026
2024-03-28 | 10:27 | 50.02
2024-03-28 | 10:27 | 50.014
2024-03-28 | 10:27 | 50.012
2024-03-28 | 10:27 | 50.009
2024-03-28 | 10:27 | 50.01
2024-03-28 | 10:27 | 50.008
2024-03-28 | 10:27 | 50.011
2024-03-28 | 10:27 | 50.018
2024-03-28 | 10:27 | 50.024
2024-03-28 | 10:27 | 50.029
2024-03-28 | 10:27 | 50.03
2024-03-28 | 10:27 | 50.031
2024-03-28 | 10:27 | 50.032
2024-03-28 | 10:27 | 50.032
2024-03-28 | 10:27 | 50.031
2024-03-28 | 10:27 | 50.028
2024-03-28 | 10:27 | 50.027
2024-03-28 | 10:27 | 50.028

## 20240329-1
In GMT
Date | Time | Freq
2024-03-29 | 7:33 | 50.042 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-29 | 7:33 | 50.035 | 222 | BRITNED | 676.211
2024-03-29 | 7:33 | 50.031 | 268 | WBURB-2 | 428.156
2024-03-29 | 7:33 | 50.024 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-29 | 7:33 | 50.023 |  | Viking Link | -648.9
2024-03-29 | 7:33 | 50.021 |  | Viking Link | 1398.96
2024-03-29 | 7:33 | 50.02 | 209 | DRAXX-3 | 626.95
2024-03-29 | 7:33 | 50.018 | 154 | CDCL-1 | 391.57
2024-03-29 | 7:33 | 50.014 | 268 | ROCK-1 | 468.495
2024-03-29 | 7:33 | 50.014 | 148 | IFA Bipole1 | 945.473
2024-03-29 | 7:33 | 50.011 | 132 | IFA Bipole1 | 999.1
2024-03-29 | 7:33 | 50.006 | 141 | IFA Bipole2 | 1000
2024-03-29 | 7:33 | 50.004 | 135 | IFA Bipole1 | 996.75
2024-03-29 | 7:33 | 50 |  | Viking Link | -780.3
2024-03-29 | 7:33 | 49.995
2024-03-29 | 7:33 | 49.993
2024-03-29 | 7:33 | 49.996
2024-03-29 | 7:33 | 49.999
2024-03-29 | 7:33 | 50.001
2024-03-29 | 7:33 | 50.002 | 130 | HEYM12 | 271.908
2024-03-29 | 7:33 | 49.998 | 228 | HUMR-1 | 303.75
2024-03-29 | 7:33 | 49.994
2024-03-29 | 7:33 | 49.99
2024-03-29 | 7:33 | 49.985
2024-03-29 | 7:33 | 49.98
2024-03-29 | 7:33 | 49.978
2024-03-29 | 7:33 | 49.979
2024-03-29 | 7:33 | 49.98
2024-03-29 | 7:33 | 49.983
2024-03-29 | 7:33 | 49.989
2024-03-29 | 7:34 | 49.993 | 211 | CDCL-1 | 291.5
2024-03-29 | 7:34 | 49.997 | 199 | STAY-2 | 413.125
2024-03-29 | 7:34 | 50.002 | 173 | CDCL-1 | 397.375
2024-03-29 | 7:34 | 50.009 | 248 | SEAB-2 | 361.25
2024-03-29 | 7:34 | 50.016 | 255 | FRANCE | 995.65
2024-03-29 | 7:34 | 50.022 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-29 | 7:34 | 50.026
2024-03-29 | 7:34 | 50.026
2024-03-29 | 7:34 | 50.021
2024-03-29 | 7:34 | 50.021
2024-03-29 | 7:34 | 50.021
2024-03-29 | 7:34 | 50.021
2024-03-29 | 7:34 | 50.018
2024-03-29 | 7:34 | 50.015
2024-03-29 | 7:34 | 50.01
2024-03-29 | 7:34 | 50.005
2024-03-29 | 7:34 | 49.998
2024-03-29 | 7:34 | 49.99
2024-03-29 | 7:34 | 49.983
2024-03-29 | 7:34 | 49.976
2024-03-29 | 7:34 | 49.969
2024-03-29 | 7:34 | 49.968
2024-03-29 | 7:34 | 49.972
2024-03-29 | 7:34 | 49.975
2024-03-29 | 7:34 | 49.977
2024-03-29 | 7:34 | 49.981
2024-03-29 | 7:34 | 49.984
2024-03-29 | 7:34 | 49.984
2024-03-29 | 7:34 | 49.981
2024-03-29 | 7:34 | 49.983
2024-03-29 | 7:34 | 49.984
2024-03-29 | 7:34 | 49.981
2024-03-29 | 7:34 | 49.981
2024-03-29 | 7:34 | 49.98
2024-03-29 | 7:34 | 49.978
2024-03-29 | 7:34 | 49.977
2024-03-29 | 7:34 | 49.978
2024-03-29 | 7:34 | 49.978
2024-03-29 | 7:34 | 49.978
2024-03-29 | 7:34 | 49.977
2024-03-29 | 7:34 | 49.978
2024-03-29 | 7:34 | 49.919
2024-03-29 | 7:34 | 49.783
2024-03-29 | 7:34 | 49.722
2024-03-29 | 7:34 | 49.704
2024-03-29 | 7:34 | 49.706
2024-03-29 | 7:34 | 49.714
2024-03-29 | 7:34 | 49.721
2024-03-29 | 7:34 | 49.724
2024-03-29 | 7:34 | 49.726
2024-03-29 | 7:34 | 49.725
2024-03-29 | 7:34 | 49.723
2024-03-29 | 7:34 | 49.725
2024-03-29 | 7:34 | 49.727
2024-03-29 | 7:34 | 49.728
2024-03-29 | 7:34 | 49.728
2024-03-29 | 7:34 | 49.727
2024-03-29 | 7:34 | 49.728
2024-03-29 | 7:34 | 49.727
2024-03-29 | 7:34 | 49.729
2024-03-29 | 7:34 | 49.731
2024-03-29 | 7:35 | 49.731
2024-03-29 | 7:35 | 49.73
2024-03-29 | 7:35 | 49.729
2024-03-29 | 7:35 | 49.729
2024-03-29 | 7:35 | 49.729
2024-03-29 | 7:35 | 49.73
2024-03-29 | 7:35 | 49.732
2024-03-29 | 7:35 | 49.734
2024-03-29 | 7:35 | 49.731
2024-03-29 | 7:35 | 49.727
2024-03-29 | 7:35 | 49.728
2024-03-29 | 7:35 | 49.73
2024-03-29 | 7:35 | 49.731
2024-03-29 | 7:35 | 49.729
2024-03-29 | 7:35 | 49.728
2024-03-29 | 7:35 | 49.726
2024-03-29 | 7:35 | 49.723
2024-03-29 | 7:35 | 49.722
2024-03-29 | 7:35 | 49.721
2024-03-29 | 7:35 | 49.722
2024-03-29 | 7:35 | 49.725
2024-03-29 | 7:35 | 49.725
2024-03-29 | 7:35 | 49.728
2024-03-29 | 7:35 | 49.731
2024-03-29 | 7:35 | 49.73
2024-03-29 | 7:35 | 49.732
2024-03-29 | 7:35 | 49.734
2024-03-29 | 7:35 | 49.732
2024-03-29 | 7:35 | 49.726
2024-03-29 | 7:35 | 49.718
2024-03-29 | 7:35 | 49.714
2024-03-29 | 7:35 | 49.711
2024-03-29 | 7:35 | 49.708
2024-03-29 | 7:35 | 49.709
2024-03-29 | 7:35 | 49.708
2024-03-29 | 7:35 | 49.705
2024-03-29 | 7:35 | 49.702
2024-03-29 | 7:35 | 49.703
2024-03-29 | 7:35 | 49.707
2024-03-29 | 7:35 | 49.711
2024-03-29 | 7:35 | 49.712
2024-03-29 | 7:35 | 49.724
2024-03-29 | 7:35 | 49.737
2024-03-29 | 7:35 | 49.748
2024-03-29 | 7:35 | 49.757
2024-03-29 | 7:35 | 49.762
2024-03-29 | 7:35 | 49.772
2024-03-29 | 7:35 | 49.777
2024-03-29 | 7:35 | 49.782
2024-03-29 | 7:35 | 49.789
2024-03-29 | 7:35 | 49.793
2024-03-29 | 7:35 | 49.794
2024-03-29 | 7:35 | 49.794
2024-03-29 | 7:35 | 49.791
2024-03-29 | 7:35 | 49.789
2024-03-29 | 7:35 | 49.788
2024-03-29 | 7:35 | 49.783
2024-03-29 | 7:35 | 49.782
2024-03-29 | 7:35 | 49.785
2024-03-29 | 7:36 | 49.784
2024-03-29 | 7:36 | 49.786
2024-03-29 | 7:36 | 49.791
2024-03-29 | 7:36 | 49.795
2024-03-29 | 7:36 | 49.799
2024-03-29 | 7:36 | 49.805
2024-03-29 | 7:36 | 49.806
2024-03-29 | 7:36 | 49.807
2024-03-29 | 7:36 | 49.803
2024-03-29 | 7:36 | 49.8
2024-03-29 | 7:36 | 49.801
2024-03-29 | 7:36 | 49.803
2024-03-29 | 7:36 | 49.802
2024-03-29 | 7:36 | 49.802
2024-03-29 | 7:36 | 49.804
2024-03-29 | 7:36 | 49.805
2024-03-29 | 7:36 | 49.806
2024-03-29 | 7:36 | 49.807
2024-03-29 | 7:36 | 49.807
2024-03-29 | 7:36 | 49.804
2024-03-29 | 7:36 | 49.802
2024-03-29 | 7:36 | 49.804
2024-03-29 | 7:36 | 49.802
2024-03-29 | 7:36 | 49.8
2024-03-29 | 7:36 | 49.799
2024-03-29 | 7:36 | 49.803
2024-03-29 | 7:36 | 49.804
2024-03-29 | 7:36 | 49.804
2024-03-29 | 7:36 | 49.803
2024-03-29 | 7:36 | 49.805
2024-03-29 | 7:36 | 49.806
2024-03-29 | 7:36 | 49.804
2024-03-29 | 7:36 | 49.803
2024-03-29 | 7:36 | 49.802
2024-03-29 | 7:36 | 49.8
2024-03-29 | 7:36 | 49.798
2024-03-29 | 7:36 | 49.796
2024-03-29 | 7:36 | 49.795
2024-03-29 | 7:36 | 49.795
2024-03-29 | 7:36 | 49.796
2024-03-29 | 7:36 | 49.792
2024-03-29 | 7:36 | 49.793
2024-03-29 | 7:36 | 49.795
2024-03-29 | 7:36 | 49.795
2024-03-29 | 7:36 | 49.796
2024-03-29 | 7:36 | 49.796
2024-03-29 | 7:36 | 49.799
2024-03-29 | 7:36 | 49.8
2024-03-29 | 7:36 | 49.797
2024-03-29 | 7:36 | 49.797
2024-03-29 | 7:36 | 49.793
2024-03-29 | 7:36 | 49.792
2024-03-29 | 7:36 | 49.791
2024-03-29 | 7:36 | 49.79
2024-03-29 | 7:36 | 49.788
2024-03-29 | 7:36 | 49.792
2024-03-29 | 7:36 | 49.794
2024-03-29 | 7:36 | 49.797
2024-03-29 | 7:36 | 49.799
2024-03-29 | 7:36 | 49.801
2024-03-29 | 7:36 | 49.804
2024-03-29 | 7:37 | 49.805
2024-03-29 | 7:37 | 49.806
2024-03-29 | 7:37 | 49.807
2024-03-29 | 7:37 | 49.816
2024-03-29 | 7:37 | 49.82
2024-03-29 | 7:37 | 49.823
2024-03-29 | 7:37 | 49.819
2024-03-29 | 7:37 | 49.822
2024-03-29 | 7:37 | 49.822
2024-03-29 | 7:37 | 49.824
2024-03-29 | 7:37 | 49.823
2024-03-29 | 7:37 | 49.824
2024-03-29 | 7:37 | 49.822
2024-03-29 | 7:37 | 49.821
2024-03-29 | 7:37 | 49.821
2024-03-29 | 7:37 | 49.822
2024-03-29 | 7:37 | 49.824
2024-03-29 | 7:37 | 49.825
2024-03-29 | 7:37 | 49.827
2024-03-29 | 7:37 | 49.828
2024-03-29 | 7:37 | 49.826
2024-03-29 | 7:37 | 49.827
2024-03-29 | 7:37 | 49.827
2024-03-29 | 7:37 | 49.828
2024-03-29 | 7:37 | 49.826
2024-03-29 | 7:37 | 49.823
2024-03-29 | 7:37 | 49.826
2024-03-29 | 7:37 | 49.83
2024-03-29 | 7:37 | 49.832
2024-03-29 | 7:37 | 49.834
2024-03-29 | 7:37 | 49.834
2024-03-29 | 7:37 | 49.832
2024-03-29 | 7:37 | 49.833
2024-03-29 | 7:37 | 49.834
2024-03-29 | 7:37 | 49.834
2024-03-29 | 7:37 | 49.832
2024-03-29 | 7:37 | 49.829
2024-03-29 | 7:37 | 49.829
2024-03-29 | 7:37 | 49.828
2024-03-29 | 7:37 | 49.827
2024-03-29 | 7:37 | 49.822
2024-03-29 | 7:37 | 49.822
2024-03-29 | 7:37 | 49.822
2024-03-29 | 7:37 | 49.822
2024-03-29 | 7:37 | 49.821
2024-03-29 | 7:37 | 49.821
2024-03-29 | 7:37 | 49.824
2024-03-29 | 7:37 | 49.826
2024-03-29 | 7:37 | 49.827
2024-03-29 | 7:37 | 49.83
2024-03-29 | 7:37 | 49.831
2024-03-29 | 7:37 | 49.832
2024-03-29 | 7:37 | 49.829
2024-03-29 | 7:37 | 49.83
2024-03-29 | 7:37 | 49.829
2024-03-29 | 7:37 | 49.828
2024-03-29 | 7:37 | 49.826
2024-03-29 | 7:37 | 49.827
2024-03-29 | 7:37 | 49.825
2024-03-29 | 7:38 | 49.825
2024-03-29 | 7:38 | 49.824
2024-03-29 | 7:38 | 49.825
2024-03-29 | 7:38 | 49.824
2024-03-29 | 7:38 | 49.825
2024-03-29 | 7:38 | 49.827
2024-03-29 | 7:38 | 49.828
2024-03-29 | 7:38 | 49.827
2024-03-29 | 7:38 | 49.828
2024-03-29 | 7:38 | 49.828
2024-03-29 | 7:38 | 49.831
2024-03-29 | 7:38 | 49.833
2024-03-29 | 7:38 | 49.833
2024-03-29 | 7:38 | 49.835
2024-03-29 | 7:38 | 49.833
2024-03-29 | 7:38 | 49.829
2024-03-29 | 7:38 | 49.826
2024-03-29 | 7:38 | 49.824
2024-03-29 | 7:38 | 49.827
2024-03-29 | 7:38 | 49.825
2024-03-29 | 7:38 | 49.824
2024-03-29 | 7:38 | 49.821
2024-03-29 | 7:38 | 49.825
2024-03-29 | 7:38 | 49.822
2024-03-29 | 7:38 | 49.819
2024-03-29 | 7:38 | 49.818
2024-03-29 | 7:38 | 49.82
2024-03-29 | 7:38 | 49.82
2024-03-29 | 7:38 | 49.82
2024-03-29 | 7:38 | 49.823
2024-03-29 | 7:38 | 49.825
2024-03-29 | 7:38 | 49.824
2024-03-29 | 7:38 | 49.822
2024-03-29 | 7:38 | 49.825
2024-03-29 | 7:38 | 49.824
2024-03-29 | 7:38 | 49.821
2024-03-29 | 7:38 | 49.82
2024-03-29 | 7:38 | 49.821
2024-03-29 | 7:38 | 49.822
2024-03-29 | 7:38 | 49.822
2024-03-29 | 7:38 | 49.821
2024-03-29 | 7:38 | 49.82
2024-03-29 | 7:38 | 49.817
2024-03-29 | 7:38 | 49.813
2024-03-29 | 7:38 | 49.816
2024-03-29 | 7:38 | 49.822
2024-03-29 | 7:38 | 49.827
2024-03-29 | 7:38 | 49.828
2024-03-29 | 7:38 | 49.831
2024-03-29 | 7:38 | 49.83
2024-03-29 | 7:38 | 49.831
2024-03-29 | 7:38 | 49.831
2024-03-29 | 7:38 | 49.831
2024-03-29 | 7:38 | 49.83
2024-03-29 | 7:38 | 49.829
2024-03-29 | 7:38 | 49.831
2024-03-29 | 7:38 | 49.836
2024-03-29 | 7:38 | 49.838
2024-03-29 | 7:38 | 49.84
2024-03-29 | 7:38 | 49.84
2024-03-29 | 7:38 | 49.84
2024-03-29 | 7:39 | 49.841
2024-03-29 | 7:39 | 49.841
2024-03-29 | 7:39 | 49.839
2024-03-29 | 7:39 | 49.841
2024-03-29 | 7:39 | 49.843
2024-03-29 | 7:39 | 49.848
2024-03-29 | 7:39 | 49.855
2024-03-29 | 7:39 | 49.863
2024-03-29 | 7:39 | 49.868
2024-03-29 | 7:39 | 49.871
2024-03-29 | 7:39 | 49.876
2024-03-29 | 7:39 | 49.881
2024-03-29 | 7:39 | 49.883
2024-03-29 | 7:39 | 49.883
2024-03-29 | 7:39 | 49.879
2024-03-29 | 7:39 | 49.882
2024-03-29 | 7:39 | 49.882
2024-03-29 | 7:39 | 49.883
2024-03-29 | 7:39 | 49.884
2024-03-29 | 7:39 | 49.889
2024-03-29 | 7:39 | 49.89
2024-03-29 | 7:39 | 49.892
2024-03-29 | 7:39 | 49.892
2024-03-29 | 7:39 | 49.899
2024-03-29 | 7:39 | 49.901
2024-03-29 | 7:39 | 49.901
2024-03-29 | 7:39 | 49.903
2024-03-29 | 7:39 | 49.903
2024-03-29 | 7:39 | 49.903
2024-03-29 | 7:39 | 49.901
2024-03-29 | 7:39 | 49.9
2024-03-29 | 7:39 | 49.896
2024-03-29 | 7:39 | 49.894
2024-03-29 | 7:39 | 49.893
2024-03-29 | 7:39 | 49.896
2024-03-29 | 7:39 | 49.894
2024-03-29 | 7:39 | 49.893
2024-03-29 | 7:39 | 49.891
2024-03-29 | 7:39 | 49.89
2024-03-29 | 7:39 | 49.89
2024-03-29 | 7:39 | 49.891
2024-03-29 | 7:39 | 49.893
2024-03-29 | 7:39 | 49.897
2024-03-29 | 7:39 | 49.895
2024-03-29 | 7:39 | 49.893
2024-03-29 | 7:39 | 49.896
2024-03-29 | 7:39 | 49.899
2024-03-29 | 7:39 | 49.902
2024-03-29 | 7:39 | 49.901
2024-03-29 | 7:39 | 49.9
2024-03-29 | 7:39 | 49.899
2024-03-29 | 7:39 | 49.9
2024-03-29 | 7:39 | 49.9
2024-03-29 | 7:39 | 49.9
2024-03-29 | 7:39 | 49.901
2024-03-29 | 7:39 | 49.9
2024-03-29 | 7:39 | 49.898
2024-03-29 | 7:39 | 49.899
2024-03-29 | 7:39 | 49.896
2024-03-29 | 7:39 | 49.899
2024-03-29 | 7:40 | 49.898
2024-03-29 | 7:40 | 49.9
2024-03-29 | 7:40 | 49.9
2024-03-29 | 7:40 | 49.9
2024-03-29 | 7:40 | 49.895
2024-03-29 | 7:40 | 49.895
2024-03-29 | 7:40 | 49.896
2024-03-29 | 7:40 | 49.901
2024-03-29 | 7:40 | 49.903
2024-03-29 | 7:40 | 49.906
2024-03-29 | 7:40 | 49.91
2024-03-29 | 7:40 | 49.91
2024-03-29 | 7:40 | 49.908
2024-03-29 | 7:40 | 49.908
2024-03-29 | 7:40 | 49.907
2024-03-29 | 7:40 | 49.906
2024-03-29 | 7:40 | 49.904
2024-03-29 | 7:40 | 49.901
2024-03-29 | 7:40 | 49.899
2024-03-29 | 7:40 | 49.897
2024-03-29 | 7:40 | 49.9
2024-03-29 | 7:40 | 49.906
2024-03-29 | 7:40 | 49.91
2024-03-29 | 7:40 | 49.908
2024-03-29 | 7:40 | 49.91
2024-03-29 | 7:40 | 49.91
2024-03-29 | 7:40 | 49.909
2024-03-29 | 7:40 | 49.908
2024-03-29 | 7:40 | 49.905
2024-03-29 | 7:40 | 49.906
2024-03-29 | 7:40 | 49.898
2024-03-29 | 7:40 | 49.895
2024-03-29 | 7:40 | 49.895
2024-03-29 | 7:40 | 49.895
2024-03-29 | 7:40 | 49.895
2024-03-29 | 7:40 | 49.898
2024-03-29 | 7:40 | 49.897
2024-03-29 | 7:40 | 49.903
2024-03-29 | 7:40 | 49.903
2024-03-29 | 7:40 | 49.9
2024-03-29 | 7:40 | 49.899
2024-03-29 | 7:40 | 49.899
2024-03-29 | 7:40 | 49.898
2024-03-29 | 7:40 | 49.895
2024-03-29 | 7:40 | 49.895
2024-03-29 | 7:40 | 49.893
2024-03-29 | 7:40 | 49.894
2024-03-29 | 7:40 | 49.894
2024-03-29 | 7:40 | 49.898
2024-03-29 | 7:40 | 49.898
2024-03-29 | 7:40 | 49.899
2024-03-29 | 7:40 | 49.902
2024-03-29 | 7:40 | 49.905
2024-03-29 | 7:40 | 49.904
2024-03-29 | 7:40 | 49.905
2024-03-29 | 7:40 | 49.906
2024-03-29 | 7:40 | 49.912
2024-03-29 | 7:40 | 49.914
2024-03-29 | 7:40 | 49.914
2024-03-29 | 7:40 | 49.914
2024-03-29 | 7:41 | 49.913
2024-03-29 | 7:41 | 49.909
2024-03-29 | 7:41 | 49.904
2024-03-29 | 7:41 | 49.901
2024-03-29 | 7:41 | 49.901
2024-03-29 | 7:41 | 49.898
2024-03-29 | 7:41 | 49.896
2024-03-29 | 7:41 | 49.898
2024-03-29 | 7:41 | 49.898
2024-03-29 | 7:41 | 49.901
2024-03-29 | 7:41 | 49.903
2024-03-29 | 7:41 | 49.904
2024-03-29 | 7:41 | 49.904
2024-03-29 | 7:41 | 49.904
2024-03-29 | 7:41 | 49.904
2024-03-29 | 7:41 | 49.908
2024-03-29 | 7:41 | 49.906
2024-03-29 | 7:41 | 49.9
2024-03-29 | 7:41 | 49.902
2024-03-29 | 7:41 | 49.899
2024-03-29 | 7:41 | 49.902
2024-03-29 | 7:41 | 49.903
2024-03-29 | 7:41 | 49.9
2024-03-29 | 7:41 | 49.902
2024-03-29 | 7:41 | 49.899
2024-03-29 | 7:41 | 49.897
2024-03-29 | 7:41 | 49.897
2024-03-29 | 7:41 | 49.9
2024-03-29 | 7:41 | 49.901
2024-03-29 | 7:41 | 49.899
2024-03-29 | 7:41 | 49.897
2024-03-29 | 7:41 | 49.899
2024-03-29 | 7:41 | 49.898
2024-03-29 | 7:41 | 49.897
2024-03-29 | 7:41 | 49.898
2024-03-29 | 7:41 | 49.898
2024-03-29 | 7:41 | 49.895
2024-03-29 | 7:41 | 49.896
2024-03-29 | 7:41 | 49.897
2024-03-29 | 7:41 | 49.899
2024-03-29 | 7:41 | 49.901
2024-03-29 | 7:41 | 49.902
2024-03-29 | 7:41 | 49.899
2024-03-29 | 7:41 | 49.896
2024-03-29 | 7:41 | 49.892
2024-03-29 | 7:41 | 49.891
2024-03-29 | 7:41 | 49.891
2024-03-29 | 7:41 | 49.893
2024-03-29 | 7:41 | 49.893
2024-03-29 | 7:41 | 49.898
2024-03-29 | 7:41 | 49.899
2024-03-29 | 7:41 | 49.9
2024-03-29 | 7:41 | 49.9
2024-03-29 | 7:41 | 49.9
2024-03-29 | 7:41 | 49.902
2024-03-29 | 7:41 | 49.903
2024-03-29 | 7:41 | 49.899
2024-03-29 | 7:41 | 49.898
2024-03-29 | 7:41 | 49.899
2024-03-29 | 7:41 | 49.896
2024-03-29 | 7:42 | 49.892
2024-03-29 | 7:42 | 49.892
2024-03-29 | 7:42 | 49.892
2024-03-29 | 7:42 | 49.891
2024-03-29 | 7:42 | 49.893
2024-03-29 | 7:42 | 49.891
2024-03-29 | 7:42 | 49.892
2024-03-29 | 7:42 | 49.89
2024-03-29 | 7:42 | 49.885
2024-03-29 | 7:42 | 49.887
2024-03-29 | 7:42 | 49.89
2024-03-29 | 7:42 | 49.891
2024-03-29 | 7:42 | 49.893
2024-03-29 | 7:42 | 49.895
2024-03-29 | 7:42 | 49.897
2024-03-29 | 7:42 | 49.896
2024-03-29 | 7:42 | 49.893
2024-03-29 | 7:42 | 49.894
2024-03-29 | 7:42 | 49.894
2024-03-29 | 7:42 | 49.891
2024-03-29 | 7:42 | 49.89
2024-03-29 | 7:42 | 49.889
2024-03-29 | 7:42 | 49.891
2024-03-29 | 7:42 | 49.892
2024-03-29 | 7:42 | 49.893
2024-03-29 | 7:42 | 49.897
2024-03-29 | 7:42 | 49.896
2024-03-29 | 7:42 | 49.894
2024-03-29 | 7:42 | 49.892
2024-03-29 | 7:42 | 49.893
2024-03-29 | 7:42 | 49.888
2024-03-29 | 7:42 | 49.89
2024-03-29 | 7:42 | 49.893
2024-03-29 | 7:42 | 49.895
2024-03-29 | 7:42 | 49.892
2024-03-29 | 7:42 | 49.886
2024-03-29 | 7:42 | 49.881
2024-03-29 | 7:42 | 49.875
2024-03-29 | 7:42 | 49.865
2024-03-29 | 7:42 | 49.855
2024-03-29 | 7:42 | 49.849
2024-03-29 | 7:42 | 49.845
2024-03-29 | 7:42 | 49.84
2024-03-29 | 7:42 | 49.839
2024-03-29 | 7:42 | 49.84
2024-03-29 | 7:42 | 49.841
2024-03-29 | 7:42 | 49.843
2024-03-29 | 7:42 | 49.848
2024-03-29 | 7:42 | 49.853
2024-03-29 | 7:42 | 49.856
2024-03-29 | 7:42 | 49.854
2024-03-29 | 7:42 | 49.854
2024-03-29 | 7:42 | 49.856
2024-03-29 | 7:42 | 49.858
2024-03-29 | 7:42 | 49.858
2024-03-29 | 7:42 | 49.861
2024-03-29 | 7:42 | 49.863
2024-03-29 | 7:42 | 49.864
2024-03-29 | 7:42 | 49.862
2024-03-29 | 7:42 | 49.861
2024-03-29 | 7:43 | 49.86
2024-03-29 | 7:43 | 49.86
2024-03-29 | 7:43 | 49.861
2024-03-29 | 7:43 | 49.861
2024-03-29 | 7:43 | 49.863
2024-03-29 | 7:43 | 49.863
2024-03-29 | 7:43 | 49.861
2024-03-29 | 7:43 | 49.864
2024-03-29 | 7:43 | 49.867
2024-03-29 | 7:43 | 49.871
2024-03-29 | 7:43 | 49.872
2024-03-29 | 7:43 | 49.873
2024-03-29 | 7:43 | 49.878
2024-03-29 | 7:43 | 49.877
2024-03-29 | 7:43 | 49.879
2024-03-29 | 7:43 | 49.878
2024-03-29 | 7:43 | 49.881
2024-03-29 | 7:43 | 49.884
2024-03-29 | 7:43 | 49.885
2024-03-29 | 7:43 | 49.886
2024-03-29 | 7:43 | 49.889
2024-03-29 | 7:43 | 49.888
2024-03-29 | 7:43 | 49.887
2024-03-29 | 7:43 | 49.89
2024-03-29 | 7:43 | 49.887
2024-03-29 | 7:43 | 49.886
2024-03-29 | 7:43 | 49.89
2024-03-29 | 7:43 | 49.893
2024-03-29 | 7:43 | 49.896
2024-03-29 | 7:43 | 49.897
2024-03-29 | 7:43 | 49.896
2024-03-29 | 7:43 | 49.893
2024-03-29 | 7:43 | 49.89
2024-03-29 | 7:43 | 49.887
2024-03-29 | 7:43 | 49.887
2024-03-29 | 7:43 | 49.886
2024-03-29 | 7:43 | 49.886
2024-03-29 | 7:43 | 49.887
2024-03-29 | 7:43 | 49.887
2024-03-29 | 7:43 | 49.89
2024-03-29 | 7:43 | 49.89
2024-03-29 | 7:43 | 49.888
2024-03-29 | 7:43 | 49.887
2024-03-29 | 7:43 | 49.885
2024-03-29 | 7:43 | 49.88
2024-03-29 | 7:43 | 49.876
2024-03-29 | 7:43 | 49.878
2024-03-29 | 7:43 | 49.884
2024-03-29 | 7:43 | 49.885
2024-03-29 | 7:43 | 49.886
2024-03-29 | 7:43 | 49.89
2024-03-29 | 7:43 | 49.889
2024-03-29 | 7:43 | 49.892
2024-03-29 | 7:43 | 49.89
2024-03-29 | 7:43 | 49.892
2024-03-29 | 7:43 | 49.892
2024-03-29 | 7:43 | 49.893
2024-03-29 | 7:43 | 49.895
2024-03-29 | 7:43 | 49.895
2024-03-29 | 7:43 | 49.895
2024-03-29 | 7:44 | 49.891
2024-03-29 | 7:44 | 49.895
2024-03-29 | 7:44 | 49.893
2024-03-29 | 7:44 | 49.892
2024-03-29 | 7:44 | 49.891
2024-03-29 | 7:44 | 49.892
2024-03-29 | 7:44 | 49.895
2024-03-29 | 7:44 | 49.894
2024-03-29 | 7:44 | 49.896
2024-03-29 | 7:44 | 49.899
2024-03-29 | 7:44 | 49.9
2024-03-29 | 7:44 | 49.902
2024-03-29 | 7:44 | 49.901
2024-03-29 | 7:44 | 49.898
2024-03-29 | 7:44 | 49.898
2024-03-29 | 7:44 | 49.895
2024-03-29 | 7:44 | 49.895
2024-03-29 | 7:44 | 49.895
2024-03-29 | 7:44 | 49.892
2024-03-29 | 7:44 | 49.889
2024-03-29 | 7:44 | 49.887
2024-03-29 | 7:44 | 49.887
2024-03-29 | 7:44 | 49.89
2024-03-29 | 7:44 | 49.887
2024-03-29 | 7:44 | 49.887
2024-03-29 | 7:44 | 49.891
2024-03-29 | 7:44 | 49.892
2024-03-29 | 7:44 | 49.89
2024-03-29 | 7:44 | 49.89
2024-03-29 | 7:44 | 49.894
2024-03-29 | 7:44 | 49.893
2024-03-29 | 7:44 | 49.892
2024-03-29 | 7:44 | 49.89
2024-03-29 | 7:44 | 49.888
2024-03-29 | 7:44 | 49.885
2024-03-29 | 7:44 | 49.88
2024-03-29 | 7:44 | 49.878
2024-03-29 | 7:44 | 49.878
2024-03-29 | 7:44 | 49.879
2024-03-29 | 7:44 | 49.88
2024-03-29 | 7:44 | 49.885
2024-03-29 | 7:44 | 49.889
2024-03-29 | 7:44 | 49.889
2024-03-29 | 7:44 | 49.889
2024-03-29 | 7:44 | 49.888
2024-03-29 | 7:44 | 49.89
2024-03-29 | 7:44 | 49.891
2024-03-29 | 7:44 | 49.893
2024-03-29 | 7:44 | 49.892
2024-03-29 | 7:44 | 49.893
2024-03-29 | 7:44 | 49.89
2024-03-29 | 7:44 | 49.891
2024-03-29 | 7:44 | 49.896
2024-03-29 | 7:44 | 49.896
2024-03-29 | 7:44 | 49.895
2024-03-29 | 7:44 | 49.893
2024-03-29 | 7:44 | 49.894
2024-03-29 | 7:44 | 49.894
2024-03-29 | 7:44 | 49.894
2024-03-29 | 7:44 | 49.893
2024-03-29 | 7:45 | 49.894
2024-03-29 | 7:45 | 49.896
2024-03-29 | 7:45 | 49.897
2024-03-29 | 7:45 | 49.896
2024-03-29 | 7:45 | 49.897
2024-03-29 | 7:45 | 49.899
2024-03-29 | 7:45 | 49.897
2024-03-29 | 7:45 | 49.896
2024-03-29 | 7:45 | 49.897
2024-03-29 | 7:45 | 49.897
2024-03-29 | 7:45 | 49.895
2024-03-29 | 7:45 | 49.897
2024-03-29 | 7:45 | 49.898
2024-03-29 | 7:45 | 49.899
2024-03-29 | 7:45 | 49.897
2024-03-29 | 7:45 | 49.895
2024-03-29 | 7:45 | 49.899
2024-03-29 | 7:45 | 49.899
2024-03-29 | 7:45 | 49.9
2024-03-29 | 7:45 | 49.902
2024-03-29 | 7:45 | 49.901
2024-03-29 | 7:45 | 49.897
2024-03-29 | 7:45 | 49.894
2024-03-29 | 7:45 | 49.893
2024-03-29 | 7:45 | 49.89
2024-03-29 | 7:45 | 49.888
2024-03-29 | 7:45 | 49.887
2024-03-29 | 7:45 | 49.888
2024-03-29 | 7:45 | 49.886
2024-03-29 | 7:45 | 49.884
2024-03-29 | 7:45 | 49.883
2024-03-29 | 7:45 | 49.884
2024-03-29 | 7:45 | 49.884
2024-03-29 | 7:45 | 49.881
2024-03-29 | 7:45 | 49.884
2024-03-29 | 7:45 | 49.885
2024-03-29 | 7:45 | 49.887
2024-03-29 | 7:45 | 49.89
2024-03-29 | 7:45 | 49.893
2024-03-29 | 7:45 | 49.894
2024-03-29 | 7:45 | 49.895
2024-03-29 | 7:45 | 49.896
2024-03-29 | 7:45 | 49.897
2024-03-29 | 7:45 | 49.898
2024-03-29 | 7:45 | 49.896
2024-03-29 | 7:45 | 49.896
2024-03-29 | 7:45 | 49.896
2024-03-29 | 7:45 | 49.897
2024-03-29 | 7:45 | 49.896
2024-03-29 | 7:45 | 49.892
2024-03-29 | 7:45 | 49.893
2024-03-29 | 7:45 | 49.891
2024-03-29 | 7:45 | 49.889
2024-03-29 | 7:45 | 49.889
2024-03-29 | 7:45 | 49.887
2024-03-29 | 7:45 | 49.884
2024-03-29 | 7:45 | 49.882
2024-03-29 | 7:45 | 49.883
2024-03-29 | 7:45 | 49.882
2024-03-29 | 7:45 | 49.88
2024-03-29 | 7:46 | 49.88
2024-03-29 | 7:46 | 49.882
2024-03-29 | 7:46 | 49.884
2024-03-29 | 7:46 | 49.888
2024-03-29 | 7:46 | 49.887
2024-03-29 | 7:46 | 49.89
2024-03-29 | 7:46 | 49.897
2024-03-29 | 7:46 | 49.898
2024-03-29 | 7:46 | 49.898
2024-03-29 | 7:46 | 49.897
2024-03-29 | 7:46 | 49.9
2024-03-29 | 7:46 | 49.9
2024-03-29 | 7:46 | 49.901
2024-03-29 | 7:46 | 49.901
2024-03-29 | 7:46 | 49.905
2024-03-29 | 7:46 | 49.903
2024-03-29 | 7:46 | 49.904
2024-03-29 | 7:46 | 49.903
2024-03-29 | 7:46 | 49.908
2024-03-29 | 7:46 | 49.907
2024-03-29 | 7:46 | 49.904
2024-03-29 | 7:46 | 49.9
2024-03-29 | 7:46 | 49.899
2024-03-29 | 7:46 | 49.895
2024-03-29 | 7:46 | 49.896
2024-03-29 | 7:46 | 49.896
2024-03-29 | 7:46 | 49.895
2024-03-29 | 7:46 | 49.895
2024-03-29 | 7:46 | 49.893
2024-03-29 | 7:46 | 49.896
2024-03-29 | 7:46 | 49.898
2024-03-29 | 7:46 | 49.896
2024-03-29 | 7:46 | 49.9
2024-03-29 | 7:46 | 49.901
2024-03-29 | 7:46 | 49.903
2024-03-29 | 7:46 | 49.903
2024-03-29 | 7:46 | 49.907
2024-03-29 | 7:46 | 49.908
2024-03-29 | 7:46 | 49.908
2024-03-29 | 7:46 | 49.907
2024-03-29 | 7:46 | 49.909
2024-03-29 | 7:46 | 49.906
2024-03-29 | 7:46 | 49.906
2024-03-29 | 7:46 | 49.904
2024-03-29 | 7:46 | 49.907
2024-03-29 | 7:46 | 49.909
2024-03-29 | 7:46 | 49.914
2024-03-29 | 7:46 | 49.911
2024-03-29 | 7:46 | 49.912
2024-03-29 | 7:46 | 49.91
2024-03-29 | 7:46 | 49.909
2024-03-29 | 7:46 | 49.909
2024-03-29 | 7:46 | 49.911
2024-03-29 | 7:46 | 49.911
2024-03-29 | 7:46 | 49.913
2024-03-29 | 7:46 | 49.914
2024-03-29 | 7:46 | 49.917
2024-03-29 | 7:46 | 49.92
2024-03-29 | 7:46 | 49.921
2024-03-29 | 7:46 | 49.921
2024-03-29 | 7:47 | 49.925
2024-03-29 | 7:47 | 49.925
2024-03-29 | 7:47 | 49.925
2024-03-29 | 7:47 | 49.926
2024-03-29 | 7:47 | 49.925
2024-03-29 | 7:47 | 49.926
2024-03-29 | 7:47 | 49.924
2024-03-29 | 7:47 | 49.925
2024-03-29 | 7:47 | 49.924
2024-03-29 | 7:47 | 49.926
2024-03-29 | 7:47 | 49.928
2024-03-29 | 7:47 | 49.93
2024-03-29 | 7:47 | 49.935
2024-03-29 | 7:47 | 49.938
2024-03-29 | 7:47 | 49.941
2024-03-29 | 7:47 | 49.948
2024-03-29 | 7:47 | 49.951
2024-03-29 | 7:47 | 49.949
2024-03-29 | 7:47 | 49.944
2024-03-29 | 7:47 | 49.943
2024-03-29 | 7:47 | 49.942
2024-03-29 | 7:47 | 49.944
2024-03-29 | 7:47 | 49.944
2024-03-29 | 7:47 | 49.948
2024-03-29 | 7:47 | 49.949
2024-03-29 | 7:47 | 49.949
2024-03-29 | 7:47 | 49.95
2024-03-29 | 7:47 | 49.954
2024-03-29 | 7:47 | 49.958
2024-03-29 | 7:47 | 49.963
2024-03-29 | 7:47 | 49.968
2024-03-29 | 7:47 | 49.977
2024-03-29 | 7:47 | 49.98
2024-03-29 | 7:47 | 49.989
2024-03-29 | 7:47 | 49.994
2024-03-29 | 7:47 | 50.007
2024-03-29 | 7:47 | 50.021
2024-03-29 | 7:47 | 50.034
2024-03-29 | 7:47 | 50.041
2024-03-29 | 7:47 | 50.047
2024-03-29 | 7:47 | 50.047
2024-03-29 | 7:47 | 50.047
2024-03-29 | 7:47 | 50.045
2024-03-29 | 7:47 | 50.048
2024-03-29 | 7:47 | 50.048
2024-03-29 | 7:47 | 50.046
2024-03-29 | 7:47 | 50.043
2024-03-29 | 7:47 | 50.041
2024-03-29 | 7:47 | 50.043
2024-03-29 | 7:47 | 50.046
2024-03-29 | 7:47 | 50.05
2024-03-29 | 7:47 | 50.054
2024-03-29 | 7:47 | 50.052
2024-03-29 | 7:47 | 50.048
2024-03-29 | 7:47 | 50.046
2024-03-29 | 7:47 | 50.045
2024-03-29 | 7:47 | 50.041
2024-03-29 | 7:47 | 50.038
2024-03-29 | 7:47 | 50.039
2024-03-29 | 7:48 | 50.045
2024-03-29 | 7:48 | 50.049
2024-03-29 | 7:48 | 50.053
2024-03-29 | 7:48 | 50.054
2024-03-29 | 7:48 | 50.057
2024-03-29 | 7:48 | 50.058
2024-03-29 | 7:48 | 50.057
2024-03-29 | 7:48 | 50.06
2024-03-29 | 7:48 | 50.056
2024-03-29 | 7:48 | 50.055
2024-03-29 | 7:48 | 50.055
2024-03-29 | 7:48 | 50.055
2024-03-29 | 7:48 | 50.057
2024-03-29 | 7:48 | 50.055
2024-03-29 | 7:48 | 50.061
2024-03-29 | 7:48 | 50.066
2024-03-29 | 7:48 | 50.07
2024-03-29 | 7:48 | 50.069
2024-03-29 | 7:48 | 50.071
2024-03-29 | 7:48 | 50.073
2024-03-29 | 7:48 | 50.075
2024-03-29 | 7:48 | 50.076
2024-03-29 | 7:48 | 50.076
2024-03-29 | 7:48 | 50.075
2024-03-29 | 7:48 | 50.07
2024-03-29 | 7:48 | 50.074
2024-03-29 | 7:48 | 50.074
2024-03-29 | 7:48 | 50.076
2024-03-29 | 7:48 | 50.073
2024-03-29 | 7:48 | 50.077
2024-03-29 | 7:48 | 50.079
2024-03-29 | 7:48 | 50.08
2024-03-29 | 7:48 | 50.08
2024-03-29 | 7:48 | 50.079
2024-03-29 | 7:48 | 50.076
2024-03-29 | 7:48 | 50.072
2024-03-29 | 7:48 | 50.067
2024-03-29 | 7:48 | 50.064
2024-03-29 | 7:48 | 50.061
2024-03-29 | 7:48 | 50.061
2024-03-29 | 7:48 | 50.061
2024-03-29 | 7:48 | 50.057
2024-03-29 | 7:48 | 50.065
2024-03-29 | 7:48 | 50.066
2024-03-29 | 7:48 | 50.069
2024-03-29 | 7:48 | 50.068
2024-03-29 | 7:48 | 50.073
2024-03-29 | 7:48 | 50.075
2024-03-29 | 7:48 | 50.075
2024-03-29 | 7:48 | 50.078
2024-03-29 | 7:48 | 50.079
2024-03-29 | 7:48 | 50.08
2024-03-29 | 7:48 | 50.081
2024-03-29 | 7:48 | 50.084
2024-03-29 | 7:48 | 50.084
2024-03-29 | 7:48 | 50.085
2024-03-29 | 7:48 | 50.084
2024-03-29 | 7:48 | 50.083
2024-03-29 | 7:48 | 50.083
2024-03-29 | 7:48 | 50.086
2024-03-29 | 7:48 | 50.088
2024-03-29 | 7:49 | 50.095
2024-03-29 | 7:49 | 50.103
2024-03-29 | 7:49 | 50.11
2024-03-29 | 7:49 | 50.113
2024-03-29 | 7:49 | 50.116
2024-03-29 | 7:49 | 50.118
2024-03-29 | 7:49 | 50.121
2024-03-29 | 7:49 | 50.122
2024-03-29 | 7:49 | 50.122
2024-03-29 | 7:49 | 50.12
2024-03-29 | 7:49 | 50.118
2024-03-29 | 7:49 | 50.117
2024-03-29 | 7:49 | 50.117
2024-03-29 | 7:49 | 50.117
2024-03-29 | 7:49 | 50.117
2024-03-29 | 7:49 | 50.114
2024-03-29 | 7:49 | 50.113
2024-03-29 | 7:49 | 50.111
2024-03-29 | 7:49 | 50.11
2024-03-29 | 7:49 | 50.109
2024-03-29 | 7:49 | 50.111
2024-03-29 | 7:49 | 50.111
2024-03-29 | 7:49 | 50.109
2024-03-29 | 7:49 | 50.109
2024-03-29 | 7:49 | 50.11
2024-03-29 | 7:49 | 50.108
2024-03-29 | 7:49 | 50.104
2024-03-29 | 7:49 | 50.102
2024-03-29 | 7:49 | 50.102

## 20240329-2
In GMT
Date | Time | Freq
2024-03-29 | 11:29 | 49.935 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-29 | 11:29 | 49.935 | 222 | BRITNED | 676.211
2024-03-29 | 11:29 | 49.934 | 268 | WBURB-2 | 428.156
2024-03-29 | 11:29 | 49.937 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-29 | 11:29 | 49.94 |  | Viking Link | -648.9
2024-03-29 | 11:29 | 49.946 |  | Viking Link | 1398.96
2024-03-29 | 11:29 | 49.95 | 209 | DRAXX-3 | 626.95
2024-03-29 | 11:29 | 49.953 | 154 | CDCL-1 | 391.57
2024-03-29 | 11:29 | 49.957 | 268 | ROCK-1 | 468.495
2024-03-29 | 11:29 | 49.955 | 148 | IFA Bipole1 | 945.473
2024-03-29 | 11:29 | 49.954 | 132 | IFA Bipole1 | 999.1
2024-03-29 | 11:29 | 49.952 | 141 | IFA Bipole2 | 1000
2024-03-29 | 11:29 | 49.949 | 135 | IFA Bipole1 | 996.75
2024-03-29 | 11:29 | 49.947 |  | Viking Link | -780.3
2024-03-29 | 11:29 | 49.942
2024-03-29 | 11:29 | 49.937
2024-03-29 | 11:29 | 49.939
2024-03-29 | 11:29 | 49.938
2024-03-29 | 11:29 | 49.938
2024-03-29 | 11:29 | 49.939 | 130 | HEYM12 | 271.908
2024-03-29 | 11:29 | 49.94 | 228 | HUMR-1 | 303.75
2024-03-29 | 11:29 | 49.94
2024-03-29 | 11:29 | 49.943
2024-03-29 | 11:29 | 49.944
2024-03-29 | 11:29 | 49.944
2024-03-29 | 11:29 | 49.945
2024-03-29 | 11:29 | 49.942
2024-03-29 | 11:29 | 49.942
2024-03-29 | 11:29 | 49.946
2024-03-29 | 11:29 | 49.944
2024-03-29 | 11:30 | 49.943 | 211 | CDCL-1 | 291.5
2024-03-29 | 11:30 | 49.943 | 199 | STAY-2 | 413.125
2024-03-29 | 11:30 | 49.944 | 173 | CDCL-1 | 397.375
2024-03-29 | 11:30 | 49.944 | 248 | SEAB-2 | 361.25
2024-03-29 | 11:30 | 49.944 | 255 | FRANCE | 995.65
2024-03-29 | 11:30 | 49.945 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-29 | 11:30 | 49.946
2024-03-29 | 11:30 | 49.947
2024-03-29 | 11:30 | 49.952
2024-03-29 | 11:30 | 49.957
2024-03-29 | 11:30 | 49.96
2024-03-29 | 11:30 | 49.963
2024-03-29 | 11:30 | 49.964
2024-03-29 | 11:30 | 49.968
2024-03-29 | 11:30 | 49.967
2024-03-29 | 11:30 | 49.966
2024-03-29 | 11:30 | 49.969
2024-03-29 | 11:30 | 49.971
2024-03-29 | 11:30 | 49.973
2024-03-29 | 11:30 | 49.974
2024-03-29 | 11:30 | 49.978
2024-03-29 | 11:30 | 49.978
2024-03-29 | 11:30 | 49.978
2024-03-29 | 11:30 | 49.982
2024-03-29 | 11:30 | 49.981
2024-03-29 | 11:30 | 49.984
2024-03-29 | 11:30 | 49.988
2024-03-29 | 11:30 | 49.879
2024-03-29 | 11:30 | 49.755
2024-03-29 | 11:30 | 49.707
2024-03-29 | 11:30 | 49.699
2024-03-29 | 11:30 | 49.712
2024-03-29 | 11:30 | 49.713
2024-03-29 | 11:30 | 49.71
2024-03-29 | 11:30 | 49.707
2024-03-29 | 11:30 | 49.712
2024-03-29 | 11:30 | 49.713
2024-03-29 | 11:30 | 49.715
2024-03-29 | 11:30 | 49.713
2024-03-29 | 11:30 | 49.715
2024-03-29 | 11:30 | 49.719
2024-03-29 | 11:30 | 49.724
2024-03-29 | 11:30 | 49.725
2024-03-29 | 11:30 | 49.727
2024-03-29 | 11:30 | 49.728
2024-03-29 | 11:30 | 49.729
2024-03-29 | 11:30 | 49.728
2024-03-29 | 11:30 | 49.726
2024-03-29 | 11:30 | 49.728
2024-03-29 | 11:30 | 49.728
2024-03-29 | 11:30 | 49.726
2024-03-29 | 11:30 | 49.726
2024-03-29 | 11:30 | 49.728
2024-03-29 | 11:30 | 49.729
2024-03-29 | 11:30 | 49.733
2024-03-29 | 11:30 | 49.735
2024-03-29 | 11:30 | 49.739
2024-03-29 | 11:30 | 49.744
2024-03-29 | 11:30 | 49.745
2024-03-29 | 11:30 | 49.745
2024-03-29 | 11:30 | 49.745
2024-03-29 | 11:31 | 49.743
2024-03-29 | 11:31 | 49.743
2024-03-29 | 11:31 | 49.745
2024-03-29 | 11:31 | 49.747
2024-03-29 | 11:31 | 49.75
2024-03-29 | 11:31 | 49.752
2024-03-29 | 11:31 | 49.754
2024-03-29 | 11:31 | 49.757
2024-03-29 | 11:31 | 49.758
2024-03-29 | 11:31 | 49.757
2024-03-29 | 11:31 | 49.756
2024-03-29 | 11:31 | 49.752
2024-03-29 | 11:31 | 49.748
2024-03-29 | 11:31 | 49.746
2024-03-29 | 11:31 | 49.744
2024-03-29 | 11:31 | 49.744
2024-03-29 | 11:31 | 49.746
2024-03-29 | 11:31 | 49.748
2024-03-29 | 11:31 | 49.748
2024-03-29 | 11:31 | 49.745
2024-03-29 | 11:31 | 49.746
2024-03-29 | 11:31 | 49.745
2024-03-29 | 11:31 | 49.748
2024-03-29 | 11:31 | 49.748
2024-03-29 | 11:31 | 49.747
2024-03-29 | 11:31 | 49.747
2024-03-29 | 11:31 | 49.747
2024-03-29 | 11:31 | 49.745
2024-03-29 | 11:31 | 49.743
2024-03-29 | 11:31 | 49.745
2024-03-29 | 11:31 | 49.743
2024-03-29 | 11:31 | 49.741
2024-03-29 | 11:31 | 49.738
2024-03-29 | 11:31 | 49.74
2024-03-29 | 11:31 | 49.74
2024-03-29 | 11:31 | 49.738
2024-03-29 | 11:31 | 49.737
2024-03-29 | 11:31 | 49.738
2024-03-29 | 11:31 | 49.736
2024-03-29 | 11:31 | 49.738
2024-03-29 | 11:31 | 49.738
2024-03-29 | 11:31 | 49.738
2024-03-29 | 11:31 | 49.743
2024-03-29 | 11:31 | 49.745
2024-03-29 | 11:31 | 49.748
2024-03-29 | 11:31 | 49.748
2024-03-29 | 11:31 | 49.747
2024-03-29 | 11:31 | 49.747
2024-03-29 | 11:31 | 49.741
2024-03-29 | 11:31 | 49.741
2024-03-29 | 11:31 | 49.744
2024-03-29 | 11:31 | 49.743
2024-03-29 | 11:31 | 49.744
2024-03-29 | 11:31 | 49.743
2024-03-29 | 11:31 | 49.742
2024-03-29 | 11:31 | 49.742
2024-03-29 | 11:31 | 49.74
2024-03-29 | 11:31 | 49.743
2024-03-29 | 11:31 | 49.745
2024-03-29 | 11:32 | 49.745
2024-03-29 | 11:32 | 49.75
2024-03-29 | 11:32 | 49.755
2024-03-29 | 11:32 | 49.755
2024-03-29 | 11:32 | 49.758
2024-03-29 | 11:32 | 49.762
2024-03-29 | 11:32 | 49.767
2024-03-29 | 11:32 | 49.767
2024-03-29 | 11:32 | 49.77
2024-03-29 | 11:32 | 49.773
2024-03-29 | 11:32 | 49.77
2024-03-29 | 11:32 | 49.767
2024-03-29 | 11:32 | 49.766
2024-03-29 | 11:32 | 49.766
2024-03-29 | 11:32 | 49.765
2024-03-29 | 11:32 | 49.761
2024-03-29 | 11:32 | 49.761
2024-03-29 | 11:32 | 49.766
2024-03-29 | 11:32 | 49.771
2024-03-29 | 11:32 | 49.771
2024-03-29 | 11:32 | 49.771
2024-03-29 | 11:32 | 49.773
2024-03-29 | 11:32 | 49.776
2024-03-29 | 11:32 | 49.777
2024-03-29 | 11:32 | 49.776
2024-03-29 | 11:32 | 49.777
2024-03-29 | 11:32 | 49.779
2024-03-29 | 11:32 | 49.78
2024-03-29 | 11:32 | 49.783
2024-03-29 | 11:32 | 49.786
2024-03-29 | 11:32 | 49.785
2024-03-29 | 11:32 | 49.783
2024-03-29 | 11:32 | 49.781
2024-03-29 | 11:32 | 49.781
2024-03-29 | 11:32 | 49.781
2024-03-29 | 11:32 | 49.777
2024-03-29 | 11:32 | 49.775
2024-03-29 | 11:32 | 49.774
2024-03-29 | 11:32 | 49.772
2024-03-29 | 11:32 | 49.771
2024-03-29 | 11:32 | 49.769
2024-03-29 | 11:32 | 49.768
2024-03-29 | 11:32 | 49.763
2024-03-29 | 11:32 | 49.764
2024-03-29 | 11:32 | 49.769
2024-03-29 | 11:32 | 49.768
2024-03-29 | 11:32 | 49.768
2024-03-29 | 11:32 | 49.77
2024-03-29 | 11:32 | 49.771
2024-03-29 | 11:32 | 49.772
2024-03-29 | 11:32 | 49.773
2024-03-29 | 11:32 | 49.773
2024-03-29 | 11:32 | 49.774
2024-03-29 | 11:32 | 49.773
2024-03-29 | 11:32 | 49.773
2024-03-29 | 11:32 | 49.774
2024-03-29 | 11:32 | 49.776
2024-03-29 | 11:32 | 49.775
2024-03-29 | 11:32 | 49.772
2024-03-29 | 11:32 | 49.771
2024-03-29 | 11:32 | 49.769
2024-03-29 | 11:33 | 49.767
2024-03-29 | 11:33 | 49.763
2024-03-29 | 11:33 | 49.761
2024-03-29 | 11:33 | 49.764
2024-03-29 | 11:33 | 49.764
2024-03-29 | 11:33 | 49.764
2024-03-29 | 11:33 | 49.768
2024-03-29 | 11:33 | 49.768
2024-03-29 | 11:33 | 49.767
2024-03-29 | 11:33 | 49.767
2024-03-29 | 11:33 | 49.765
2024-03-29 | 11:33 | 49.765
2024-03-29 | 11:33 | 49.765
2024-03-29 | 11:33 | 49.765
2024-03-29 | 11:33 | 49.772
2024-03-29 | 11:33 | 49.77
2024-03-29 | 11:33 | 49.769
2024-03-29 | 11:33 | 49.769
2024-03-29 | 11:33 | 49.772
2024-03-29 | 11:33 | 49.774
2024-03-29 | 11:33 | 49.77
2024-03-29 | 11:33 | 49.768
2024-03-29 | 11:33 | 49.768
2024-03-29 | 11:33 | 49.771
2024-03-29 | 11:33 | 49.772
2024-03-29 | 11:33 | 49.771
2024-03-29 | 11:33 | 49.771
2024-03-29 | 11:33 | 49.774
2024-03-29 | 11:33 | 49.775
2024-03-29 | 11:33 | 49.775
2024-03-29 | 11:33 | 49.772
2024-03-29 | 11:33 | 49.771
2024-03-29 | 11:33 | 49.772
2024-03-29 | 11:33 | 49.774
2024-03-29 | 11:33 | 49.775
2024-03-29 | 11:33 | 49.775
2024-03-29 | 11:33 | 49.774
2024-03-29 | 11:33 | 49.771
2024-03-29 | 11:33 | 49.772
2024-03-29 | 11:33 | 49.767
2024-03-29 | 11:33 | 49.765
2024-03-29 | 11:33 | 49.761
2024-03-29 | 11:33 | 49.761
2024-03-29 | 11:33 | 49.757
2024-03-29 | 11:33 | 49.758
2024-03-29 | 11:33 | 49.758
2024-03-29 | 11:33 | 49.763
2024-03-29 | 11:33 | 49.761
2024-03-29 | 11:33 | 49.763
2024-03-29 | 11:33 | 49.763
2024-03-29 | 11:33 | 49.766
2024-03-29 | 11:33 | 49.764
2024-03-29 | 11:33 | 49.763
2024-03-29 | 11:33 | 49.763
2024-03-29 | 11:33 | 49.761
2024-03-29 | 11:33 | 49.759
2024-03-29 | 11:33 | 49.76
2024-03-29 | 11:33 | 49.765
2024-03-29 | 11:33 | 49.768
2024-03-29 | 11:34 | 49.769
2024-03-29 | 11:34 | 49.769
2024-03-29 | 11:34 | 49.769
2024-03-29 | 11:34 | 49.768
2024-03-29 | 11:34 | 49.769
2024-03-29 | 11:34 | 49.774
2024-03-29 | 11:34 | 49.776
2024-03-29 | 11:34 | 49.777
2024-03-29 | 11:34 | 49.773
2024-03-29 | 11:34 | 49.776
2024-03-29 | 11:34 | 49.779
2024-03-29 | 11:34 | 49.781
2024-03-29 | 11:34 | 49.784
2024-03-29 | 11:34 | 49.786
2024-03-29 | 11:34 | 49.79
2024-03-29 | 11:34 | 49.791
2024-03-29 | 11:34 | 49.793
2024-03-29 | 11:34 | 49.794
2024-03-29 | 11:34 | 49.797
2024-03-29 | 11:34 | 49.797
2024-03-29 | 11:34 | 49.8
2024-03-29 | 11:34 | 49.804
2024-03-29 | 11:34 | 49.806
2024-03-29 | 11:34 | 49.808
2024-03-29 | 11:34 | 49.808
2024-03-29 | 11:34 | 49.81
2024-03-29 | 11:34 | 49.811
2024-03-29 | 11:34 | 49.813
2024-03-29 | 11:34 | 49.814
2024-03-29 | 11:34 | 49.82
2024-03-29 | 11:34 | 49.818
2024-03-29 | 11:34 | 49.813
2024-03-29 | 11:34 | 49.811
2024-03-29 | 11:34 | 49.813
2024-03-29 | 11:34 | 49.812
2024-03-29 | 11:34 | 49.811
2024-03-29 | 11:34 | 49.815
2024-03-29 | 11:34 | 49.817
2024-03-29 | 11:34 | 49.817
2024-03-29 | 11:34 | 49.818
2024-03-29 | 11:34 | 49.818
2024-03-29 | 11:34 | 49.819
2024-03-29 | 11:34 | 49.818
2024-03-29 | 11:34 | 49.82
2024-03-29 | 11:34 | 49.823
2024-03-29 | 11:34 | 49.827
2024-03-29 | 11:34 | 49.826
2024-03-29 | 11:34 | 49.824
2024-03-29 | 11:34 | 49.826
2024-03-29 | 11:34 | 49.827
2024-03-29 | 11:34 | 49.829
2024-03-29 | 11:34 | 49.83
2024-03-29 | 11:34 | 49.832
2024-03-29 | 11:34 | 49.836
2024-03-29 | 11:34 | 49.835
2024-03-29 | 11:34 | 49.84
2024-03-29 | 11:34 | 49.841
2024-03-29 | 11:34 | 49.839
2024-03-29 | 11:34 | 49.832
2024-03-29 | 11:34 | 49.832
2024-03-29 | 11:34 | 49.831
2024-03-29 | 11:35 | 49.83
2024-03-29 | 11:35 | 49.824
2024-03-29 | 11:35 | 49.823
2024-03-29 | 11:35 | 49.82
2024-03-29 | 11:35 | 49.82
2024-03-29 | 11:35 | 49.817
2024-03-29 | 11:35 | 49.816
2024-03-29 | 11:35 | 49.817
2024-03-29 | 11:35 | 49.818
2024-03-29 | 11:35 | 49.82
2024-03-29 | 11:35 | 49.823
2024-03-29 | 11:35 | 49.823
2024-03-29 | 11:35 | 49.82
2024-03-29 | 11:35 | 49.82
2024-03-29 | 11:35 | 49.821
2024-03-29 | 11:35 | 49.822
2024-03-29 | 11:35 | 49.822
2024-03-29 | 11:35 | 49.822
2024-03-29 | 11:35 | 49.822
2024-03-29 | 11:35 | 49.823
2024-03-29 | 11:35 | 49.821
2024-03-29 | 11:35 | 49.818
2024-03-29 | 11:35 | 49.819
2024-03-29 | 11:35 | 49.82
2024-03-29 | 11:35 | 49.819
2024-03-29 | 11:35 | 49.821
2024-03-29 | 11:35 | 49.825
2024-03-29 | 11:35 | 49.829
2024-03-29 | 11:35 | 49.834
2024-03-29 | 11:35 | 49.842
2024-03-29 | 11:35 | 49.846
2024-03-29 | 11:35 | 49.849
2024-03-29 | 11:35 | 49.849
2024-03-29 | 11:35 | 49.851
2024-03-29 | 11:35 | 49.853
2024-03-29 | 11:35 | 49.851
2024-03-29 | 11:35 | 49.849
2024-03-29 | 11:35 | 49.846
2024-03-29 | 11:35 | 49.849
2024-03-29 | 11:35 | 49.846
2024-03-29 | 11:35 | 49.845
2024-03-29 | 11:35 | 49.843
2024-03-29 | 11:35 | 49.844
2024-03-29 | 11:35 | 49.845
2024-03-29 | 11:35 | 49.846
2024-03-29 | 11:35 | 49.847
2024-03-29 | 11:35 | 49.847
2024-03-29 | 11:35 | 49.845
2024-03-29 | 11:35 | 49.845
2024-03-29 | 11:35 | 49.847
2024-03-29 | 11:35 | 49.847
2024-03-29 | 11:35 | 49.846
2024-03-29 | 11:35 | 49.848
2024-03-29 | 11:35 | 49.847
2024-03-29 | 11:35 | 49.85
2024-03-29 | 11:35 | 49.852
2024-03-29 | 11:35 | 49.852
2024-03-29 | 11:35 | 49.857
2024-03-29 | 11:35 | 49.861
2024-03-29 | 11:36 | 49.863
2024-03-29 | 11:36 | 49.864
2024-03-29 | 11:36 | 49.867
2024-03-29 | 11:36 | 49.867
2024-03-29 | 11:36 | 49.866
2024-03-29 | 11:36 | 49.868
2024-03-29 | 11:36 | 49.87
2024-03-29 | 11:36 | 49.867
2024-03-29 | 11:36 | 49.865
2024-03-29 | 11:36 | 49.869
2024-03-29 | 11:36 | 49.87
2024-03-29 | 11:36 | 49.868
2024-03-29 | 11:36 | 49.87
2024-03-29 | 11:36 | 49.872
2024-03-29 | 11:36 | 49.874
2024-03-29 | 11:36 | 49.877
2024-03-29 | 11:36 | 49.878
2024-03-29 | 11:36 | 49.878
2024-03-29 | 11:36 | 49.882
2024-03-29 | 11:36 | 49.888
2024-03-29 | 11:36 | 49.891
2024-03-29 | 11:36 | 49.895
2024-03-29 | 11:36 | 49.897
2024-03-29 | 11:36 | 49.895
2024-03-29 | 11:36 | 49.894
2024-03-29 | 11:36 | 49.893
2024-03-29 | 11:36 | 49.893
2024-03-29 | 11:36 | 49.891
2024-03-29 | 11:36 | 49.893
2024-03-29 | 11:36 | 49.898
2024-03-29 | 11:36 | 49.898
2024-03-29 | 11:36 | 49.895
2024-03-29 | 11:36 | 49.897
2024-03-29 | 11:36 | 49.901
2024-03-29 | 11:36 | 49.9
2024-03-29 | 11:36 | 49.9
2024-03-29 | 11:36 | 49.898
2024-03-29 | 11:36 | 49.899
2024-03-29 | 11:36 | 49.902
2024-03-29 | 11:36 | 49.901
2024-03-29 | 11:36 | 49.901
2024-03-29 | 11:36 | 49.905
2024-03-29 | 11:36 | 49.905
2024-03-29 | 11:36 | 49.902
2024-03-29 | 11:36 | 49.903
2024-03-29 | 11:36 | 49.904
2024-03-29 | 11:36 | 49.903
2024-03-29 | 11:36 | 49.899
2024-03-29 | 11:36 | 49.893
2024-03-29 | 11:36 | 49.89
2024-03-29 | 11:36 | 49.887
2024-03-29 | 11:36 | 49.886
2024-03-29 | 11:36 | 49.888
2024-03-29 | 11:36 | 49.891
2024-03-29 | 11:36 | 49.889
2024-03-29 | 11:36 | 49.891
2024-03-29 | 11:36 | 49.894
2024-03-29 | 11:36 | 49.896
2024-03-29 | 11:36 | 49.897
2024-03-29 | 11:36 | 49.901
2024-03-29 | 11:36 | 49.902
2024-03-29 | 11:37 | 49.904
2024-03-29 | 11:37 | 49.902
2024-03-29 | 11:37 | 49.903
2024-03-29 | 11:37 | 49.905
2024-03-29 | 11:37 | 49.903
2024-03-29 | 11:37 | 49.902
2024-03-29 | 11:37 | 49.903
2024-03-29 | 11:37 | 49.901
2024-03-29 | 11:37 | 49.901
2024-03-29 | 11:37 | 49.901
2024-03-29 | 11:37 | 49.9
2024-03-29 | 11:37 | 49.903
2024-03-29 | 11:37 | 49.902
2024-03-29 | 11:37 | 49.9
2024-03-29 | 11:37 | 49.901
2024-03-29 | 11:37 | 49.903
2024-03-29 | 11:37 | 49.906
2024-03-29 | 11:37 | 49.907
2024-03-29 | 11:37 | 49.913
2024-03-29 | 11:37 | 49.917
2024-03-29 | 11:37 | 49.921
2024-03-29 | 11:37 | 49.922
2024-03-29 | 11:37 | 49.929
2024-03-29 | 11:37 | 49.931
2024-03-29 | 11:37 | 49.933
2024-03-29 | 11:37 | 49.933
2024-03-29 | 11:37 | 49.935
2024-03-29 | 11:37 | 49.936
2024-03-29 | 11:37 | 49.933
2024-03-29 | 11:37 | 49.932
2024-03-29 | 11:37 | 49.931
2024-03-29 | 11:37 | 49.931
2024-03-29 | 11:37 | 49.93
2024-03-29 | 11:37 | 49.932
2024-03-29 | 11:37 | 49.936
2024-03-29 | 11:37 | 49.937
2024-03-29 | 11:37 | 49.939
2024-03-29 | 11:37 | 49.941
2024-03-29 | 11:37 | 49.941
2024-03-29 | 11:37 | 49.94
2024-03-29 | 11:37 | 49.938
2024-03-29 | 11:37 | 49.939
2024-03-29 | 11:37 | 49.94
2024-03-29 | 11:37 | 49.94
2024-03-29 | 11:37 | 49.94
2024-03-29 | 11:37 | 49.942
2024-03-29 | 11:37 | 49.946
2024-03-29 | 11:37 | 49.948
2024-03-29 | 11:37 | 49.95
2024-03-29 | 11:37 | 49.951
2024-03-29 | 11:37 | 49.952
2024-03-29 | 11:37 | 49.953
2024-03-29 | 11:37 | 49.953
2024-03-29 | 11:37 | 49.956
2024-03-29 | 11:37 | 49.961
2024-03-29 | 11:37 | 49.962
2024-03-29 | 11:37 | 49.964
2024-03-29 | 11:37 | 49.964
2024-03-29 | 11:37 | 49.964
2024-03-29 | 11:38 | 49.96
2024-03-29 | 11:38 | 49.957
2024-03-29 | 11:38 | 49.958
2024-03-29 | 11:38 | 49.958
2024-03-29 | 11:38 | 49.957
2024-03-29 | 11:38 | 49.954
2024-03-29 | 11:38 | 49.954
2024-03-29 | 11:38 | 49.954
2024-03-29 | 11:38 | 49.953
2024-03-29 | 11:38 | 49.954
2024-03-29 | 11:38 | 49.955
2024-03-29 | 11:38 | 49.952
2024-03-29 | 11:38 | 49.95
2024-03-29 | 11:38 | 49.949
2024-03-29 | 11:38 | 49.95
2024-03-29 | 11:38 | 49.95
2024-03-29 | 11:38 | 49.951
2024-03-29 | 11:38 | 49.953
2024-03-29 | 11:38 | 49.956
2024-03-29 | 11:38 | 49.958
2024-03-29 | 11:38 | 49.959
2024-03-29 | 11:38 | 49.961
2024-03-29 | 11:38 | 49.961
2024-03-29 | 11:38 | 49.959
2024-03-29 | 11:38 | 49.954
2024-03-29 | 11:38 | 49.952
2024-03-29 | 11:38 | 49.953
2024-03-29 | 11:38 | 49.951
2024-03-29 | 11:38 | 49.953
2024-03-29 | 11:38 | 49.956
2024-03-29 | 11:38 | 49.958
2024-03-29 | 11:38 | 49.958
2024-03-29 | 11:38 | 49.963
2024-03-29 | 11:38 | 49.969
2024-03-29 | 11:38 | 49.973
2024-03-29 | 11:38 | 49.974
2024-03-29 | 11:38 | 49.972
2024-03-29 | 11:38 | 49.975
2024-03-29 | 11:38 | 49.98
2024-03-29 | 11:38 | 49.98
2024-03-29 | 11:38 | 49.983
2024-03-29 | 11:38 | 49.985
2024-03-29 | 11:38 | 49.985
2024-03-29 | 11:38 | 49.983
2024-03-29 | 11:38 | 49.984
2024-03-29 | 11:38 | 49.987
2024-03-29 | 11:38 | 49.99
2024-03-29 | 11:38 | 49.994
2024-03-29 | 11:38 | 49.999
2024-03-29 | 11:38 | 50.002
2024-03-29 | 11:38 | 50.007
2024-03-29 | 11:38 | 50.016
2024-03-29 | 11:38 | 50.023
2024-03-29 | 11:38 | 50.03
2024-03-29 | 11:38 | 50.029
2024-03-29 | 11:38 | 50.03
2024-03-29 | 11:38 | 50.029
2024-03-29 | 11:38 | 50.029
2024-03-29 | 11:38 | 50.026
2024-03-29 | 11:38 | 50.023
2024-03-29 | 11:39 | 50.022
2024-03-29 | 11:39 | 50.023
2024-03-29 | 11:39 | 50.022
2024-03-29 | 11:39 | 50.022
2024-03-29 | 11:39 | 50.025
2024-03-29 | 11:39 | 50.027
2024-03-29 | 11:39 | 50.025
2024-03-29 | 11:39 | 50.023
2024-03-29 | 11:39 | 50.023
2024-03-29 | 11:39 | 50.023
2024-03-29 | 11:39 | 50.022
2024-03-29 | 11:39 | 50.021
2024-03-29 | 11:39 | 50.021
2024-03-29 | 11:39 | 50.024
2024-03-29 | 11:39 | 50.026
2024-03-29 | 11:39 | 50.033
2024-03-29 | 11:39 | 50.037
2024-03-29 | 11:39 | 50.037
2024-03-29 | 11:39 | 50.041
2024-03-29 | 11:39 | 50.042
2024-03-29 | 11:39 | 50.047
2024-03-29 | 11:39 | 50.046
2024-03-29 | 11:39 | 50.044
2024-03-29 | 11:39 | 50.045
2024-03-29 | 11:39 | 50.042
2024-03-29 | 11:39 | 50.041
2024-03-29 | 11:39 | 50.037
2024-03-29 | 11:39 | 50.037
2024-03-29 | 11:39 | 50.038
2024-03-29 | 11:39 | 50.034
2024-03-29 | 11:39 | 50.033
2024-03-29 | 11:39 | 50.033
2024-03-29 | 11:39 | 50.033
2024-03-29 | 11:39 | 50.036
2024-03-29 | 11:39 | 50.041
2024-03-29 | 11:39 | 50.042
2024-03-29 | 11:39 | 50.041
2024-03-29 | 11:39 | 50.037
2024-03-29 | 11:39 | 50.033
2024-03-29 | 11:39 | 50.028
2024-03-29 | 11:39 | 50.031
2024-03-29 | 11:39 | 50.033
2024-03-29 | 11:39 | 50.036
2024-03-29 | 11:39 | 50.035
2024-03-29 | 11:39 | 50.032
2024-03-29 | 11:39 | 50.031
2024-03-29 | 11:39 | 50.031
2024-03-29 | 11:39 | 50.032
2024-03-29 | 11:39 | 50.033
2024-03-29 | 11:39 | 50.033
2024-03-29 | 11:39 | 50.036
2024-03-29 | 11:39 | 50.037
2024-03-29 | 11:39 | 50.039
2024-03-29 | 11:39 | 50.043
2024-03-29 | 11:39 | 50.044
2024-03-29 | 11:39 | 50.047
2024-03-29 | 11:39 | 50.045
2024-03-29 | 11:39 | 50.048
2024-03-29 | 11:39 | 50.052
2024-03-29 | 11:39 | 50.058
2024-03-29 | 11:40 | 50.059
2024-03-29 | 11:40 | 50.057
2024-03-29 | 11:40 | 50.055
2024-03-29 | 11:40 | 50.056
2024-03-29 | 11:40 | 50.055
2024-03-29 | 11:40 | 50.058
2024-03-29 | 11:40 | 50.062
2024-03-29 | 11:40 | 50.059
2024-03-29 | 11:40 | 50.062
2024-03-29 | 11:40 | 50.064
2024-03-29 | 11:40 | 50.068
2024-03-29 | 11:40 | 50.07
2024-03-29 | 11:40 | 50.074
2024-03-29 | 11:40 | 50.074
2024-03-29 | 11:40 | 50.072
2024-03-29 | 11:40 | 50.07
2024-03-29 | 11:40 | 50.066
2024-03-29 | 11:40 | 50.069
2024-03-29 | 11:40 | 50.074
2024-03-29 | 11:40 | 50.077
2024-03-29 | 11:40 | 50.077
2024-03-29 | 11:40 | 50.084
2024-03-29 | 11:40 | 50.091
2024-03-29 | 11:40 | 50.094
2024-03-29 | 11:40 | 50.095
2024-03-29 | 11:40 | 50.093
2024-03-29 | 11:40 | 50.089
2024-03-29 | 11:40 | 50.085
2024-03-29 | 11:40 | 50.084
2024-03-29 | 11:40 | 50.081

## 20240329-3
In GMT
Date | Time | Freq
2024-03-29 | 12:29 | 50.107 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-29 | 12:29 | 50.105 | 222 | BRITNED | 676.211
2024-03-29 | 12:29 | 50.104 | 268 | WBURB-2 | 428.156
2024-03-29 | 12:29 | 50.099 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-29 | 12:29 | 50.094 |  | Viking Link | -648.9
2024-03-29 | 12:29 | 50.084 |  | Viking Link | 1398.96
2024-03-29 | 12:29 | 50.07 | 209 | DRAXX-3 | 626.95
2024-03-29 | 12:29 | 50.058 | 154 | CDCL-1 | 391.57
2024-03-29 | 12:29 | 50.053 | 268 | ROCK-1 | 468.495
2024-03-29 | 12:29 | 50.051 | 148 | IFA Bipole1 | 945.473
2024-03-29 | 12:29 | 50.049 | 132 | IFA Bipole1 | 999.1
2024-03-29 | 12:29 | 50.046 | 141 | IFA Bipole2 | 1000
2024-03-29 | 12:29 | 50.044 | 135 | IFA Bipole1 | 996.75
2024-03-29 | 12:29 | 50.042 |  | Viking Link | -780.3
2024-03-29 | 12:29 | 50.04
2024-03-29 | 12:29 | 50.039
2024-03-29 | 12:29 | 50.038
2024-03-29 | 12:29 | 50.035
2024-03-29 | 12:29 | 50.035
2024-03-29 | 12:29 | 50.034 | 130 | HEYM12 | 271.908
2024-03-29 | 12:29 | 50.04 | 228 | HUMR-1 | 303.75
2024-03-29 | 12:29 | 50.045
2024-03-29 | 12:29 | 50.046
2024-03-29 | 12:29 | 50.044
2024-03-29 | 12:29 | 50.043
2024-03-29 | 12:29 | 50.047
2024-03-29 | 12:29 | 50.043
2024-03-29 | 12:29 | 50.04
2024-03-29 | 12:29 | 50.04
2024-03-29 | 12:29 | 50.04
2024-03-29 | 12:30 | 50.04 | 211 | CDCL-1 | 291.5
2024-03-29 | 12:30 | 50.039 | 199 | STAY-2 | 413.125
2024-03-29 | 12:30 | 50.039 | 173 | CDCL-1 | 397.375
2024-03-29 | 12:30 | 50.036 | 248 | SEAB-2 | 361.25
2024-03-29 | 12:30 | 50.031 | 255 | FRANCE | 995.65
2024-03-29 | 12:30 | 50.029 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-29 | 12:30 | 50.029
2024-03-29 | 12:30 | 50.031
2024-03-29 | 12:30 | 50.03
2024-03-29 | 12:30 | 50.033
2024-03-29 | 12:30 | 50.037
2024-03-29 | 12:30 | 50.042
2024-03-29 | 12:30 | 50.042
2024-03-29 | 12:30 | 50.042
2024-03-29 | 12:30 | 50.037
2024-03-29 | 12:30 | 50.035
2024-03-29 | 12:30 | 50.031
2024-03-29 | 12:30 | 50.032
2024-03-29 | 12:30 | 50.036
2024-03-29 | 12:30 | 50.034
2024-03-29 | 12:30 | 50.035
2024-03-29 | 12:30 | 50.035
2024-03-29 | 12:30 | 50.034
2024-03-29 | 12:30 | 50.032
2024-03-29 | 12:30 | 50.029
2024-03-29 | 12:30 | 50.033
2024-03-29 | 12:30 | 50.032
2024-03-29 | 12:30 | 50.026
2024-03-29 | 12:30 | 50.021
2024-03-29 | 12:30 | 50.018
2024-03-29 | 12:30 | 50.017
2024-03-29 | 12:30 | 50.021
2024-03-29 | 12:30 | 50.017
2024-03-29 | 12:30 | 50.015
2024-03-29 | 12:30 | 50.013
2024-03-29 | 12:30 | 50.014
2024-03-29 | 12:30 | 50.012
2024-03-29 | 12:30 | 50.008
2024-03-29 | 12:30 | 50.005
2024-03-29 | 12:30 | 50.002
2024-03-29 | 12:30 | 50.001
2024-03-29 | 12:30 | 50.007
2024-03-29 | 12:30 | 50.011
2024-03-29 | 12:30 | 49.891
2024-03-29 | 12:30 | 49.745
2024-03-29 | 12:30 | 49.683
2024-03-29 | 12:30 | 49.679
2024-03-29 | 12:30 | 49.7
2024-03-29 | 12:30 | 49.722
2024-03-29 | 12:30 | 49.736
2024-03-29 | 12:30 | 49.739
2024-03-29 | 12:30 | 49.738
2024-03-29 | 12:30 | 49.735
2024-03-29 | 12:30 | 49.735
2024-03-29 | 12:30 | 49.728
2024-03-29 | 12:30 | 49.724
2024-03-29 | 12:30 | 49.723
2024-03-29 | 12:30 | 49.722
2024-03-29 | 12:30 | 49.72
2024-03-29 | 12:30 | 49.716
2024-03-29 | 12:30 | 49.715
2024-03-29 | 12:31 | 49.71
2024-03-29 | 12:31 | 49.71
2024-03-29 | 12:31 | 49.712
2024-03-29 | 12:31 | 49.713
2024-03-29 | 12:31 | 49.713
2024-03-29 | 12:31 | 49.714
2024-03-29 | 12:31 | 49.715
2024-03-29 | 12:31 | 49.717
2024-03-29 | 12:31 | 49.719
2024-03-29 | 12:31 | 49.719
2024-03-29 | 12:31 | 49.719
2024-03-29 | 12:31 | 49.722
2024-03-29 | 12:31 | 49.723
2024-03-29 | 12:31 | 49.719
2024-03-29 | 12:31 | 49.715
2024-03-29 | 12:31 | 49.713
2024-03-29 | 12:31 | 49.713
2024-03-29 | 12:31 | 49.711
2024-03-29 | 12:31 | 49.712
2024-03-29 | 12:31 | 49.713
2024-03-29 | 12:31 | 49.715
2024-03-29 | 12:31 | 49.716
2024-03-29 | 12:31 | 49.717
2024-03-29 | 12:31 | 49.718
2024-03-29 | 12:31 | 49.718
2024-03-29 | 12:31 | 49.716
2024-03-29 | 12:31 | 49.715
2024-03-29 | 12:31 | 49.716
2024-03-29 | 12:31 | 49.719
2024-03-29 | 12:31 | 49.72
2024-03-29 | 12:31 | 49.719
2024-03-29 | 12:31 | 49.718
2024-03-29 | 12:31 | 49.718
2024-03-29 | 12:31 | 49.718
2024-03-29 | 12:31 | 49.719
2024-03-29 | 12:31 | 49.722
2024-03-29 | 12:31 | 49.721
2024-03-29 | 12:31 | 49.719
2024-03-29 | 12:31 | 49.719
2024-03-29 | 12:31 | 49.717
2024-03-29 | 12:31 | 49.716
2024-03-29 | 12:31 | 49.722
2024-03-29 | 12:31 | 49.726
2024-03-29 | 12:31 | 49.725
2024-03-29 | 12:31 | 49.724
2024-03-29 | 12:31 | 49.723
2024-03-29 | 12:31 | 49.727
2024-03-29 | 12:31 | 49.728
2024-03-29 | 12:31 | 49.728
2024-03-29 | 12:31 | 49.729
2024-03-29 | 12:31 | 49.735
2024-03-29 | 12:31 | 49.737
2024-03-29 | 12:31 | 49.739
2024-03-29 | 12:31 | 49.739
2024-03-29 | 12:31 | 49.741
2024-03-29 | 12:31 | 49.74
2024-03-29 | 12:31 | 49.743
2024-03-29 | 12:31 | 49.746
2024-03-29 | 12:31 | 49.747
2024-03-29 | 12:32 | 49.748
2024-03-29 | 12:32 | 49.746
2024-03-29 | 12:32 | 49.747
2024-03-29 | 12:32 | 49.747
2024-03-29 | 12:32 | 49.744
2024-03-29 | 12:32 | 49.741
2024-03-29 | 12:32 | 49.741
2024-03-29 | 12:32 | 49.743
2024-03-29 | 12:32 | 49.742
2024-03-29 | 12:32 | 49.742
2024-03-29 | 12:32 | 49.744
2024-03-29 | 12:32 | 49.742
2024-03-29 | 12:32 | 49.742
2024-03-29 | 12:32 | 49.74
2024-03-29 | 12:32 | 49.744
2024-03-29 | 12:32 | 49.743
2024-03-29 | 12:32 | 49.741
2024-03-29 | 12:32 | 49.741
2024-03-29 | 12:32 | 49.748
2024-03-29 | 12:32 | 49.748
2024-03-29 | 12:32 | 49.748
2024-03-29 | 12:32 | 49.746
2024-03-29 | 12:32 | 49.75
2024-03-29 | 12:32 | 49.751
2024-03-29 | 12:32 | 49.75
2024-03-29 | 12:32 | 49.751
2024-03-29 | 12:32 | 49.751
2024-03-29 | 12:32 | 49.75
2024-03-29 | 12:32 | 49.746
2024-03-29 | 12:32 | 49.744
2024-03-29 | 12:32 | 49.744
2024-03-29 | 12:32 | 49.743
2024-03-29 | 12:32 | 49.743
2024-03-29 | 12:32 | 49.744
2024-03-29 | 12:32 | 49.748
2024-03-29 | 12:32 | 49.75
2024-03-29 | 12:32 | 49.75
2024-03-29 | 12:32 | 49.749
2024-03-29 | 12:32 | 49.752
2024-03-29 | 12:32 | 49.751
2024-03-29 | 12:32 | 49.75
2024-03-29 | 12:32 | 49.747
2024-03-29 | 12:32 | 49.745
2024-03-29 | 12:32 | 49.746
2024-03-29 | 12:32 | 49.749
2024-03-29 | 12:32 | 49.748
2024-03-29 | 12:32 | 49.75
2024-03-29 | 12:32 | 49.751
2024-03-29 | 12:32 | 49.754
2024-03-29 | 12:32 | 49.752
2024-03-29 | 12:32 | 49.753
2024-03-29 | 12:32 | 49.753
2024-03-29 | 12:32 | 49.755
2024-03-29 | 12:32 | 49.755
2024-03-29 | 12:32 | 49.757
2024-03-29 | 12:32 | 49.758
2024-03-29 | 12:32 | 49.758
2024-03-29 | 12:32 | 49.76
2024-03-29 | 12:32 | 49.759
2024-03-29 | 12:32 | 49.768
2024-03-29 | 12:32 | 49.761
2024-03-29 | 12:33 | 49.762
2024-03-29 | 12:33 | 49.764
2024-03-29 | 12:33 | 49.768
2024-03-29 | 12:33 | 49.772
2024-03-29 | 12:33 | 49.775
2024-03-29 | 12:33 | 49.777
2024-03-29 | 12:33 | 49.78
2024-03-29 | 12:33 | 49.781
2024-03-29 | 12:33 | 49.784
2024-03-29 | 12:33 | 49.788
2024-03-29 | 12:33 | 49.796
2024-03-29 | 12:33 | 49.803
2024-03-29 | 12:33 | 49.807
2024-03-29 | 12:33 | 49.808
2024-03-29 | 12:33 | 49.801
2024-03-29 | 12:33 | 49.803
2024-03-29 | 12:33 | 49.805
2024-03-29 | 12:33 | 49.806
2024-03-29 | 12:33 | 49.806
2024-03-29 | 12:33 | 49.806
2024-03-29 | 12:33 | 49.811
2024-03-29 | 12:33 | 49.811
2024-03-29 | 12:33 | 49.811
2024-03-29 | 12:33 | 49.811
2024-03-29 | 12:33 | 49.809
2024-03-29 | 12:33 | 49.809
2024-03-29 | 12:33 | 49.811
2024-03-29 | 12:33 | 49.81
2024-03-29 | 12:33 | 49.812
2024-03-29 | 12:33 | 49.813
2024-03-29 | 12:33 | 49.819
2024-03-29 | 12:33 | 49.822
2024-03-29 | 12:33 | 49.82
2024-03-29 | 12:33 | 49.819
2024-03-29 | 12:33 | 49.818
2024-03-29 | 12:33 | 49.816
2024-03-29 | 12:33 | 49.809
2024-03-29 | 12:33 | 49.806
2024-03-29 | 12:33 | 49.804
2024-03-29 | 12:33 | 49.804
2024-03-29 | 12:33 | 49.8
2024-03-29 | 12:33 | 49.8
2024-03-29 | 12:33 | 49.803
2024-03-29 | 12:33 | 49.803
2024-03-29 | 12:33 | 49.797
2024-03-29 | 12:33 | 49.796
2024-03-29 | 12:33 | 49.803
2024-03-29 | 12:33 | 49.804
2024-03-29 | 12:33 | 49.798
2024-03-29 | 12:33 | 49.798
2024-03-29 | 12:33 | 49.802
2024-03-29 | 12:33 | 49.802
2024-03-29 | 12:33 | 49.8
2024-03-29 | 12:33 | 49.798
2024-03-29 | 12:33 | 49.802
2024-03-29 | 12:33 | 49.805
2024-03-29 | 12:33 | 49.807
2024-03-29 | 12:33 | 49.807
2024-03-29 | 12:33 | 49.812
2024-03-29 | 12:34 | 49.818
2024-03-29 | 12:34 | 49.822
2024-03-29 | 12:34 | 49.825
2024-03-29 | 12:34 | 49.831
2024-03-29 | 12:34 | 49.834
2024-03-29 | 12:34 | 49.837
2024-03-29 | 12:34 | 49.841
2024-03-29 | 12:34 | 49.848
2024-03-29 | 12:34 | 49.851
2024-03-29 | 12:34 | 49.854
2024-03-29 | 12:34 | 49.858
2024-03-29 | 12:34 | 49.859
2024-03-29 | 12:34 | 49.862
2024-03-29 | 12:34 | 49.86
2024-03-29 | 12:34 | 49.863
2024-03-29 | 12:34 | 49.865
2024-03-29 | 12:34 | 49.865
2024-03-29 | 12:34 | 49.867
2024-03-29 | 12:34 | 49.867
2024-03-29 | 12:34 | 49.872
2024-03-29 | 12:34 | 49.873
2024-03-29 | 12:34 | 49.874
2024-03-29 | 12:34 | 49.88
2024-03-29 | 12:34 | 49.877
2024-03-29 | 12:34 | 49.876
2024-03-29 | 12:34 | 49.878
2024-03-29 | 12:34 | 49.879
2024-03-29 | 12:34 | 49.881
2024-03-29 | 12:34 | 49.88
2024-03-29 | 12:34 | 49.88
2024-03-29 | 12:34 | 49.878
2024-03-29 | 12:34 | 49.876
2024-03-29 | 12:34 | 49.871
2024-03-29 | 12:34 | 49.872
2024-03-29 | 12:34 | 49.875
2024-03-29 | 12:34 | 49.877
2024-03-29 | 12:34 | 49.877
2024-03-29 | 12:34 | 49.881
2024-03-29 | 12:34 | 49.886
2024-03-29 | 12:34 | 49.89
2024-03-29 | 12:34 | 49.888
2024-03-29 | 12:34 | 49.889
2024-03-29 | 12:34 | 49.888
2024-03-29 | 12:34 | 49.887
2024-03-29 | 12:34 | 49.888
2024-03-29 | 12:34 | 49.893
2024-03-29 | 12:34 | 49.898
2024-03-29 | 12:34 | 49.893
2024-03-29 | 12:34 | 49.895
2024-03-29 | 12:34 | 49.895
2024-03-29 | 12:34 | 49.891
2024-03-29 | 12:34 | 49.889
2024-03-29 | 12:34 | 49.89
2024-03-29 | 12:34 | 49.895
2024-03-29 | 12:34 | 49.897
2024-03-29 | 12:34 | 49.899
2024-03-29 | 12:34 | 49.902
2024-03-29 | 12:34 | 49.908
2024-03-29 | 12:34 | 49.91
2024-03-29 | 12:34 | 49.908
2024-03-29 | 12:34 | 49.908
2024-03-29 | 12:35 | 49.907
2024-03-29 | 12:35 | 49.915
2024-03-29 | 12:35 | 49.919
2024-03-29 | 12:35 | 49.922
2024-03-29 | 12:35 | 49.926
2024-03-29 | 12:35 | 49.926
2024-03-29 | 12:35 | 49.924
2024-03-29 | 12:35 | 49.925
2024-03-29 | 12:35 | 49.926
2024-03-29 | 12:35 | 49.924
2024-03-29 | 12:35 | 49.924
2024-03-29 | 12:35 | 49.922
2024-03-29 | 12:35 | 49.922
2024-03-29 | 12:35 | 49.92
2024-03-29 | 12:35 | 49.921
2024-03-29 | 12:35 | 49.924
2024-03-29 | 12:35 | 49.924
2024-03-29 | 12:35 | 49.926
2024-03-29 | 12:35 | 49.927
2024-03-29 | 12:35 | 49.928
2024-03-29 | 12:35 | 49.932
2024-03-29 | 12:35 | 49.934
2024-03-29 | 12:35 | 49.936
2024-03-29 | 12:35 | 49.942
2024-03-29 | 12:35 | 49.942
2024-03-29 | 12:35 | 49.942
2024-03-29 | 12:35 | 49.945
2024-03-29 | 12:35 | 49.949
2024-03-29 | 12:35 | 49.947
2024-03-29 | 12:35 | 49.942
2024-03-29 | 12:35 | 49.94
2024-03-29 | 12:35 | 49.937
2024-03-29 | 12:35 | 49.934
2024-03-29 | 12:35 | 49.936
2024-03-29 | 12:35 | 49.933
2024-03-29 | 12:35 | 49.933
2024-03-29 | 12:35 | 49.931
2024-03-29 | 12:35 | 49.93
2024-03-29 | 12:35 | 49.931
2024-03-29 | 12:35 | 49.93
2024-03-29 | 12:35 | 49.931
2024-03-29 | 12:35 | 49.927
2024-03-29 | 12:35 | 49.926
2024-03-29 | 12:35 | 49.927
2024-03-29 | 12:35 | 49.926
2024-03-29 | 12:35 | 49.929
2024-03-29 | 12:35 | 49.929
2024-03-29 | 12:35 | 49.93
2024-03-29 | 12:35 | 49.929
2024-03-29 | 12:35 | 49.933
2024-03-29 | 12:35 | 49.936
2024-03-29 | 12:35 | 49.936
2024-03-29 | 12:35 | 49.936
2024-03-29 | 12:35 | 49.938
2024-03-29 | 12:35 | 49.942
2024-03-29 | 12:35 | 49.94
2024-03-29 | 12:35 | 49.941
2024-03-29 | 12:35 | 49.938
2024-03-29 | 12:35 | 49.942
2024-03-29 | 12:36 | 49.938
2024-03-29 | 12:36 | 49.939
2024-03-29 | 12:36 | 49.94
2024-03-29 | 12:36 | 49.944
2024-03-29 | 12:36 | 49.948
2024-03-29 | 12:36 | 49.946
2024-03-29 | 12:36 | 49.949
2024-03-29 | 12:36 | 49.947
2024-03-29 | 12:36 | 49.945
2024-03-29 | 12:36 | 49.946
2024-03-29 | 12:36 | 49.948
2024-03-29 | 12:36 | 49.953
2024-03-29 | 12:36 | 49.953
2024-03-29 | 12:36 | 49.954
2024-03-29 | 12:36 | 49.958
2024-03-29 | 12:36 | 49.963
2024-03-29 | 12:36 | 49.964
2024-03-29 | 12:36 | 49.97
2024-03-29 | 12:36 | 49.979
2024-03-29 | 12:36 | 49.982
2024-03-29 | 12:36 | 49.981
2024-03-29 | 12:36 | 49.981
2024-03-29 | 12:36 | 49.986
2024-03-29 | 12:36 | 49.989
2024-03-29 | 12:36 | 49.988
2024-03-29 | 12:36 | 49.985
2024-03-29 | 12:36 | 49.986
2024-03-29 | 12:36 | 49.988
2024-03-29 | 12:36 | 49.992
2024-03-29 | 12:36 | 49.994
2024-03-29 | 12:36 | 49.996
2024-03-29 | 12:36 | 49.998
2024-03-29 | 12:36 | 49.998
2024-03-29 | 12:36 | 50.002
2024-03-29 | 12:36 | 50.007
2024-03-29 | 12:36 | 50.013
2024-03-29 | 12:36 | 50.018
2024-03-29 | 12:36 | 50.026
2024-03-29 | 12:36 | 50.034
2024-03-29 | 12:36 | 50.036
2024-03-29 | 12:36 | 50.036
2024-03-29 | 12:36 | 50.037
2024-03-29 | 12:36 | 50.044
2024-03-29 | 12:36 | 50.04
2024-03-29 | 12:36 | 50.04
2024-03-29 | 12:36 | 50.039
2024-03-29 | 12:36 | 50.035
2024-03-29 | 12:36 | 50.032
2024-03-29 | 12:36 | 50.03
2024-03-29 | 12:36 | 50.03
2024-03-29 | 12:36 | 50.031
2024-03-29 | 12:36 | 50.027
2024-03-29 | 12:36 | 50.022
2024-03-29 | 12:36 | 50.023
2024-03-29 | 12:36 | 50.023
2024-03-29 | 12:36 | 50.019
2024-03-29 | 12:36 | 50.018
2024-03-29 | 12:36 | 50.021
2024-03-29 | 12:36 | 50.021
2024-03-29 | 12:36 | 50.018
2024-03-29 | 12:36 | 50.016
2024-03-29 | 12:37 | 50.015
2024-03-29 | 12:37 | 50.014
2024-03-29 | 12:37 | 50.011
2024-03-29 | 12:37 | 50.009
2024-03-29 | 12:37 | 50.006
2024-03-29 | 12:37 | 50.001
2024-03-29 | 12:37 | 49.995
2024-03-29 | 12:37 | 49.99
2024-03-29 | 12:37 | 49.989
2024-03-29 | 12:37 | 49.983
2024-03-29 | 12:37 | 49.978
2024-03-29 | 12:37 | 49.975
2024-03-29 | 12:37 | 49.972
2024-03-29 | 12:37 | 49.974
2024-03-29 | 12:37 | 49.975
2024-03-29 | 12:37 | 49.975
2024-03-29 | 12:37 | 49.98
2024-03-29 | 12:37 | 49.981
2024-03-29 | 12:37 | 49.982
2024-03-29 | 12:37 | 49.985
2024-03-29 | 12:37 | 49.989
2024-03-29 | 12:37 | 49.991
2024-03-29 | 12:37 | 49.991
2024-03-29 | 12:37 | 49.997
2024-03-29 | 12:37 | 49.994
2024-03-29 | 12:37 | 49.997
2024-03-29 | 12:37 | 49.991
2024-03-29 | 12:37 | 49.987
2024-03-29 | 12:37 | 49.984
2024-03-29 | 12:37 | 49.98
2024-03-29 | 12:37 | 49.978
2024-03-29 | 12:37 | 49.976
2024-03-29 | 12:37 | 49.975
2024-03-29 | 12:37 | 49.977
2024-03-29 | 12:37 | 49.983
2024-03-29 | 12:37 | 49.987
2024-03-29 | 12:37 | 49.991
2024-03-29 | 12:37 | 49.993
2024-03-29 | 12:37 | 50
2024-03-29 | 12:37 | 50.004
2024-03-29 | 12:37 | 50.007
2024-03-29 | 12:37 | 50.007
2024-03-29 | 12:37 | 50.006
2024-03-29 | 12:37 | 50.001
2024-03-29 | 12:37 | 50.002
2024-03-29 | 12:37 | 50.004
2024-03-29 | 12:37 | 50.006
2024-03-29 | 12:37 | 50.006
2024-03-29 | 12:37 | 50.004
2024-03-29 | 12:37 | 50.004
2024-03-29 | 12:37 | 50.012
2024-03-29 | 12:37 | 50.02
2024-03-29 | 12:37 | 50.025
2024-03-29 | 12:37 | 50.028
2024-03-29 | 12:37 | 50.029
2024-03-29 | 12:37 | 50.03
2024-03-29 | 12:37 | 50.027
2024-03-29 | 12:37 | 50.023
2024-03-29 | 12:37 | 50.02
2024-03-29 | 12:38 | 50.022
2024-03-29 | 12:38 | 50.019
2024-03-29 | 12:38 | 50.019
2024-03-29 | 12:38 | 50.021
2024-03-29 | 12:38 | 50.019
2024-03-29 | 12:38 | 50.02
2024-03-29 | 12:38 | 50.022
2024-03-29 | 12:38 | 50.024
2024-03-29 | 12:38 | 50.025
2024-03-29 | 12:38 | 50.025
2024-03-29 | 12:38 | 50.025
2024-03-29 | 12:38 | 50.021
2024-03-29 | 12:38 | 50.017
2024-03-29 | 12:38 | 50.015
2024-03-29 | 12:38 | 50.016
2024-03-29 | 12:38 | 50.016
2024-03-29 | 12:38 | 50.013
2024-03-29 | 12:38 | 50.014
2024-03-29 | 12:38 | 50.014
2024-03-29 | 12:38 | 50.016
2024-03-29 | 12:38 | 50.02
2024-03-29 | 12:38 | 50.019
2024-03-29 | 12:38 | 50.021
2024-03-29 | 12:38 | 50.028
2024-03-29 | 12:38 | 50.027
2024-03-29 | 12:38 | 50.028
2024-03-29 | 12:38 | 50.028
2024-03-29 | 12:38 | 50.031
2024-03-29 | 12:38 | 50.032
2024-03-29 | 12:38 | 50.028

## 20240330-1
In GMT
Date | Time | Freq
2024-03-30 | 12:47 | 49.886 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-03-30 | 12:47 | 49.888 | 222 | BRITNED | 676.211
2024-03-30 | 12:47 | 49.888 | 268 | WBURB-2 | 428.156
2024-03-30 | 12:47 | 49.889 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-03-30 | 12:47 | 49.886 |  | Viking Link | -648.9
2024-03-30 | 12:47 | 49.886 |  | Viking Link | 1398.96
2024-03-30 | 12:47 | 49.887 | 209 | DRAXX-3 | 626.95
2024-03-30 | 12:47 | 49.884 | 154 | CDCL-1 | 391.57
2024-03-30 | 12:47 | 49.886 | 268 | ROCK-1 | 468.495
2024-03-30 | 12:47 | 49.887 | 148 | IFA Bipole1 | 945.473
2024-03-30 | 12:47 | 49.888 | 132 | IFA Bipole1 | 999.1
2024-03-30 | 12:47 | 49.887 | 141 | IFA Bipole2 | 1000
2024-03-30 | 12:47 | 49.89 | 135 | IFA Bipole1 | 996.75
2024-03-30 | 12:47 | 49.889 |  | Viking Link | -780.3
2024-03-30 | 12:47 | 49.89
2024-03-30 | 12:47 | 49.888
2024-03-30 | 12:47 | 49.891
2024-03-30 | 12:47 | 49.891
2024-03-30 | 12:47 | 49.893
2024-03-30 | 12:47 | 49.893 | 130 | HEYM12 | 271.908
2024-03-30 | 12:47 | 49.892 | 228 | HUMR-1 | 303.75
2024-03-30 | 12:47 | 49.889
2024-03-30 | 12:47 | 49.89
2024-03-30 | 12:47 | 49.891
2024-03-30 | 12:47 | 49.893
2024-03-30 | 12:47 | 49.892
2024-03-30 | 12:47 | 49.893
2024-03-30 | 12:47 | 49.895
2024-03-30 | 12:47 | 49.896
2024-03-30 | 12:47 | 49.896
2024-03-30 | 12:47 | 49.897 | 211 | CDCL-1 | 291.5
2024-03-30 | 12:48 | 49.893 | 199 | STAY-2 | 413.125
2024-03-30 | 12:48 | 49.891 | 173 | CDCL-1 | 397.375
2024-03-30 | 12:48 | 49.888 | 248 | SEAB-2 | 361.25
2024-03-30 | 12:48 | 49.887 | 255 | FRANCE | 995.65
2024-03-30 | 12:48 | 49.887 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-03-30 | 12:48 | 49.889
2024-03-30 | 12:48 | 49.889
2024-03-30 | 12:48 | 49.891
2024-03-30 | 12:48 | 49.892
2024-03-30 | 12:48 | 49.89
2024-03-30 | 12:48 | 49.888
2024-03-30 | 12:48 | 49.889
2024-03-30 | 12:48 | 49.889
2024-03-30 | 12:48 | 49.888
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.888
2024-03-30 | 12:48 | 49.886
2024-03-30 | 12:48 | 49.888
2024-03-30 | 12:48 | 49.886
2024-03-30 | 12:48 | 49.888
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.888
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.891
2024-03-30 | 12:48 | 49.89
2024-03-30 | 12:48 | 49.889
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.884
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.888
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.885
2024-03-30 | 12:48 | 49.889
2024-03-30 | 12:48 | 49.889
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.887
2024-03-30 | 12:48 | 49.886
2024-03-30 | 12:48 | 49.886
2024-03-30 | 12:48 | 49.883
2024-03-30 | 12:48 | 49.88
2024-03-30 | 12:48 | 49.877
2024-03-30 | 12:48 | 49.878
2024-03-30 | 12:48 | 49.881
2024-03-30 | 12:48 | 49.884
2024-03-30 | 12:48 | 49.885
2024-03-30 | 12:48 | 49.885
2024-03-30 | 12:48 | 49.886
2024-03-30 | 12:48 | 49.884
2024-03-30 | 12:48 | 49.882
2024-03-30 | 12:48 | 49.879
2024-03-30 | 12:48 | 49.878
2024-03-30 | 12:48 | 49.877
2024-03-30 | 12:48 | 49.877
2024-03-30 | 12:48 | 49.871
2024-03-30 | 12:48 | 49.873
2024-03-30 | 12:49 | 49.874
2024-03-30 | 12:49 | 49.875
2024-03-30 | 12:49 | 49.881
2024-03-30 | 12:49 | 49.88
2024-03-30 | 12:49 | 49.884
2024-03-30 | 12:49 | 49.883
2024-03-30 | 12:49 | 49.884
2024-03-30 | 12:49 | 49.885
2024-03-30 | 12:49 | 49.887
2024-03-30 | 12:49 | 49.894
2024-03-30 | 12:49 | 49.893
2024-03-30 | 12:49 | 49.894
2024-03-30 | 12:49 | 49.893
2024-03-30 | 12:49 | 49.893
2024-03-30 | 12:49 | 49.891
2024-03-30 | 12:49 | 49.895
2024-03-30 | 12:49 | 49.896
2024-03-30 | 12:49 | 49.898
2024-03-30 | 12:49 | 49.898
2024-03-30 | 12:49 | 49.9
2024-03-30 | 12:49 | 49.9
2024-03-30 | 12:49 | 49.899
2024-03-30 | 12:49 | 49.902
2024-03-30 | 12:49 | 49.903
2024-03-30 | 12:49 | 49.899
2024-03-30 | 12:49 | 49.897
2024-03-30 | 12:49 | 49.895
2024-03-30 | 12:49 | 49.892
2024-03-30 | 12:49 | 49.889
2024-03-30 | 12:49 | 49.889
2024-03-30 | 12:49 | 49.888
2024-03-30 | 12:49 | 49.888
2024-03-30 | 12:49 | 49.889
2024-03-30 | 12:49 | 49.889
2024-03-30 | 12:49 | 49.89
2024-03-30 | 12:49 | 49.892
2024-03-30 | 12:49 | 49.892
2024-03-30 | 12:49 | 49.889
2024-03-30 | 12:49 | 49.889
2024-03-30 | 12:49 | 49.886
2024-03-30 | 12:49 | 49.887
2024-03-30 | 12:49 | 49.887
2024-03-30 | 12:49 | 49.887
2024-03-30 | 12:49 | 49.89
2024-03-30 | 12:49 | 49.889
2024-03-30 | 12:49 | 49.889
2024-03-30 | 12:49 | 49.886
2024-03-30 | 12:49 | 49.884
2024-03-30 | 12:49 | 49.881
2024-03-30 | 12:49 | 49.876
2024-03-30 | 12:49 | 49.877
2024-03-30 | 12:49 | 49.874
2024-03-30 | 12:49 | 49.875
2024-03-30 | 12:49 | 49.877
2024-03-30 | 12:49 | 49.877
2024-03-30 | 12:49 | 49.876
2024-03-30 | 12:49 | 49.877
2024-03-30 | 12:49 | 49.876
2024-03-30 | 12:49 | 49.876
2024-03-30 | 12:49 | 49.874
2024-03-30 | 12:49 | 49.874
2024-03-30 | 12:50 | 49.877
2024-03-30 | 12:50 | 49.876
2024-03-30 | 12:50 | 49.879
2024-03-30 | 12:50 | 49.876
2024-03-30 | 12:50 | 49.878
2024-03-30 | 12:50 | 49.88
2024-03-30 | 12:50 | 49.885
2024-03-30 | 12:50 | 49.884
2024-03-30 | 12:50 | 49.887
2024-03-30 | 12:50 | 49.887
2024-03-30 | 12:50 | 49.886
2024-03-30 | 12:50 | 49.883
2024-03-30 | 12:50 | 49.881
2024-03-30 | 12:50 | 49.88
2024-03-30 | 12:50 | 49.883
2024-03-30 | 12:50 | 49.882
2024-03-30 | 12:50 | 49.885
2024-03-30 | 12:50 | 49.884
2024-03-30 | 12:50 | 49.886
2024-03-30 | 12:50 | 49.881
2024-03-30 | 12:50 | 49.883
2024-03-30 | 12:50 | 49.879
2024-03-30 | 12:50 | 49.88
2024-03-30 | 12:50 | 49.879
2024-03-30 | 12:50 | 49.877
2024-03-30 | 12:50 | 49.877
2024-03-30 | 12:50 | 49.877
2024-03-30 | 12:50 | 49.875
2024-03-30 | 12:50 | 49.877
2024-03-30 | 12:50 | 49.878
2024-03-30 | 12:50 | 49.878
2024-03-30 | 12:50 | 49.878
2024-03-30 | 12:50 | 49.879
2024-03-30 | 12:50 | 49.882
2024-03-30 | 12:50 | 49.885
2024-03-30 | 12:50 | 49.889
2024-03-30 | 12:50 | 49.894
2024-03-30 | 12:50 | 49.899
2024-03-30 | 12:50 | 49.904
2024-03-30 | 12:50 | 49.909
2024-03-30 | 12:50 | 49.916
2024-03-30 | 12:50 | 49.917
2024-03-30 | 12:50 | 49.92
2024-03-30 | 12:50 | 49.922
2024-03-30 | 12:50 | 49.922
2024-03-30 | 12:50 | 49.922
2024-03-30 | 12:50 | 49.926
2024-03-30 | 12:50 | 49.926
2024-03-30 | 12:50 | 49.922
2024-03-30 | 12:50 | 49.923
2024-03-30 | 12:50 | 49.922
2024-03-30 | 12:50 | 49.925
2024-03-30 | 12:50 | 49.926
2024-03-30 | 12:50 | 49.926
2024-03-30 | 12:50 | 49.92
2024-03-30 | 12:50 | 49.919
2024-03-30 | 12:50 | 49.917
2024-03-30 | 12:50 | 49.915
2024-03-30 | 12:50 | 49.916
2024-03-30 | 12:51 | 49.914
2024-03-30 | 12:51 | 49.915
2024-03-30 | 12:51 | 49.919
2024-03-30 | 12:51 | 49.921
2024-03-30 | 12:51 | 49.923
2024-03-30 | 12:51 | 49.923
2024-03-30 | 12:51 | 49.922
2024-03-30 | 12:51 | 49.921
2024-03-30 | 12:51 | 49.923
2024-03-30 | 12:51 | 49.926
2024-03-30 | 12:51 | 49.927
2024-03-30 | 12:51 | 49.928
2024-03-30 | 12:51 | 49.929
2024-03-30 | 12:51 | 49.927
2024-03-30 | 12:51 | 49.924
2024-03-30 | 12:51 | 49.923
2024-03-30 | 12:51 | 49.925
2024-03-30 | 12:51 | 49.928
2024-03-30 | 12:51 | 49.928
2024-03-30 | 12:51 | 49.926
2024-03-30 | 12:51 | 49.925
2024-03-30 | 12:51 | 49.922
2024-03-30 | 12:51 | 49.917
2024-03-30 | 12:51 | 49.914
2024-03-30 | 12:51 | 49.915
2024-03-30 | 12:51 | 49.915
2024-03-30 | 12:51 | 49.915
2024-03-30 | 12:51 | 49.918
2024-03-30 | 12:51 | 49.921
2024-03-30 | 12:51 | 49.923
2024-03-30 | 12:51 | 49.923
2024-03-30 | 12:51 | 49.927
2024-03-30 | 12:51 | 49.925
2024-03-30 | 12:51 | 49.925
2024-03-30 | 12:51 | 49.924
2024-03-30 | 12:51 | 49.923
2024-03-30 | 12:51 | 49.923
2024-03-30 | 12:51 | 49.919
2024-03-30 | 12:51 | 49.918
2024-03-30 | 12:51 | 49.919
2024-03-30 | 12:51 | 49.922
2024-03-30 | 12:51 | 49.925
2024-03-30 | 12:51 | 49.928
2024-03-30 | 12:51 | 49.932
2024-03-30 | 12:51 | 49.932
2024-03-30 | 12:51 | 49.933
2024-03-30 | 12:51 | 49.934
2024-03-30 | 12:51 | 49.935
2024-03-30 | 12:51 | 49.936
2024-03-30 | 12:51 | 49.934
2024-03-30 | 12:51 | 49.935
2024-03-30 | 12:51 | 49.935
2024-03-30 | 12:51 | 49.934
2024-03-30 | 12:51 | 49.934
2024-03-30 | 12:51 | 49.937
2024-03-30 | 12:51 | 49.94
2024-03-30 | 12:51 | 49.943
2024-03-30 | 12:51 | 49.943
2024-03-30 | 12:51 | 49.945
2024-03-30 | 12:51 | 49.949
2024-03-30 | 12:51 | 49.95
2024-03-30 | 12:52 | 49.95
2024-03-30 | 12:52 | 49.95
2024-03-30 | 12:52 | 49.951
2024-03-30 | 12:52 | 49.948
2024-03-30 | 12:52 | 49.952
2024-03-30 | 12:52 | 49.952
2024-03-30 | 12:52 | 49.955
2024-03-30 | 12:52 | 49.954
2024-03-30 | 12:52 | 49.955
2024-03-30 | 12:52 | 49.954
2024-03-30 | 12:52 | 49.956
2024-03-30 | 12:52 | 49.951
2024-03-30 | 12:52 | 49.951
2024-03-30 | 12:52 | 49.947
2024-03-30 | 12:52 | 49.95
2024-03-30 | 12:52 | 49.946
2024-03-30 | 12:52 | 49.944
2024-03-30 | 12:52 | 49.946
2024-03-30 | 12:52 | 49.945
2024-03-30 | 12:52 | 49.943
2024-03-30 | 12:52 | 49.943
2024-03-30 | 12:52 | 49.942
2024-03-30 | 12:52 | 49.942
2024-03-30 | 12:52 | 49.94
2024-03-30 | 12:52 | 49.94
2024-03-30 | 12:52 | 49.943
2024-03-30 | 12:52 | 49.943
2024-03-30 | 12:52 | 49.942
2024-03-30 | 12:52 | 49.943
2024-03-30 | 12:52 | 49.943
2024-03-30 | 12:52 | 49.939
2024-03-30 | 12:52 | 49.933
2024-03-30 | 12:52 | 49.932
2024-03-30 | 12:52 | 49.93
2024-03-30 | 12:52 | 49.928
2024-03-30 | 12:52 | 49.928
2024-03-30 | 12:52 | 49.93
2024-03-30 | 12:52 | 49.928
2024-03-30 | 12:52 | 49.927
2024-03-30 | 12:52 | 49.931
2024-03-30 | 12:52 | 49.937
2024-03-30 | 12:52 | 49.935
2024-03-30 | 12:52 | 49.935
2024-03-30 | 12:52 | 49.937
2024-03-30 | 12:52 | 49.941
2024-03-30 | 12:52 | 49.94
2024-03-30 | 12:52 | 49.938
2024-03-30 | 12:52 | 49.937
2024-03-30 | 12:52 | 49.935
2024-03-30 | 12:52 | 49.933
2024-03-30 | 12:52 | 49.935
2024-03-30 | 12:52 | 49.936
2024-03-30 | 12:52 | 49.941
2024-03-30 | 12:52 | 49.942
2024-03-30 | 12:52 | 49.944
2024-03-30 | 12:52 | 49.943
2024-03-30 | 12:52 | 49.942
2024-03-30 | 12:52 | 49.94
2024-03-30 | 12:52 | 49.935
2024-03-30 | 12:52 | 49.932
2024-03-30 | 12:53 | 49.93
2024-03-30 | 12:53 | 49.928
2024-03-30 | 12:53 | 49.925
2024-03-30 | 12:53 | 49.922
2024-03-30 | 12:53 | 49.92
2024-03-30 | 12:53 | 49.92
2024-03-30 | 12:53 | 49.923
2024-03-30 | 12:53 | 49.928
2024-03-30 | 12:53 | 49.931
2024-03-30 | 12:53 | 49.931
2024-03-30 | 12:53 | 49.933
2024-03-30 | 12:53 | 49.938
2024-03-30 | 12:53 | 49.94
2024-03-30 | 12:53 | 49.94
2024-03-30 | 12:53 | 49.943
2024-03-30 | 12:53 | 49.946
2024-03-30 | 12:53 | 49.947
2024-03-30 | 12:53 | 49.946
2024-03-30 | 12:53 | 49.945
2024-03-30 | 12:53 | 49.944
2024-03-30 | 12:53 | 49.946
2024-03-30 | 12:53 | 49.947
2024-03-30 | 12:53 | 49.948
2024-03-30 | 12:53 | 49.949
2024-03-30 | 12:53 | 49.953
2024-03-30 | 12:53 | 49.955
2024-03-30 | 12:53 | 49.96
2024-03-30 | 12:53 | 49.965
2024-03-30 | 12:53 | 49.968
2024-03-30 | 12:53 | 49.969
2024-03-30 | 12:53 | 49.972
2024-03-30 | 12:53 | 49.974
2024-03-30 | 12:53 | 49.974
2024-03-30 | 12:53 | 49.972
2024-03-30 | 12:53 | 49.972
2024-03-30 | 12:53 | 49.969
2024-03-30 | 12:53 | 49.965
2024-03-30 | 12:53 | 49.959
2024-03-30 | 12:53 | 49.954
2024-03-30 | 12:53 | 49.955
2024-03-30 | 12:53 | 49.956
2024-03-30 | 12:53 | 49.955
2024-03-30 | 12:53 | 49.957
2024-03-30 | 12:53 | 49.957
2024-03-30 | 12:53 | 49.956
2024-03-30 | 12:53 | 49.96
2024-03-30 | 12:53 | 49.962
2024-03-30 | 12:53 | 49.963
2024-03-30 | 12:53 | 49.964
2024-03-30 | 12:53 | 49.961
2024-03-30 | 12:53 | 49.96
2024-03-30 | 12:53 | 49.956
2024-03-30 | 12:53 | 49.958
2024-03-30 | 12:53 | 49.959
2024-03-30 | 12:53 | 49.962
2024-03-30 | 12:53 | 49.962
2024-03-30 | 12:53 | 49.964
2024-03-30 | 12:53 | 49.967
2024-03-30 | 12:53 | 49.972
2024-03-30 | 12:54 | 49.975
2024-03-30 | 12:54 | 49.978
2024-03-30 | 12:54 | 49.978
2024-03-30 | 12:54 | 49.979
2024-03-30 | 12:54 | 49.981
2024-03-30 | 12:54 | 49.981
2024-03-30 | 12:54 | 49.983
2024-03-30 | 12:54 | 49.986
2024-03-30 | 12:54 | 49.988
2024-03-30 | 12:54 | 49.989
2024-03-30 | 12:54 | 49.992
2024-03-30 | 12:54 | 49.991
2024-03-30 | 12:54 | 49.993
2024-03-30 | 12:54 | 49.991
2024-03-30 | 12:54 | 49.991
2024-03-30 | 12:54 | 49.993
2024-03-30 | 12:54 | 49.993
2024-03-30 | 12:54 | 49.992
2024-03-30 | 12:54 | 49.993
2024-03-30 | 12:54 | 49.996
2024-03-30 | 12:54 | 49.996
2024-03-30 | 12:54 | 50
2024-03-30 | 12:54 | 50.001
2024-03-30 | 12:54 | 50.002
2024-03-30 | 12:54 | 50
2024-03-30 | 12:54 | 50.001
2024-03-30 | 12:54 | 50.001
2024-03-30 | 12:54 | 50.004
2024-03-30 | 12:54 | 50.003
2024-03-30 | 12:54 | 50.004
2024-03-30 | 12:54 | 50.008
2024-03-30 | 12:54 | 50.008
2024-03-30 | 12:54 | 50.009
2024-03-30 | 12:54 | 50.009
2024-03-30 | 12:54 | 50.012
2024-03-30 | 12:54 | 50.014
2024-03-30 | 12:54 | 50.016
2024-03-30 | 12:54 | 50.019
2024-03-30 | 12:54 | 50.016
2024-03-30 | 12:54 | 50.016
2024-03-30 | 12:54 | 50.012
2024-03-30 | 12:54 | 50.011
2024-03-30 | 12:54 | 50.01
2024-03-30 | 12:54 | 50.008
2024-03-30 | 12:54 | 50.005
2024-03-30 | 12:54 | 50.004
2024-03-30 | 12:54 | 50.005
2024-03-30 | 12:54 | 50.001
2024-03-30 | 12:54 | 50.003
2024-03-30 | 12:54 | 50.004
2024-03-30 | 12:54 | 50.003
2024-03-30 | 12:54 | 50.003
2024-03-30 | 12:54 | 50.006
2024-03-30 | 12:54 | 50.009
2024-03-30 | 12:54 | 50.014
2024-03-30 | 12:54 | 50.016
2024-03-30 | 12:54 | 50.015
2024-03-30 | 12:54 | 50.014
2024-03-30 | 12:54 | 50.013
2024-03-30 | 12:54 | 50.013
2024-03-30 | 12:54 | 50.016
2024-03-30 | 12:55 | 50.016
2024-03-30 | 12:55 | 50.014
2024-03-30 | 12:55 | 50.013
2024-03-30 | 12:55 | 50.016
2024-03-30 | 12:55 | 50.016
2024-03-30 | 12:55 | 50.014
2024-03-30 | 12:55 | 50.01
2024-03-30 | 12:55 | 50.008
2024-03-30 | 12:55 | 50.005
2024-03-30 | 12:55 | 50.005
2024-03-30 | 12:55 | 50.008
2024-03-30 | 12:55 | 50.007
2024-03-30 | 12:55 | 50.007
2024-03-30 | 12:55 | 50.008
2024-03-30 | 12:55 | 50.01
2024-03-30 | 12:55 | 50.013
2024-03-30 | 12:55 | 50.019
2024-03-30 | 12:55 | 50.022
2024-03-30 | 12:55 | 50.024
2024-03-30 | 12:55 | 50.024
2024-03-30 | 12:55 | 50.024
2024-03-30 | 12:55 | 50.024
2024-03-30 | 12:55 | 50.024
2024-03-30 | 12:55 | 50.022
2024-03-30 | 12:55 | 50.024
2024-03-30 | 12:55 | 50.022
2024-03-30 | 12:55 | 50.022
2024-03-30 | 12:55 | 50.021
2024-03-30 | 12:55 | 50.018
2024-03-30 | 12:55 | 50.013
2024-03-30 | 12:55 | 50.012
2024-03-30 | 12:55 | 50.015
2024-03-30 | 12:55 | 50.018
2024-03-30 | 12:55 | 50.023
2024-03-30 | 12:55 | 50.028
2024-03-30 | 12:55 | 50.035
2024-03-30 | 12:55 | 50.038
2024-03-30 | 12:55 | 50.036
2024-03-30 | 12:55 | 50.037
2024-03-30 | 12:55 | 50.04
2024-03-30 | 12:55 | 50.042
2024-03-30 | 12:55 | 50.042
2024-03-30 | 12:55 | 50.045
2024-03-30 | 12:55 | 50.047
2024-03-30 | 12:55 | 50.047
2024-03-30 | 12:55 | 50.047
2024-03-30 | 12:55 | 50.047
2024-03-30 | 12:55 | 50.049
2024-03-30 | 12:55 | 50.051
2024-03-30 | 12:55 | 50.047
2024-03-30 | 12:55 | 50.049
2024-03-30 | 12:55 | 50.051
2024-03-30 | 12:55 | 50.052
2024-03-30 | 12:55 | 50.052
2024-03-30 | 12:55 | 50.056
2024-03-30 | 12:55 | 50.058
2024-03-30 | 12:55 | 50.06
2024-03-30 | 12:55 | 50.059
2024-03-30 | 12:55 | 50.06
2024-03-30 | 12:56 | 50.059
2024-03-30 | 12:56 | 50.056
2024-03-30 | 12:56 | 50.054
2024-03-30 | 12:56 | 50.054
2024-03-30 | 12:56 | 50.053
2024-03-30 | 12:56 | 50.051
2024-03-30 | 12:56 | 50.053
2024-03-30 | 12:56 | 50.054
2024-03-30 | 12:56 | 50.058
2024-03-30 | 12:56 | 50.059
2024-03-30 | 12:56 | 50.062
2024-03-30 | 12:56 | 50.067
2024-03-30 | 12:56 | 50.067
2024-03-30 | 12:56 | 50.068
2024-03-30 | 12:56 | 50.07
2024-03-30 | 12:56 | 50.076
2024-03-30 | 12:56 | 50.081
2024-03-30 | 12:56 | 50.084
2024-03-30 | 12:56 | 50.089
2024-03-30 | 12:56 | 50.086
2024-03-30 | 12:56 | 50.084
2024-03-30 | 12:56 | 50.082
2024-03-30 | 12:56 | 50.082
2024-03-30 | 12:56 | 50.082
2024-03-30 | 12:56 | 50.08
2024-03-30 | 12:56 | 50.076
2024-03-30 | 12:56 | 50.073
2024-03-30 | 12:56 | 50.071
2024-03-30 | 12:56 | 50.067
2024-03-30 | 12:56 | 50.063