## Sheet2
Column1 | Proposal by? | Please state whether you are responding as an individual or representing the views of an organisation | What is the specific part of the thermal constraints problem this proposal is addressing? | How does it solve the problem? | Which of the below categories does your solution fall into (you can choose more than 1 category and please elaborate if ‘other’) | What is the value to the consumer? (value for money) | What is the value to the control room? (efficient dispatch) | What is the value to the service provider?(efficient investment) | What is the carbon saving value? (helps 2035 target) | Does this project provide other value to the system? (e.g., stability, frequency)? | What are the potential challenges with implementation? | When would we contract? (e.g., day ahead, T-1, T-4) | How long is the contracting period? | How would prices be set? | What is the lead time? | Other comments
1 | Niall Stuart on behalf of AMP Clean Energy | Organisation | Increasing demand for power in constrained areas | By increasing demand for power in constrained areas through contracting with demand to import at times of constraint. This could be for variable or fixed number of hours, but would require to be significantly greater than the current proposal for up to 50 hours (20x?) We believe there is around 1GW of manufacturing heat demand currently being met through fossil fuels which could be electrified. | Reduce overall volume of ESO actions;Reduce price of ESO actions; | Lower cost than status quo (ie constraining off wind) Reduced carbon emissions from industry, at lower cost than alternatives such as hydrogen and CCUS Lower levels of investment in transmission infrastructure as a result of increased 'local' demand reducing need for greater 'export' capacity Optimised usage of existing grid infrastructure Greater use of renewable generation capacity | Increased suite of options when it comes to balancing network in constrained areas, both in terms of geography but also in terms of technology | Lower cost decarbonisation | We calculate that 1GW of flexible industrial demand would save 185 tonnes of CO2 for every hour in which renewable power displaces fossil fuel demand. | Longer duration demand than that provided by BESS | Grid costs for electrification projects are significantly greater than staying on gas as a result of DUoS and TNUoS residual amongst other things, and there are also connection costs. In addition, projects importing power have to pay Final Consumption Levies to meet the costs of support for renewables through CfD, RO and FiT (around £45 per MWh). And the costs of power per unit compared to gas are around 5x These all make electrification challenging from an investment perspective. | T-2 | This would depend on the price per MWh and numbers of hour contracted per year. | We would propose a quarterly or six-monthly tender. | There will be projects ready to go now. We have financed and are constructing one project which is underpinned by use of biomass and the RHI at Simpsons in Berwick - see https://www.ampcleanenergy.com/articles/revolutionising-the-scotch-whisky-sector-amp-clean-energy-and-simpsons-malt-limited-collaborate-to-tackle-carbon-emissions-and-grid-constraints/ | We are essentially proposing a model whereby ESO would contract with flexible demand to import power for a certain number of hours each year at a certain price. This would support the shift to electrification in areas of constraint and save money to consumers, through providing a revenue floor to flexible demand. This could also be banded, eg 1,000 hours @ £x, next thousand hours @ £y etc to improve VfM.
2 | Simon Gill | Both - Myself and on behalf of Scottish Renewables | Note that this submission summarises a recent report published by Scottish Renewables which is available here: https://www.scottishrenewables.com/publications/1488-exploring-options-for-constraint-management-in-the-gb-electricity-system-the-potential-for-constraint-management-markets The report describes a number of different potential approaches which can be combined into a 'constraint management portfolio' with a clear well defined objective, which should specifically consider management of consumer risk as well as minimizing of consumer costs In summary the main parts of the portfolio would be the development of short term (day ahead / intra day) and long term (months / years) ahead constraint management markets which can provide cheaper alternatives for both 'turn down' actions behind a constraint and 'turn up' actions in front of a constraint. It broadly reduces the price that the ESO needs to pay for constraint management and provides more flexible procurement options including availability / utilisation contracting. | By providing the ESO with a greater number of tools and procurement options at a range of timescale leading up to gate closure. | Reduce price of ESO actions; | The consumer value is two fold: firstly the potential to reduce the price; secondly the potential to better manage constraint risk. For example, the portfolio and constraint management markets can draw in a greater number of cheaper providers. And through the use of availability / utilisation payments in both short and long term constraint management markets they can provide a hedge for consumers against price uncertainty on certain volumes of constraints. | The short term constraint management markets can help build confidence of dispatch or of availability with pre-defined prices for utilisation for particular assets from day-ahead onwards. This gives the control room visibility earlier in the run in to gate closure and a pre-defined set of constraint management actions (with prices) ready to dispatch. | It will create the first real clearly defined 'constraint' revenue stream for developers capable of relieving constraints, with the appropriate locational signal to invest in the right location in order to access the revenue stream. The long-term constraint management contracting element of the portfolio can provide a clear revenue stream, or cost-fixing mechanism for developers of flexible demand or energy storage. | We expect the mechanism to support the development of energy storage (potentially longer duration than currently supported by ancillary service markets), and new forms of electrified demand such as hydrogen electrolysis. Both of these will lead to carbon savings across the energy system | Many assets supported would likely be capable of providing other ancillary services | The report discussed three areas of challenge: forecasting constraints effectively, the potential for interactions (including gaming) between a constraint management market, the wholesale market and the BM, and the challenge of including interconnectors. The report provides more detail | For short term constraint managment markets: likely day ahead and intraday contracting. For long term constraint management markets: potentially from month ahead to multiple years ahead. | To be determined. | Short term markets: through a competitive auction similar to how ancillary services are contracted. Long term markets: through competitive tendering or auctions | To be determined | This is a brief summary of multiple ideas mentioned within our report. There is value in reviewing that document and I am happy to discuss the ideas in more detail simon@energylandscape.co.uk
3 | Eneus Energy | Organisation | Curtailment of generation in Scotland, north of Boundary B6, is already having a considerable impact on generation volumes and is forecast to grow to 10GW or more by 2030. This means significant loss of low carbon energy (principally wind energy) which is detrimental to our efforts to tackle climate change whilst also being economically inefficient. New flexible demand in Scotland could ease these problems however current mechanisms do not provide strong enough locational signals for such demand to be investable. | This product will solve the problem by facilitating investment in new flexible PtX production projects north of B6 which will utilise large volumes of otherwise curtailed energy to produce green hydrogen and related derivatives such as ammonia and sustainable fuels. Green hydrogen (and derivatives) production merits particular focus for NG ESO due to strict additionality requirements which require hourly matching of hydrogen production with renewable power production thereby directly addressing imbalance issues which in Scotland are very largely driven by variations in wind output. Such projects also provide benefits in terms of scale, rate of growth, savings for NG ESO and consumers, and alignment with 2035 grid decarbonisation and 2050 net zero objectives (discussed below). | Reduce overall volume of ESO actions;Reduce price of ESO actions; | This product will significantly limit curtailment of generators and wasted renewable energy. The energy is purchased at a low enough price to enable investment in production of hydrogen and ammonia in Scotland, whilst reducing costs for the ESO to balance the network thus lessening the impact of BSUoS charges to end consumers. Our studies suggest that these cost savings could be around £100m pa. per 1GWe of production, based on current curtailment volumes, rising further by 2030. | P2X plant will by design follow wind production profiles on an hourly matching basis, as described above, thereby maximising utilisation of otherwise curtailed energy. In addition the latest generation of electrolyser technology also also has the ability to ramp up and down on shorter timeframes to help support the control room with system stabilisation, dealing with unplanned outage issues and stress events. | This product will provide long term investment signals of sufficient robustness and magnitude to facilitate funding, construction and operation of new flexible P2X plant at locations north of the B6 boundary, thereby supporting growth of a clean sector delivering jobs and economic value for Scotland and the UK as a whole. Each 1GWe plant will create capital investment of some £2bn-£3bn along with in excess of 100 long term jobs (plant lifetime 30years+). Without this product (or something very similar) such investment will not be possible and PtX projects will not proceed. | Utilisation of green hydrogen within the UK will directly support the planned full decarbonisation of the grid by 2035, with hydrogen's value as a "bridge" between the power and gas systems being seen as increasingly important. This is exemplified in the recent report by AFRY for the Climate Change Committee "Delivering a reliable decarbonised power system" which identifies a need for hydrogen fueled power generation (in addition to uses in industry and transport) of around 14GW by 2035, producing 30TWh annually. Build out is anticipated from the late 20s with the gas network playing a key role in transporting hydrogen from production in the north to power generation locations in the south (noting that storage will be required to provide temporal matching). An example 1GWe green hydrogen and/or ammonia plant will reduce global carbon emissions by over 1 million tons of CO2 per annum. | The latest generation of electrolyser technology has the ability to ramp up and down on short timeframes to help support the control room with system stabilisation, dealing with unplanned outage issues and stress events. Droop control is possible, and reactive power services can be provided. Discussion is recommended at an early stage to feed into discussions with the OEMs and procurement specifications. | The interface between this scheme and the existing RO and CfD regimes will need to be carefully considered to ensure workability for wind generators and that the benefits for consumers are fully maximised. | Contract award two years ahead of earliest COD is recommended with flexibility to allow for any remaining uncertainties in construction timing at that point and also for phased growth of the project as more demand materialises. A four year period could be appropriate in this regard, for discussion. Clarity on contracting terms should be provided as early as possible in order to facilitate accelerated development timelines by providing investor conifidence. | A contracting period of 15 years is ideal for investor requirements given alignment with debt repayment terms, however we acknowledge 10 years may be more in line with the "temporary" nature of this arrangement ahead of wider market reform and possible locational pricing. Further discussion is recommended. | Either through bilateral negotiations, or by tendering. Equally important to price is the volume of discounted energy available. Our studies show that a 1GWe green hydrogen or ammonia plant could consume up to 1.8TWh of curtailed energy per annum, based on current curtailment levels and subject to detailed assessment of curtailed energy at specific locations. Commercial viability and thereby investability of our projects will depend on us being able to maximise access to large volumes of heavily discounted or zero priced otherwise-curtailed energy, which we believe can be done whilst also delivering very substantial savings to NG ESO and consumers. | The NG ESO consultative approach is welcomed and will help developers and other interested parties to move forward with greater certainty. Early visibility of product structure, indicative pricing/volumes and contracting terms is important and is needed from 2024. The contract itself needs to be ready for signing at FID as part of the process where all parties, including funders, commit to the construction of the project. This means contract awards from 2025 onwards. | As our product proposal is linked to green hydrogen and related derivatives we suggest it is named Flex PtX.
4 | Nicky Ferguson | This proposal represents the views of Eku Energy | The existing transmission lines are not being used to their maximum potential, leading to curtailment of renewables, long connection times for new generation and increased congestion and balancing costs for consumers. From October 2021 to September 2022, the ESO spent £2.0bn managing transmission constraints, a 165% y-o-y increase in costs. The cost and volumes are expected to continue to grow with the introduction of more renewable energy and the electrification of heat and outpacing transmission build out. Various iterations of ESO’s modelling shows costs peaking at £2.5bn per year in the mid-2020s or £3bn in mid-2030s, and that is still assuming transmission is built on time. The increased costs of managing constraint actions must eventually be paid by consumers’ electricity bills, which are already at an all-time high. Thermal constraints are continuing to make up the bulk of the growing volume and cost of constraints. The ESO’s current approach uses the Dx suite to rapidly respond to frequency deviations caused by a fault. This requires a minimum of 1.5 GW of dynamic response to be reserved and ready to be injected within 1 s. If a fault occurs and the intertrips shut down generation, the frequency dips nationally, and the frequency response will result in an injection of power everywhere on the grid. The ESO then relies on manual redispatch of generation within 10 minutes to return the system to a secure state and uses a 10-minute line overrating for their transmission wires. There are three issues with using a national, automatic frequency response service to manage faults. 1) Frequency response will occur on both sides of the boundary, including on the same side where generation has been paid to stop via the intertrips. This could potentially be mitigated by changes to the balancing mechanism with local frequency products, but it would require increasing costs and NESO actions. 2) It is difficult to ensure there is sufficient capacity on the correct side of all boundaries to counteract the loss of generation. In order to achieve this, the NESO performs extensive calculations and holds large contingency of dynamic capacity. The further south the boundary limit is, the harder it is to ensure sufficient reserves on the demand side! 3) Major faults, may need support for multiple grid challenges (e.g. voltage stability, inertia, short circuit power, and power oscillation dampening). For instance, in the aftermath of a significant fault event, the system's strength will be jeopardized, resulting in low voltage. The utilization of balancing reserves to offset intertrip consequences will also lead to a low frequency. The lower the short circuit levels and inertia, the greater the impact area and risk of subsequent faults. In areas like the North that already have low short circuit power, a low voltage event may cause more generation in the area to disconnect, requiring even more frequency and voltage support. Due to these issues, the ESO continues to use a 10-minute line rating, relying on thermal plants for security. The issue with using the 10-minute line overrating is the ESO is not able to take advantage of incremental Available Transmission Capacity (ATC) isn’t utilising the transmission lines to their full efficiency. As a result, the NESO is reliant on expensive long term network upgrades or market reform to slowly improve the situation (which will get worse if they are delayed). | It is possible to increase transmission capacity sooner for lower cost to reduce thermal constraints. Our solution focuses on a means to reduce the line rating from 10 minutes to 3 minutes or less on specific boundaries. Using the table from NESO’s congestion management report to determine transmission capacity for 400kV lines, if a 3-minute line rating were used instead of a 10-minute rating, we could see up to a 40% increase in transmission capacity, depending on the location and assuming protection settings are adjusted. This could unlock GWs of spare capacity in a short time with the same, or increased, security of supply. To use the 3-minute or less line rating and increase the ATC requires a nearly instantaneous injection of active and reactive power at the load end of the transmission line while simultaneously disconnecting or absorbing a generation source of the equivalent size on the generation end of the transmission line. The quicker the response, the shorter the line rating that can be used. This would all need to be done to a high level of certainty and maintained for at least 10 minutes, when further generation is able to be re-dispatched. Intertrips have been proven and cost-effective way to reduce control room actions and costs to balance and secure the system in anticipation of a fault. Our proposal is to implement a complimentary solution on the load side of a fault in the form of a battery or other fast responding generation that could, similarly to an intertrip, be armed and instantly activated via a point-to-point communication in the case of a fault and thereby export power and reactive power. How does our solution address the problem of thermal constraints? First, the intertrips and batteries can both respond nearly instantaneously, particularly if triggered by point-to-point high speed communication. Batteries can also maintain their power for whatever length of time is needed for redispatch. The batteries would need to be charged prior to the fault, so they would need to be armed when capacity limits are expected, similar to the intertrip scheme. Since grid forming batteries are able to provide a wide range of post-fault services, such as frequency, voltage, inertia and angular stability support upon activation, it will stay connected and respond to voltage events – providing further short circuit support. The solution will ensure voltage support and have longer time to redispatch, in turn increasing system security and the quality of the response to reduce the line rating needed. This would allow a line rating of 3 minutes or less to be used, increasing ATC by up to 40%. Our initial analysis shows that in the UK across the major constrained boundaries, such as the B6, 1 GW of battery capacity in the right locations could increase transmission capacity by up to 1 GW. How does this address the problem of the costs and volume of constraint actions? Firstly, the NESO can reduce their response capacity because they know they will have sufficient volume on the load side of the fault. Secondly, they would not need to activate expensive thermal units in the balancing mechanism after a fault to provide voltage support or the range of other services the battery can provide. Since the response from the battery could be longer than 10 minutes (which is required to restore the response capacity), the NESO could have more time to redispatch the lower cost options. This solution works as a form of locational response that is only armed some of the time, therefore assets are able to participate in other markets and keep the service cost low. Finally, by increasing the ATC, the volume of constraints should decrease. This solution has been proven by TSOs around the globe, with introductions in Australia, Germany, Lithuania and the US. The NESO has the opportunity to tailor the solution to meet their needs at a specific constrained location to maximise the benefits to the system. | Reduce overall costs to consumers;Increase effective network capacity; | The increase in transmission capacity by up to 40% will reduce the total cost of the system. These savings will be passed through to the consumer through a wide range of benefits: 1. Increased flow of renewable energy – this results in demand being able to be met through more low cost, low carbon energy that would have previously been curtailed. This reduces the wholesale cost of energy, passed through to consumers in their p/kWh price. While not a monetary value, this also results in faster connections of more low carbon demand / generation (speeding up the energy transition) and increased domestic energy security. 2. Increased utilisation of existing transmission network – reducing transmission costs that could be passed to consumers through Transmission Network Use of System costs (TNUoS). 3. High security fault management solution decreases balancing reserves and actions needed during periods of overloading– reducing balancing costs for constraints passed through to consumers via Balancing Services Use of System costs (BSUoS). 4. Integration of more short-term low carbon flexibility on the system increases system stability and security of supply - decreasing balancing and electricity costs. Thermal constraints currently cost around £1-2bn/yr, representing a major cost passed through to consumers via the TNUoS and BSUoS costs. 85% of constraints costs are related to turn up costs, of which 95% are large gas peakers (CCGTs). What could be the value to the consumer of 1 GW additional capacity? A study by SSEN in response to the REMA consultation showed an improvement of 500MW to the B6 boundary could lead to gross savings around £250m for consumers from January 2020 to July 2022 (i.e. £200m/GW/yr) and nearly £750m over 3 boundaries in that same time (£600m/GW/yr). A study by Ofgem on the economic assessment of the Eastern HVDC, determined that delaying the 4 GW project across the B6 by 1 year would lead to constraint costs of £400m. Our service will provide a similar benefit for 1 GW instead of 4 GW, so we can simplify and assume the savings in costs of constraints from our service could be £100m/GW/yr. In reality, the higher cost constraints would be avoided with the first GW with decreasing returns – so the figure could resemble closer to SSEN’s value. If we assume the service is provided for 10 years until network reinforcement and that the gross savings is somewhere between the two sources. Therefore, £1-2bn/GW of gross constraint costs could be saved. To determine the net benefit, the price for the service must be included. A conservative case would require the service cover the cost of building a new 1 GW battery. In practice, the costs would likely be significantly reduced since batteries earn other revenues. BNEF says it costs $400/kW for a 1 hr battery in 2025, or £330m for a 1 GW/GWh battery. Thus, the net savings for 1 GW increased transmission capacity for a 10-year service would be minimum of £0.7-1.7bn savings. This value does not include the additional system value of the extra flexibility, the value of decarbonising the power system or of bolstering the domestic energy security. This solution is location specific, so analysis at the required boundary is needed to determine the actual costs and benefits to the system. The best solutions will target specific boundaries that would benefit most from increased ATC, either because of high overloading or difficulty/long time frames for upgrading lines. It is also possible a battery could increase transmission capacity for multiple boundaries if placed in the right location. From the customer perspective, it provides new options and some complimentary competition to the dominant answers on constraint management (delay connections / build new lines). This is aligned to the NESO license conditions, and so we are happy to have the NESO working with industry to allow more solutions to the problem in addition to the traditional approaches. | The current approach to fault management requires a high number of manual actions from the control room during periods of high loading on thermally constrained boundaries. In our solution, the control room won’t have to focus on re-establishing the balancing reserves during outages on the power system. This is achieved because the increased transmission capacity reduces the periods of overloading as well as decreases the need for activating bids and offers in the balancing mechanism pre-fault as a precaution. Having certainty of fault management in the location needed will reduce complicated contingency plans that the control room would need to make to ensure there is sufficient response ready in the right locations. In other words, it provides a reserve product in a useful location that can be prioritised and automatically activated whenever the control room needs it. In addition, having the solution include power and voltage support at the same time means less actions need to be taken by the control centre post-fault. This then enables the control room to only focus on re-dispatching generation to return to stable operations, rather than on generation tripping due to voltage fluctuations. Finally, utilising a designated battery (or batteries) rather than the dynamic response suite means the NESO is no longer constrained to providing re-dispatching services in 10 minutes. This opens up the option for the control centre to have more time to redispatch, allowing lower cost or more efficient solutions. This extra time may be particularly important as more and more thermal plants retire in the South reducing typical options for redispatch. In addition, a battery can participate in all the other markets when it isn’t armed to provide other sources of fast responding, low-cost flexibility to the control room, similar to how the System Integration Protection Scheme (SIPs) service is done in Australia. When it is armed, it could still technically participate in system strength, voltage control and system restoration services. | The UK is currently fighting for investment in storage and renewables on a global stage. Despite being an initial leader in battery deployments, the UK risks falling behind with a consistent lack of policy/market support at odds with other EU countries (e.g. Italy 71GWh support mechanism, ‘Gridboosters’ in Germany and more). With decreasing battery revenues in the UK due to a saturated market, new sources of revenue along with quicker grid connections will be critical to ensuring the UK remains competitive to investors. At a time when global investors are wanting to invest, this is an opportunity to maintain the UK’s position as a global battery leader, through enabling the technology to compete to solve system issues at lower cost. Longer term contracts enable efficient investment, particularly if there are strong locational signals. If the contract is set for a sufficiently long duration and attractive price, it would allow generation to secure debt financing at a lower cost to the investor, and therefore to provide the service. It would also ensure accurate locational signals are sent to the investor, to know that the asset will be located where it will be valuable to the system. By allowing the service provider to participate in other markets, it will create the opportunity for a merchant upside in addition to the contracted revenues. The network service opportunities will attract investment in higher quality flexible assets by reputable suppliers. If paired with support for a quicker grid connection, this would allow investors to invest in assets that can operate at the right time and place to help lower overall system costs. | The solution increases the transmission capacity on the AC transmission system. As a result, there should be reduced annual curtailment from overloading. This will increase both the GW of connected renewable energy and the GWh of renewable energy that can be utilised by demand in the UK. This should decrease the carbon intensity of the electricity grid. For 1 GW additional transmission capacity from a 1 GW BESS, we could assume it may be able to replace the need for a CCGT operating 50% of the time below the B6 constraint. If so, something in the range of 1.5mtonnes of CO2 emissions could be saved. In addition, more renewables can be connected to the grid before reinforcement, helping to meet the 2035 targets. In addition, the battery/generation would be able to provide a range of other services to the grid that will help increase stability as the grid decarbonises, having further knock-on effects to the capacity of renewables that can be integrated in the grid. | When using BESS to alleviate thermal constraints, you are also building a BESS that can provide system-strength, stability, inertia, frequency, electricity restoration (black start) and energy balancing to ensure a high security of supply. Some of the products will be available when the BESS is armed like system strength, dynamic reactive power and system restauration, while other products will only be available when it’s not armed or after the service contract is over. This will ensure increased competition in the different markets and thereby a lower system cost. | There are some requirements to create the service contract, update the control room and get the asset online. The first challenge will be designing the contract/service to determine the highest benefit option for the lowest cost. The first thing to do will be to determine the best boundaries/substations for the service based on current and projected thermal constraints, projected overloading data and the plans for upgrading those lines. The second thing to determine is the timing requirements. For this, it will be important to determine the compromise point between the maximum certainty in the control room and the lowest cost of delivery. The longer the duration of the contract (in years) and the more time that the generation does not have to be armed (hours), the lower the necessary value of the contract. This can be used to determine how often the service is needed and for how long in a given location to allow competitive tendering of the base contract price. Eku would be happy to support with this analysis. For the control room, this solution will require that the generation is armed and able to be activated. Forecasting and signaling when to arm generation should be similar to the current process used to arm the intertrips. The load flow tool used to calculate the contingency (n-1) needs to be adapted to include the automatic activation of the BESS. The final task will be to ensure that the hard wiring of the asset to constrained line for communication of activation meets the standards of the control room. For the asset, the main requirement will be to ensure timely delivery prior to line upgrades and reforms. The biggest challenge here will be to ensure that a new asset is able to get a grid connection on a constrained line in time. To do this, NESO may need to support the project’s grid connection process, since it will be increasing the capacity of lines and accelerating investment in that location. The delivery will also be contingent on timely construction which can be a risk given current supply chain bottlenecks. A strong delivery team for the asset developers will be critical to maintain timelines. | We would propose T-3 or T-4, but it depends on the amount of generation needed, the specific location, and the potential of existing sites to provide the service. Sufficient existing sites may not be available that can meet the location, sizing and technical requirements to create a competitive tender process. In terms of location, the site will have to be within a specific electrical distance of the transmission corridor (voltage and electrical distance). Projects that are further away will be affected by a reduction constant. In terms of technical requirements, they would need to meet at a minimum the single point of failure standard in the Security and Quality of Supply Standard (SQSS), along with having grid-forming capabilities. This could be explored first, and if there were enough sites, a T-1 option would be sufficient for wiring a connection. If there are not enough sites, the contracting period should account for building new assets, including the setup of communication and grid connection. For most new assets, this can be done in T-3 (maybe shorter if there is support for grid connections). It could be possible to have the contract start upon completion of testing if this is earlier than the back-stop contract date. | This needs to be refined, but we think around 4 years would be ideal. When determining contracting period, a trade-off needs to be made in terms of short contracts allowing NESO flexibility, and longer contracts allowing new investments. As there is a need for high quality protection to be added following the UK grid code with two independent systems and communication lines that may cost up to £100,000 as well as potentially a need for a bespoke or expensive battery to meet the no single point of failure standards, the contract will need to be longer than 1 year. We believe a contract length of 4+ years should incentivise new builds. This would also offer the NESO flexibility and enough time to align grid buildout timings and market reform. Longer tenure will reduce the overall costs for the end consumer and the benefits of increased ATC. Some degree of prequalification of parties will be needed as this will be a high-quality service. | Prices will be set through a competitive tender. The exact format of the pricing is flexible. One option would be to have a similar payment structure to that of the Constraint Management Pathfinders, which includes: a. Arming payment (per MWh per settlement period) – for when the service is armed. This needs to account for the need to charge up the batteries during this time. b. Utilisation fee – (per MWh usage) payment when the fault occurs for all units that had been armed and then generates, to compensate for the generation. To incentivise investment, some revenue certainty would be required. This could come in the form of a fixed minimum amount of arming payments based on historical values or future projections. In order to ensure revenue certainty in merchant markets as well, it would be worthwhile to include a maximum amount of arming, or constraints to certain times of the year/day. For example in Australia, it was agreed that the battery would only be armed in the summer months, and only utilised 18 times per year for up to 1 hour each. A price can then be set for a specific length of contract and minimum amount of arming. Additional hours can also be acquired at a set price. The winning bid will be decided via a combination of: • Fixed yearly price combined with set parameters for arming each year; • Additional arming /utilisation priced separately. | The lead time will vary depending on how long it takes the NESO to develop the contract, and if they decide to use new build or existing assets. Tendering and contracting could be done by end of 2024 if the decision is taken quickly. For existing assets, this could then be live by end of 2025 including building new communication and testing. If building new assets, it is expected that a solution could be available within 2-4 years of contracting, depending on grid connection and construction times. | Thank you for the opportunity to respond to this consultation. We would welcome the opportunity to have a conversation with the NESO to better understand how this solution or others could meet the NESO’s needs and be delivered in the shortest time frame for the least cost. Please contact Nicky (nicky.ferguson@ekuenergy.com) and Bo (Bo.Hesselbaeck@ekuenergy.com) for further information. About us: Eku Energy is a global battery storage business working across the full project life cycle to develop, build, and manage energy storage assets with the aim of advancing the energy transition and facilitating the delivery of safe, secure, reliable clean energy worldwide. The company has a 4.6GWh global project portfolio which aims to provide vital grid services in key markets around the world, including the UK, Australia, Italy, and Japan. Eku Energy is jointly owned by a Macquarie Asset Management managed fund and British Columbia Investment Management Corporation (BCI).
5 | Kona Energy Limited | Kona Energy | Consumers are paying more for their electricity than they should. Rising costs of thermal constraints from £1.3bn to £3bn particularly in Scotland with 4TWh of curtailment with the concomitant energy and reserve replacement costs and the management of frequency through balancing actions. New transmission infrastructure is costly and takes a long time to build (even in a post Electricity Commissioner’s report world). This solution is ready to deploy across the B6 boundary but is valid for other constrained zones now and in the future. | Using paired storage systems across key boundaries (B6 in this instance but not limited to this) can be used as a pre-or post-fault contingency or action. Acting in synchronism paired batteries charging and discharging across zones enables less wind curtailment reducing constraint costs and reducing costs to consumer. With scale and diversification multiple storage devices can act as virtual power flow system managing power balances across constrained zones. In the short term this offers significant reductions in constraint costs, deployable quickly and reduces the overall capacity for transmission reinforcements. | All of the above; virtual transmission line would result in increasing capacity (virtual transmission lines) ; | Analysis in 2016 demonstrated that a solution of this type could save £1.6bn over 20 years. This figure is demonstrated with hindsight (in 2016 the annualised cost of constraints in Scotland (B6) was £200m (£100m in constrained off payments alone), we predicted that would rise and there is a clear case for significant reduction in costs to consumers for significant volumes of low cost financed options using storage technology. The solution can operate as a pre-fault or post-fault solution and is particularly effective in pre-fault mode to manage heavily constrained zones such as Scotland currently. Reduces the need for balancing actions and exposure to BM prices for constraint resolution. Tendered or market solutions can drive down contracted price. Solution is symmetrical and therefore reduces the number of consequential balancing actions such as reserve replacement costs, energy replacement costs and frequency control measures (as a minimum this is equivalent to perfectly timed matched balanced bid and offer acceptances allowing reserve to continue to be held). | The physical solution would result in the arming of the solution as for inter-trips, but unlike inter-trips energy imbalance will be resolved and frequency maintained. This reduces the number of actions in the Control Room (CR) in both initiating and controlling the required subsequent actions (replacement energy and reserve and managing frequency) and alleviates the requirement for generator inter-trips which can result in physical damage, and this allows CRs to concentrate on system integrity and fault recovery. With scale and diversification significant pre-fault constraints can be reduced. | Stable, long-term requirements, attracts investors improving the business case for storage (especially in times when BM is inefficient/does not fairly value storage) whilst retaining the ability to provide other services to the system operator. (Frequency, voltage support etc). | Significant reduction in CCGT 'turn-on' balancing costs, south of B6 boundary and higher utilisation/less curtailment of renewable sources North of B6 boundary. Lower requirement for transmission build out. | This project includes the provision for the replacement of other control room and balancing actions (such as reserve and energy replacement), it simplifies the reserve allocation problem, directly provides frequency control for the operation of the service and the devices can provide other stability, reactive, frequency and black start provisions also. | Business Model for Constraint Management • Historically the business model for this has not been understood well and that needs clarifying • Resolving the contract form • Contract length Access to the Transmission System • Provision of connections • Implementation of the 5-point plan • Connection reform to facilitate storage use in this way rather than inhibiting it | At this stage in the penetration of storage there needs to be provision for long notice contracting, as for reactive and stability, this allows new entrants to finance and build. Quick build of storage due to modularity would favour T-2 to T-4 contracts. Connection reform would be critical to allow assets to connect more quickly. | Our preference would be for long contract terms, reducing the financing costs and cost to the end-consumer. Project WACC would also reduce through provision of a fixed contract. Just as transmission infrastructure is a long-term asset providing long term returns consideration needs to be given to creating sufficient liquidity to deliver value, or longer contracted periods. Shorter market and commodity solutions may theoretically increase liquidity and reduce costs, but that assumes a commodity solution which will have sufficient market liquidity. This is likely to be difficult due to timescales and limited points of connection etc. | Market tender | There are existing storage systems on the market, but Kona has a paired solution across B6 that could be delivered in two years if the connections can be resolved. Except for the current connection challenges and, the treatment of storage as part of that, this technology is ready to be deployed and with the appropriate procurement and market signals could create a regionally diverse scalable resource for constraint management and offset some asset investment. | In the past NGESO has been concerned that its assessment of the investment case for the use of storage as a solution for constraints is uneconomic (Storage for Constraint Management 2022). As an investor, we disagree and believe there is an investment case that developers can invest in. This solution reduces the cost to the consumer and allows reasonable returns on the investment. Permanent infrastructure is generally the costliest solution, and we welcome ESO’s approach in exploring alternatives to conventional infrastructure solutions. With sufficient scale and diversification storage can be a very cost-effective way of reducing constraint costs and easing the CR burden in managing faults. Additionally, it can offset transmission investment and if utilised as a system reduce the need for ever larger single storage solutions and provide the basis for seasonal levelling of the demand curve.
6 | Zenobe Energy | Organisation | Battery storage can alleviate the impact of wind gusts during thermal constraints, unlocking extra network capacity at constrained boundaries. | During thermal constraints in Scotland, ESO do not use maximum boundary transfer capabilities due to a need to keep reserve capacity, or headroom, on the network. If ESO did not keep this headroom, then a wind gust could suddenly increase power flows across transmission boundaries, pushing them beyond safe limits. A powerful gust of wind can create +100MW power spikes within minutes. This problem is present during all periods of constraint, but is more challenging during certain times of demand and wind volatility – for example, during late evening lulls in demand. From discussions with ESO control room operators, Zenobe believes there is a unique case for battery storage assets to be used as a ‘transfer booster’. The battery asset(s) would act like a shock absorber – importing power during wind gusts and exporting power during wind lulls, all during a continuous period of constraint. Battery storage, with rapid, bi-directional response times, is uniquely suited for this service. This service makes balancing the system significantly easier for ESO during constraints and allows ESO more optimally to use existing network capacity. Note, this service differs from what the post-fault intertrip scheme is protecting against, which ESO expect to only use in extreme 1-in-25-year event (e.g., fishing vessel dropping anchor and tearing the subsea Western Link). | Increase effective network capacity;Reduce overall costs to consumers; | £180m in balancing costs based on our estimates and provided to ESO already over 5 years from 2025 | Avoided curtailment and more response and inertia in high wind periods | Greater utilisation of asset capability | 890 ktCO2e over 5-years | Inertia response | Comms between key circuits – needs very fast network and flexible logic Interaction with other services needs planning - frequency | T-4 and T-1 | 1 to 10 years | Tender | Long if having to build new assets, short with existing | Already shared with ESO
7 | Zenobe | Organisation | Pre gate closure constraint management products using Sch 7 Trade Mechanism Absence of pre-gate closure Constraint Management Markets. The ESO’s primary tool for management of constraints is the Balancing Mechanism. The Balancing Mechanism runs from 0 – 90 mins ahead while participation in the Balancing Mechanism is mostly from Generation. The short timescales and limited asset classes participating in the BM means that flexibility from other asset classes and in timescales concordant with the expected constraint duration and lead times are unable to assist with the management of the constraint. We propose that the ESO uses existing forward trading tools to create a transparent constraint market, open to all energy market participants with flexibility in the relevant location. This would serve to increase participation and competition in constraint management. Our proposal is to initially make enhanced use of ‘Shedule 7’ forward trades at day-ahead timescales. Further constraint management products acting in longer timescales or enhanced optionality could then be build on top of this core product. | The existing Schedule 7 Trade mechanism allows the ESO to take actions ahead of gate closure. Schedule 7 trades are frequently used to manage interconnector flows. When the ESO wishes to reduce import (Sell) power over an interconnector it runs an auction for the relevant profile, accepting bids from parties able to fulfil the requirement (nominate interconnector flows). Winning bidders enter into a forward trade with the ESO, the trade price being conditional on the counterparty changing their nominated position on the relevant interconnector. We believe this mechanism could be extended to manage flows in constraints. The ESO would conduct an auction at the DAH stage when constraints are expected. Successful bidders would need to provide some assurance (via PN change for BM participants and/or metering vs baselines) that the trades had been delivered in order to access the clearing price. This would allow providers who have day-ahead (but not real-time) flexibility to enter the market for constraint management and allow BM and non-BM sources of flexibility to compete directly. Given the use and modest adaptation of existing contracts and settlement structures we believe this mechanism could be implemented quickly. Further, By taking both legs of the trade with Storage providers (e.g. Buying back the energy after the constraint has ended) the ESO could alleviate concerns about storage re-sell timing. By using a pay-as-cleared mechanism, the ESO could set an explicit price for the constraint against which it could design further contracts. For example, if the ESO wished to enter into a long-term constraint management agreement with a demand source, that contract could be settled with reference to the outturn tendered DAH ‘constraint’ price | Reduce overall costs to consumers;Reduce overall volume of ESO actions; | More competition with access granted to more providers. Able to access less flexible providers with more notice than BM. | Reduced need to BOA wind on short notice. | Able to access less flexible providers with more notice than BM. Improved confidence of utilisation given auction prices. | Likely to increase over and above BM as ability to secure from parties ahead of time. | None | Sch 7 sign up process, verifying physical delta of NBM providers. | Day ahead of further ahead | hours-days | Bilateral but could be more competitive | Da or further | Short term win as existing tools to utilise more assets during constraints
8 | Zenobe | Organisation | Intertrip scheme utilisation Underutilisation of boundary capacity due to limitations of current intertrip schemes. Intertrip schemes are a powerful tool for making better use of existing network capacity. By reducing export to zero near instantaneously following the trip of a boundary circuit, flows across the boundary are reduced by the quantity of generation tripped. This near instantaneous reduction in post fault flows avoids the need for pre-fault curtailment. In principle, the avoided curtailment is 1:1 with the quantity of generation armed on the intertrip, resulting in very significant avoided cost for capital spend orders of magnitude below additional transmission capacity. We suggest that the ESO explore the factors which limit use of intertrip schemes. Specifically, we believe that the use of intertrip schemes could be enhanced by: Procuring more Inertia, Response and Reserve in order to facilitate larger quantities of generation to be armed. Improving I/T design to expand the number of circuits an asset can be selected for. Allowing “short” duration storage to participate in future Constraint Management Pathfinder rounds. Applying the intertrip on all storage behind constraints but allowing ESO the choice to manage them. Changing trip-logic and auto-arming to enable scalable ‘repeat-cycling’ of storage assets behind constraints. | Increasing Quantity of Generation Armed The most cost-onerous constraints over the next decade relate to the North-South flow in periods of high wind. Since (asynchronous) wind generation does not naturally provide inertia, periods of high wind generation are also periods of reduced inertia. Reduced inertia means that for a given instantaneous loss of power infeed, the rate of change of frequency will be faster, the frequency nadir lower and the quantity and speed of response larger. Traditionally, increasing inertia has meant synchronising additional synchronous machines (usually CCGT units). This places additional generation onto the system which in turn creates the dis-benefit of reducing negative reserve availability. Zenobe are participating in Inertia pathfinder projects to deliver the benefits of Grid-Forming Inverter technology. We believe Grid-Forming Inverters will enable the ESO to procure significant quantities of inertia without the expensive dis-benefit of buying energy required to synchronize machines and find additional downward reserve flexibility. By raising Inertia levels over-night in this way, the ESO would be able to tolerate a larger instantaneous loss – thus allowing more generation to be selected to the intertrip. We also note that the saturation of frequency response markets: There are already sufficient fast flexible assets available to increase the level of response held to arrest a larger instantaneous loss. We believe that by making intelligent use of BESS with GFI to provide inertia and/or additional response and reserve, the ESO could accommodate significantly more generation armed to the intertrip in the periods of highest wind. Improving Intertrip Design To be effective, generation must be tripped very rapidly (~100ms) following the trip of a boundary circuit. This requires fast communication between switchgear. We believe there is scope to expand the intertrip scheme logic to accommodate more circuits on other important transmission boundaries. By designing a more extensive network of selectable circuits and generation sources, the ESO could use intertrips to increase flows across more boundaries. (E.g. a generator in the north of Scotland may be effective in increasing flows on several boundaries if selected to trip for key circuits on B2 through B7). Improving use of Short Duration storage on Intertrips Without Intertrip, short duration storage is able to transport a single cycle out of the the constraint by importing (hence offsetting the need for curtailment) during the constraint and exporting once the constraint is alleviated. When a storage asset is placed on an intertrip while exporting, the exports do not add to curtailment. Once the export is complete, the battery is empty again allowing for further imports. In effect, by using the intertrip the battery is able to cycle energy out of the constraint repeatedly, instead of once. Enabling repeat-cycling in this way enhances the impact of shorter duration storage on constraints, allowing the storage to cycle more energy out of the constraint. In practice, this means the ESO must make many selections and deselections to the intertrip. To enable repeat-cycling to scale to many storage assets, we recommend changing trip logic to only fire when exporting (and not when importing). The intertrip can then be left armed for the duration of the constraint instead of being armed/disarmed for each period of import. The benefits of repeat cycling of BESS with intertrips should be considered in future CMP tender rounds, removing unnecessary duration requirements. ESO can procure more MWs than needed in order to hold reserve MWs to utilize during constraints in case assets are contracted for other services during the same period. | Increase effective network capacity;Reduce overall volume of ESO actions; | Significant avoided curtailment | Avoided curtailment and more response and inertia in high wind periods | Greater utilisation of asset capability | Significant avoided thermal generation | Inertial response | Comms between key circuits – needs very fast network and flexible logic. Cost of intertrip services. | T-1 or T-4 | 1- 10 years | Tendering/auction | Depends on assets | Mandatory intertrip on all storage in Scotland to enable ability to export without restriction, but protection to ESO for managing the constraint boundaries
9 | Zenobe | Active Network Management / Generation Export Management optimisation/trading | There are already a number of Active Network Management (ANM) zones and Generation Export Management (GEMS) that could be utilised to allow either ESO/DSO or bilateral arrangements between parties to help manage flows. A storage asset is able to import power from renewable generators in that ANM/GEMS that could other have to flow over the boundary and potentially exceed the constraint that may be over a wider area. | A storage asset or demand is able to import power from renewable generators in that zone that could other have to flow over the boundary and potentially exceed the constraint. ANMs currently limit the ability of assets to export, but don’t allow for management of flows by different assets within the ANM to reduce actions by the ESO and manage locally – demand, storage, renewables. The are multiple ways to arrange this, either: ESO/DSO monitoring ANMs/GEMS when they are expected to exceed the constraint and utilise the storage to import and allow the renewables to continue to export, assessing this across ANMs/GEMS and wider constraints Parties to transact ahead of time bilaterally to manage behaviour on behalf of the system operator – Sharing forecasts ahead of time in the ANM would allow people to traded ahead of time and avoid actions by the operators also | Increase effective network capacity;Reduce overall volume of ESO actions; | Extra flows over the boundary More competition Utilising existing ANMs/GEMs that already manage constraints | Avoided actions if bilateral, potentially lower cost and more options | More options in constrained areas | To be confirmed – lack of transparency to inform number | Inertial response from storage | Interaction between ANMS and GEMS, with wider constraints Interaction with ESO and DSO system tool External party tools such as Piclo could be used to create market | day ahead and within day | half hourly to day | bilaterally ort submission to DSO/ESO | Short | Could be like a BM in an ANM or ideally through third party tools
10 | Damian Jackman | Field | The existing B6 CMIS intertrip service is already the least cost action of reducing constraint costs. Therefore this proposal simply aims to increase the volume of the current intertrip service by increasing the GB system largest infeed limit (which is the limiting factor of this service). We propose that the ESO explores the possibiltiy of gradually increasing the Largest Infeed Limit up to 2GW (or a value they believe will maximise the value of the CMIS vs the cost of the higher infeed limit) | The Constraint Management Pathfinder appears to have increased the pre-fault B6 boundary capacity by around 1GW and is saving several hundred million / year in combined bid and offer costs (we believe the ESO is significantly understating the savings for reasons which are not clear) The challenge to increasing the volume of the constraint management service further is the size of the Largest Infeed Loss (LIL); currently 1400 MW and expected to increase to 1800 MW once Hinckley Point C is operational. In turn, the challenge to increasing the LIL is cost - but our analysis is that this will be significantly lower than it has historically been, and that there are wider system benefits from a higher LIL (which may in themselves justify the cost, irrespective of reduced constraint costs). | Reduce overall volume of ESO actions;Reduce overall costs to consumers; | The imediate benefit of increasing the LIL is that it increases the size of the intertrip capacity and thus limits curtailment of generators and wasted renewable energy. For example the cost of the B6 intertrip service arming fees for 1700 MW reduced significantly in 2024 and is now no more than £5.8m / year. Our analysis is that the existing intertrip service is saving ~£600m/year and that that could be increased to >£700m if the LIL is increases (after factoring in the costs of increasing inertia, response and reserve). | Less wind curtailment and associated energy balancing actions. Increased system resilience Our analysis is that the exisitng intertrip service is saving about 3.2TWh/year of renewable energy per year from being wasted (68% reduction compared to no intertrip). The savings increase to 4.1TWh/year (85%) with by increasing the LIL. | Allows wind to continue to be constructed in regions with the best resources thereby producing the lowest energy costs whilst deferring the cost of new network build | Increases the use of zero carbon energy sources and reduces the use of gas generation (both self-dispatch and for balancing actions) Our analysis is that the exisitng intertrip service is saving about 1.1MtCO2/year of renewable energy per year from being wasted (67% reduction compared to no intertrip). The savings increase to 1.4TWh (85% saving) by increasing the LIL. | Increasing the Largest Infeed Limit would also have much wider system benefits that reduce cost to the consumer and increase system security: - Greater system resilience for multiple generator / HVDC system faults such as those on 9th August 2019 and 22nd December 2023. - Larger maximum generator sizes; offshore windfarms are currently limited in size by the maximum connection capacity so increasing the largest infeed limit would allow larger grid connections with minimal increase in grid costs and so reduce the LCOE of the windfarm; this benefit would be seen through lower CfD auction prices which would pay back to the consumer whenver the system price rises above the strike price - Simpler offshore network design; the ESO's Holistic Network Design foresees an integrated offshore HVDC system and Multi-Purpose Interconnectors. Having a larger infeed limit allows a simpler design with less complex DC protection | Increasing the LIL requires increasing holding of: - Inertia (to maintain RoCoF within limits post-fault) - Response (to maintain frequency within limits post-fault) - Reserve (to restore frequency to within limits post-fault) Historically increasing the size of the LIL has been a significant cost however this is changing: - Inertia will be increasingly procurred in Y-1 and Day-ahead markets from 2025 onwards. The Stability Pathfinders 2 and 3 for 10 year contracts showed that inertia (with no unwanted MW) could be procured as low as £0.08 / MWs / SP equivalent to £160 / GWs / Hour. We suggest that to minimise costs and given the large amount of inertia that would need to be added (> 50 GWs) the ESO considerers further national interia auctions for multi-year periods (similar to Stability Pathfinder 1 but to include grid-forming providers) to bring about the lowest possible prices - Response prices since early 2023 have trended consistently as low as £1 / MW / Hr implying that there is very little cost to increasing response holding (provided it occurs in line with battery capacity growth) - Reserve costs are also likely to decline as more generation sits idle whilst wind is generating and as more batteries are constructed and with the creation of new, more open and transperent Quick and Slow reserve markets Also, the existing intertrip communications system would need to extend to include more windfarms in Scotland but given the cost savings of this service this should not be a barrier to implementation. | We suggest procurement of the intertrip service remains annual to allow time to install the required comms links with publication of armed systems published in advance of all day-ahead markets. With inertia, response and reserve all moving to DA markets, increasing the LIL could be achieved on a DA basis. If a higher, minimum (rather than maximum) LIL is chosen then procurring for the longer term (i.e six or 10 year contracts) could achieve a lower cost per unit of inertia | Annual for intertrip; varying timescales for inertia, response and reserve. | Continue as normal using DA markets, except increase volumes to match the chosen LIL | Subject to detailed stability analysis by the ESO of increasing the LIL | Analysis needs to be done on the post-fault stability of the B6 (and other?) boundaries. This is something we recommend NESO lead, possibly support by academics from e.g. Cardiff University.
11 | Chris Wickins | Field | This proposal defers or avoids costs associated with building network infrastructure by allowing a higher pre-fault power flow over the main AC circuits across the most constrained boundaries. It is an evolution of the intertrip system but does not require additional inertia / response or reserve to be held. | Virtual transmission schemes using storage have been examined by many TSOs. For example the 'Grid-booster' concept in Germany uses pre-armed batteries to simultanously decrease and increase output (in the event of a fault) at the sending and receiving ends of a line respectively. This service enables the ESO to increase the pre-fault power flow up to the maximum limit of the line (either thermal or stability depending on the location) without also having to increase the Largest Infeed Loss limit and the associated increase in cost that would bring through higher inertia and response holding. In effect, most of the extra costs that would have occurred for increasing the Largest Infeed Limit (LIL) and increasing the size of the intertrip service (see other proposal) and redispatch following a fault are wrapped into the service costs - which in turn, are based on the providers' costs. We would expect the lowest cost providers at the sending end to be more wind generators who take a contract (like for the CMIS service) and at the receiving end we expect only batteries in unconstrained zones would have the fast MW ramping capability required to inject power within the timescales to retain stability This service relies upon very fast and simultanous response (within 140ms). This speed is proven for generator intertripping but has yet to be proven in the UK for batteries. We note in Ireland that batteries have demonstrated ramp times to full output within 140ms and discussions with suppliers have indicated 100ms is achieveable. A significant attraction is that many transmission connected batteries in England are already in construction and this service could be in operation many years before the first HVDC bootstaps become operational thereby buying additional time / insurance in case of late delivery of the bootstrap links. Our analysis is that the cost of this service will be cheaper than the HVDC bootstraps in any case and therefore that it should be prioritised first and on a 'least-regret' basis. | Reduce overall costs to consumers;Increase effective network capacity; | The 'grid-booster' concept increases the pre-fault capacity of the line and limits curtailment of generators and wasted renewable energy. Our analysis is that the existing intertrip service is saving ~£600m/year and that that could be increased to ~£800m (87%) if 3.6GW of grid booster service was procured (in addition to the existing intertrip) after factoring in the costs of the additional wind farms with intertrips and the batteries providing the symmetric turn-up service. | Less wind curtailment and balancing action Our analysis is that the exisitng intertrip service is saving about 3.2TWh/year of renewable energy per year from being wasted (68% reduction compared to no intertrip). The savings increase to 4.8TWh/year (98%) using grid boosters | Allows wind to continue to be constructed in regions with the best resources thereby producing the lowest energy costs whilst deferring the cost of new network build | Increases the use of zero carbon energy sources and reduces the use of gas generation (both self-dispatch and for balancing actions) Our analysis is that the exisitng intertrip service is saving about 1.1MtCO2/year of renewable energy per year from being wasted (67% reduction compared to no intertrip). The savings increase to 1.7TWh (98% saving) by using a grid-booster service | Potentially defers cost of a single 2GW HVDC link depending on how much volume the ESO is willing to procure. CAPEX cost of such links is around £2bn. But the principle advantage is that this service could be deployed quickly (3 years?) and so buys time for such links to be built by allowing more wind to connect whilst minimising constraint costs. The attraction of this service is that in theory there is no impact on the system from its operation; only additional reserve costs are required to allow the ESO to respond within the timescale this service allows. Extending the timescale for the ESO to respond in the event of it activing (e.g. to 20min) would be a trade off between higher pre-fault power flows with lower constraint costs vs higher service costs and higher reserve costs. If batteries on the receiving end were of sufficient duration, it could be the case that no additional reserve is required since a 2-hour battery is sufficient time to start a CCGT from cold. | The existing intertrip communications system would need to extend to include more windfarms in Scotland but given the cost savings of this service this should not be a barrier to implementation. A new intertrip communications system for activing batteries armed to ramp quickly would need to be created to batteries in England. To minimise service costs from batteries in England, the service would need to be stackable with other services (e.g Capacity Market, inertia, reactive power, wholesale services when not armed). It's critical for the batteries that they are only armed when needed rather than being left armed (as we believe windfarms currently are). The cost of batteries providing the service would increase with the duration of time the service is required; for example, if the service is only required 10% of the year (during periods of highest wind) it is likely this has no opportunity costs to a battery and therefore a battery would take whatever price it could get. However if the service period increases above 20%, a battery would start to account in its price for the lost opportunity cost of other markets. Therefore to obtain the lowest cost it is vital that this service is as "stackable" with as many other revenue streams as possible. We expect batteries would be happy to provide this service for £10/MW/hour. The greatest challenge is likely to be in gaining confidence that the batteries will respond quickly enough - given that failure to respond will cause a drop in system frequency - but this can be done through monitoring, small scale pilot projects using existing batteries and scaling up as confidence is gained, just as occurred for the Enhanced Frequency Response as a precursor to the Dynamic Containment service. (Indeed deliberate trips to measure performance using small scale volume of a grid-booster service could be performed within the current largest infeed limit) | Expected to be on a Y-1 or DA basis. Initial procurement could be longer-term Y-4 contracts until there is sufficient liquidity in the market (from batteries able to provide the service). | Ultimately 1 year or DA. Initial longer-term contracts may be required until there is sufficient liquidity. | Tendered (like CMIS) | We believe this a trial service could be operational within 12 months with a full scale service within 2 years; the limiting step is likely the intetrip communications network which is within the limit of NGET | Analysis needs to be done on the post-fault stability of the B6 (and other?) boundaries. This is something we recommend NESO lead, possibly support by academics from e.g. Cardiff University. This concept is not new - it is being tendered in Australia and Germany. See: 1. TenneT Grid Booster: https://tennet-drupal.s3.eu-central-1.amazonaws.com/default/2022-09/TenneT_Factsheet_Netzbooster_Ottenhofen.pdf; Note the proposal is for the TSO to own and operate the asset, so that during times the asset is not needed it cannot participate in wholesale markets 2. Systems Integrity Protection Scheme (SIPS) contract with the Victoria 'Big Battery' for 250 MW 3. Virtual transmission lines: https://blog.fluenceenergy.com/australia-energy-storage-solutions-transmission-asset 4. Virtual Transmission Lines Overview: https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Jul/IRENA_Virtual_power_lines_2020.pdf?la=en&hash=C58043124D596D1CF75395066817C38B55AC1983
12 | Statkraft | Organisation | Currently thermal constraints across the B6 and beyond are resolved by curtailing renewable generators resulting in costly actions as the marginal cost to run is very low and ROC certificates need to be compensated for. The existing mechanism to alleviate constraints (the balancing mechanism), is a high value but low certainty for demand. The balancing mechanism is designed to dispatch existing generation and demand, it has high prices (large negative bids) but low levels of certainty. To be capture BM revenues, demand would also need to not run, in anticipation of being instructed, which is likely to be inefficient for both the ESO and the demand project. The low certainty in dispatch results in revenues associated with the BM not being bankable for FiD decisions. This proposal provides a simple signal to stimulate flexible demand, at scale to locate in areas which will reduce thermal constraint volumes and costs to the ESO (and therefore consumer) and make use of renewable electricity that would otherwise be wasted. This will not only greatly reduce the costs of thermal constraints, but also of decarbonising other demand side applications. | A demand signal product is proposed to incentivize new build, long-duration demand to locate behind specific borders, reducing costs and wasted renewable energy. The Electricity System Operator (ESO) would sell power at a discount for fixed hours per year, choosing the timing. Demand would be located where it saves on balancing thermal constraints. The payment mechanism could be a fixed power sale or availability payments. For large-scale investments like hydrogen, a fixed power sale provides certainty and de-risks projects. Shifting demand north reduces constraint costs. Availability payments offer a fixed discount on wholesale prices but may force providers into loss-making situations. Utilization payments could work with guaranteed periods but pose similar risks. Different capacity factors may require separate allocation pots or a formula for clearing prices to ensure fairness and efficiency. | Reduce overall volume of ESO actions;Other: May help generators to accept REMA, as the increased demand will reduce the volatility and negative pricing in zones with lots of generation but little demand. It will also help to reverse some of the increases in TNUoS charges. ; | This product would significantly lower the cost of alleviating constraints costs to the ESO and therefore reducing balancing costs. The value of the savings depends on whether the product has shifted demand that would otherwise have been located south of the constraint, or whether the demand is additional demand on the system that would not change how much demand is located in the south. Hydrogen has a 5GWth (7GWe) electrolytic target of FiD by 2030. The current balancing mechanism does not incentivise hydrogen production behind constraints as it would require an electrolyser to not produce, and hope that it is instructed. This results in allocation uncertainty and a very low capacity factor, making such a project uncompetitive and un-investable. Similarly there is so much uncertainty regarding REMA and the outcome of potential locational marginal pricing and implementation dates, it is not a credible investment signal for projects contributing to the 2030 target. As a result, in the absence of a locational demand signal in the short to medium term, the 7GWe brought forward will be near industrial demand in the south. This product would effectively shift hydrogen production from the south to Scotland, therefore the following value impacts can be considered (indicative figures only): Cost of constraint without product: Market price: -£70/MWh (compensation to generator) Constraint bid: -£65/MWh (paid to wind generator to compensate for ROCs) Offer price: -£80/MWh (paid to generator south of constraint to turn up) Total cost -£215/MWh If this product shifts hydrogen production (or other demand) north of constraint: Market price -£70/MWh (ESO needs to purchase power) Constraint bid £0/MWh (No generator to pay bid to) Offer price £0/MWh (turn up is not necessary) Revenue from product £10/MWh (example fix power price paid) Total constraint cost -£60/MWh Total saving to ESO from product is £155/MWh. Note for hydrogen, lower power prices, and partial price fixes will result in lower hydrogen strike prices in the hydrogen CfD allocations, and therefore lower cost to consumer, so there are additional savings on top of that outlined above. This product is a huge opportunity to save consumers money and incentivise the correct location of hydrogen generation to reap the benefits of sector coupling. If this product encourages new, additional demand north of constraint: Here additional demand is created in the north, but this doesn’t result in less demand in the south, an example might be electrifying a district heating scheme. Cost of new constraint with new product: Market price -£70/MWh (ESO needs to purchase power) Constraint bid £0/MWh (No generator to pay bid to) Offer price -£80/MWh (turn up is still necessary to meet demand in south) Revenue from product £10/MWh (example fix power price paid) Total cost of constraint: -£140/MWh Total saving to the ESO from product: £75/MWh ROCs Under the shifting of demand calculation, one additional ROC is generated, however, if a ROC is curtailed under an existing constraint mitigation, this isn’t money saved by the consumer, as suppliers will still need to meet their obligations, and will therefore have to pay into the buy out fund instead of presenting the lost ROC. The ROC cost to consumers is the same. Similarly, if additional demand is created, when the ROC target is set this will increase overall demand, and therefore when ROC targets are set, the obligation per MWh is reduced (and to the extent that the new demand pays ROCs, the overall obligation to all other demand users decreases. If the new demand does not pay ROCs by virtue of the EII, then the overall obligation to demand users is unchanged). Additional demand is not as beneficial as shifting demand, however there is still a significant benefit, and in either instance, the otherwise wasted renewable power is put to good use decarbonising other sectors. | Reduced constraint costs and constraint volumes over the contract period and on an enduring basis after the initial contract term has finished. | The service provider gets access to lower power prices and ‘additional’ renewable energy that is compliant under RTFO or HPBM, and is able to fix a proportion of their power. This will improve the ability to reach FiD for projects looking to provide green hydrogen, green hydrogen derivatives, or heat applications. | The product will unlock significant volumes of low carbon power for use in decarbonising other sectors (industry, hydrogen production, hydrogen derivative production, heat etc) that would otherwise have been wasted by traditional constraint management approaches. | It is expected that it could provide additional flex demand providers could bid into other frequency and reserve products when not instructed by this product or after the initial contract period. Similarly it is expected that it will bring forward providers that will be able to abate emissions in difficult to decarbonise sectors such as heat, industry, or transport. | Not all projects will have the same level of maturity. If very stringent deliverability requirements are set, it will reduce the pool of potential projects that can apply, but equally if there are no deliverability checks, speculative bids and projects may mean auctions are allocated to projects that fail to materialise, at the expense of real projects that could have delivered. We suggest some form of deliverability assessment should be made in particular for larger hydrogen projects, this could include evidence of a grid connection or engagement with land to reduce unrealistic speculative bids. However for smaller less flexible lower capacity projects, this may discourage applications, and so could potentially be waived. One of the failings of the BM is that for demand to participate, it must not offtake, and instead hope that it is dispatched. This provides the wrong signals (and could actually increase constraints, as demand is held back in anticipation). It is important that dispatch is sufficiently in advance that energy can be procured if necessary, after dispatch, if the product hasn’t been instructed. The options for this would be: • Same day - if dispatch same day, it should be sufficiently in advance of gate closure so power can be procured in the spot market. This could be challenging and would increase projects power trading costs. • Day Ahead – If dispatch were sufficiently in advance of the day ahead auction, power could be procured on the day ahead market if not dispatched. • Week ahead – Greater notice would allow more flexible trading and the lowest power procurement costs to projects, meaning on average more competitive bidding into the product. We understand this is a trade-off, as the product will be more valuable to the ESO the closer it is to real time dispatch. However, we would expect that at least day ahead should be sufficient notice to predict most constraints with a high degree of accuracy – and therefore is likely the best option. | This product is envisioned to bring forward or shift large new demand side projects. As a result some flexibility in delivery years is likely to be necessary, we would expect that T-4 with some flexibility in start year would be appropriate (i.e. tendered in 2024, for start years of 2028, 2029 or 2030). As these are new potentially large scale projects, the contract should allow for a flex in delivery start date once awarded. | The main driver to enable investment in new demand is price and allocation certainty. The longer the duration, the stronger the signal to the additional demand to locate behind the B6 boundary. Large scale hydrogen and derivative projects will typically be bidding into the HPBM, with 15 year contracts – 15 years would be the optimal duration for these projects. However, 10 years would still represent a significant benefit, shorter durations (for example 5 years) would still improve economics, but the value placed on such a project would be much smaller, and therefore it would provide a reduced incentive to locate demand behind constraints. | Pay as clear has been very effective mechanism for reducing costs in renewable CfD allocations. We think a similar approach would remove gaming, and encourage projects to bid in their genuinely most competitive price into any allocation auction. If separate pots are used for different capacity factors, these would have different clearing prices. | To be advised by ESO, but a 2024 auction would allow for example hydrogen projects in HAR 2 certainty to bid lower before BAFOs by end of the year. If the processes from power CfD were followed, this could reduce implementation times. | Price range: We understand that there could be some reluctance to allow negative price bids, as part of the price paid to wind farms is to compensate for a lost ROC, and there is a belief that because a ROC is not generated, the consumer would then not pay for it. We do not believe this logic is correct, as it is not how the ROC market works. A ROC target is set annually, if one less ROC is produced due to a wind farm being constrained the supplier obligation targets stay the same, but a supplier will have to pay into the buy-out fund the value of a ROC (in lieu of a certificate). This means when a ROC wind farm is constrained the consumer both pays for the ROC via the balancing charges, and via the supplier having to contribute to the buyout fund. Even if an auction for this demand product cleared at a negative value, (e.g. -£10/MWh for power) the ESO would still make significant savings. Modelling considerations: Most capex investments in hydrogen or derivative products will be for 25 years+, therefore in any term less than this is used, additional demand will be present after the initial product duration. This demand will still help constraints on an enduring basis, and this should be captured in any cost/benefit analysis. BSUoS – As this product is being developed to reduce system balancing costs, it does not make sense for demand instructed under this product to pay BSUoS. If additional demand does pay BSUoS, it will reduce the costs to consumers (as the charging base will have increased). If it is procedurally too challenging for BSUoS not to be charged under this project, there are two options that could be taken: a) The clearing price for purchasing energy could be defined as £X/MWh less the prevailing BSUoS rate. This should be simpler to administer and within the ESO’s power to decide, and probably a preferable option than trying to instigate wider industry changes. Alternatively, it could be done alongside, i.e. this mechanism persists until industry change is enacted. b) The ESO’s modelling takes into account the added BSUoS into the charging pot in the cost/benefit analysis. TNUoS Demand locational signal: The TNUoS model floors the demand locational signal at zero, even though it would otherwise be significantly negatively, this is not cost reflective. To ensure demand is incentivised to correctly locate, we suggest the flooring mechanism is removed. Final Consumption Levies The impact on final consumption levies will depend on whether demand is additional and whether the demand is required to pay final consumption levies. These levies include FiT, CfD, CM and RO. Other smaller considerations include elexon charges and AAHEDC. If demand is shifted, there is no change to FiT/CfD/CM/RO/Elexon charges. The demand would have paid the same in the south as the it will in the north, irrespective of if that demand is EII or not, the same amount of money is contributed to the relevant subsidy funding. Similarly, if the demand is additional, but EII eligible, it will not change the overall funding into FiT/CfD/CM or RO, but will pay into Elexon charges. However, if demand is additional and not EII eligible, it will be paying significant amounts (circa £50+/MWh) into final consumption levies, the CM and elexon charges. This will reduce the amount that other demand users will pay.
13 | Alastair Martin | Responding as Flexitricity Ltd | THE BIG FRIENDLY BATTERY Thermal constraints on B6 are often active for several hours, restricting the usefulness of short-duration batteries in alleivating it. This proposal uses co-operation to create an effective long-duration battery using existing and soon-to-be-commissioned capacity north of B6. | Existing and near-completion batteries in Scotland amount to at least 800MWh of storage capacity, with a further 4,800MWh to be added within the next two years. These batteries are generally sized for 1.5-2 hours of delivery at maximum power. However, by working together and consuming at lower power, these batteries could provide over 700MW of constraint alleviation for at least eight hours. They could simultaneously provide ESO's entire requirement dynamic high response, using revenue-stacking to reduce the cost of the constraint management service and imposing no additional burdens on the constraint. They would further be available in the BM for offers, allowing ENCC to manage their state of charge during less constrained settlement periods and "save" volume for later. No new hardware or build is required; this proposal would be delivered entirely through contracts. | Reduce overall costs to consumers;Reduce overall volume of ESO actions; | Delivering this service at 700MW for an eight-hour period of constraint on B6 would save the consumer approximately £450,000 on each event. Because the service is stackable with activities that do not themselves exacerbate the constraint, contracting costs for each such event are contained, and are likely to be of the order of £50,000 per event. This service would be a baseline approach to constraints, taken before wind turndown, hence it is likely to be used on many days each year. The net benefit could be around £40m on an annual basis (used on 100 days/year), passes to consumer through BSUoS. It may be possible to reduce gas burn on the other side of the B6 constraint by constructing an equal-and-opposite service using batteries located in England and Wales. This could substantially increase the net benefit. | Reduced curtailment, a highly responsive constraint-management resource, a means of attracting batteries out of NIV-chasing and into the BM where they are visible and controllable. | Immediate revenue for making best use of available renewable energy which can be simultaneously stacked with certain other services, providing revenue resilience and supporting investability for future projects in Scotland. | 5,600MWh of zero-carbon energy is stored per event, for later consumption, thus reducing fossil burn. If used for 100 days/year this amounts to 560GWh of additional renewable energy in the GB system. If an equal-and-opposite service were deployed, the carbon benefit would increase as less thermal replacement energy in England and Wales would be requuired. | Dynamic high response is stackable with this service. | The challenge is purely contractual and entirely tractable. It is possible that multiple battery operators could work together to provide an effective long-duration "big friendly battery", but it may be easier for ESO to construct a service and purchase centrally. Providers would effectively be agreeing to have a low state of charge at a particular time of day, and to commence charging at 15-20% of full power on instruction from ENCC. | This service could be procured day-ahead; this would be ample time for operators to choose how they would achieve the necessary state of charge at the beginning of the service period. | A specific sequence of settlement periods of around eight hours duration. | Prices could be set using the EAC, allowing providers to arbitrage different opportunities as conditions dictate. Alternatively (for a limited period while auction access was set up) a benchmark price could be drawn from a combination of DCMR and day-ahead EPEX prices. | This project is purely contractual, hence the timescales are driven by administrative tasks. No hardware build is required. | None
14 | SSE Energy Businesses | Organisation | Improving Transparency of Interconnector Redispatch What is being proposed? We propose several measures to improve the transparency and arrangements for interconnector dispatch and redispatch. In the first instance, we propose that the ESO publishes more detailed information on the reasons for making schedule 8 interconnector counter trades and where the price paid is high for reversing explicitly traded interconnector flows the justification for this price. As short-term constraint management products are developed, such as short-term constraint management contracts (see our proposal ‘Competitively allocated short-term constraint management contracts – up to 7 days ahead of time’), explicitly traded interconnectors should be integrated into these products. In his recent report (here) for Scottish Renewables, Simon Gill notes that this would only require formalising existing NGESO countertrading arrangements and could take place for existing interconnectors to France, Netherlands, and Belgium. In the long-term, the ESO should conduct a review, alongside industry, of interconnector trading and balancing arrangements to identify options for incentivising optimal interconnector dispatch as an alternative to locational pricing. The problem it is addressing: There are times when interconnector flows can exacerbate over-supply or under-supply of electricity by flowing in the opposite direction to the system or local need. The ESO’s Markets Roadmap (March 2023) states that in 2022, the cost of interconnector trades to address thermal constraints reached a historic annual high of £193m. This figure was considerably higher than the two previous years, and the ESO expect this cost to rise in future. In his report, Simon Gill highlights that the ESO’s interconnector trading and management does not operate within a formal, transparent, and well-structured framework leading to difficulties in understanding the ESO’s decision-making. Reversing interconnector flows via a Power Exchange Linked Interconnector (PELI) trade by the ESO with a party that holds capacity on that interconnector involves a bilateral trade that is not open to competition. The alternative is waiting until gate closure and addressing the constraint through domestic actions in the BM, which can increase the cost of balancing actions. Whilst ESO publishes information on interconnector countertrades and high-level reasons for these trades which is helpful, this does not currently provide sufficient information to understand why a trade was entered into and if the price is high, why it was the lowest cost option. Given that ESO is concerned about the scale of cost that interconnectors currently impose on the system and is advocating for locational pricing as a mechanism for resolving this issue (alongside others), it is particularly important that the cause of any costs incurred are transparent and the reasons why lower prices could not have been achieved are clear. For example, it should be clear where the cost was incurred due to an unexpected change to the system such as a sudden outage, or if it was something that could have been foreseen and planned for. As a first step, greater transparency in the decisions to enter Schedule 8 trades is both good practice and allows for accountability. Following this, ensuring issues are identified and addressed as early as possible and opening the provision of the solution to competition should lead to lower cost outcomes. However, this does not resolve the underlying problem that is causing interconnectors to seek to flow in the wrong direction. This would be the purpose of a review to identify how this issue can be addressed via a change to market arrangements for interconnectors without significant consequences for the domestic market (as would be the case if locational marginal pricing were the solution). | By providing a clearer view of the extent of the problem of interconnector redispatch it will help inform discussions on how to address costs incurred by interconnector redispatch. Incorporating explicitly traded interconnectors into competitive constraints management contracts should reduce redispatch costs of interconnectors in the shorter term. Improving dispatch price signals to reduce the need for interconnector redispatch in the longer term. | Reduce overall costs to consumers;Reduce overall volume of ESO actions; | Improved operational dispatch (and redispatch) of interconnectors, reducing the price of constraint management actions leading to lower BSUoS costs. | Reduced need for interconnector redispatch and earlier planning reducing the number of post gate closure actions. | Domestic generation and demand are on a more even playing field with imported generation. | Difficult to assess. | Requires further assessment. | Interconnectors are more complicated because they connect two markets, require trading between parties based in both jurisdictions, and are dependent on the regulations and terms of any trade agreement between the jurisdictions. In addition, not all interconnectors are traded in the same way i.e., explicitly traded or implicitly traded. It may not be possible to apply this approach to implicitly traded interconnectors and so redispatch is not possible. Some interconnectors are built with the support of the interconnector cap and floor arrangements supported by GB consumers and so these interconnectors would be expected to provide a positive contribution to the GB electricity system. Consideration of all these issues is required in determining the most appropriate approach for interconnectors and this is the reason why for the longer term we propose a review of interconnector arrangements rather than arriving at a solution at this stage. | For short term constraints management please refer to our proposal 'Competitively Allocated Short-term Constraint Management Contracts'. | See answer to Q12. | See answer to Q12. | Providing greater transparency on existing interconnector trades should be implementable within 6 months. A longer-term review of interconnector arrangements would likely take 1-2 years. | N/A.
15 | Alastair Martin | Responding as Flexitricity Ltd | The Regulatory Repair Shop Customer load capacity with the immediate capability to alleviate constraints and put green energy to work is held back by regulatory and service design issues, particularly around imbalance payments and volume allocation. Fixing these issues will set the Local Constraints Market up for success in the short term, and the BM and P415 in the medium term. | The LCM, the BM and (after November) the wholesale markets all admit customer load capacity and allow it to respond to negative prices on an elective basis. In all cases, the incorrect allocation of imbalance between suppliers and aggregators penalises the majority of customers who wish to participate. By correcting imbalance volumes in the LCM (which can be done quickly through a known C16 intervention) and correcting supplier/aggregator compensation in the BSC (through a code review), proper "buy" signals will be available to all customers, and their capacity will come to market. Eligible capacity includes a disproportionate population of domestic heat pumps (many Scottish homes are off the gas grid), ground-source heat pumps used in agriculture for crop drying and storage, large-scale heat pumps and cold storage sites, and a fast-growing population of domestic and commercial electric vehicles. Responsive customers will shift their demand to periods of low or negative prices, putting green energy to work and reducing consumption at other, less constrained periods. | Reduce overall volume of ESO actions;Reduce overall costs to consumers; | Cost savings in energy consumption of around £70-£80/MWh across all market opportunities, and a greater proportion of their usage being drawn from demonstrably green sources. | Better pre-gate balancing of wind generation north of B6, greater liquidity in the BM bid stack to help alleviate B6 constraints in real time resulting in price competition and a lower cost outcome, and a Local Constraints Market that delivers material megawatts at day-ahead stage. | Service provider receives a proportion of the value saved by the consumer in purchasing renewable energy that would otherwise be discarded. | Direct benefit: each MWh of true customer load brought forward during wind constraint periods through prompt wholesale market trades, the BM and the LCM reduces carbon emissions in accordance with the fossil content of electricity at the time. Indirect benefit: increased liquidity and utilisation in these markets adds to the investment case for future flexible capacity at customer sites, such as heat and "coolth" stores. | Once incentivised to enter the market, customer load capacity can participate in other markets while constraints are not active. This increased liquidity helps to keep costs down across the year. For example, it should be expected that customers bidding to consume green energy during a constraint would also be able to offer to reduce consumption during peaks. | The LCM interim fix is known and only requires sign-off from Ofgem and implemention by ESO. A permanent solution to incorrect allocation of volumes between suppliers and either aggregators or directly-participating customers would require engagement with the regulator. | LCM: day ahead. Wholesale: day-ahead and within day. BM: within gate. | Individual settlement periods (in the case of the BM, arbitrary within-gate periods). | Market structures exist for all price-setting. | LCM: we believe this could be implemented within a few weeks. A comprehesive solution for wholesale and BM may take 18-24 months. | None
16 | ScottishPower | Representing the views of ScottishPower | To encourage discretionary demand (eg hydrogen production and electricity storage) to locate in areas with network constraints | By providing fixed payments to the discretionary demand if they locate in areas with network constraints | Reduce overall volume of ESO actions;Reduce overall costs to consumers; | There would be a reduction in constraint payments going from the ESO to renewable generators. These would be offset by the payments to discretionary demand (eg hydrogen production and electricity storage). Overall, there is potential for the costs to consumers to reduce. In addition, there would be value in the green hydrogen that would be produced using the renewables that would have otherwise been constrained and the electricity that could be fed back into the system from the electricity storage. | There would be a reduction in the prices in the balancing mechanism when compared to the counterfactual which would promote more efficient dispatch. | The increased certainty as a result of the payments would improve the business case for the discretionary demand and reduce the risk associated with the project (with the potential benefits from a reduced cost of capital). | The primary carbon saving relates to the use of renewable electricity that would have otherwise been constrained. | Both hydrogen production and electricity storage could provide other value to the system. This would need to be considered further. | There are number of potential challenges including: Ensuring demand is consuming power when electricity is being curtailed (or would otherwise have been curtailed). This could be achieved by adopting a system of penalties that eligible demand would face if they were not consuming power, similar to the penalties applied in schemes such as the Capacity Market. To ensure a level playing field with existing sources of demand clear additionality and eligibility criteria could be put in place. If there is a change to TNUoS or adoption of alternative models such as ScottishPower’s proposed OpTIC model, it would be important to ensure that projects do not have double benefits during the overlap period. One solution would be to adjust payments to account for revenue or reduced costs as a result of reform. Appropriate conditions would be required to prevent gaming and promote additionality. | At T-4, given the development and construction times for discretionary demand. | Fixed term of at least [x] years with an ability to extend if boundary problems persist. Longer terms would provide more certainty to developers. | Options for basis of payment New discretionary demand would always pay market prices for electricity, both constrained and unconstrained (including at time of negative pricing), as any existing demand would. The discretionary demand would then receive a payment from the ESO to reflect the additional estimated/modelled amount that the ESO would have paid to renewable generators in the counterfactual (ie without the new discretionary demand). This payment could be fixed on a monthly, annual, or 5-year basis or for the full term of the agreement (a longer period would be preferable as it would provide a higher degree of certainty to new demand). There are various other alternative options that could be considered which may provide additional certainty for discretionary demand, including a fixed ‘strike price’ (or total revenues) with payments to demand offset by lower prices in the balancing market. It would be important to consult on the detail of how this payment would work. Allocation process/eligibility Contracts available to any new demand locating in a particular area after a set date (when it was clear that the constraints contract would be available) to provide additionality. No tender or auctioning necessarily required as this would be distorted by other mechanisms such as the Hydogen Production Business Model (HPBM) or long-term storage models. Similar to the current situation where renewable generation does not tender for constraint payments. Check on nature of demand to ensure it’s not ‘wasteful’ (eg minimum level of energy efficiency to end use). Hydrogen production, electricity storage, distilleries etc eligible. Minimum threshold (5MW or equivalent as HPBM?). | The lead time for implementing the scheme could be relatively short but would need to be discussed | This response is intended to contribute to the development of this project and we would very much welcome the opportunity for further engagement.
17 | Alastair Martin | Responding as Flexitricity Ltd | COOLER HEATING Industrial, commercial and domestic heating in Scotland includes several traditional technology types which are amenable to grid-friendly repowering through capital investment. Such investments would make Scottish commercial heat loads into responsive assets able to alleviate contraints by load-shifting. The principles of heat repowering would also be applicable to other means of delivery, including hydrogen hubs. | ESO would support, either with its own capital or using alternative methods such as cap-and-collar contracts for flexibility services, investment in heat repowering technologies including: - District energy with combined heat and power engines (136MW), which at operate at temperatures where a large-scale heat pump could be added as an additional heat source. - Whisky distilleries (heat consumption 14,000GWh pa) many of which use fossil fuels, but for which electric heating options with heat storage are now entering the market. - Ground source and water source heat pumps with limited heat storage capability, where the fitting of heat stores would greatly increase flexibility. In the case of CHP, it is normal for gas engines to continue to generate electricity regardless of constraints because the engines are the prime source of heat for the network. This exacerbates the constraint, but by co-optimising between a CHP and a large-scale heat pump, district heating networks can respond both to wind constraints and dunkelflaute events. Distilleries would repower to electric heating with storage given the right investment case. Adding heat stores to large-scale heat pumps is a highly cost-effective way to make these heat loads flexible and thus responsive to constraints. By either investing or creating investibility through cap and collar contract forms, ESO would create a large repowered heat resource that would participate in constraint alleviation. Using a blend of contractual arrangements, ESO would be able to ensure that the sites which had received the deepest investment would be subject to the firmest requirements for delivery of flexiblity. Any site not wishing to receive investment support could nevertheless deliver flexibility on a fully merchant basis. Other technologies able to deliver equivalent benefits include hydrogen electrolysis; it is possible that such alternative technologies could be incorporated within the system. | Reduce overall volume of ESO actions;Reduce overall costs to consumers; | Heat repowering delivers a double benefit, both in alleviating the constraint and in reducing the fossil fuel consumption associated with the heat load. Lower carbon and lower cost heating in district heating schemes, distilleries and agriculture creates economic and environmental benefits while making best use of available renewable resources. | Balancing costs reduce due to the availability of flexible load within constrained areas. Participating sites create long-term certainty of availability of flexibility to the extent that ESO has supported them with capital investment. | Because this approach can make use of a blend of investment and investibility tools, service providers can bring a variety of projects to the scheme. Some district energy projects, for example, are already progressing large-scale heat pump installation. Others may already have done so, and merely lack adequate heat storage capablity. These might take minimal or no investment from ESO and thus have full merchant freedom in flexibility markets. Others might not have been able to commit to their repowering plans, but ESO capital or other support may make the difference. In return, they commit to providing certain amounts of constraint management service at modest cost. Providers and site owners thus have the ability to choose the package that works with their project and their ability to access capital. | By repowering 136MW of gas engine CHP and up to 14,000GWh of direct fossil heating at distilleries, the equivalent volume of carbon is saved. Where heat pumps are the chosen repowering technology, the coefficient of performance multiplies the carbon effect. | Distillery heat loads will be capable of delivering static FFR, through time-shifted stacking or (where allowable) simultaneous stacking. The retention of CHP engines at district energy schemes allows the scheme to continue to respond to dunkelflaute conditions by switching back from heat pump to CHP engine. | The main challenge with the scheme itself is finding a blend of capital investment and cap-and-collar (or similar) investibility support that unlocks the widest range of capability. Each repowering scheme is likely to carry its own challenges, which may range for planning permission for hot water stores at district energy networks and grain drying facilities to technical integration with distillery heat needs. By having a broad range of eligible participants, the most economic and most shovel-ready projects will be incentivised to come forward early. Fair access to flexibility opportunities is also required, hence progression with "Regulatory Repair Shop" should happen alongside this. | Projects should be able to stipulate their own delivery times to the extent possible. If this cannot be squared with market transparency, then a combination of T-1 and T-4 timescales has been shown to be workable for investment. | As above: projects should be able to stipulate their own contract durations, although any making significant investments would require 3-5 years as a minimum. | A benchmark could be developed based on ESO's system needs projections; alternatively, annual auctions similar to the Capacity Market could be operated (though a much simpler format with less administrative burden would be necessary given the highly local nature of the projects concerned). | For shovel-ready projects, 18-24 months may be adequate. Other projects may require up to 4 years. | None
18 | SSE Energy Businesses | Organisation | Public Forecasts of Constraints What is being proposed? We propose that the ESO publishes forecasted locational constraint data across a range of timescales, from season ahead through to week ahead (in four-hourly resolution), moving to day-ahead (half-hourly resolution). The timescales for the publication of this data aligns with our proposals for the introduction of new market-based constraint management products (please see our “seasonal constraint product” and “short-term constraint product” proposals). This forecast data should be updated dynamically, and cover the depth of the constraint, the unconstrained capacity, and the available operational network capacity in the relevant period . The ESO should also publish aggregated locational forecasts of demand and generation, corresponding to the constraint data forecasts outlined above. This would allow market participants to understand how the constraint depth forecasts have been derived. The problem it is addressing: A key recommendation of the Energy Data Taskforce (EDTF) around maximising the value of data, is the principle that energy system data should be presumed open access. We are supportive of the EDTF recommendation and believe that more market data leads to fairer competition and greater transparency will mean market participants’ actions are open to greater scrutiny. There is currently limited data available to market participants to determine when and where a constraint may occur and thus parties are less able to efficiently optimise assets to support management of constraints. Publication of forecasts of locational constraint data in operational timescales (half-hourly at the day ahead stage), would allow market participants to efficiently respond and support the ESO in managing constraints in a cost-effective manner. For example, if a storage operator knew when a constraint was coming, they would discharge ahead of an expected constraint, so that they could then charge during the constraint utilising additional wind capacity which could then be discharged back into the system during a period of lower wind. This option would work well in combination with short term constraints management contracts which could then provide greater certainty to operators ahead of time that they are required to respond to a constraint with a fixed price for doing so. This is in contrast to either being dispatched through the BM or risking not receiving the full value of the service provided through the wholesale market. | Increased availability of forecast locational constraint data with supporting aggregated locational demand and generation data in operational timescales, would allow market participants to optimise their assets operations to respond to constraints supporting the ESO in managing constraints in a cost-effective manner. The proposal allows market participants to be prepared for constraints and so should widen the competition for responding to a constraint leading to a reduction in the cost of managing constraints. | Reduce overall volume of ESO actions;Reduce overall costs to consumers; | Consumer benefits would be realised through more efficient operation of plant, leading to lower constraint management costs. | Better able to plan actions based on the expected length of a constraint. | Increased data transparency allows market participants to make the most economic operational decisions. | Greater utilisation of low carbon generation through: (1) Improved scheduling of low carbon plant maintenance to account for constraints, (2) Improved optimisation of electricity storage using excess low carbon electricity when charging and displacing gas generation in unconstrained periods when discharging, and (3) Demand flexibility using low carbon generation at the times where there may be a local surplus due to transmission constraints. | A better understanding of what the local capacity mix is likely to be will help better understand the system needs e.g. inertia, voltage control etc. | Ensuring this is aligned with other changes to ESO products and processes e.g. constraints management contracts. Noting the difficulties associated with longer-term forecasts, the ESO could work collaboratively with industry to develop principles behind an appropriate forecasting methodology/algorithm, including the relevant data inputs. This engagement could be facilitated through the ESO’s Forecasting Stakeholder Working Group. | N/A – this is about provision of information rather than sourcing a service. | N/A – this is about provision of information rather than sourcing a service. | N/A – this is about provision of information rather than sourcing a service. | This should be possible to implement in 1 year. | N/A
19 | Alastair Martin | Responding as Flexitricity Ltd | ESO's trading function has very limited access to customer-side capacity. A review of ESO's operational trading arrangements could be conducted which would achieve the following: - Trading with more diverse participant types using Schedule 7/7A GTMA trades, enhancing liquidity at pre-gate timescales - A variety of trading horizons could be applied allowing customers with different capabilities to offer their capacity, increasing optionality for ESO ahead of gate. | Increasing the number and range of types of participants with whom ESO has the ability to trade before gate under Schedule 7/7A will create a "rainbow" of trading options using which ESO can alleviate a constraint before BM bids must be taken from wind farms. These would include customer demand categories such as EV chargepoint operators, hydrogen production, industrial and commercial heat (see "Cooler Heating"), cold storage and water pumping. This enhancement of optionality is a means for ESO to seek the best price for constraint remediation on within-day timescales. | Reduce overall volume of ESO actions;Reduce overall costs to consumers; | Consumers can offer their flexibility on an ad-hoc basis direct to ESO's traders, who are the only market participants able to value location in pre-gate timescales. This creates value from constraint alleviation and an impetus to further investment in flexibility. | Greater optionality on pre-gate timescales means lower prices, more capacity and less requirement to curtail wind within the gate. Because this proposal would create a range of trading horizons against which capacity providers could offer according to their capability, ESO would be able to select the most appropriate timescale at which to commit. This is likely to include a large proportion of within-day trades, many of which would be close to gate. Therefore ESO would buy at a time when the requirement was more accurately known. | The service provider and customer see revenue and cost reductions from purchasing energy that ESO would otherwise have to pay to discard. | Each MWh of consumption instructed through pre-gate trade is a MWh of zero-carbon renewable energy which is put to useful work rather than being discarded. | Enhancing participation at this level of flexibility encourages market entrants who may have additional capabilities to deliver system services. | "Regulatory Repair Shop" is a prerequisite to success with Trading Rainbows. ESO's trading teams should be closely involved in designing the forms which such pre-gate trading should take, so that participating capacity has a high chance of being useful and thus being rewarded. | Various timescales from day ahead to SOP preparation to immediately pre gate | Individual settlement periods | A liquid pre-gate market will follow market prices | This project is purely contractual, hence the timescales are driven by administrative tasks. No hardware build is required. | None
20 | Andrew Bruce | Scottish Futures Trust (SFT have also engaged with a number of members of the Scottish Hydrogen Industry Forum in developing this response) | The proposal is for a long term contract to manage a portion of the forecast constraint volumes in different locations in Scotland. Given the scale of renewable development forecast in Scotland, and the lead times for completing new transmission reinforcement, there is anticipated to be a high degree of confidence that the contracted hours will be necessary. Therefore: - This provides a greater range of options to the control room in addressing constraints ahead of Balancing Mechanism actions by enabling the production of green hydrogen and derivatives. - This aligns well with the UK Government (UKG) announcement that hydrogen blending into the methane distribution network (subject to safety clearance) might be a strategic enabler of electrolytic hydrogen production in areas of grid constraint. (here) - A contract (or series of contracts) to reliably reduce the cost of the Balancing Mechanism in key locations might also underpin an accelerated investment in new wind investment in Scotland, if there remain doubts about the speed of delivery of new transmission links (especially if the decision has been taken to implement LMP under REMA) In summary therefore, the proposal can reduce costs and manage risk for the system operator whilst providing a locational signal on investment timescales for the development of a key part of both the UK and Scottish wider net zero energy strategy | A contract holder is obligated to take (or be available to take) a pre agreed number of demand hours per annum and hence reduces the extent of actions required through the Balancing Mechanism. As set out in Scottish Renewables’ recent report on constraints (here), there are different options around firm hours or firm availability that could be assessed (and this is work that Arup have also been doing for ESO). The report suggests that dispatch of agreed hours would be made closer to real time and could be designed through engagement between the system operator and potential providers. | Increase effective network capacity;Reduce overall costs to consumers; | The cost of the contract would be less than the equivalent Balancing Mechanism action and hence the overall cost to consumers is lower. It will also provide a locational investment signal which will draw flexibility to the parts of the country where it is most valuable. In the case of hydrogen electrolysis, this means it provides a clear investment signal for electrolysers in areas of constraint in Scotland. The result will be to further lower constraint bills. | The extent of power needing to be constrained through the Balancing Mechanism is reduced. Depending on the form of contract, it may also provide optionality to the control room in dealing with curtailment. | An additional income stream can become available to the service provider which can complete the investment case for large scale green hydrogen production. In particular, this income stream is locationally specific and helps ensure that service providers come forward in areas of the country where there is highest need for constraint management. | There would be significant carbon savings from a reduced need to turn up gas fired plants south of the constraints and making more full use of renewable generation north of the constraint. | The proposal would support the wider decarbonisation of the GB energy system through the support and the signals it would provide to hydrogen electrolysers. It would also align constraint management with the current Low Carbon Hydrogen Standard (LCHS) and Hydrogen Production Business Model (HPBM). The HPBM, a CfD style support mechanism for low carbon hydrogen producers, requires compliance with the LCHS. The LCHS recognises that electrolysers using electricity procured by Balancing Mechanism actions to reduce renewable curtailment likely represents low carbon input to the production of hydrogen and is therefore likely to be compliant with the standard. However, electrolysers are less likely to invest based on uncertain Balancing Mechanism revenue streams, and operationally, relying on the Balancing Mechanism is likely to be challenging; certainty for investment would be increased with long term confidence of their revenue and cost streams. This proposal can help deliver that whilst aligning with policy, regulation and support schemes in both electricity and hydrogen sectors. | Aligning any contracts with forecast changes to generation and transmission in Scotland to ensure value for money for consumers. Aligning any contracts with changes coming out of electricity market reform to ensure value for money for consumers. Finding the most appropriate balance between the value of long term contracts in supporting low carbon investment and hedging future costs against the risk of procuring services several years in advance which are then not needed. | Contract would be signed over a long period of time and therefore well ahead of gate closure. | A period of 10-15 years would provide the strongest investment signal for new hydrogen investment, but shorter term contracts may also provide some stimulus for projects that were closer to viability prior to signing the contract. | Under competition and open to all technologies. | This might take 6-12 months to develop and contract for. | SFT proposes to undertake additional research to develop this idea further, including gathering forecast data on curtailment by location in Scotland and considering what proportion of the required load factor for an electrolyser the contracted hours from ESO might represent. We would be keen to discuss this with ESO to ensure that work we carry out is relevant and useful.
21 | SSE Energy Businesses | Organisation | IT System Upgrades What is being proposed? We propose to allow market participants to submit, one set of Dynamic Parameters (DPs) and prices for the true technical limits of a Balancing Mechanism Unit (BMU) and another set that represents the most economically efficient running of a BMU (similar proposal as explored under BSC Issue 98). This change would enable the most economic and efficient operation of the electricity system by ensuring ESO has sufficient information to choose the lowest cost balancing option. In the Balancing Mechanism (BM), there is a difference between the absolute limit of a technical parameter that a unit can operate at and the level at which it can do so most economically and efficiently. The ESO is constrained to the use of certain balancing actions because at present, DPs must reflect the technical capabilities of a BMU, rather than the most economic operation (Ofgem’s enforcement findings, in combination with the published letters, set an expectation that dynamic parameters should reflect the physical capabilities of a BMU). The problem it is addressing: Various factors can influence a BM bid/offer and how the generation plant is operated affects the operational costs and therefore the prices that can be offered e.g. ramp rates can be quickened but would cost more depending on the risk the plant incurs in doing so. It is therefore not always possible to capture the running options and associated prices in a single BM bid/offer. Example: The Stable Export Limit (SEL) is defined as "the minimum value at which the BM Unit, under stable conditions, may export (in MW) to the GB Transmission System…". From a technical perspective, this parameter will often be a fixed value below which, the BMU is at high risk of tripping and unable to generate. However, for some generators, operating at the SEL may increase physical wear on the unit and thus the BM price may need to reflect a premium associated with this additional cost. There may be a level above the SEL at which the generator faces lower levels of physical wear and can operate more economically, offering a lower price in the BM. In this scenario, there may be a commercially efficient level, where the ESO can purchase more volume but at a reduced unit rate, resulting in NGESO paying a lower price overall than if the generator were paid to operate at SEL. The inability to set DPs based on optimal commercial/economic outcomes for plant operators means the ESO often must balance the system with a set of actions that are not the true lowest cost. This can result in the ESO having fewer and potentially more expensive options to choose from, which ultimately increases costs to the end consumer. In the longer term, generating plant may need to balance their operations with environmental or maintenance limits, which often BM bids/offers cannot incorporate. | It allows generators to submit bid/offer prices and DPs in a way that: (1) maximises the ESO’s access to the lowest cost flexibility in the market, (2) enables effective competition between providers; and (3) allows the ESO to get closer to the true lowest cost solution when balancing the system. This would result in a lower cost of managing the system. | Reduce overall costs to consumers; | This proposal would result in increased cost reflectivity and competition in the BM, reducing the cost of constraint management, which is ultimately borne by consumers. | Gives the control room increased options to better manage the system at lower cost. | Allows market providers to compete more effectively to operate their plant in the most economic manner for the system. | Market participants will be able to balance their operations with environmental or maintenance limits, via the most efficient BM bids/offers. | To be explored through further assessment. | The Grid Code, BSC & ESO systems would need to be changed (explored further under BSC Issue 98). | This proposal would build additional sets of dynamic parameters under the BAU bid/offer submission process. | N/A. | Via the current system of BM bids and offers. | Total lead time would be a function of the time needed complete amendments to Grid Code, BSC and ESO systems this should be possible within a 1-2 year timeframe. | We present additional suggestions below of changes to increase data transparency, aligning with the Energy Data Taskforce (EDTF) recommendations, leading to more efficient market outcomes. (1) Automate current manual data submission processes and consolidation data platforms: Automation of manual workarounds allows data risks to be reduced and decreases the time required for ESO to process data, possibly leading to more cost-effective constraint management decision making. (2) The current manual processes for NAG (Notification of Additional Generation) and APR (Active Power Reduction) should be reviewed, automated, and published on an industry agreed market platform e.g. BMRS. Additionally, data and information published on the SONAR portal e.g. warming instructions, should be made more accessible to the wider market and moved to an approved platform e.g. BMRS. Delayed publication of this data creates inefficiencies in the market, as participants do not have full information before dispatch decisions are made. Improved data exchange processes would allow asset flexibility to be communicated to ESO more efficiently. The removal of manual data submission processes also reduces administrative burden and data risks for market participants. We have also identified improvements to the current categorisation of BOA actions/potential alternatives that would support increased transparency of the ESO’s operational decision making. (1) We believe there is benefit from more granular reason groups when categorising and publishing BOA actions e.g. “system” could be further broken down into specific reason categories such as thermal, voltage, inertia etc. More granular reason groups would better support the ESO in prioritising operational improvement activities. The ESO should consult industry on what these categories should be and how they should be defined. (2) BOA reasons should also be accompanied by specific network information e.g. loading on the network at that point in time and spare network capacity (covered in our “ESO to provide public forecast of constrains” proposal). If the market had access to this data, participants could respond to these signals through appropriate investment and better support ESO in cost-efficient system management. (3) We also note that the category of “zonal management” is used significantly as part of the Potential Alternatives dataset. Limited description is provided as to what falls into this category and similarly this should be broken down into more granular reason groups.
22 | SSE Energy Businesses | Organisation | Competitively Allocated Short-term Constraint Management Contracts - Up to 7 days ahead of time What is being proposed? We propose that the ESO introduces competitively allocated short-term constraint management contracts, with contracting taking place from T-7 days up to day-ahead depending on the duration and depth of anticipated constraints. Currently, most of the ESO’s balancing actions to address constraints are taken after gate closure via the Balancing Mechanism (BM). Competitively allocated short-term constraint management products are a way of contracting for constraint management actions both in front of and behind a constraint in advance of gate closure – this applies to both generation and demand. They would differ from the current arrangements by providing greater notice to assets of when they will need to respond, and how long that response will last for, to improve operational planning and efficiency. Whilst this is already possible to some extent through Schedule 7, this is not commonly used and is also a bilateral contract rather than competitively allocated. The decision to allocate contracts including the duration and volume will be dependent on forecasts of ESO constraints (see our proposal titled “ESO provide public forecasts of constraints”). The problem it is addressing: In the absence of prior notice, assets cannot ensure that they are fully ready to respond e.g. batteries being in the right state of charge or thermal assets reaching minimum stable load. This means they either: a) may not be able to respond and higher priced assets are taken instead, or b) they must respond very quickly and so may incur an additional cost in doing so that will be accounted for in the BM bid or offer price e.g. greater wear and tear, greater risk of tripping, lost opportunity costs for storage of responding in a later period. They also do not know how long they will need to respond for as future periods may not have been settled and so they must assume the worst-case scenario for those future periods in any bid or offer e.g. fixed costs such as warm-up fuel use must be recovered over a shorter period. This results in assets experiencing higher costs and accounting for the highest level of anticipated risk in their bid and offer prices, both of which result in higher costs in the BM. | Contracting for firm response (or the option for firm response) with sufficient notice of operational requirements, in particular duration and volume, allows for assets to be operated more efficiently. This lowers the cost of running the assets to manage constraints which can be reflected in pricing. Having the potential for these contracts to be allocated up to seven days in advance will enable assets with longer lead times to offer constraints management where they might not otherwise be able to compete e.g. better managing a CCGT unit’s Minimum Zero Time or discharging long-duration storage ahead of an expected long period of constraints. Contracting for several periods at one time provides assets with a clearer view of how many hours they will be running for, so in circumstances where they are running for several hours, they don’t need to incorporate the costs of ramping up and ramping down over the shortest potential timescale to cover the risk they will not be kept on beyond that. | Reduce overall volume of ESO actions;Reduce overall costs to consumers; | Increased competition and lower operational costs due to asset optimisation feeding into lower cost to managing constraints. This would reduce the price and volume of constraint management actions leading to lower BSUoS costs. | Reducing the volume of actions to be taken after gate closure. | Provides clearer operational dispatch signals and helps with scheduling maintenance. | Greater use of electricity storage over gas: (1) Behind a constraint it can charge using renewables and then discharge to displace gas in unconstrained periods, and (2) in front of a constraint, it can discharge during a constraint in place of gas. The greater foresight of constraints could allow greater demand-side flexibility which may not be possible to plan for at short notice. | It is possible that where contracts are for increased CCGT output in front of a constraint then it will also offer greater system stability. More generally, by providing greater forward notice of the future generation mix, taking account of constraints, it may be clearer what the future need for stability and frequency response services will be. For storage that can provide a range of system and energy balancing services, greater foresight of constraints management needs, allows for greater optimisation between services offered. | This is reliant on accuracy of ESO forecasting anticipated constraints and requirements for addressing those constraints including location, duration, and volume (as covered in our proposal titled “ESO provide public forecasts of constraints”) Unlike for balancing reserve, which is fixed at the day ahead stage, this product may not suit a specified timescale and may need to allow for some flexibility according to the nature of the constraints anticipated. There may be times that there are few or only a single project that can meet the desired need, meaning that allocation may not elicit effective levels of competition, however, if it is transparent and allows for more operational efficiency than contracting through the BM it is still likely to save costs. In his recent report for Scottish Renewables 'Exploring Options for Constraint Management in the GB Electricity System', Simon Gill demonstrates an example (‘Box 3’) where a forward constraint management contract with a price less than the anticipated cost of constraint would deliver savings for the consumer relative to BM actions. The interaction with other system services and energy balancing products to enable projects to stack and optimise across services e.g. balancing reserve, stability markets and the Capacity Market. This also includes interactions with other constraints management products that may emerge from the Constraints Collaboration Project or in future. | From T-7 days up to day-ahead depending on duration and depth of anticipated constraints. It may be that staged allocation rounds are required as better forecast data becomes available. The benefit of T-7 procurement is that it will allow CCGT’s to be ready if they require a cold start. For long-duration storage, advance notice is also beneficial as it may most be efficient for them to charge/discharge over several days. | One day (service day) – covering the ‘response windows’ for that contracted 24 hours. | Competitive allocation process. | This should be implementable within a year. | N/A.
23 | SSE Energy Businesses | Organisation | Competitively Allocated Season Ahead Constraint Management Availability Contracts What is being proposed? We propose that the ESO introduces competitively allocated season ahead constraint management contracts designed in two parts (1) Availability; and (2) Utilisation, with tendering occurring for availability price and a utilisation price paid only if the asset is dispatched. Currently, most of the ESO’s balancing actions to address constraints are taken after gate closure via the Balancing Mechanism (BM). Season ahead competitive allocation is a way of securing constraint management services much earlier from thermal generators in front of a constraint, allowing the prices of these actions to be fixed in advance. Whilst this could be technology agnostic, this product should be structured to ensure it works for thermal generators in front of constraints as a large contributor towards constraint costs. The decision to allocate contracts including the duration and volume will be dependent on forecasts of ESO constraints (see our proposal on ‘Public forecasts of constraints’). The problem it is addressing: In his recent report for Scottish Renewables 'Exploring Options for Constraint Management in the GB Electricity System', Simon Gill highlights that the recent increase in average constraint costs (£/MWh) was driven almost exclusively by the ‘turn up’ cost of gas generation in front of the constraint to replace constrained electricity behind the constraint. Average constraint costs in 2019/20 were £109/MWh, in 2022/23 they were £370/MWh. Whilst this was largely driven by increased gas prices, allowing generators to plan ahead will help minimise these costs. When gas generation offers to turn up in the BM it does not know how much revenue it will earn over the season. Therefore, it is reliant on inframarginal rent and, where appropriate, scarcity pricing to cover its annual fixed costs. This has two implications: (1) Projections of inframarginal rent may not be sufficient for an asset to remain on the system, and (2) Higher bids are required during periods of scarcity to insure against the risk of low use during the rest of the season or future seasons. | Contracting season ahead can provide greater revenue certainty to thermal generators and limit the cost of constraint management actions for consumers. Greater notice for assets to be ready to respond means that ESO should have a wider range of assets to choose from in its dispatch decisions. | Reduce overall costs to consumers; | Reduced constraint action costs of gas turn up actions and increased number of potential projects that are available for turn up. This would reduce the price of constraint management actions leading to lower BSUoS costs. | Greater forward planning means that post gate closure decisions should be more straightforward. | Provides increased revenue certainty via contracts instead of uncertain BM revenues. Provides clearer operational dispatch signals and so the operation and maintenance of assets can be managed more efficiently. | Improved operational efficiency by providing greater notice to assets of when they will need to respond and for how long allows (e.g. for efficient start up and shut down), as well as more efficient use of demand-side flexibility and storage. | Constraints are likely to happen when there is high wind on the system, so if it's known ahead of time what thermal generation will be online in particular locations, it will make the need for BM actions to address inertia, voltage control and other system services easier to assess. | This is reliant on the accuracy of ESO forecasting anticipated constraints and associated turn-up/turn-down requirements in a season-ahead timeframe (this would not need to be as in-depth as for short-term constraints markets), and determining the appropriate notice periods for when to dispatch plant. The interaction with other system services and energy balancing products to enable projects to stack and optimise across services e.g. balancing reserve, stability markets, and the Capacity Market. This also includes interactions with other constraints management products that may emerge from the Constraints Collaboration Project or in future. | Season-ahead availability contracting – e.g., April for Oct – Mar ‘season’ and October for April – Sept ‘season’. | Potentially two 6-month periods (e.g., 1st Oct – 31st Mar & 1st Apr – 30th Sept) for availability – covering issues experienced in both ‘Winter’ and ‘Summer’ periods. Firm response (or the option to provide firm response) confirmed from T-7 days up to day-ahead stage for a nominated response period, with contracting periods reliant on ESO forecasting anticipated constraints and their characteristics. | Competitive allocation process for projects that can meet the specific location and any other technical requirements set by ESO to enable effective response in front of a known constraint e.g. B6 boundary, with contracts designed in two parts: (1) Availability, and (2) Utilisation. Availability payments are provided across ‘seasons’, with utilisation payments made only when assets are physically dispatched via ESO instruction under this arrangement. For thermal generators, this utilisation payment would take the form of a fixed return above gas and carbon prices at the time of the firm commitment. | This should be implementable within a year. | N/A
24 | John Costa | EDF | "DFS inverse" - proposal to incentivise Demand turn-up at a lower cost to consumers via a daily/ d-1 (and week-ahead?) auction of excess wind that would otherwise be curtailed. 1. This would reduce thermal constraint volumes and costs behind and in front of the constraint. 2. Thermal Constraint costs are large and escalating fast and need to urgently be reduced in the interest of consumers given the transmission capacity needed to meet the 50GW of wind aiming to connect by 2050 will continue to fall short. ESO analysis shows that currently 4TWh/y of excess wind is being paid off each year in Scotland alone stating that by 2030 this could rise to 10TWh/y with B6 alone being constrained 1/3 of the year with an average of 4GWs of constraint actions | 1. D-1/ daily or even week-ahead auction of forecast excess wind by constrained zone – using the Demand Flex Service but inversely to incentivise demand to soak up excess Wind at times when the ESO can forecast constraints (wind normally accurate to forecast 1 week ahead). 2. Resolving / reducing forecast constraints early would reduce the cost of panic offering on flexible CCGTs in front of the constraint on the day so close to gate closure. 3. Will allow more Renewable and low carbon generation to run in line with NZ ambitions. | Reduce overall costs to consumers;Increase effective network capacity; | see answer to 4 above – BSUOS costs come down from reduction in wind bids, reduction in some CCGTs offers + consumer pays less for | Yes value in less ESO actions, more time for control room operatives to make better decisions and concentrate on securing system security. | yes to the extent it incentivises new demand and flexible assets like batteries | Not clear but potentially yes to the extent it would lead to less need to switch on CCGTs in front of the constraint. | In theory yes from switching less Generation on and off all the time which could impact stable Frequency | this DFS turn up solution should be relatively simple to implement given it’s a tried and tested process… | Day ahead…but a week ahead could also work? | HH to hourly periods of forecasted constrained period | Suppliers and assets submit their price for certain amount of volume and ESO takes the cheapest batch that meet their target requirement (similar to DFS) and share the savings with consumers. | D-1 or Week-ahead | the market needs historical and long-term forecasts (weekly/ monthly) of curtailed wind and what time of the day on top of this market design to participate effectively and efficiently.
25 | SSE Energy Businesses | Organisation | Enhance Utilisation of the Transmission Network What is being proposed? We propose that the ESO, alongside input from industry, conduct a risk-based review to identify where levels of operational redundancy can be relaxed to make the best use of the network capacity that exists. This review should include a review of the SQSS, as well as other relevant procedures regarding system operation, and should be conducted in a way that is transparent and involves relevant experts across industry. Any changes, that emerge from the review to standards, criteria/assumptions, and/or methodologies and operational procedures should be fully evaluated, and their economic and social consequences considered before proposals are taken forward. A result of this review could be for the ESO to procure more commercial intertrip services through their Constraint Management Intertrip Service (CMIS) – we note that in its first year, the CMIS across the B6 boundary enabled 367GWh of extra renewable electricity generation, saving £95.2m in costs ('ESO to deliver consumer savings through early start of new constraint management service' - 2 Feb 2024). In addition, the outcome of the review could lead to further SO:TO optimisation by identifying where enhanced services can be provided, resulting in increased net benefits as identified by Ofgem because of the RIIO-2 Output Delivery Incentive (ODI). The problem it is addressing: Currently on the transmission network, boundary transfer capacity is held in reserve, to ensure power can continue to flow in case of a fault occurring on one or more circuits. By holding this reserve and curtailing wind as a first resort, the ESO is operating the system as if those circuit outages have already happened, instead of planning how best to respond in the rare case that it did happen. We believe that alternatives may be available to keep the system secure, without holding back the current level of reserve transfer capacity. The SQSS was developed for an electricity system dominated by dispatchable thermal generation and therefore does not accurately reflect the current and emerging generation mix. Operational redundancy requirements of the network are higher than they need to be, resulting in higher volumes of generation being constrained than is necessary. A review of the SQSS in the context of the current and emerging energy mix can provide an up to date and accurate view of the appropriate operational redundancy requirements, allowing the value of new network build to be accurately assessed which can then feed into strategic network planning processes. | Enabling greater flows for given levels of operational network capacity will lower the amount of constraint management actions taken by the ESO in the BM, reducing consumer cost. | Reduce overall volume of ESO actions;Increase effective network capacity; | Increasing effective network capacity reduces the frequency and depth of constraints and so will reduce the overall cost of constraints – reducing cost recovery via BSUoS pot providing consumer savings. The cost of utilising fault services (e.g., intertrip services) is often lower than the cost of always holding back reserve in case a fault arises. For example, the tripping fee on an intertrip contract is only incurred when a fault occurs, which under the current EC5 Constraint Management Intertrip report, is estimated to be once every 42 years. The significant benefits of intertrip services have already been identified by the ESO ('ESO to deliver consumer savings through early start of new constraint management service' - 2 Feb 2024). | Increased utilisation of the network should mean less actions required by the control room. | The service provider in this case is the combination of the TOs and the SO. Up to date views of network capacity limits given generation and demand expectations can allow the TO/SO to provide a more effective service in terms of energy carried and reliable secure supply delivered. | Utilising more network capacity allows more renewable generation to stay on the system. The alternative to constraining renewable generation is that the renewable generation is lost, and often carbon intensive generation is then utilised to make up the lost power, leading to an increase in carbon emissions. From intertripping alone, 144kilotons of CO2 was saved in the first year of the B6 boundary CMIS by enabling 367GWh of extra renewable electricity generation ('ESO to deliver consumer savings through early start of new constraint management service' - 2 Feb 2024'). | To be explored through further assessment. | Ensuring that where any relaxation in redundancy requirements results in an increased risk of fault, that it is accompanied by appropriate mitigation measures e.g. intertripping contracts. Coordinating with other changes e.g. strategic planning, but not allowing such changes to slow progress on achieving an ‘easy fix’ where redundancy requirements can be relaxed. | N/A. | N/A. | N/A. | N/A. | N/A.
26 | SSE Energy Businesses | Organisation | Long-term Constraint Management Contracts What is being proposed? We propose that a long-term locational investment signal is provided via constraint management contracts to sources of demand located in areas of high renewable resources. This is a variation of ESO’s proposed ‘demand for constraints’ and Simon Gill’s long-term constraints management contracts, proposed in his recent report for Scottish Renewables 'Exploring Options for Constraint Management in the GB Electricity System'. The key aspect of this proposal is that it aligns payment with the ability of the demand to relieve constraints, covers all types of demand, and aligns with the necessary investment timescales of the type of demand. The value of the contract should be linked to the extent to which that demand is expected to be active during times when constraints are expected to occur, to either reduce the depth of those constraints or avoid them occurring altogether. Eligibility should be open to all forms of demand, including long-duration electricity storage which may take an investment decision up to eight years prior to commissioning. The problem it is addressing: There is an absence of an investment signal to incentivise sources of demand to locate in areas of high constraint volumes. | Incentivising new demand to locate in these areas (where an investment signal has the potential to impact on the investment decision) can offer a cost-effective solution to reducing constraint costs by providing an alternative to renewable curtailment. | Reduce overall volume of ESO actions;Reduce overall costs to consumers; | Reduces cost of constraint actions by utilising sources of demand in place of renewable curtailment. | Reduced volume of actions required. | Lower overall cost of electricity consumption relative to locating in front of a constraint to recognise that the marginal cost of the electricity used in constraint periods is close to zero or even negative (avoids wind curtailment). The value of this contract could encourage positive decisions to invest in high renewable areas. | Higher utilisation of renewable energy in place of carbon-emitting generation if the demand is either flexible (and so shifts to periods of high renewables) and/or it impacts the decision on where to locate the demand such that it is located behind rather than in front of a constraint. | Certain types of demand can provide other system services. For example, electricity storage, particularly synchronous storage from pumped hydro storage in Scotland, could provide a wide range of services including inertia (which does not travel as far as energy), black start, reserve, and frequency response. | How to link the payment to the ability of a particular type of demand to relieve constraints. Ensuring that competitive allocation timescales and contract lengths are aligned with investment timescales so that these contracts can meaningfully impact on investment decisions. | Up to T-8 years depending on an assessment of the required timeframe for investment by different demand sources. | It may be necessary to have more than one contract length e.g. for smaller scale and larger scale investments. For large scale investments, it should align with other investment timescales e.g. 15-year CfD agreements, and 15-year CM agreements. | Competitive Allocation – For example, competitive tender process or pay as clear auction (£/kW). | This should be implementable within a year. | N/A.
27 | John Costa | EDF | a more cost reflective Tnuos Generation charge for BESS to reflect they are not generators but provide benefits to the system 1. Reducing thermal constraint volumes and costs by incentivising more BESS to connect in constrained zones to balance out the excess wind that is increasingly being curtailed. 2. Thermal Constraint costs are large and escalating fast and need to urgently be reduced in the interest of consumers given the transmission capacity needed to meet the 50GW of wind aiming to connect by 2050 will continue to fall short. ESO analysis shows that currently 4TWh/y of excess wind is being paid off each year in Scotland alone stating that by 2030 this could rise to 10TWh/y with B6 alone being constrained 1/3 of the year with an average of 4GWs of constraint actions required when it is. | 1. Currently batteries are charged as generators for the purposes of TNUoS. This signals to them to not locate in high wind deployment areas where constraints are also likely to be high. 2. However, NGESO and the transmission companies have revised their grid construction planning assumptions to show that in general batteries do not increase network build as they are likely to operate at times that are beneficial. 3. Given this TNUoS charges for batteries need to be updated to align with network planning assumptions. 4. A revised cost reflective charge would incentivise more BESS to locate in constrained areas like Scotland. This has the potential for BESS to soak up some proportion of the excess wind to release back into the system once the constraint has ended. This in turn would allow more wind to run to meet extra demand thereby reducing thermal network constraints and the cost of resolving them while also allowing low carbon generation to run more in line with NZ ambitions. | Reduce overall volume of ESO actions;Increase effective network capacity; | lower BSUOS costs from a reduction in wind bids, and potentially a reduction in the amount of last minute CCGTs panic offers in front of the constraint close to real time. It would also allow better use of renewable energy in line with NZ2050 ambitions. | Yes if it leads to more BESS connecting, value in less ESO actions, more time for control room operatives to make better decisions and concentrate on securing system security. | yes to the extent it incentivises new demand and flexible assets like batteries | Potentially yes if it means less CCGTs offered on in front of constraints. | In theory yes from switching less Generation on and off all the time which will impact Frequency. If correct this will also reduce the amount of Freq. response services the ESO procures to manage this risk as BESS provide fast response. | link to charging reviews? | N/a | N/a | N/a | asap? | none
28 | John Costa | EDF | Long-term auction of excess wind via T-[x] tenders for [x] contracted years 1. Reducing thermal constraint volumes and costs behind and in front of the constraint. 2. Thermal Constraint costs are large and escalating fast and need to urgently be reduced in the interest of consumers given the transmission capacity needed to meet the 50GW of wind aiming to connect by 2050 will continue to fall short. ESO analysis shows that currently 4TWh/y of excess wind is being paid off each year in Scotland alone stating that by 2030 this could rise to 10TWh/y with B6 alone being constrained 1/3 of the year with an average of 4GWs of constraint actions required when it is. 3. auctioning off a baseload chunk of excess wind on a long-term basis via T-[x] tenders will reduce thermal network constraints and the cost of resolving them plus also allow Renewable and low carbon generation to run more in line with NZ ambitions. | 1. A Long-term auction of excess renewable energy to the highest bidder would not only avoid ESO/ consumer costs from long-term curtailment and replacement offers from carbon intensive CCGTs on the other side of the constraint but the ESO could get money in return thereby reducing BSOUS costs even further. 2. This would incentivise large capital-intensive demand assets to locate to constrained areas through 5 to 10y or even 15-year contracts depending on the type of asset (Electrolyser for example would need 15 years) and depending on the ESO’s forecast of constraint volumes and costs. 3. It would kill two birds with one stone by creating a proper long-term market similar to others that the industry can understand/ stack (CM, and Stability/ Reactive mkt design etc) while enabling capital intensive projects such as Electrolysers, large Distillery, Batteries to locate to constrained areas which will avoid some network build/ reinforcement in the long-run. 4. Long-term auctions/ contracts would also help banks lend money against these projects. 5. We need to have lots more detailed constraint cost breakdowns and also long-term forecast of how much volume will be curtailed in say 2030, 2035 and 2040 etc for capital investment projects know the size of the market in the future. | Reduce overall volume of ESO actions;Reduce overall costs to consumers; | see answer to 4 above BSUOS costs come down from reduction in wind bids, reduction in some CCGTs offers. Would also capital intensive projects necessary for NetZero like Electrolyers to connect. | yes lots of value from lower ESO actions, more time for control room operatives to make better decisions and concentrate on securing system security. | yes see answer 4 above. Investors could have more revenue certainty from LT contracts which banks would more easily lend against. | there will be a carbon saving especially if it leads to Electrolysers being built but difficult to quantify. | In theory yes from switching less Generation on and off all the time which will impact Frequency. If correct this will also reduce the amount of Freq. response services the ESO procures to manage this risk as Demand can be fast acting. | the systems involved and the timing of delivering them but the ESO has experience in this tenders so hopefully could design something quickly. | it depends on the asset – for data centres then yes a T-1 might suffice but for larger more capital intensive assets such as electrolysers it could be T-4/5. | Again see answer to 4 above. The contract length could be 10 or 15years depending on the type of solutions being sought to hit NZ targets. | Ascending clock auction or just a tender to the highest bidder for that chunk of energy/ window ? | answer to 12 above | the market needs lots more information like historical curtailed wind volumes and long-term forecasts of curtailed wind (weekly/ monthly) and what time of the day on top of this market design so that parties can decide to invest more effectively.
29 | John Costa | EDF | weekly generation turndown auction at D-7 to allow more competition in available generation which should lower bids 1. Reducing thermal constraint volumes and costs behind and in front of the constraint. 2. Thermal Constraint costs are large and escalating fast and need to urgently be reduced in the interest of consumers given the transmission capacity needed to meet the 50GW of wind aiming to connect by 2050 will continue to fall short. ESO analysis shows that currently 4TWh/y of excess wind is being paid off each year in Scotland alone stating that by 2030 this could rise to 10TWh/y with B6 alone being constrained 1/3 of the year with an average of 4GWs of constraint actions required when it is. 3. weekly generation turndown auction at d-7 to allow more competition in available generation at lower price/ cost than panic buying off wind on the day and close to gate closure. | Going week-ahead as well as D-1 will get more competition and cheaper prices than the [£45-£80/MWh] it currently pays from panic buying off generation on the day close to real-time (similar to the rationale in moving Balancing Reserve to D-1). | Reduce overall costs to consumers; | see answer to 4 above | potentially yes if it leads to lower amount of ESO actions on the day (assuming they get the amount right week or day ahead. | better planning at week-ahead stage. | n/a | not clear | the systems involved and the timing of delivering it. | Week ahead d-7 to day ahead. | the length of forecasted constraint. | Competitive market to understand who would be willing to be curtailed ahead of time | d-7 | none
30 | John Costa | EDF | allow TNuos Demand to go negative – remove £0 floor 1. Reducing thermal constraint volumes and costs by incentivising more demand to connect in constrained zones to soak up excess curtailed wind. 2. Thermal Constraint costs are large and escalating fast and need to urgently be reduced in the interest of consumers given the transmission capacity needed to meet the 50GW of wind aiming to connect by 2050 will continue to fall short. ESO analysis shows that currently 4TWh/y of excess wind is being paid off each year in Scotland alone stating that by 2030 this could rise to 10TWh/y with B6 alone being constrained 1/3 of the year with an average of 4GWs of constraint actions required when it is. | TNUoS D is capped at zero meaning the locational signal cannot fully represent the benefits of siting demand in generation dominated areas. Removing the £0 floor cap would incentivise more Demand to locate in constrained areas like Scotland. This in turn would allow more wind to run to meet extra demand thereby reducing thermal network constraints and the cost of resolving them while also allowing low carbon generation to run more in line with NZ ambitions. | Reduce overall volume of ESO actions;Reduce overall costs to consumers; | see answer to 4 above – BSUOS costs come down from a reduction in wind bids, reduction in some CCGTs offers and consumer pays less for their energy plus better use of renewable energy. | Yes less wind curtailment means value in less ESO actions, more time for control room operatives to make better decisions and concentrate on securing system security. | yes to the extent it incentivises new demand and flexible assets like batteries | Yes if it means less CCGTs being offered on in front of the constraint. | In theory yes from switching less Generation on and off all the time which will impact Frequency. If correct this will also reduce the amount of Freq. response services the ESO procures to manage this risk as Demand can be fast acting. | time to determine a suitable cost reflective TNous G charge. | n/a | n/a | n/a | asap? | none