## FRCR2024
Question | Answer
Can FRCR publish planned yr on yr trajectory towards lower inertia (say to 2030), within programme highlight milestones on market developments & others assumed? | FRCR focuses on short-term policies for managing system frequency risks. However, this year, we have expanded the outlook to a two-year timeframe, which includes the period of 2025-26. This extension allows us to consider future system dynamics in our analysis. For a broader perspective on the roadmap towards a 2030 system, other work streams such as the Electricity Ten Year Statement and Operability Strategy Report provide detailed discussions. These documents explore the strategies and considerations necessary for achieving the goals outlined for the electricity system by 2030. They provide insights into the long-term planning and operational aspects required to ensure the reliability and efficiency of the power system.
You've not been able to reduce to your target 120GVAs inertia level implemented last June because of SS oscillations in Scotland in July so is 102 GVAs risky? | We implemented the minimum inertia policy of 130 GVA.s in late Feburary 2024. Since then, we observed system inertia had been lowering towards 130 GVA.s and quite a few occasions close to the 130 GVA.s limit. We are continuously monitoring the overall performance of the wider system and finalising the operational plan to operate at 120 GVA.s of minimum inertia. Regarding the sub-synchronous events experienced last summer, the investigation has determined that they were not directly related to system inertia. To address wider system operability issues and achieve our goals for 2025 as the initial step towards a zero-carbon system by 2035, the ESO has established work streams dedicated to developing operational tools and improving our models.
As inertia levels from T connected gen falls, demand side inertia will become increasingly important Can ESO explain how they model demand side inertia please | Demand side inertia is calculated based on historical frequency events we experienced and the value is under continuous review and update into our operational and procurement tools to ensure we can secure the system.
Agree reflect on op experience important after each change. How evaluated- need PMU availability?accuracy of inertia estimation tools?other(eg DG visibility)? | Thank you for your comments. We are working with external and wider industry to improve our real-time visibility and monitoring on system frequency and inertia via different technologies. Those technology and work are under validation stage and have not been implemented into operation. We are collaborating proactively with industry on this area.
Does FRCR analysis consider the impact of mandatory underfrequency response from BESS? Does this help secure against simultaneous events triggering LFDD? | In our FRCR analysis and daily response requirement setting, we do not currently consider the provision from LFSM-U (Limited Frequency Sensitive Mode - Underfrequency). However, we acknowledge that LFSM can play a role in reducing the possibilities of LFDD with an additional layer of buffer in the system. We will continue to evaluate and refine our frequency management strategies. Therefore, we have included LFSM in the future work of FRCR (stated in Section 8.3) and will incorporate it in future FRCRs. It is also worth noting that the Grid Code was updated in 2023 through Grid Code Mod GC0148 which places obligations on BESS so that if they are in an import mode of operation they can transition to an export mode of operation if there is a low frequency event.
Will you reconsider simultaneous losses again following the 22 December event with 3 large trips/losses in 12 seconds on that day. | Simultaneous events are considered since the second edition of FRCR, i.e. FRCR 2022. The size and the occurrence probability of simultaneous events are reviewed and updated in this year’s FRCR and we believe the statistical summary of simultaneous events occurrence with their loss sizes remains a good representation of system risks.
How do the lower inertia levels sit with large outfeed losses which is seldom tested in anger? | With a lower inertia level, the frequency dynamics are not expected to undergo significant changes. Currently, the largest outfeed loss in the system occurs when interconnections are exporting at full capacity. It is worth noting that due to the tighter high-frequency limit of 50.5 Hz, we have studied the largest outfeed loss and as a result the requirements for Dynamic Containment High have seen a substantial increase compared to previous years. In fact, the Dynamic Containment High requirements are generally higher than the DC-Low requirements. This adjustment reflects the need to maintain system stability and control within the specified frequency limits under varying operating conditions.
Is the FRCR considering if increased volumes for DM and DR will be needed? | In our FRCR analysis, we incorporate the standard requirement of 350MW of Dynamic Regulation (DR) and 150MW of Dynamic Moderation (DM) in the system to ensure pre-fault frequency stability. While the requirement for pre-fault purposes falls outside the scope of FRCR, we are currently conducting a review of the necessary services and reassessing the DR/DM cap.
Why did the OTF report on 22 Dec event not disclose units impacted, but page 34 of https://www.nationalgrideso.com/document/301306/download does? | Thanks for your question. It is the OTF’s specific policy that we do not name the individual unit. The link provided is Incentives Report, which has a different rule on the names.
Can OBP dispatch units in the BM in realtime after a large generation loss? FRCR 2024 doesn't mention OBP but that's a very useful tool for Control Room | Thanks very much for your feedback on OBP. As a nutshell, OBP will enable us in real time to dispatch units more efficiently so ESO can manage system changes promptly and effectively. FRCR is a policy review to set up the high level policy and guidance for frequency management. The implementation plan including tools and operational observations will be monitored by the ESO. Therefore we will engage and disseminate the implementation plan via OTF separately from FRCR consultation and webinar process. Again, we will feed back to relevant team in ESO if you have further questions related to OBP.
Can you breakdown your £132m cost benefit of reducing to 120gvas + publish it please as you only show the results. We need the data inputs to be validate also. | The breakdown of the savings can be found in Section 6.1.1 of the report. It states that the total savings are the result of reduced inertia costs and increased response costs. However, it is important to note that the increase in response costs compared to the savings from reduced inertia costs is minimal. This indicates Dynamic Containment is a more effective tool for managing frequency risks.
Can you clarify why there have been delays in FRCR 2023 implementation? | As we lower our requirements and consider cost / risk benefits we are conscious of our responsibility to operate a safe and secure system. Several events over the last year have occurred that means that we have considered it prudent to leave our inertia requirements higher while we take time to fully understand the cause of those events.
Have VS protection systems been changed like RoCof based islanding protection system have? | As part of the Accelerated Loss of Mains Change Programme, VS protection is no longer permitted.
VS protection is no longer permitted, but why is there no requirement for VS ride though? This has been excluded from GC0155. | The current Grid Code requirements for fault ride through state that plant is required to remain connected and stable for a fault / votlage disturbance at the connection point or a fault on the transmission system. A plant connected to the system via a heathly circuit should not trip for any reason unless the specific reasons identified through GC0155. VS is not included in the list of exceptions.
Interested parties may have more buy in if ESO shared a reasonably detailed review of all large freq events. There are probably only around ten per annum. | Thank you for your feedback and we will raise this issue with our investigation team to hopefully increase transparency on this matter.
Would help for FRCR provide info on (IBR)withstand assumptions- e.g. instantaneous phase jump, df/dt, freq& voltage jump as simulated in system at that inertia | This is linked to the Grid Forming work and we are doing a lot of work behind the scenes on these issues. We already have requirements in the Grid Code to include Grid Forming – Grid Code Mod GC0137, we have produced a Grid Forming Best Practice Guide and we will also be developing another expert group in the near future to consider the wider changes to the industry codes (eg Grid Code etc) in respect of Grid Forming. This will also overlap with future FRCR work.
Have you analysed events & trips reported under GC0105 to test your assumptions of trips, performance of the responses and probabilities of events? | Event risk statistics are derived from two aspects: Generator trips that caused more than 250 MW power loss - fault statistics can be found in eGAMA for any fault/unplanned outages. Transmission fault that caused more than 250 MW power loss - fault statistic can be found in CG105 System Incidents Report. We review these statistics annually to make sure they are up to date and can represent the latest status of the system.
When in Summer do you plan to lower minimum inertia to 120 GVA.s? How will you communicate it? Do you plan to procure more DC when that happens? | Thanks for the question. We implemented 130 GVA.s min inertia policy on 28 Feb 2024 and are continue running system at this level to gain adequate operational experience, our operational tools and processes are fully capable of operating the system under lower inertia levels and no unintended wider operability risks. We are monitoring system conditions and finalising the date to implement 120 GVA.s and will provide at least five working days advanced notice to industry on OTF or similar forum. As our BAU process we constantly monitor system needs to procure different levels of response services and will communicate to ensure the markets can provide what we need to secure the system.
A quick plea: inertia is hard enough to explain as is, so it would help if you could be clear in your use of units. GVA-seconds rather than gee vee ays! | Sure. The unit is Gee-V-A seconds, someone read it as G-V-A-S someone read it fully. But it would be good use consistent way .
The minimum inertia is 120GVA now. What is the size of the biggest loss that you consider? What is the RoCoF limit you use now? | In FRCR assessment, we assess all possible events in the system, which are the BMU-only, BMU+VS and simultaneous events mentioned in the report. The peak simultaneous events are close to 3000MW loss. In real system operation we consider the largest single infeed and outfeed loss at the moment. In terms of the RoCoF, if the infeed loss will trigger the 0.125Hz/s or 0.2 Hz/s then we will cover those additional losses as well.
when do you intend on buying the 100MW extra of DC that you mention in the report? It doesn't say...unless i've missed something? | We will submit FRCR 2024 to Ofgem to approve. Once it is approved we will start to implement the introduced changes. i.e. additional DC. We will ensure further communications to the industry and also communication will be via our BAU process prior to procurement.