## Sheet1
PRIMARY RESTORATION SERVICE PROVIDERS
| ESR Tender - South West & Midlands Region 2024 |  | PROVIDER NAME
ITT5 SUBMISSION / SCORING
| Requirement |  |  | Score
| Time to Connect (h) | Phase 1, 2 or 3 |  | Pass/Fail | Other Info
| Service Availability (%) |  |  |  | Installed Capacity (MW)
| Voltage Regulation (Leading) (%) |  |  |  | Contracted Units for ESR (Number and Ref)
| Voltage Regulation (Lagging) (%) |  |  |  | Time Between Blocks of Load (min)
| Frequency Regulation (Lower) (Hz) |  |  |  | Point of Connection (kV & Substation)
| Frequency Regulation (Upper) (Hz) |  |  |  | Local DNO (UKPN-L / UKPN-SE/ UKPN-E)
Resilience of supply, Black Start Service (h)
Resilience of Supply, BS Auxiliary Unit(s) (h)
Block loading size (MW)
Reactive Capability (MVAr)
Sequential Black Starts (number)
Connection Voltage (kV)
Short-circuit level, t ≤ 80ms (kA)
Short-circuit level, t > 80ms (kA)
Inertia (MVA.s)
| Connection to Network / Transmission - Distribution Connected |  | T | 2%
| Connection to Network / Multiple - Single connections to the Network |  | 2 | 3%
| Other BS Service Provider(s) in the same Substation |  | N | 3%
| Time to Connect (h) |  | 0.5 | 5%
| Service Availability (%) |  | 500 | 10%
| Power Output / Reactive Capability at 0MW (MVAr) |  | 500 | 10%
| Power Output / Active Capability (MW) |  | 500 | 15%
| Block Loading Size (MW) |  | 500 | 10%
| Resilience of Supply / BS service at contracted Power Output (h) |  | 500 | 15%
| Resilience of Supply / BS Auxiliary Units (h) |  | 500 | 5%
| Contribution to System Stability / Short Circuit Level, t ≤ 80ms (kA) |  | 500 | 4%
| Contribution to System Stability / Short circuit Level, t > 80ms (kA) |  | 500 | 3%
| Contribution to System Stability / Inertia (MVA.s) |  | 1500 | 5%
| Contribution to Restoration Time (h) |  |  | 0%
PROVIDER SCORE - TECHNICAL |  |  |  | 90%
Note on D7: Format - Number (Example: "1.7")
Note on E7: For ESO to populate: "Pass" or "Fail"
Note on D8: Format - Number (Example: "100") Expected to be ≥ 80
Note on D9: Format - number Expected: "+10"
Note on D10: Format - number Expected: "-10"
Note on D11: Format - number Expected: "47.5"
Note on D12: Format - number Expected: "52"
Note on D13: Format - number Expected to be ≥10
Note on D14: Format - number Expected to be ≥72
Note on D15: Format - number Expected to be ≥10
Note on D16: Format - number Expected to be ≥50
Note on D17: Format - integer Expected to be ≥3
Note on D18: Format - number Expected to be: 11, 33, 132, 275 or 400.
Note on D19: Format - number (Example: "1.32")
Note on D20: Format - number (Example: "1.32")
Note on D21: Format - number Expected to be ≥400
Note on D22: Format - letter Expected to be a "T" or a "D"
Note on D23: Format - number (integer) Expected to be ≥1 Note: Number of physical connections onto the Network that will enable the delivery of the full contracted service.
Note on D24: To be populated by the ESO: "Y" or "N"
Note on D25: Format - number (Example: "1.7") Note: should match the same requirement listed previously/above
Note on D26: Format - Number (Example: "100") Expected to be ≥ 80 Note: should match the same requirement listed previously/above
Note on D27: Format - number Expected to be ≥50 Note: should match the same requirement listed previously/above
Note on D28: Format - number Note: contracted MW for the provision of the ESR Service
Note on D29: Format - number Expected to be ≥10 Note: should match the same requirement listed previously/above
Note on D30: Format - number(integer) Expected to be ≥10 Notes: - Should match the same requirement listed previously/above - If "Indefinite", please include "121"
Note on D31: Format - number Expected to be ≥72 Note: should match the same requirement listed previously/above
Note on D32: Format - number Note: should match the same requirement listed previously/above
Note on D33: Format - number Note: should match the same requirement listed previously/above
Note on D34: Format - number Expected to be ≥400 Note: should match the same requirement listed previously/above
Note on D35: For ESO to populate