## Version
Date | Version | Details
2024-08-15 | 1 | This file only contains the indicative reporting associated with draft data for GC0151 for August 2024. This file will be updated in September 2024 to reflect the full data set.
2024-09-16 | 2 | This file only contains the indicative reporting associated with data for GC0151 for August 2024. This file is updated in September 2024 to reflect the full data set.
2024-10-31 | 3 | This file contains the reporting associated with data for GC0105 & GC0151 for August 2024.

## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.
MW trip/loss of all generation/ interconnection related to the incident | Positive sign: indicates a loss of infeed, generator or importing interconnector. Negative sign: indicates a loss of outfeed, exporting interconnector.

## Transmission Faults (GC0151)
Location | Network Operator | Date Time | Voltage Trace (Refer to sheet) | Notes
An Suidhe - Port Ann - Crossaig (DPR) 132kV circuit | SHETL | 2024-08-01 05:33
Fleet - Lovedean 1 400kV circuit and Mesh Corner 1 and SGT1A | NGET | 2024-08-01 16:58
Markhill - Tralorg 132kV circuit | SPT | 2024-08-07 19:15
Amersham Main - East Claydon - Iver 1 Circuit, Amersham 400/132kV SGT1, Iver 400/275kV SGT6A and 6B | NGET | 2024-08-08 01:27
Staythorpe 132/25kV GT3 | NGET | 2024-08-10 10:53
Kintore - Craigiebuckler (XCN and XCS) 132kV Double circuit | SHETL | 2024-08-12 12:20
Dalchork - Loch Buidhe 2 (DLB2) 132kV circuit | SHETL | 2024-08-15 06:33
Carrington - Daines 2 400kV/Carrington 400/275kV SGT6 and Carrington - Daines 3 400kV circuits | NGET | 2024-08-20 22:27 | V20240820-1
Pembroke - Swansea North 3 400kV circuit and Mesh Corner 1 | NGET | 2024-08-21 05:46
Windyhill - Whistlefield - Dunoon - Sloy East 1 132kV circuit | SHETL | 2024-08-28 19:50

## System Incidents (GC0105)
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) | Transmission fault | Voltage Dip | Additional data
20240812-1 | Trip of IFA Bipole 2 | Importing from France to GB | 2024-08-12 15:41 | 20240812-1 | 49.923 | 49.755 | -0.10597 | 177 | IFA BP2 | 679.12
20240822-1 | Trip of IFA2 | Exporting from GB to France | 2024-08-22 00:16 | 20240822-1 | 50.035 | 50.238 | 0.14326 | 157 | IFA2 | 924.43
20240827-1 | Trip of GRAI-6 |  | 2024-08-27 22:22 | 20240827-1 | 49.967 | 49.909 | -0.01794 | 199 | GRAI-6 | 267.6
20240828-1 | Trip of IFA2 | Importing from France to GB | 2024-08-28 09:02 | 20240828-1 | 49.937 | 49.705 | -0.14651 | 171 | IFA2 | 990.54
20240828-2 | Trip of DRAXX-4 |  | 2024-08-28 20:57 | 20240828-2 | 49.976 | 49.812 | -0.059013 | 246 | DRAXX-4 | 648.56

## 20240812-1
In GMT
Date | Time | Freq
2024-08-12 | 14:40 | 49.917 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-08-12 | 14:40 | 49.912 | 222 | BRITNED | 676.211
2024-08-12 | 14:40 | 49.915 | 268 | WBURB-2 | 428.156
2024-08-12 | 14:40 | 49.917 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-08-12 | 14:40 | 49.92 |  | Viking Link | -648.9
2024-08-12 | 14:40 | 49.922 |  | Viking Link | 1398.96
2024-08-12 | 14:40 | 49.923 | 209 | DRAXX-3 | 626.95
2024-08-12 | 14:40 | 49.929 | 154 | CDCL-1 | 391.57
2024-08-12 | 14:40 | 49.93 | 268 | ROCK-1 | 468.495
2024-08-12 | 14:40 | 49.929 | 148 | IFA Bipole1 | 945.473
2024-08-12 | 14:40 | 49.928 | 132 | IFA Bipole1 | 999.1
2024-08-12 | 14:40 | 49.928 | 141 | IFA Bipole2 | 1000
2024-08-12 | 14:40 | 49.925 | 135 | IFA Bipole1 | 996.75
2024-08-12 | 14:40 | 49.926 |  | Viking Link | -780.3
2024-08-12 | 14:40 | 49.927
2024-08-12 | 14:40 | 49.927
2024-08-12 | 14:40 | 49.921
2024-08-12 | 14:40 | 49.922
2024-08-12 | 14:40 | 49.917
2024-08-12 | 14:40 | 49.916 | 130 | HEYM12 | 271.908
2024-08-12 | 14:40 | 49.915 | 228 | HUMR-1 | 303.75
2024-08-12 | 14:40 | 49.909
2024-08-12 | 14:40 | 49.906
2024-08-12 | 14:40 | 49.901
2024-08-12 | 14:40 | 49.897
2024-08-12 | 14:40 | 49.894
2024-08-12 | 14:40 | 49.889
2024-08-12 | 14:40 | 49.888
2024-08-12 | 14:40 | 49.887
2024-08-12 | 14:40 | 49.889
2024-08-12 | 14:40 | 49.889 | 211 | CDCL-1 | 291.5
2024-08-12 | 14:41 | 49.887 | 199 | STAY-2 | 413.125
2024-08-12 | 14:41 | 49.883 | 173 | CDCL-1 | 397.375
2024-08-12 | 14:41 | 49.883 | 248 | SEAB-2 | 361.25
2024-08-12 | 14:41 | 49.885 | 255 | FRANCE | 995.65
2024-08-12 | 14:41 | 49.887 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-08-12 | 14:41 | 49.887
2024-08-12 | 14:41 | 49.888
2024-08-12 | 14:41 | 49.892
2024-08-12 | 14:41 | 49.897
2024-08-12 | 14:41 | 49.899
2024-08-12 | 14:41 | 49.9
2024-08-12 | 14:41 | 49.898
2024-08-12 | 14:41 | 49.895
2024-08-12 | 14:41 | 49.889
2024-08-12 | 14:41 | 49.888
2024-08-12 | 14:41 | 49.886
2024-08-12 | 14:41 | 49.883
2024-08-12 | 14:41 | 49.885
2024-08-12 | 14:41 | 49.892
2024-08-12 | 14:41 | 49.891
2024-08-12 | 14:41 | 49.891
2024-08-12 | 14:41 | 49.897
2024-08-12 | 14:41 | 49.897
2024-08-12 | 14:41 | 49.899
2024-08-12 | 14:41 | 49.903
2024-08-12 | 14:41 | 49.903
2024-08-12 | 14:41 | 49.902
2024-08-12 | 14:41 | 49.903
2024-08-12 | 14:41 | 49.903
2024-08-12 | 14:41 | 49.902
2024-08-12 | 14:41 | 49.9
2024-08-12 | 14:41 | 49.899
2024-08-12 | 14:41 | 49.898
2024-08-12 | 14:41 | 49.899
2024-08-12 | 14:41 | 49.9
2024-08-12 | 14:41 | 49.9
2024-08-12 | 14:41 | 49.903
2024-08-12 | 14:41 | 49.907
2024-08-12 | 14:41 | 49.907
2024-08-12 | 14:41 | 49.902
2024-08-12 | 14:41 | 49.901
2024-08-12 | 14:41 | 49.901
2024-08-12 | 14:41 | 49.902
2024-08-12 | 14:41 | 49.902
2024-08-12 | 14:41 | 49.905
2024-08-12 | 14:41 | 49.907
2024-08-12 | 14:41 | 49.911
2024-08-12 | 14:41 | 49.911
2024-08-12 | 14:41 | 49.912
2024-08-12 | 14:41 | 49.914
2024-08-12 | 14:41 | 49.911
2024-08-12 | 14:41 | 49.909
2024-08-12 | 14:41 | 49.912
2024-08-12 | 14:41 | 49.913
2024-08-12 | 14:41 | 49.916
2024-08-12 | 14:41 | 49.916
2024-08-12 | 14:41 | 49.918
2024-08-12 | 14:41 | 49.923
2024-08-12 | 14:41 | 49.84
2024-08-12 | 14:42 | 49.786
2024-08-12 | 14:42 | 49.761
2024-08-12 | 14:42 | 49.755
2024-08-12 | 14:42 | 49.757
2024-08-12 | 14:42 | 49.759
2024-08-12 | 14:42 | 49.762
2024-08-12 | 14:42 | 49.764
2024-08-12 | 14:42 | 49.763
2024-08-12 | 14:42 | 49.765
2024-08-12 | 14:42 | 49.763
2024-08-12 | 14:42 | 49.764
2024-08-12 | 14:42 | 49.763
2024-08-12 | 14:42 | 49.762
2024-08-12 | 14:42 | 49.764
2024-08-12 | 14:42 | 49.77
2024-08-12 | 14:42 | 49.77
2024-08-12 | 14:42 | 49.77
2024-08-12 | 14:42 | 49.769
2024-08-12 | 14:42 | 49.769
2024-08-12 | 14:42 | 49.768
2024-08-12 | 14:42 | 49.768
2024-08-12 | 14:42 | 49.771
2024-08-12 | 14:42 | 49.771
2024-08-12 | 14:42 | 49.77
2024-08-12 | 14:42 | 49.77
2024-08-12 | 14:42 | 49.768
2024-08-12 | 14:42 | 49.767
2024-08-12 | 14:42 | 49.77
2024-08-12 | 14:42 | 49.774
2024-08-12 | 14:42 | 49.778
2024-08-12 | 14:42 | 49.775
2024-08-12 | 14:42 | 49.768
2024-08-12 | 14:42 | 49.766
2024-08-12 | 14:42 | 49.762
2024-08-12 | 14:42 | 49.766
2024-08-12 | 14:42 | 49.771
2024-08-12 | 14:42 | 49.778
2024-08-12 | 14:42 | 49.777
2024-08-12 | 14:42 | 49.779
2024-08-12 | 14:42 | 49.783
2024-08-12 | 14:42 | 49.786
2024-08-12 | 14:42 | 49.79
2024-08-12 | 14:42 | 49.794
2024-08-12 | 14:42 | 49.8
2024-08-12 | 14:42 | 49.81
2024-08-12 | 14:42 | 49.815
2024-08-12 | 14:42 | 49.818
2024-08-12 | 14:42 | 49.824
2024-08-12 | 14:42 | 49.831
2024-08-12 | 14:42 | 49.838
2024-08-12 | 14:42 | 49.842
2024-08-12 | 14:42 | 49.847
2024-08-12 | 14:42 | 49.852
2024-08-12 | 14:42 | 49.857
2024-08-12 | 14:42 | 49.86
2024-08-12 | 14:42 | 49.864
2024-08-12 | 14:42 | 49.869
2024-08-12 | 14:42 | 49.875
2024-08-12 | 14:42 | 49.879
2024-08-12 | 14:42 | 49.887
2024-08-12 | 14:42 | 49.888
2024-08-12 | 14:43 | 49.891
2024-08-12 | 14:43 | 49.893
2024-08-12 | 14:43 | 49.895
2024-08-12 | 14:43 | 49.894
2024-08-12 | 14:43 | 49.893
2024-08-12 | 14:43 | 49.892
2024-08-12 | 14:43 | 49.893
2024-08-12 | 14:43 | 49.897
2024-08-12 | 14:43 | 49.896
2024-08-12 | 14:43 | 49.897
2024-08-12 | 14:43 | 49.901
2024-08-12 | 14:43 | 49.9
2024-08-12 | 14:43 | 49.899
2024-08-12 | 14:43 | 49.894
2024-08-12 | 14:43 | 49.895
2024-08-12 | 14:43 | 49.894
2024-08-12 | 14:43 | 49.895
2024-08-12 | 14:43 | 49.898
2024-08-12 | 14:43 | 49.9
2024-08-12 | 14:43 | 49.902
2024-08-12 | 14:43 | 49.906
2024-08-12 | 14:43 | 49.91
2024-08-12 | 14:43 | 49.914
2024-08-12 | 14:43 | 49.915
2024-08-12 | 14:43 | 49.919
2024-08-12 | 14:43 | 49.92
2024-08-12 | 14:43 | 49.921
2024-08-12 | 14:43 | 49.92
2024-08-12 | 14:43 | 49.92
2024-08-12 | 14:43 | 49.922
2024-08-12 | 14:43 | 49.921
2024-08-12 | 14:43 | 49.924
2024-08-12 | 14:43 | 49.927
2024-08-12 | 14:43 | 49.933
2024-08-12 | 14:43 | 49.934
2024-08-12 | 14:43 | 49.933
2024-08-12 | 14:43 | 49.934
2024-08-12 | 14:43 | 49.939
2024-08-12 | 14:43 | 49.94
2024-08-12 | 14:43 | 49.942
2024-08-12 | 14:43 | 49.938
2024-08-12 | 14:43 | 49.936
2024-08-12 | 14:43 | 49.934
2024-08-12 | 14:43 | 49.932
2024-08-12 | 14:43 | 49.928
2024-08-12 | 14:43 | 49.928
2024-08-12 | 14:43 | 49.931
2024-08-12 | 14:43 | 49.932
2024-08-12 | 14:43 | 49.929
2024-08-12 | 14:43 | 49.928
2024-08-12 | 14:43 | 49.927
2024-08-12 | 14:43 | 49.928
2024-08-12 | 14:43 | 49.931
2024-08-12 | 14:43 | 49.932
2024-08-12 | 14:43 | 49.933
2024-08-12 | 14:43 | 49.93
2024-08-12 | 14:43 | 49.931
2024-08-12 | 14:43 | 49.935
2024-08-12 | 14:43 | 49.937
2024-08-12 | 14:44 | 49.936
2024-08-12 | 14:44 | 49.932
2024-08-12 | 14:44 | 49.931
2024-08-12 | 14:44 | 49.928
2024-08-12 | 14:44 | 49.925
2024-08-12 | 14:44 | 49.927
2024-08-12 | 14:44 | 49.929
2024-08-12 | 14:44 | 49.928
2024-08-12 | 14:44 | 49.929
2024-08-12 | 14:44 | 49.929
2024-08-12 | 14:44 | 49.932
2024-08-12 | 14:44 | 49.929
2024-08-12 | 14:44 | 49.93
2024-08-12 | 14:44 | 49.93
2024-08-12 | 14:44 | 49.932
2024-08-12 | 14:44 | 49.933
2024-08-12 | 14:44 | 49.934
2024-08-12 | 14:44 | 49.931
2024-08-12 | 14:44 | 49.934
2024-08-12 | 14:44 | 49.935
2024-08-12 | 14:44 | 49.932
2024-08-12 | 14:44 | 49.935
2024-08-12 | 14:44 | 49.934
2024-08-12 | 14:44 | 49.932
2024-08-12 | 14:44 | 49.93
2024-08-12 | 14:44 | 49.932
2024-08-12 | 14:44 | 49.931
2024-08-12 | 14:44 | 49.933
2024-08-12 | 14:44 | 49.934
2024-08-12 | 14:44 | 49.937
2024-08-12 | 14:44 | 49.934
2024-08-12 | 14:44 | 49.932
2024-08-12 | 14:44 | 49.934
2024-08-12 | 14:44 | 49.932
2024-08-12 | 14:44 | 49.928
2024-08-12 | 14:44 | 49.926
2024-08-12 | 14:44 | 49.928
2024-08-12 | 14:44 | 49.926
2024-08-12 | 14:44 | 49.922
2024-08-12 | 14:44 | 49.92
2024-08-12 | 14:44 | 49.92
2024-08-12 | 14:44 | 49.921
2024-08-12 | 14:44 | 49.921
2024-08-12 | 14:44 | 49.921
2024-08-12 | 14:44 | 49.924
2024-08-12 | 14:44 | 49.923
2024-08-12 | 14:44 | 49.926
2024-08-12 | 14:44 | 49.929
2024-08-12 | 14:44 | 49.926
2024-08-12 | 14:44 | 49.927
2024-08-12 | 14:44 | 49.927
2024-08-12 | 14:44 | 49.93
2024-08-12 | 14:44 | 49.935
2024-08-12 | 14:44 | 49.936
2024-08-12 | 14:44 | 49.938
2024-08-12 | 14:44 | 49.94
2024-08-12 | 14:44 | 49.942
2024-08-12 | 14:44 | 49.945
2024-08-12 | 14:44 | 49.947
2024-08-12 | 14:44 | 49.952
2024-08-12 | 14:44 | 49.957
2024-08-12 | 14:45 | 49.961
2024-08-12 | 14:45 | 49.969
2024-08-12 | 14:45 | 49.979
2024-08-12 | 14:45 | 49.988
2024-08-12 | 14:45 | 49.994
2024-08-12 | 14:45 | 49.994
2024-08-12 | 14:45 | 49.998
2024-08-12 | 14:45 | 49.998
2024-08-12 | 14:45 | 49.996
2024-08-12 | 14:45 | 49.996
2024-08-12 | 14:45 | 49.997
2024-08-12 | 14:45 | 49.995
2024-08-12 | 14:45 | 49.996
2024-08-12 | 14:45 | 49.99
2024-08-12 | 14:45 | 49.989
2024-08-12 | 14:45 | 49.985
2024-08-12 | 14:45 | 49.982
2024-08-12 | 14:45 | 49.982
2024-08-12 | 14:45 | 49.983
2024-08-12 | 14:45 | 49.981
2024-08-12 | 14:45 | 49.978
2024-08-12 | 14:45 | 49.977
2024-08-12 | 14:45 | 49.978
2024-08-12 | 14:45 | 49.98
2024-08-12 | 14:45 | 49.982
2024-08-12 | 14:45 | 49.981
2024-08-12 | 14:45 | 49.978
2024-08-12 | 14:45 | 49.976
2024-08-12 | 14:45 | 49.973
2024-08-12 | 14:45 | 49.972
2024-08-12 | 14:45 | 49.971
2024-08-12 | 14:45 | 49.969
2024-08-12 | 14:45 | 49.965
2024-08-12 | 14:45 | 49.964
2024-08-12 | 14:45 | 49.962
2024-08-12 | 14:45 | 49.965
2024-08-12 | 14:45 | 49.964
2024-08-12 | 14:45 | 49.962
2024-08-12 | 14:45 | 49.96
2024-08-12 | 14:45 | 49.954
2024-08-12 | 14:45 | 49.951
2024-08-12 | 14:45 | 49.95
2024-08-12 | 14:45 | 49.951
2024-08-12 | 14:45 | 49.952
2024-08-12 | 14:45 | 49.95
2024-08-12 | 14:45 | 49.952
2024-08-12 | 14:45 | 49.952
2024-08-12 | 14:45 | 49.95
2024-08-12 | 14:45 | 49.95
2024-08-12 | 14:45 | 49.95
2024-08-12 | 14:45 | 49.952
2024-08-12 | 14:45 | 49.951
2024-08-12 | 14:45 | 49.955
2024-08-12 | 14:45 | 49.955
2024-08-12 | 14:45 | 49.958
2024-08-12 | 14:45 | 49.96
2024-08-12 | 14:45 | 49.96
2024-08-12 | 14:45 | 49.963
2024-08-12 | 14:45 | 49.967
2024-08-12 | 14:46 | 49.968
2024-08-12 | 14:46 | 49.97
2024-08-12 | 14:46 | 49.971
2024-08-12 | 14:46 | 49.969
2024-08-12 | 14:46 | 49.966
2024-08-12 | 14:46 | 49.968
2024-08-12 | 14:46 | 49.969
2024-08-12 | 14:46 | 49.97
2024-08-12 | 14:46 | 49.971
2024-08-12 | 14:46 | 49.971
2024-08-12 | 14:46 | 49.971
2024-08-12 | 14:46 | 49.967
2024-08-12 | 14:46 | 49.963
2024-08-12 | 14:46 | 49.963
2024-08-12 | 14:46 | 49.966
2024-08-12 | 14:46 | 49.967
2024-08-12 | 14:46 | 49.968
2024-08-12 | 14:46 | 49.968
2024-08-12 | 14:46 | 49.967
2024-08-12 | 14:46 | 49.964
2024-08-12 | 14:46 | 49.966
2024-08-12 | 14:46 | 49.969
2024-08-12 | 14:46 | 49.971
2024-08-12 | 14:46 | 49.97
2024-08-12 | 14:46 | 49.972
2024-08-12 | 14:46 | 49.972
2024-08-12 | 14:46 | 49.973
2024-08-12 | 14:46 | 49.971
2024-08-12 | 14:46 | 49.97
2024-08-12 | 14:46 | 49.968
2024-08-12 | 14:46 | 49.973
2024-08-12 | 14:46 | 49.971
2024-08-12 | 14:46 | 49.969
2024-08-12 | 14:46 | 49.97
2024-08-12 | 14:46 | 49.967
2024-08-12 | 14:46 | 49.965
2024-08-12 | 14:46 | 49.963
2024-08-12 | 14:46 | 49.958
2024-08-12 | 14:46 | 49.955
2024-08-12 | 14:46 | 49.957
2024-08-12 | 14:46 | 49.961
2024-08-12 | 14:46 | 49.962
2024-08-12 | 14:46 | 49.962
2024-08-12 | 14:46 | 49.958
2024-08-12 | 14:46 | 49.962
2024-08-12 | 14:46 | 49.966
2024-08-12 | 14:46 | 49.966
2024-08-12 | 14:46 | 49.963
2024-08-12 | 14:46 | 49.963
2024-08-12 | 14:46 | 49.961
2024-08-12 | 14:46 | 49.959
2024-08-12 | 14:46 | 49.961
2024-08-12 | 14:46 | 49.958
2024-08-12 | 14:46 | 49.953
2024-08-12 | 14:46 | 49.951
2024-08-12 | 14:46 | 49.952
2024-08-12 | 14:46 | 49.955
2024-08-12 | 14:46 | 49.955
2024-08-12 | 14:46 | 49.955
2024-08-12 | 14:46 | 49.957
2024-08-12 | 14:46 | 49.96
2024-08-12 | 14:47 | 49.965
2024-08-12 | 14:47 | 49.967
2024-08-12 | 14:47 | 49.97
2024-08-12 | 14:47 | 49.974
2024-08-12 | 14:47 | 49.974
2024-08-12 | 14:47 | 49.972
2024-08-12 | 14:47 | 49.972
2024-08-12 | 14:47 | 49.972
2024-08-12 | 14:47 | 49.973
2024-08-12 | 14:47 | 49.975
2024-08-12 | 14:47 | 49.978
2024-08-12 | 14:47 | 49.978
2024-08-12 | 14:47 | 49.98
2024-08-12 | 14:47 | 49.985
2024-08-12 | 14:47 | 49.989
2024-08-12 | 14:47 | 49.995
2024-08-12 | 14:47 | 50.003
2024-08-12 | 14:47 | 50.009
2024-08-12 | 14:47 | 50.019
2024-08-12 | 14:47 | 50.023
2024-08-12 | 14:47 | 50.021
2024-08-12 | 14:47 | 50.018
2024-08-12 | 14:47 | 50.016
2024-08-12 | 14:47 | 50.013
2024-08-12 | 14:47 | 50.009
2024-08-12 | 14:47 | 50.007
2024-08-12 | 14:47 | 50.012
2024-08-12 | 14:47 | 50.014
2024-08-12 | 14:47 | 50.018
2024-08-12 | 14:47 | 50.02
2024-08-12 | 14:47 | 50.022
2024-08-12 | 14:47 | 50.024
2024-08-12 | 14:47 | 50.026
2024-08-12 | 14:47 | 50.025
2024-08-12 | 14:47 | 50.026
2024-08-12 | 14:47 | 50.024
2024-08-12 | 14:47 | 50.026
2024-08-12 | 14:47 | 50.027
2024-08-12 | 14:47 | 50.027
2024-08-12 | 14:47 | 50.023
2024-08-12 | 14:47 | 50.021
2024-08-12 | 14:47 | 50.019
2024-08-12 | 14:47 | 50.014
2024-08-12 | 14:47 | 50.01
2024-08-12 | 14:47 | 50.006
2024-08-12 | 14:47 | 50.004
2024-08-12 | 14:47 | 50.001
2024-08-12 | 14:47 | 49.997
2024-08-12 | 14:47 | 49.997
2024-08-12 | 14:47 | 50.005
2024-08-12 | 14:47 | 50.009
2024-08-12 | 14:47 | 50.012
2024-08-12 | 14:47 | 50.015
2024-08-12 | 14:47 | 50.016
2024-08-12 | 14:47 | 50.014
2024-08-12 | 14:47 | 50.009
2024-08-12 | 14:47 | 50.007
2024-08-12 | 14:47 | 50.002
2024-08-12 | 14:47 | 49.996
2024-08-12 | 14:48 | 49.994
2024-08-12 | 14:48 | 49.995
2024-08-12 | 14:48 | 49.997
2024-08-12 | 14:48 | 50.002
2024-08-12 | 14:48 | 50.005
2024-08-12 | 14:48 | 50.011
2024-08-12 | 14:48 | 50.012
2024-08-12 | 14:48 | 50.012
2024-08-12 | 14:48 | 50.015
2024-08-12 | 14:48 | 50.018
2024-08-12 | 14:48 | 50.02
2024-08-12 | 14:48 | 50.02
2024-08-12 | 14:48 | 50.02
2024-08-12 | 14:48 | 50.018
2024-08-12 | 14:48 | 50.021
2024-08-12 | 14:48 | 50.02
2024-08-12 | 14:48 | 50.023
2024-08-12 | 14:48 | 50.025
2024-08-12 | 14:48 | 50.026
2024-08-12 | 14:48 | 50.023
2024-08-12 | 14:48 | 50.021
2024-08-12 | 14:48 | 50.022
2024-08-12 | 14:48 | 50.027
2024-08-12 | 14:48 | 50.029
2024-08-12 | 14:48 | 50.029
2024-08-12 | 14:48 | 50.029
2024-08-12 | 14:48 | 50.028
2024-08-12 | 14:48 | 50.029
2024-08-12 | 14:48 | 50.028
2024-08-12 | 14:48 | 50.032
2024-08-12 | 14:48 | 50.034

## 20240822-1
In GMT
Date | Time | Freq
2024-08-21 | 23:15 | 50.059 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-08-21 | 23:15 | 50.055 | 222 | BRITNED | 676.211
2024-08-21 | 23:15 | 50.052 | 268 | WBURB-2 | 428.156
2024-08-21 | 23:15 | 50.052 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-08-21 | 23:15 | 50.055 |  | Viking Link | -648.9
2024-08-21 | 23:15 | 50.055 |  | Viking Link | 1398.96
2024-08-21 | 23:15 | 50.058 | 209 | DRAXX-3 | 626.95
2024-08-21 | 23:15 | 50.06 | 154 | CDCL-1 | 391.57
2024-08-21 | 23:15 | 50.062 | 268 | ROCK-1 | 468.495
2024-08-21 | 23:15 | 50.065 | 148 | IFA Bipole1 | 945.473
2024-08-21 | 23:15 | 50.063 | 132 | IFA Bipole1 | 999.1
2024-08-21 | 23:15 | 50.061 | 141 | IFA Bipole2 | 1000
2024-08-21 | 23:15 | 50.06 | 135 | IFA Bipole1 | 996.75
2024-08-21 | 23:15 | 50.06 |  | Viking Link | -780.3
2024-08-21 | 23:15 | 50.061
2024-08-21 | 23:15 | 50.062
2024-08-21 | 23:15 | 50.064
2024-08-21 | 23:15 | 50.065
2024-08-21 | 23:15 | 50.059
2024-08-21 | 23:15 | 50.06 | 130 | HEYM12 | 271.908
2024-08-21 | 23:15 | 50.057 | 228 | HUMR-1 | 303.75
2024-08-21 | 23:15 | 50.057
2024-08-21 | 23:15 | 50.057
2024-08-21 | 23:15 | 50.057
2024-08-21 | 23:15 | 50.06
2024-08-21 | 23:15 | 50.062
2024-08-21 | 23:15 | 50.06
2024-08-21 | 23:15 | 50.063
2024-08-21 | 23:15 | 50.064
2024-08-21 | 23:15 | 50.065
2024-08-21 | 23:16 | 50.065 | 211 | CDCL-1 | 291.5
2024-08-21 | 23:16 | 50.067 | 199 | STAY-2 | 413.125
2024-08-21 | 23:16 | 50.066 | 173 | CDCL-1 | 397.375
2024-08-21 | 23:16 | 50.068 | 248 | SEAB-2 | 361.25
2024-08-21 | 23:16 | 50.067 | 255 | FRANCE | 995.65
2024-08-21 | 23:16 | 50.067 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-08-21 | 23:16 | 50.063
2024-08-21 | 23:16 | 50.06
2024-08-21 | 23:16 | 50.058
2024-08-21 | 23:16 | 50.058
2024-08-21 | 23:16 | 50.057
2024-08-21 | 23:16 | 50.055
2024-08-21 | 23:16 | 50.054
2024-08-21 | 23:16 | 50.055
2024-08-21 | 23:16 | 50.057
2024-08-21 | 23:16 | 50.058
2024-08-21 | 23:16 | 50.059
2024-08-21 | 23:16 | 50.061
2024-08-21 | 23:16 | 50.06
2024-08-21 | 23:16 | 50.061
2024-08-21 | 23:16 | 50.062
2024-08-21 | 23:16 | 50.062
2024-08-21 | 23:16 | 50.061
2024-08-21 | 23:16 | 50.059
2024-08-21 | 23:16 | 50.059
2024-08-21 | 23:16 | 50.058
2024-08-21 | 23:16 | 50.058
2024-08-21 | 23:16 | 50.059
2024-08-21 | 23:16 | 50.062
2024-08-21 | 23:16 | 50.063
2024-08-21 | 23:16 | 50.065
2024-08-21 | 23:16 | 50.063
2024-08-21 | 23:16 | 50.059
2024-08-21 | 23:16 | 50.056
2024-08-21 | 23:16 | 50.053
2024-08-21 | 23:16 | 50.053
2024-08-21 | 23:16 | 50.052
2024-08-21 | 23:16 | 50.05
2024-08-21 | 23:16 | 50.049
2024-08-21 | 23:16 | 50.05
2024-08-21 | 23:16 | 50.051
2024-08-21 | 23:16 | 50.054
2024-08-21 | 23:16 | 50.052
2024-08-21 | 23:16 | 50.05
2024-08-21 | 23:16 | 50.043
2024-08-21 | 23:16 | 50.039
2024-08-21 | 23:16 | 50.035
2024-08-21 | 23:16 | 50.11
2024-08-21 | 23:16 | 50.158
2024-08-21 | 23:16 | 50.222
2024-08-21 | 23:16 | 50.238
2024-08-21 | 23:16 | 50.23
2024-08-21 | 23:16 | 50.222
2024-08-21 | 23:16 | 50.213
2024-08-21 | 23:16 | 50.206
2024-08-21 | 23:16 | 50.207
2024-08-21 | 23:16 | 50.209
2024-08-21 | 23:16 | 50.209
2024-08-21 | 23:16 | 50.209
2024-08-21 | 23:16 | 50.21
2024-08-21 | 23:16 | 50.213
2024-08-21 | 23:17 | 50.211
2024-08-21 | 23:17 | 50.208
2024-08-21 | 23:17 | 50.207
2024-08-21 | 23:17 | 50.209
2024-08-21 | 23:17 | 50.211
2024-08-21 | 23:17 | 50.215
2024-08-21 | 23:17 | 50.217
2024-08-21 | 23:17 | 50.217
2024-08-21 | 23:17 | 50.218
2024-08-21 | 23:17 | 50.22
2024-08-21 | 23:17 | 50.224
2024-08-21 | 23:17 | 50.223
2024-08-21 | 23:17 | 50.222
2024-08-21 | 23:17 | 50.225
2024-08-21 | 23:17 | 50.224
2024-08-21 | 23:17 | 50.22
2024-08-21 | 23:17 | 50.22
2024-08-21 | 23:17 | 50.22
2024-08-21 | 23:17 | 50.219
2024-08-21 | 23:17 | 50.218
2024-08-21 | 23:17 | 50.22
2024-08-21 | 23:17 | 50.219
2024-08-21 | 23:17 | 50.219
2024-08-21 | 23:17 | 50.219
2024-08-21 | 23:17 | 50.217
2024-08-21 | 23:17 | 50.218
2024-08-21 | 23:17 | 50.22
2024-08-21 | 23:17 | 50.22
2024-08-21 | 23:17 | 50.217
2024-08-21 | 23:17 | 50.218
2024-08-21 | 23:17 | 50.221
2024-08-21 | 23:17 | 50.217
2024-08-21 | 23:17 | 50.22
2024-08-21 | 23:17 | 50.22
2024-08-21 | 23:17 | 50.223
2024-08-21 | 23:17 | 50.223
2024-08-21 | 23:17 | 50.221
2024-08-21 | 23:17 | 50.225
2024-08-21 | 23:17 | 50.229
2024-08-21 | 23:17 | 50.228
2024-08-21 | 23:17 | 50.231
2024-08-21 | 23:17 | 50.231
2024-08-21 | 23:17 | 50.23
2024-08-21 | 23:17 | 50.224
2024-08-21 | 23:17 | 50.23
2024-08-21 | 23:17 | 50.23
2024-08-21 | 23:17 | 50.231
2024-08-21 | 23:17 | 50.237
2024-08-21 | 23:17 | 50.238
2024-08-21 | 23:17 | 50.239
2024-08-21 | 23:17 | 50.241
2024-08-21 | 23:17 | 50.242
2024-08-21 | 23:17 | 50.244
2024-08-21 | 23:17 | 50.247
2024-08-21 | 23:17 | 50.247
2024-08-21 | 23:17 | 50.245
2024-08-21 | 23:17 | 50.242
2024-08-21 | 23:17 | 50.241
2024-08-21 | 23:17 | 50.239
2024-08-21 | 23:18 | 50.238
2024-08-21 | 23:18 | 50.241
2024-08-21 | 23:18 | 50.242
2024-08-21 | 23:18 | 50.244
2024-08-21 | 23:18 | 50.243
2024-08-21 | 23:18 | 50.243
2024-08-21 | 23:18 | 50.246
2024-08-21 | 23:18 | 50.243
2024-08-21 | 23:18 | 50.242
2024-08-21 | 23:18 | 50.242
2024-08-21 | 23:18 | 50.242
2024-08-21 | 23:18 | 50.247
2024-08-21 | 23:18 | 50.246
2024-08-21 | 23:18 | 50.245
2024-08-21 | 23:18 | 50.245
2024-08-21 | 23:18 | 50.244
2024-08-21 | 23:18 | 50.245
2024-08-21 | 23:18 | 50.248
2024-08-21 | 23:18 | 50.247
2024-08-21 | 23:18 | 50.244
2024-08-21 | 23:18 | 50.243
2024-08-21 | 23:18 | 50.247
2024-08-21 | 23:18 | 50.249
2024-08-21 | 23:18 | 50.248
2024-08-21 | 23:18 | 50.251
2024-08-21 | 23:18 | 50.25
2024-08-21 | 23:18 | 50.25
2024-08-21 | 23:18 | 50.247
2024-08-21 | 23:18 | 50.246
2024-08-21 | 23:18 | 50.242
2024-08-21 | 23:18 | 50.233
2024-08-21 | 23:18 | 50.223
2024-08-21 | 23:18 | 50.215
2024-08-21 | 23:18 | 50.212
2024-08-21 | 23:18 | 50.212
2024-08-21 | 23:18 | 50.212
2024-08-21 | 23:18 | 50.212
2024-08-21 | 23:18 | 50.209
2024-08-21 | 23:18 | 50.203
2024-08-21 | 23:18 | 50.2
2024-08-21 | 23:18 | 50.199
2024-08-21 | 23:18 | 50.201
2024-08-21 | 23:18 | 50.201
2024-08-21 | 23:18 | 50.203
2024-08-21 | 23:18 | 50.204
2024-08-21 | 23:18 | 50.203
2024-08-21 | 23:18 | 50.205
2024-08-21 | 23:18 | 50.204
2024-08-21 | 23:18 | 50.205
2024-08-21 | 23:18 | 50.205
2024-08-21 | 23:18 | 50.201
2024-08-21 | 23:18 | 50.202
2024-08-21 | 23:18 | 50.202
2024-08-21 | 23:18 | 50.206
2024-08-21 | 23:18 | 50.204
2024-08-21 | 23:18 | 50.206
2024-08-21 | 23:18 | 50.206
2024-08-21 | 23:18 | 50.207
2024-08-21 | 23:18 | 50.211
2024-08-21 | 23:18 | 50.211
2024-08-21 | 23:18 | 50.206
2024-08-21 | 23:19 | 50.202
2024-08-21 | 23:19 | 50.198
2024-08-21 | 23:19 | 50.195
2024-08-21 | 23:19 | 50.193
2024-08-21 | 23:19 | 50.194
2024-08-21 | 23:19 | 50.196
2024-08-21 | 23:19 | 50.198
2024-08-21 | 23:19 | 50.196
2024-08-21 | 23:19 | 50.193
2024-08-21 | 23:19 | 50.194
2024-08-21 | 23:19 | 50.196
2024-08-21 | 23:19 | 50.195
2024-08-21 | 23:19 | 50.191
2024-08-21 | 23:19 | 50.19
2024-08-21 | 23:19 | 50.19
2024-08-21 | 23:19 | 50.192
2024-08-21 | 23:19 | 50.191
2024-08-21 | 23:19 | 50.192
2024-08-21 | 23:19 | 50.192
2024-08-21 | 23:19 | 50.188
2024-08-21 | 23:19 | 50.187
2024-08-21 | 23:19 | 50.187
2024-08-21 | 23:19 | 50.186
2024-08-21 | 23:19 | 50.189
2024-08-21 | 23:19 | 50.189
2024-08-21 | 23:19 | 50.189
2024-08-21 | 23:19 | 50.189
2024-08-21 | 23:19 | 50.185
2024-08-21 | 23:19 | 50.186
2024-08-21 | 23:19 | 50.183
2024-08-21 | 23:19 | 50.181
2024-08-21 | 23:19 | 50.175
2024-08-21 | 23:19 | 50.175
2024-08-21 | 23:19 | 50.175
2024-08-21 | 23:19 | 50.177
2024-08-21 | 23:19 | 50.177
2024-08-21 | 23:19 | 50.176
2024-08-21 | 23:19 | 50.174
2024-08-21 | 23:19 | 50.172
2024-08-21 | 23:19 | 50.17
2024-08-21 | 23:19 | 50.171
2024-08-21 | 23:19 | 50.169
2024-08-21 | 23:19 | 50.17
2024-08-21 | 23:19 | 50.168
2024-08-21 | 23:19 | 50.168
2024-08-21 | 23:19 | 50.168
2024-08-21 | 23:19 | 50.168
2024-08-21 | 23:19 | 50.165
2024-08-21 | 23:19 | 50.162
2024-08-21 | 23:19 | 50.164
2024-08-21 | 23:19 | 50.163
2024-08-21 | 23:19 | 50.157
2024-08-21 | 23:19 | 50.155
2024-08-21 | 23:19 | 50.154
2024-08-21 | 23:19 | 50.153
2024-08-21 | 23:19 | 50.15
2024-08-21 | 23:19 | 50.15
2024-08-21 | 23:19 | 50.15
2024-08-21 | 23:19 | 50.146
2024-08-21 | 23:20 | 50.147
2024-08-21 | 23:20 | 50.149
2024-08-21 | 23:20 | 50.15
2024-08-21 | 23:20 | 50.147
2024-08-21 | 23:20 | 50.144
2024-08-21 | 23:20 | 50.146
2024-08-21 | 23:20 | 50.147
2024-08-21 | 23:20 | 50.146
2024-08-21 | 23:20 | 50.145
2024-08-21 | 23:20 | 50.145
2024-08-21 | 23:20 | 50.144
2024-08-21 | 23:20 | 50.143
2024-08-21 | 23:20 | 50.141
2024-08-21 | 23:20 | 50.143
2024-08-21 | 23:20 | 50.144
2024-08-21 | 23:20 | 50.143
2024-08-21 | 23:20 | 50.144
2024-08-21 | 23:20 | 50.148
2024-08-21 | 23:20 | 50.147
2024-08-21 | 23:20 | 50.145
2024-08-21 | 23:20 | 50.142
2024-08-21 | 23:20 | 50.141
2024-08-21 | 23:20 | 50.14
2024-08-21 | 23:20 | 50.14
2024-08-21 | 23:20 | 50.136
2024-08-21 | 23:20 | 50.138
2024-08-21 | 23:20 | 50.139
2024-08-21 | 23:20 | 50.133
2024-08-21 | 23:20 | 50.129
2024-08-21 | 23:20 | 50.129
2024-08-21 | 23:20 | 50.129
2024-08-21 | 23:20 | 50.124
2024-08-21 | 23:20 | 50.122
2024-08-21 | 23:20 | 50.12
2024-08-21 | 23:20 | 50.122
2024-08-21 | 23:20 | 50.122
2024-08-21 | 23:20 | 50.122
2024-08-21 | 23:20 | 50.121
2024-08-21 | 23:20 | 50.119
2024-08-21 | 23:20 | 50.117
2024-08-21 | 23:20 | 50.119
2024-08-21 | 23:20 | 50.119
2024-08-21 | 23:20 | 50.117
2024-08-21 | 23:20 | 50.117
2024-08-21 | 23:20 | 50.12
2024-08-21 | 23:20 | 50.12
2024-08-21 | 23:20 | 50.116
2024-08-21 | 23:20 | 50.113
2024-08-21 | 23:20 | 50.113
2024-08-21 | 23:20 | 50.112
2024-08-21 | 23:20 | 50.114
2024-08-21 | 23:20 | 50.114
2024-08-21 | 23:20 | 50.115
2024-08-21 | 23:20 | 50.116
2024-08-21 | 23:20 | 50.114
2024-08-21 | 23:20 | 50.115
2024-08-21 | 23:20 | 50.114
2024-08-21 | 23:20 | 50.115
2024-08-21 | 23:20 | 50.113
2024-08-21 | 23:20 | 50.111
2024-08-21 | 23:20 | 50.113
2024-08-21 | 23:21 | 50.111
2024-08-21 | 23:21 | 50.11
2024-08-21 | 23:21 | 50.109
2024-08-21 | 23:21 | 50.109
2024-08-21 | 23:21 | 50.11
2024-08-21 | 23:21 | 50.109
2024-08-21 | 23:21 | 50.114
2024-08-21 | 23:21 | 50.116
2024-08-21 | 23:21 | 50.114
2024-08-21 | 23:21 | 50.112
2024-08-21 | 23:21 | 50.11
2024-08-21 | 23:21 | 50.109
2024-08-21 | 23:21 | 50.111
2024-08-21 | 23:21 | 50.111
2024-08-21 | 23:21 | 50.114
2024-08-21 | 23:21 | 50.116
2024-08-21 | 23:21 | 50.113
2024-08-21 | 23:21 | 50.113
2024-08-21 | 23:21 | 50.11
2024-08-21 | 23:21 | 50.108
2024-08-21 | 23:21 | 50.109
2024-08-21 | 23:21 | 50.107
2024-08-21 | 23:21 | 50.108
2024-08-21 | 23:21 | 50.109
2024-08-21 | 23:21 | 50.107
2024-08-21 | 23:21 | 50.107
2024-08-21 | 23:21 | 50.108
2024-08-21 | 23:21 | 50.107
2024-08-21 | 23:21 | 50.109
2024-08-21 | 23:21 | 50.109
2024-08-21 | 23:21 | 50.109
2024-08-21 | 23:21 | 50.108
2024-08-21 | 23:21 | 50.105
2024-08-21 | 23:21 | 50.102
2024-08-21 | 23:21 | 50.101
2024-08-21 | 23:21 | 50.102
2024-08-21 | 23:21 | 50.101
2024-08-21 | 23:21 | 50.097
2024-08-21 | 23:21 | 50.096
2024-08-21 | 23:21 | 50.095
2024-08-21 | 23:21 | 50.096
2024-08-21 | 23:21 | 50.1
2024-08-21 | 23:21 | 50.106
2024-08-21 | 23:21 | 50.105
2024-08-21 | 23:21 | 50.104
2024-08-21 | 23:21 | 50.102
2024-08-21 | 23:21 | 50.101
2024-08-21 | 23:21 | 50.102
2024-08-21 | 23:21 | 50.101
2024-08-21 | 23:21 | 50.102
2024-08-21 | 23:21 | 50.101
2024-08-21 | 23:21 | 50.093
2024-08-21 | 23:21 | 50.09
2024-08-21 | 23:21 | 50.09
2024-08-21 | 23:21 | 50.088
2024-08-21 | 23:21 | 50.086
2024-08-21 | 23:21 | 50.087
2024-08-21 | 23:21 | 50.088
2024-08-21 | 23:21 | 50.089
2024-08-21 | 23:22 | 50.091
2024-08-21 | 23:22 | 50.091
2024-08-21 | 23:22 | 50.089
2024-08-21 | 23:22 | 50.087
2024-08-21 | 23:22 | 50.083
2024-08-21 | 23:22 | 50.082
2024-08-21 | 23:22 | 50.083
2024-08-21 | 23:22 | 50.087
2024-08-21 | 23:22 | 50.089
2024-08-21 | 23:22 | 50.093
2024-08-21 | 23:22 | 50.091
2024-08-21 | 23:22 | 50.09
2024-08-21 | 23:22 | 50.088
2024-08-21 | 23:22 | 50.09
2024-08-21 | 23:22 | 50.091
2024-08-21 | 23:22 | 50.09
2024-08-21 | 23:22 | 50.088
2024-08-21 | 23:22 | 50.088
2024-08-21 | 23:22 | 50.088
2024-08-21 | 23:22 | 50.087
2024-08-21 | 23:22 | 50.085
2024-08-21 | 23:22 | 50.086
2024-08-21 | 23:22 | 50.086
2024-08-21 | 23:22 | 50.084
2024-08-21 | 23:22 | 50.083
2024-08-21 | 23:22 | 50.083
2024-08-21 | 23:22 | 50.082
2024-08-21 | 23:22 | 50.081
2024-08-21 | 23:22 | 50.078
2024-08-21 | 23:22 | 50.075
2024-08-21 | 23:22 | 50.073
2024-08-21 | 23:22 | 50.07
2024-08-21 | 23:22 | 50.07
2024-08-21 | 23:22 | 50.069
2024-08-21 | 23:22 | 50.065
2024-08-21 | 23:22 | 50.066
2024-08-21 | 23:22 | 50.069
2024-08-21 | 23:22 | 50.069
2024-08-21 | 23:22 | 50.07
2024-08-21 | 23:22 | 50.068
2024-08-21 | 23:22 | 50.067
2024-08-21 | 23:22 | 50.069
2024-08-21 | 23:22 | 50.07
2024-08-21 | 23:22 | 50.072
2024-08-21 | 23:22 | 50.073
2024-08-21 | 23:22 | 50.073
2024-08-21 | 23:22 | 50.073
2024-08-21 | 23:22 | 50.073
2024-08-21 | 23:22 | 50.074
2024-08-21 | 23:22 | 50.073
2024-08-21 | 23:22 | 50.072
2024-08-21 | 23:22 | 50.071
2024-08-21 | 23:22 | 50.069
2024-08-21 | 23:22 | 50.072
2024-08-21 | 23:22 | 50.073
2024-08-21 | 23:22 | 50.071
2024-08-21 | 23:22 | 50.076
2024-08-21 | 23:22 | 50.08
2024-08-21 | 23:22 | 50.08
2024-08-21 | 23:22 | 50.076
2024-08-21 | 23:22 | 50.073
2024-08-21 | 23:23 | 50.068
2024-08-21 | 23:23 | 50.066
2024-08-21 | 23:23 | 50.064
2024-08-21 | 23:23 | 50.064
2024-08-21 | 23:23 | 50.061
2024-08-21 | 23:23 | 50.059
2024-08-21 | 23:23 | 50.058
2024-08-21 | 23:23 | 50.057
2024-08-21 | 23:23 | 50.055
2024-08-21 | 23:23 | 50.054
2024-08-21 | 23:23 | 50.054
2024-08-21 | 23:23 | 50.053
2024-08-21 | 23:23 | 50.051
2024-08-21 | 23:23 | 50.048
2024-08-21 | 23:23 | 50.046
2024-08-21 | 23:23 | 50.047
2024-08-21 | 23:23 | 50.047
2024-08-21 | 23:23 | 50.047
2024-08-21 | 23:23 | 50.049
2024-08-21 | 23:23 | 50.05
2024-08-21 | 23:23 | 50.05
2024-08-21 | 23:23 | 50.051
2024-08-21 | 23:23 | 50.055
2024-08-21 | 23:23 | 50.054
2024-08-21 | 23:23 | 50.05
2024-08-21 | 23:23 | 50.046
2024-08-21 | 23:23 | 50.044
2024-08-21 | 23:23 | 50.043
2024-08-21 | 23:23 | 50.042
2024-08-21 | 23:23 | 50.043
2024-08-21 | 23:23 | 50.044
2024-08-21 | 23:23 | 50.046
2024-08-21 | 23:23 | 50.046
2024-08-21 | 23:23 | 50.049
2024-08-21 | 23:23 | 50.053
2024-08-21 | 23:23 | 50.053
2024-08-21 | 23:23 | 50.05
2024-08-21 | 23:23 | 50.051
2024-08-21 | 23:23 | 50.051
2024-08-21 | 23:23 | 50.05
2024-08-21 | 23:23 | 50.049
2024-08-21 | 23:23 | 50.051
2024-08-21 | 23:23 | 50.054
2024-08-21 | 23:23 | 50.054
2024-08-21 | 23:23 | 50.053
2024-08-21 | 23:23 | 50.052
2024-08-21 | 23:23 | 50.052
2024-08-21 | 23:23 | 50.049
2024-08-21 | 23:23 | 50.046
2024-08-21 | 23:23 | 50.047
2024-08-21 | 23:23 | 50.048
2024-08-21 | 23:23 | 50.049
2024-08-21 | 23:23 | 50.049
2024-08-21 | 23:23 | 50.049
2024-08-21 | 23:23 | 50.05
2024-08-21 | 23:23 | 50.049
2024-08-21 | 23:23 | 50.049
2024-08-21 | 23:23 | 50.05
2024-08-21 | 23:23 | 50.049
2024-08-21 | 23:24 | 50.047
2024-08-21 | 23:24 | 50.046
2024-08-21 | 23:24 | 50.044
2024-08-21 | 23:24 | 50.042
2024-08-21 | 23:24 | 50.039
2024-08-21 | 23:24 | 50.037
2024-08-21 | 23:24 | 50.038
2024-08-21 | 23:24 | 50.04
2024-08-21 | 23:24 | 50.042
2024-08-21 | 23:24 | 50.044
2024-08-21 | 23:24 | 50.042
2024-08-21 | 23:24 | 50.04
2024-08-21 | 23:24 | 50.04
2024-08-21 | 23:24 | 50.039
2024-08-21 | 23:24 | 50.041
2024-08-21 | 23:24 | 50.04
2024-08-21 | 23:24 | 50.038
2024-08-21 | 23:24 | 50.042
2024-08-21 | 23:24 | 50.05
2024-08-21 | 23:24 | 50.058
2024-08-21 | 23:24 | 50.063
2024-08-21 | 23:24 | 50.067
2024-08-21 | 23:24 | 50.065
2024-08-21 | 23:24 | 50.062
2024-08-21 | 23:24 | 50.056
2024-08-21 | 23:24 | 50.057
2024-08-21 | 23:24 | 50.058
2024-08-21 | 23:24 | 50.059
2024-08-21 | 23:24 | 50.061
2024-08-21 | 23:24 | 50.061
2024-08-21 | 23:24 | 50.061
2024-08-21 | 23:24 | 50.058
2024-08-21 | 23:24 | 50.056
2024-08-21 | 23:24 | 50.055
2024-08-21 | 23:24 | 50.053
2024-08-21 | 23:24 | 50.052
2024-08-21 | 23:24 | 50.055
2024-08-21 | 23:24 | 50.059
2024-08-21 | 23:24 | 50.059
2024-08-21 | 23:24 | 50.058
2024-08-21 | 23:24 | 50.058
2024-08-21 | 23:24 | 50.056
2024-08-21 | 23:24 | 50.056
2024-08-21 | 23:24 | 50.056
2024-08-21 | 23:24 | 50.056
2024-08-21 | 23:24 | 50.055
2024-08-21 | 23:24 | 50.056
2024-08-21 | 23:24 | 50.056
2024-08-21 | 23:24 | 50.057
2024-08-21 | 23:24 | 50.059
2024-08-21 | 23:24 | 50.06
2024-08-21 | 23:24 | 50.058
2024-08-21 | 23:24 | 50.06
2024-08-21 | 23:24 | 50.058
2024-08-21 | 23:24 | 50.054
2024-08-21 | 23:24 | 50.051
2024-08-21 | 23:24 | 50.054
2024-08-21 | 23:24 | 50.054
2024-08-21 | 23:24 | 50.051
2024-08-21 | 23:24 | 50.052
2024-08-21 | 23:24 | 50.052
2024-08-21 | 23:25 | 50.052
2024-08-21 | 23:25 | 50.051
2024-08-21 | 23:25 | 50.05
2024-08-21 | 23:25 | 50.051
2024-08-21 | 23:25 | 50.049
2024-08-21 | 23:25 | 50.048
2024-08-21 | 23:25 | 50.048
2024-08-21 | 23:25 | 50.046
2024-08-21 | 23:25 | 50.047
2024-08-21 | 23:25 | 50.045
2024-08-21 | 23:25 | 50.043
2024-08-21 | 23:25 | 50.045
2024-08-21 | 23:25 | 50.045
2024-08-21 | 23:25 | 50.044
2024-08-21 | 23:25 | 50.043
2024-08-21 | 23:25 | 50.041
2024-08-21 | 23:25 | 50.037
2024-08-21 | 23:25 | 50.031
2024-08-21 | 23:25 | 50.028
2024-08-21 | 23:25 | 50.025
2024-08-21 | 23:25 | 50.021
2024-08-21 | 23:25 | 50.02
2024-08-21 | 23:25 | 50.021
2024-08-21 | 23:25 | 50.025
2024-08-21 | 23:25 | 50.027
2024-08-21 | 23:25 | 50.029
2024-08-21 | 23:25 | 50.03
2024-08-21 | 23:25 | 50.029
2024-08-21 | 23:25 | 50.031
2024-08-21 | 23:25 | 50.033
2024-08-21 | 23:25 | 50.031
2024-08-21 | 23:25 | 50.024
2024-08-21 | 23:25 | 50.019
2024-08-21 | 23:25 | 50.016
2024-08-21 | 23:25 | 50.014
2024-08-21 | 23:25 | 50.012
2024-08-21 | 23:25 | 50.011
2024-08-21 | 23:25 | 50.011
2024-08-21 | 23:25 | 50.009
2024-08-21 | 23:25 | 50.007
2024-08-21 | 23:25 | 50.004
2024-08-21 | 23:25 | 50.005
2024-08-21 | 23:25 | 50.007
2024-08-21 | 23:25 | 50.007
2024-08-21 | 23:25 | 50.008
2024-08-21 | 23:25 | 50.01
2024-08-21 | 23:25 | 50.014
2024-08-21 | 23:25 | 50.018
2024-08-21 | 23:25 | 50.018
2024-08-21 | 23:25 | 50.022
2024-08-21 | 23:25 | 50.021
2024-08-21 | 23:25 | 50.021
2024-08-21 | 23:25 | 50.019
2024-08-21 | 23:25 | 50.019
2024-08-21 | 23:25 | 50.017
2024-08-21 | 23:25 | 50.016
2024-08-21 | 23:25 | 50.016
2024-08-21 | 23:25 | 50.018
2024-08-21 | 23:25 | 50.019
2024-08-21 | 23:26 | 50.02
2024-08-21 | 23:26 | 50.021
2024-08-21 | 23:26 | 50.024
2024-08-21 | 23:26 | 50.027
2024-08-21 | 23:26 | 50.026
2024-08-21 | 23:26 | 50.025
2024-08-21 | 23:26 | 50.023
2024-08-21 | 23:26 | 50.019
2024-08-21 | 23:26 | 50.012
2024-08-21 | 23:26 | 50.009
2024-08-21 | 23:26 | 50.006
2024-08-21 | 23:26 | 50.001
2024-08-21 | 23:26 | 49.997
2024-08-21 | 23:26 | 49.994
2024-08-21 | 23:26 | 49.992
2024-08-21 | 23:26 | 49.988
2024-08-21 | 23:26 | 49.985
2024-08-21 | 23:26 | 49.985
2024-08-21 | 23:26 | 49.984
2024-08-21 | 23:26 | 49.982
2024-08-21 | 23:26 | 49.981
2024-08-21 | 23:26 | 49.983
2024-08-21 | 23:26 | 49.982
2024-08-21 | 23:26 | 49.978
2024-08-21 | 23:26 | 49.974
2024-08-21 | 23:26 | 49.972
2024-08-21 | 23:26 | 49.973
2024-08-21 | 23:26 | 49.973
2024-08-21 | 23:26 | 49.977
2024-08-21 | 23:26 | 49.978
2024-08-21 | 23:26 | 49.976
2024-08-21 | 23:26 | 49.972
2024-08-21 | 23:26 | 49.969
2024-08-21 | 23:26 | 49.968
2024-08-21 | 23:26 | 49.968
2024-08-21 | 23:26 | 49.969
2024-08-21 | 23:26 | 49.973
2024-08-21 | 23:26 | 49.976
2024-08-21 | 23:26 | 49.976
2024-08-21 | 23:26 | 49.976
2024-08-21 | 23:26 | 49.975
2024-08-21 | 23:26 | 49.975
2024-08-21 | 23:26 | 49.972
2024-08-21 | 23:26 | 49.97
2024-08-21 | 23:26 | 49.967
2024-08-21 | 23:26 | 49.967
2024-08-21 | 23:26 | 49.966
2024-08-21 | 23:26 | 49.968
2024-08-21 | 23:26 | 49.97
2024-08-21 | 23:26 | 49.97
2024-08-21 | 23:26 | 49.973
2024-08-21 | 23:26 | 49.976
2024-08-21 | 23:26 | 49.979
2024-08-21 | 23:26 | 49.981
2024-08-21 | 23:26 | 49.98
2024-08-21 | 23:26 | 49.978
2024-08-21 | 23:26 | 49.977
2024-08-21 | 23:26 | 49.978
2024-08-21 | 23:26 | 49.979
2024-08-21 | 23:26 | 49.977
2024-08-21 | 23:26 | 49.975
2024-08-21 | 23:27 | 49.97
2024-08-21 | 23:27 | 49.966
2024-08-21 | 23:27 | 49.964
2024-08-21 | 23:27 | 49.963
2024-08-21 | 23:27 | 49.961
2024-08-21 | 23:27 | 49.961
2024-08-21 | 23:27 | 49.962
2024-08-21 | 23:27 | 49.97
2024-08-21 | 23:27 | 49.975
2024-08-21 | 23:27 | 49.978
2024-08-21 | 23:27 | 49.981
2024-08-21 | 23:27 | 49.982
2024-08-21 | 23:27 | 49.979
2024-08-21 | 23:27 | 49.979
2024-08-21 | 23:27 | 49.977
2024-08-21 | 23:27 | 49.974
2024-08-21 | 23:27 | 49.97
2024-08-21 | 23:27 | 49.97
2024-08-21 | 23:27 | 49.974
2024-08-21 | 23:27 | 49.976
2024-08-21 | 23:27 | 49.973
2024-08-21 | 23:27 | 49.968
2024-08-21 | 23:27 | 49.964
2024-08-21 | 23:27 | 49.969
2024-08-21 | 23:27 | 49.968
2024-08-21 | 23:27 | 49.967
2024-08-21 | 23:27 | 49.965
2024-08-21 | 23:27 | 49.966
2024-08-21 | 23:27 | 49.96
2024-08-21 | 23:27 | 49.955

## 20240827-1
In GMT
Date | Time | Freq
2024-08-27 | 21:20 | 49.962 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-08-27 | 21:20 | 49.973 | 222 | BRITNED | 676.211
2024-08-27 | 21:20 | 49.967 | 268 | WBURB-2 | 428.156
2024-08-27 | 21:20 | 49.963 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-08-27 | 21:20 | 49.975 |  | Viking Link | -648.9
2024-08-27 | 21:20 | 49.96 |  | Viking Link | 1398.96
2024-08-27 | 21:20 | 49.965 | 209 | DRAXX-3 | 626.95
2024-08-27 | 21:20 | 49.971 | 154 | CDCL-1 | 391.57
2024-08-27 | 21:20 | 49.961 | 268 | ROCK-1 | 468.495
2024-08-27 | 21:20 | 49.967 | 148 | IFA Bipole1 | 945.473
2024-08-27 | 21:20 | 49.972 | 132 | IFA Bipole1 | 999.1
2024-08-27 | 21:20 | 49.963 | 141 | IFA Bipole2 | 1000
2024-08-27 | 21:20 | 49.971 | 135 | IFA Bipole1 | 996.75
2024-08-27 | 21:20 | 49.98 |  | Viking Link | -780.3
2024-08-27 | 21:20 | 49.968
2024-08-27 | 21:20 | 49.974
2024-08-27 | 21:20 | 49.982
2024-08-27 | 21:20 | 49.988
2024-08-27 | 21:20 | 49.977
2024-08-27 | 21:20 | 49.973 | 130 | HEYM12 | 271.908
2024-08-27 | 21:20 | 49.979 | 228 | HUMR-1 | 303.75
2024-08-27 | 21:20 | 49.984
2024-08-27 | 21:20 | 49.977
2024-08-27 | 21:20 | 49.975
2024-08-27 | 21:20 | 49.979
2024-08-27 | 21:20 | 49.978
2024-08-27 | 21:20 | 49.967
2024-08-27 | 21:20 | 49.975
2024-08-27 | 21:20 | 49.981
2024-08-27 | 21:20 | 49.973
2024-08-27 | 21:20 | 49.969 | 211 | CDCL-1 | 291.5
2024-08-27 | 21:21 | 49.977 | 199 | STAY-2 | 413.125
2024-08-27 | 21:21 | 49.97 | 173 | CDCL-1 | 397.375
2024-08-27 | 21:21 | 49.966 | 248 | SEAB-2 | 361.25
2024-08-27 | 21:21 | 49.973 | 255 | FRANCE | 995.65
2024-08-27 | 21:21 | 49.974 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-08-27 | 21:21 | 49.963
2024-08-27 | 21:21 | 49.97
2024-08-27 | 21:21 | 49.974
2024-08-27 | 21:21 | 49.964
2024-08-27 | 21:21 | 49.973
2024-08-27 | 21:21 | 49.977
2024-08-27 | 21:21 | 49.974
2024-08-27 | 21:21 | 49.976
2024-08-27 | 21:21 | 49.981
2024-08-27 | 21:21 | 49.975
2024-08-27 | 21:21 | 49.969
2024-08-27 | 21:21 | 49.974
2024-08-27 | 21:21 | 49.975
2024-08-27 | 21:21 | 49.961
2024-08-27 | 21:21 | 49.97
2024-08-27 | 21:21 | 49.976
2024-08-27 | 21:21 | 49.967
2024-08-27 | 21:21 | 49.969
2024-08-27 | 21:21 | 49.978
2024-08-27 | 21:21 | 49.964
2024-08-27 | 21:21 | 49.968
2024-08-27 | 21:21 | 49.976
2024-08-27 | 21:21 | 49.973
2024-08-27 | 21:21 | 49.969
2024-08-27 | 21:21 | 49.975
2024-08-27 | 21:21 | 49.978
2024-08-27 | 21:21 | 49.975
2024-08-27 | 21:21 | 49.975
2024-08-27 | 21:21 | 49.979
2024-08-27 | 21:21 | 49.976
2024-08-27 | 21:21 | 49.969
2024-08-27 | 21:21 | 49.971
2024-08-27 | 21:21 | 49.967
2024-08-27 | 21:21 | 49.956
2024-08-27 | 21:21 | 49.961
2024-08-27 | 21:21 | 49.946
2024-08-27 | 21:21 | 49.948
2024-08-27 | 21:21 | 49.953
2024-08-27 | 21:21 | 49.943
2024-08-27 | 21:21 | 49.962
2024-08-27 | 21:21 | 49.954
2024-08-27 | 21:21 | 49.959
2024-08-27 | 21:21 | 49.964
2024-08-27 | 21:21 | 49.952
2024-08-27 | 21:21 | 49.969
2024-08-27 | 21:21 | 49.967
2024-08-27 | 21:21 | 49.965
2024-08-27 | 21:21 | 49.977
2024-08-27 | 21:21 | 49.967
2024-08-27 | 21:21 | 49.969
2024-08-27 | 21:21 | 49.977
2024-08-27 | 21:21 | 49.972
2024-08-27 | 21:21 | 49.969
2024-08-27 | 21:21 | 49.977
2024-08-27 | 21:22 | 49.983
2024-08-27 | 21:22 | 49.972
2024-08-27 | 21:22 | 49.98
2024-08-27 | 21:22 | 49.986
2024-08-27 | 21:22 | 49.985
2024-08-27 | 21:22 | 49.981
2024-08-27 | 21:22 | 49.982
2024-08-27 | 21:22 | 49.993
2024-08-27 | 21:22 | 49.982
2024-08-27 | 21:22 | 49.969
2024-08-27 | 21:22 | 49.977
2024-08-27 | 21:22 | 49.981
2024-08-27 | 21:22 | 49.973
2024-08-27 | 21:22 | 49.968
2024-08-27 | 21:22 | 49.969
2024-08-27 | 21:22 | 49.954
2024-08-27 | 21:22 | 49.958
2024-08-27 | 21:22 | 49.969
2024-08-27 | 21:22 | 49.963
2024-08-27 | 21:22 | 49.959
2024-08-27 | 21:22 | 49.962
2024-08-27 | 21:22 | 49.952
2024-08-27 | 21:22 | 49.964
2024-08-27 | 21:22 | 49.952
2024-08-27 | 21:22 | 49.955
2024-08-27 | 21:22 | 49.966
2024-08-27 | 21:22 | 49.947
2024-08-27 | 21:22 | 49.959
2024-08-27 | 21:22 | 49.956
2024-08-27 | 21:22 | 49.953
2024-08-27 | 21:22 | 49.967
2024-08-27 | 21:22 | 49.949
2024-08-27 | 21:22 | 49.944
2024-08-27 | 21:22 | 49.933
2024-08-27 | 21:22 | 49.936
2024-08-27 | 21:22 | 49.909
2024-08-27 | 21:22 | 49.928
2024-08-27 | 21:22 | 49.918
2024-08-27 | 21:22 | 49.916
2024-08-27 | 21:22 | 49.934
2024-08-27 | 21:22 | 49.912
2024-08-27 | 21:22 | 49.914
2024-08-27 | 21:22 | 49.924
2024-08-27 | 21:22 | 49.904
2024-08-27 | 21:22 | 49.914
2024-08-27 | 21:22 | 49.907
2024-08-27 | 21:22 | 49.898
2024-08-27 | 21:22 | 49.914
2024-08-27 | 21:22 | 49.905
2024-08-27 | 21:22 | 49.892
2024-08-27 | 21:22 | 49.899
2024-08-27 | 21:22 | 49.912
2024-08-27 | 21:22 | 49.897
2024-08-27 | 21:22 | 49.897
2024-08-27 | 21:22 | 49.915
2024-08-27 | 21:22 | 49.909
2024-08-27 | 21:22 | 49.893
2024-08-27 | 21:22 | 49.894
2024-08-27 | 21:22 | 49.917
2024-08-27 | 21:22 | 49.895
2024-08-27 | 21:22 | 49.888
2024-08-27 | 21:23 | 49.901
2024-08-27 | 21:23 | 49.913
2024-08-27 | 21:23 | 49.893
2024-08-27 | 21:23 | 49.89
2024-08-27 | 21:23 | 49.911
2024-08-27 | 21:23 | 49.906
2024-08-27 | 21:23 | 49.893
2024-08-27 | 21:23 | 49.898
2024-08-27 | 21:23 | 49.912
2024-08-27 | 21:23 | 49.907
2024-08-27 | 21:23 | 49.896
2024-08-27 | 21:23 | 49.919
2024-08-27 | 21:23 | 49.914
2024-08-27 | 21:23 | 49.903
2024-08-27 | 21:23 | 49.924
2024-08-27 | 21:23 | 49.917
2024-08-27 | 21:23 | 49.914
2024-08-27 | 21:23 | 49.937
2024-08-27 | 21:23 | 49.916
2024-08-27 | 21:23 | 49.936
2024-08-27 | 21:23 | 49.928
2024-08-27 | 21:23 | 49.926
2024-08-27 | 21:23 | 49.932
2024-08-27 | 21:23 | 49.917
2024-08-27 | 21:23 | 49.938
2024-08-27 | 21:23 | 49.915
2024-08-27 | 21:23 | 49.918
2024-08-27 | 21:23 | 49.926
2024-08-27 | 21:23 | 49.912
2024-08-27 | 21:23 | 49.936
2024-08-27 | 21:23 | 49.92
2024-08-27 | 21:23 | 49.932
2024-08-27 | 21:23 | 49.926
2024-08-27 | 21:23 | 49.922
2024-08-27 | 21:23 | 49.936
2024-08-27 | 21:23 | 49.913
2024-08-27 | 21:23 | 49.916
2024-08-27 | 21:23 | 49.917
2024-08-27 | 21:23 | 49.907
2024-08-27 | 21:23 | 49.931
2024-08-27 | 21:23 | 49.913
2024-08-27 | 21:23 | 49.914
2024-08-27 | 21:23 | 49.928
2024-08-27 | 21:23 | 49.909
2024-08-27 | 21:23 | 49.925
2024-08-27 | 21:23 | 49.919
2024-08-27 | 21:23 | 49.904
2024-08-27 | 21:23 | 49.921
2024-08-27 | 21:23 | 49.909
2024-08-27 | 21:23 | 49.895
2024-08-27 | 21:23 | 49.912
2024-08-27 | 21:23 | 49.91
2024-08-27 | 21:23 | 49.89
2024-08-27 | 21:23 | 49.895
2024-08-27 | 21:23 | 49.909
2024-08-27 | 21:23 | 49.901
2024-08-27 | 21:23 | 49.886
2024-08-27 | 21:23 | 49.892
2024-08-27 | 21:23 | 49.908
2024-08-27 | 21:24 | 49.907
2024-08-27 | 21:24 | 49.893
2024-08-27 | 21:24 | 49.899
2024-08-27 | 21:24 | 49.908
2024-08-27 | 21:24 | 49.905
2024-08-27 | 21:24 | 49.894
2024-08-27 | 21:24 | 49.903
2024-08-27 | 21:24 | 49.926
2024-08-27 | 21:24 | 49.906
2024-08-27 | 21:24 | 49.914
2024-08-27 | 21:24 | 49.93
2024-08-27 | 21:24 | 49.912
2024-08-27 | 21:24 | 49.925
2024-08-27 | 21:24 | 49.93
2024-08-27 | 21:24 | 49.909
2024-08-27 | 21:24 | 49.918
2024-08-27 | 21:24 | 49.922
2024-08-27 | 21:24 | 49.911
2024-08-27 | 21:24 | 49.932
2024-08-27 | 21:24 | 49.916
2024-08-27 | 21:24 | 49.917
2024-08-27 | 21:24 | 49.928
2024-08-27 | 21:24 | 49.916
2024-08-27 | 21:24 | 49.933
2024-08-27 | 21:24 | 49.918
2024-08-27 | 21:24 | 49.921
2024-08-27 | 21:24 | 49.926
2024-08-27 | 21:24 | 49.916
2024-08-27 | 21:24 | 49.93
2024-08-27 | 21:24 | 49.906
2024-08-27 | 21:24 | 49.902
2024-08-27 | 21:24 | 49.914
2024-08-27 | 21:24 | 49.901
2024-08-27 | 21:24 | 49.888
2024-08-27 | 21:24 | 49.896
2024-08-27 | 21:24 | 49.914
2024-08-27 | 21:24 | 49.896
2024-08-27 | 21:24 | 49.905
2024-08-27 | 21:24 | 49.916
2024-08-27 | 21:24 | 49.902
2024-08-27 | 21:24 | 49.897
2024-08-27 | 21:24 | 49.915
2024-08-27 | 21:24 | 49.907
2024-08-27 | 21:24 | 49.893
2024-08-27 | 21:24 | 49.902
2024-08-27 | 21:24 | 49.92
2024-08-27 | 21:24 | 49.902
2024-08-27 | 21:24 | 49.904
2024-08-27 | 21:24 | 49.92
2024-08-27 | 21:24 | 49.902
2024-08-27 | 21:24 | 49.896
2024-08-27 | 21:24 | 49.913
2024-08-27 | 21:24 | 49.907
2024-08-27 | 21:24 | 49.9
2024-08-27 | 21:24 | 49.92
2024-08-27 | 21:24 | 49.92
2024-08-27 | 21:24 | 49.906
2024-08-27 | 21:24 | 49.927
2024-08-27 | 21:24 | 49.919
2024-08-27 | 21:24 | 49.924
2024-08-27 | 21:25 | 49.934
2024-08-27 | 21:25 | 49.911
2024-08-27 | 21:25 | 49.923
2024-08-27 | 21:25 | 49.915
2024-08-27 | 21:25 | 49.899
2024-08-27 | 21:25 | 49.905
2024-08-27 | 21:25 | 49.913
2024-08-27 | 21:25 | 49.897
2024-08-27 | 21:25 | 49.902
2024-08-27 | 21:25 | 49.924
2024-08-27 | 21:25 | 49.905
2024-08-27 | 21:25 | 49.912
2024-08-27 | 21:25 | 49.931
2024-08-27 | 21:25 | 49.918
2024-08-27 | 21:25 | 49.936
2024-08-27 | 21:25 | 49.925
2024-08-27 | 21:25 | 49.939
2024-08-27 | 21:25 | 49.931
2024-08-27 | 21:25 | 49.93
2024-08-27 | 21:25 | 49.932
2024-08-27 | 21:25 | 49.931
2024-08-27 | 21:25 | 49.924
2024-08-27 | 21:25 | 49.904
2024-08-27 | 21:25 | 49.914
2024-08-27 | 21:25 | 49.913
2024-08-27 | 21:25 | 49.897
2024-08-27 | 21:25 | 49.904
2024-08-27 | 21:25 | 49.916
2024-08-27 | 21:25 | 49.897
2024-08-27 | 21:25 | 49.904
2024-08-27 | 21:25 | 49.912
2024-08-27 | 21:25 | 49.905
2024-08-27 | 21:25 | 49.896
2024-08-27 | 21:25 | 49.905
2024-08-27 | 21:25 | 49.909
2024-08-27 | 21:25 | 49.895
2024-08-27 | 21:25 | 49.903
2024-08-27 | 21:25 | 49.922
2024-08-27 | 21:25 | 49.904
2024-08-27 | 21:25 | 49.913
2024-08-27 | 21:25 | 49.925
2024-08-27 | 21:25 | 49.901
2024-08-27 | 21:25 | 49.9
2024-08-27 | 21:25 | 49.913
2024-08-27 | 21:25 | 49.906
2024-08-27 | 21:25 | 49.891
2024-08-27 | 21:25 | 49.905
2024-08-27 | 21:25 | 49.92
2024-08-27 | 21:25 | 49.905
2024-08-27 | 21:25 | 49.914
2024-08-27 | 21:25 | 49.924
2024-08-27 | 21:25 | 49.916
2024-08-27 | 21:25 | 49.919
2024-08-27 | 21:25 | 49.931
2024-08-27 | 21:25 | 49.92
2024-08-27 | 21:25 | 49.947
2024-08-27 | 21:25 | 49.927
2024-08-27 | 21:25 | 49.947
2024-08-27 | 21:25 | 49.926
2024-08-27 | 21:25 | 49.938
2024-08-27 | 21:26 | 49.927
2024-08-27 | 21:26 | 49.94
2024-08-27 | 21:26 | 49.929
2024-08-27 | 21:26 | 49.927
2024-08-27 | 21:26 | 49.934
2024-08-27 | 21:26 | 49.937
2024-08-27 | 21:26 | 49.939
2024-08-27 | 21:26 | 49.934
2024-08-27 | 21:26 | 49.942
2024-08-27 | 21:26 | 49.933
2024-08-27 | 21:26 | 49.942
2024-08-27 | 21:26 | 49.934
2024-08-27 | 21:26 | 49.941
2024-08-27 | 21:26 | 49.922
2024-08-27 | 21:26 | 49.944
2024-08-27 | 21:26 | 49.923
2024-08-27 | 21:26 | 49.938
2024-08-27 | 21:26 | 49.928
2024-08-27 | 21:26 | 49.93
2024-08-27 | 21:26 | 49.935
2024-08-27 | 21:26 | 49.932
2024-08-27 | 21:26 | 49.936
2024-08-27 | 21:26 | 49.93
2024-08-27 | 21:26 | 49.938
2024-08-27 | 21:26 | 49.932
2024-08-27 | 21:26 | 49.939
2024-08-27 | 21:26 | 49.936
2024-08-27 | 21:26 | 49.939
2024-08-27 | 21:26 | 49.95
2024-08-27 | 21:26 | 49.937
2024-08-27 | 21:26 | 49.946
2024-08-27 | 21:26 | 49.931
2024-08-27 | 21:26 | 49.944
2024-08-27 | 21:26 | 49.93
2024-08-27 | 21:26 | 49.939
2024-08-27 | 21:26 | 49.93
2024-08-27 | 21:26 | 49.941
2024-08-27 | 21:26 | 49.929
2024-08-27 | 21:26 | 49.926
2024-08-27 | 21:26 | 49.932
2024-08-27 | 21:26 | 49.923
2024-08-27 | 21:26 | 49.935
2024-08-27 | 21:26 | 49.914
2024-08-27 | 21:26 | 49.926
2024-08-27 | 21:26 | 49.922
2024-08-27 | 21:26 | 49.911
2024-08-27 | 21:26 | 49.937
2024-08-27 | 21:26 | 49.917
2024-08-27 | 21:26 | 49.929
2024-08-27 | 21:26 | 49.929
2024-08-27 | 21:26 | 49.933
2024-08-27 | 21:26 | 49.936
2024-08-27 | 21:26 | 49.923
2024-08-27 | 21:26 | 49.945
2024-08-27 | 21:26 | 49.924
2024-08-27 | 21:26 | 49.939
2024-08-27 | 21:26 | 49.929
2024-08-27 | 21:26 | 49.941
2024-08-27 | 21:26 | 49.934
2024-08-27 | 21:26 | 49.945
2024-08-27 | 21:26 | 49.933
2024-08-27 | 21:27 | 49.942
2024-08-27 | 21:27 | 49.934
2024-08-27 | 21:27 | 49.931
2024-08-27 | 21:27 | 49.936
2024-08-27 | 21:27 | 49.929
2024-08-27 | 21:27 | 49.933
2024-08-27 | 21:27 | 49.93
2024-08-27 | 21:27 | 49.937
2024-08-27 | 21:27 | 49.917
2024-08-27 | 21:27 | 49.929
2024-08-27 | 21:27 | 49.916
2024-08-27 | 21:27 | 49.919
2024-08-27 | 21:27 | 49.927
2024-08-27 | 21:27 | 49.912
2024-08-27 | 21:27 | 49.929
2024-08-27 | 21:27 | 49.916
2024-08-27 | 21:27 | 49.916
2024-08-27 | 21:27 | 49.93
2024-08-27 | 21:27 | 49.908
2024-08-27 | 21:27 | 49.912
2024-08-27 | 21:27 | 49.923
2024-08-27 | 21:27 | 49.91
2024-08-27 | 21:27 | 49.93
2024-08-27 | 21:27 | 49.924
2024-08-27 | 21:27 | 49.921
2024-08-27 | 21:27 | 49.931
2024-08-27 | 21:27 | 49.918
2024-08-27 | 21:27 | 49.936
2024-08-27 | 21:27 | 49.92
2024-08-27 | 21:27 | 49.924
2024-08-27 | 21:27 | 49.92
2024-08-27 | 21:27 | 49.904
2024-08-27 | 21:27 | 49.916
2024-08-27 | 21:27 | 49.906
2024-08-27 | 21:27 | 49.891
2024-08-27 | 21:27 | 49.901
2024-08-27 | 21:27 | 49.916
2024-08-27 | 21:27 | 49.896
2024-08-27 | 21:27 | 49.892
2024-08-27 | 21:27 | 49.912
2024-08-27 | 21:27 | 49.91
2024-08-27 | 21:27 | 49.893
2024-08-27 | 21:27 | 49.898
2024-08-27 | 21:27 | 49.914
2024-08-27 | 21:27 | 49.906
2024-08-27 | 21:27 | 49.893
2024-08-27 | 21:27 | 49.897
2024-08-27 | 21:27 | 49.917
2024-08-27 | 21:27 | 49.894
2024-08-27 | 21:27 | 49.887
2024-08-27 | 21:27 | 49.895
2024-08-27 | 21:27 | 49.911
2024-08-27 | 21:27 | 49.894
2024-08-27 | 21:27 | 49.89
2024-08-27 | 21:27 | 49.91
2024-08-27 | 21:27 | 49.916
2024-08-27 | 21:27 | 49.896
2024-08-27 | 21:27 | 49.904
2024-08-27 | 21:27 | 49.918
2024-08-27 | 21:28 | 49.907
2024-08-27 | 21:28 | 49.915
2024-08-27 | 21:28 | 49.93
2024-08-27 | 21:28 | 49.91
2024-08-27 | 21:28 | 49.913
2024-08-27 | 21:28 | 49.926
2024-08-27 | 21:28 | 49.906
2024-08-27 | 21:28 | 49.908
2024-08-27 | 21:28 | 49.924
2024-08-27 | 21:28 | 49.907
2024-08-27 | 21:28 | 49.913
2024-08-27 | 21:28 | 49.92
2024-08-27 | 21:28 | 49.908
2024-08-27 | 21:28 | 49.925
2024-08-27 | 21:28 | 49.92
2024-08-27 | 21:28 | 49.931
2024-08-27 | 21:28 | 49.93
2024-08-27 | 21:28 | 49.916
2024-08-27 | 21:28 | 49.938
2024-08-27 | 21:28 | 49.919
2024-08-27 | 21:28 | 49.929
2024-08-27 | 21:28 | 49.921
2024-08-27 | 21:28 | 49.909
2024-08-27 | 21:28 | 49.931
2024-08-27 | 21:28 | 49.908
2024-08-27 | 21:28 | 49.908
2024-08-27 | 21:28 | 49.915
2024-08-27 | 21:28 | 49.905
2024-08-27 | 21:28 | 49.896
2024-08-27 | 21:28 | 49.925
2024-08-27 | 21:28 | 49.915
2024-08-27 | 21:28 | 49.91
2024-08-27 | 21:28 | 49.923
2024-08-27 | 21:28 | 49.906
2024-08-27 | 21:28 | 49.909
2024-08-27 | 21:28 | 49.927
2024-08-27 | 21:28 | 49.906
2024-08-27 | 21:28 | 49.912
2024-08-27 | 21:28 | 49.923
2024-08-27 | 21:28 | 49.906
2024-08-27 | 21:28 | 49.925
2024-08-27 | 21:28 | 49.918
2024-08-27 | 21:28 | 49.912
2024-08-27 | 21:28 | 49.937
2024-08-27 | 21:28 | 49.918
2024-08-27 | 21:28 | 49.937
2024-08-27 | 21:28 | 49.929
2024-08-27 | 21:28 | 49.924
2024-08-27 | 21:28 | 49.93
2024-08-27 | 21:28 | 49.929
2024-08-27 | 21:28 | 49.935
2024-08-27 | 21:28 | 49.919
2024-08-27 | 21:28 | 49.942
2024-08-27 | 21:28 | 49.925
2024-08-27 | 21:28 | 49.945
2024-08-27 | 21:28 | 49.936
2024-08-27 | 21:28 | 49.954
2024-08-27 | 21:28 | 49.937
2024-08-27 | 21:28 | 49.958
2024-08-27 | 21:28 | 49.933
2024-08-27 | 21:29 | 49.948
2024-08-27 | 21:29 | 49.937
2024-08-27 | 21:29 | 49.945
2024-08-27 | 21:29 | 49.933
2024-08-27 | 21:29 | 49.942
2024-08-27 | 21:29 | 49.938
2024-08-27 | 21:29 | 49.944
2024-08-27 | 21:29 | 49.93
2024-08-27 | 21:29 | 49.941
2024-08-27 | 21:29 | 49.926
2024-08-27 | 21:29 | 49.943
2024-08-27 | 21:29 | 49.923
2024-08-27 | 21:29 | 49.945
2024-08-27 | 21:29 | 49.925
2024-08-27 | 21:29 | 49.946
2024-08-27 | 21:29 | 49.928
2024-08-27 | 21:29 | 49.94
2024-08-27 | 21:29 | 49.928
2024-08-27 | 21:29 | 49.942
2024-08-27 | 21:29 | 49.93
2024-08-27 | 21:29 | 49.927
2024-08-27 | 21:29 | 49.935
2024-08-27 | 21:29 | 49.929
2024-08-27 | 21:29 | 49.937
2024-08-27 | 21:29 | 49.934
2024-08-27 | 21:29 | 49.942
2024-08-27 | 21:29 | 49.94
2024-08-27 | 21:29 | 49.939
2024-08-27 | 21:29 | 49.925
2024-08-27 | 21:29 | 49.951
2024-08-27 | 21:29 | 49.926
2024-08-27 | 21:29 | 49.938
2024-08-27 | 21:29 | 49.917
2024-08-27 | 21:29 | 49.92
2024-08-27 | 21:29 | 49.924
2024-08-27 | 21:29 | 49.911
2024-08-27 | 21:29 | 49.924
2024-08-27 | 21:29 | 49.918
2024-08-27 | 21:29 | 49.903
2024-08-27 | 21:29 | 49.924
2024-08-27 | 21:29 | 49.91
2024-08-27 | 21:29 | 49.909
2024-08-27 | 21:29 | 49.915
2024-08-27 | 21:29 | 49.903
2024-08-27 | 21:29 | 49.891
2024-08-27 | 21:29 | 49.903
2024-08-27 | 21:29 | 49.914
2024-08-27 | 21:29 | 49.896
2024-08-27 | 21:29 | 49.903
2024-08-27 | 21:29 | 49.92
2024-08-27 | 21:29 | 49.906
2024-08-27 | 21:29 | 49.898
2024-08-27 | 21:29 | 49.918
2024-08-27 | 21:29 | 49.911
2024-08-27 | 21:29 | 49.898
2024-08-27 | 21:29 | 49.923
2024-08-27 | 21:29 | 49.915
2024-08-27 | 21:29 | 49.906
2024-08-27 | 21:29 | 49.927
2024-08-27 | 21:29 | 49.916
2024-08-27 | 21:30 | 49.921
2024-08-27 | 21:30 | 49.927
2024-08-27 | 21:30 | 49.914
2024-08-27 | 21:30 | 49.935
2024-08-27 | 21:30 | 49.923
2024-08-27 | 21:30 | 49.937
2024-08-27 | 21:30 | 49.927
2024-08-27 | 21:30 | 49.93
2024-08-27 | 21:30 | 49.935
2024-08-27 | 21:30 | 49.921
2024-08-27 | 21:30 | 49.945
2024-08-27 | 21:30 | 49.925
2024-08-27 | 21:30 | 49.945
2024-08-27 | 21:30 | 49.926
2024-08-27 | 21:30 | 49.936
2024-08-27 | 21:30 | 49.924
2024-08-27 | 21:30 | 49.92
2024-08-27 | 21:30 | 49.922
2024-08-27 | 21:30 | 49.91
2024-08-27 | 21:30 | 49.924
2024-08-27 | 21:30 | 49.918
2024-08-27 | 21:30 | 49.912
2024-08-27 | 21:30 | 49.924
2024-08-27 | 21:30 | 49.91
2024-08-27 | 21:30 | 49.925
2024-08-27 | 21:30 | 49.922
2024-08-27 | 21:30 | 49.915
2024-08-27 | 21:30 | 49.935
2024-08-27 | 21:30 | 49.916
2024-08-27 | 21:30 | 49.934
2024-08-27 | 21:30 | 49.929
2024-08-27 | 21:30 | 49.946
2024-08-27 | 21:30 | 49.932
2024-08-27 | 21:30 | 49.935
2024-08-27 | 21:30 | 49.933
2024-08-27 | 21:30 | 49.929
2024-08-27 | 21:30 | 49.935
2024-08-27 | 21:30 | 49.935
2024-08-27 | 21:30 | 49.939
2024-08-27 | 21:30 | 49.939
2024-08-27 | 21:30 | 49.94
2024-08-27 | 21:30 | 49.932
2024-08-27 | 21:30 | 49.941
2024-08-27 | 21:30 | 49.932
2024-08-27 | 21:30 | 49.943
2024-08-27 | 21:30 | 49.938
2024-08-27 | 21:30 | 49.947
2024-08-27 | 21:30 | 49.948
2024-08-27 | 21:30 | 49.942
2024-08-27 | 21:30 | 49.934
2024-08-27 | 21:30 | 49.942
2024-08-27 | 21:30 | 49.936
2024-08-27 | 21:30 | 49.937
2024-08-27 | 21:30 | 49.927
2024-08-27 | 21:30 | 49.942
2024-08-27 | 21:30 | 49.922
2024-08-27 | 21:30 | 49.942
2024-08-27 | 21:30 | 49.921
2024-08-27 | 21:30 | 49.939
2024-08-27 | 21:30 | 49.929
2024-08-27 | 21:30 | 49.931
2024-08-27 | 21:31 | 49.939
2024-08-27 | 21:31 | 49.937
2024-08-27 | 21:31 | 49.946
2024-08-27 | 21:31 | 49.956
2024-08-27 | 21:31 | 49.945
2024-08-27 | 21:31 | 49.961
2024-08-27 | 21:31 | 49.945
2024-08-27 | 21:31 | 49.96
2024-08-27 | 21:31 | 49.966
2024-08-27 | 21:31 | 49.964
2024-08-27 | 21:31 | 49.972
2024-08-27 | 21:31 | 49.981
2024-08-27 | 21:31 | 49.969
2024-08-27 | 21:31 | 49.977
2024-08-27 | 21:31 | 49.984
2024-08-27 | 21:31 | 49.978
2024-08-27 | 21:31 | 49.971
2024-08-27 | 21:31 | 49.975
2024-08-27 | 21:31 | 49.976
2024-08-27 | 21:31 | 49.966
2024-08-27 | 21:31 | 49.975
2024-08-27 | 21:31 | 49.984
2024-08-27 | 21:31 | 49.98
2024-08-27 | 21:31 | 49.97
2024-08-27 | 21:31 | 49.976
2024-08-27 | 21:31 | 49.976
2024-08-27 | 21:31 | 49.964
2024-08-27 | 21:31 | 49.972
2024-08-27 | 21:31 | 49.981
2024-08-27 | 21:31 | 49.976
2024-08-27 | 21:31 | 49.971
2024-08-27 | 21:31 | 49.976
2024-08-27 | 21:31 | 49.978
2024-08-27 | 21:31 | 49.964
2024-08-27 | 21:31 | 49.97
2024-08-27 | 21:31 | 49.974
2024-08-27 | 21:31 | 49.963
2024-08-27 | 21:31 | 49.969
2024-08-27 | 21:31 | 49.973
2024-08-27 | 21:31 | 49.971
2024-08-27 | 21:31 | 49.969
2024-08-27 | 21:31 | 49.977
2024-08-27 | 21:31 | 49.974
2024-08-27 | 21:31 | 49.971
2024-08-27 | 21:31 | 49.98
2024-08-27 | 21:31 | 49.98
2024-08-27 | 21:31 | 49.973
2024-08-27 | 21:31 | 49.982
2024-08-27 | 21:31 | 49.992
2024-08-27 | 21:31 | 49.994
2024-08-27 | 21:31 | 50.002
2024-08-27 | 21:31 | 50.007
2024-08-27 | 21:31 | 50.014
2024-08-27 | 21:31 | 50.021
2024-08-27 | 21:31 | 50.022
2024-08-27 | 21:31 | 50.025
2024-08-27 | 21:31 | 50.023
2024-08-27 | 21:31 | 50.021
2024-08-27 | 21:31 | 50.018
2024-08-27 | 21:32 | 50.018
2024-08-27 | 21:32 | 50.02
2024-08-27 | 21:32 | 50.018
2024-08-27 | 21:32 | 50.019
2024-08-27 | 21:32 | 50.021
2024-08-27 | 21:32 | 50.021
2024-08-27 | 21:32 | 50.02
2024-08-27 | 21:32 | 50.02
2024-08-27 | 21:32 | 50.02
2024-08-27 | 21:32 | 50.017
2024-08-27 | 21:32 | 50.013
2024-08-27 | 21:32 | 50.01
2024-08-27 | 21:32 | 50.01
2024-08-27 | 21:32 | 50.004
2024-08-27 | 21:32 | 50.002
2024-08-27 | 21:32 | 49.998
2024-08-27 | 21:32 | 49.994
2024-08-27 | 21:32 | 49.998
2024-08-27 | 21:32 | 50.003
2024-08-27 | 21:32 | 50.007
2024-08-27 | 21:32 | 50.012
2024-08-27 | 21:32 | 50.014
2024-08-27 | 21:32 | 50.016
2024-08-27 | 21:32 | 50.019
2024-08-27 | 21:32 | 50.021
2024-08-27 | 21:32 | 50.024
2024-08-27 | 21:32 | 50.024
2024-08-27 | 21:32 | 50.025
2024-08-27 | 21:32 | 50.025
2024-08-27 | 21:32 | 50.023
2024-08-27 | 21:32 | 50.026
2024-08-27 | 21:32 | 50.024
2024-08-27 | 21:32 | 50.025
2024-08-27 | 21:32 | 50.02
2024-08-27 | 21:32 | 50.016
2024-08-27 | 21:32 | 50.013
2024-08-27 | 21:32 | 50.012
2024-08-27 | 21:32 | 50.009
2024-08-27 | 21:32 | 50.013
2024-08-27 | 21:32 | 50.013
2024-08-27 | 21:32 | 50.016
2024-08-27 | 21:32 | 50.016
2024-08-27 | 21:32 | 50.015
2024-08-27 | 21:32 | 50.016
2024-08-27 | 21:32 | 50.015
2024-08-27 | 21:32 | 50.014
2024-08-27 | 21:32 | 50.013
2024-08-27 | 21:32 | 50.012
2024-08-27 | 21:32 | 50.009
2024-08-27 | 21:32 | 50.011
2024-08-27 | 21:32 | 50.008
2024-08-27 | 21:32 | 50.01

## 20240828-1
In GMT
Date | Time | Freq
2024-08-28 | 8:01 | 50.079 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-08-28 | 8:01 | 50.073 | 222 | BRITNED | 676.211
2024-08-28 | 8:01 | 50.068 | 268 | WBURB-2 | 428.156
2024-08-28 | 8:01 | 50.063 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-08-28 | 8:01 | 50.059 |  | Viking Link | -648.9
2024-08-28 | 8:01 | 50.05 |  | Viking Link | 1398.96
2024-08-28 | 8:01 | 50.041 | 209 | DRAXX-3 | 626.95
2024-08-28 | 8:01 | 50.031 | 154 | CDCL-1 | 391.57
2024-08-28 | 8:01 | 50.023 | 268 | ROCK-1 | 468.495
2024-08-28 | 8:01 | 50.017 | 148 | IFA Bipole1 | 945.473
2024-08-28 | 8:01 | 50.009 | 132 | IFA Bipole1 | 999.1
2024-08-28 | 8:01 | 50.001 | 141 | IFA Bipole2 | 1000
2024-08-28 | 8:01 | 49.987 | 135 | IFA Bipole1 | 996.75
2024-08-28 | 8:01 | 49.976 |  | Viking Link | -780.3
2024-08-28 | 8:01 | 49.966
2024-08-28 | 8:01 | 49.955
2024-08-28 | 8:01 | 49.945
2024-08-28 | 8:01 | 49.938
2024-08-28 | 8:01 | 49.931
2024-08-28 | 8:01 | 49.925 | 130 | HEYM12 | 271.908
2024-08-28 | 8:01 | 49.923 | 228 | HUMR-1 | 303.75
2024-08-28 | 8:01 | 49.922
2024-08-28 | 8:01 | 49.923
2024-08-28 | 8:01 | 49.925
2024-08-28 | 8:01 | 49.928
2024-08-28 | 8:01 | 49.932
2024-08-28 | 8:01 | 49.935
2024-08-28 | 8:01 | 49.939
2024-08-28 | 8:01 | 49.942
2024-08-28 | 8:01 | 49.944
2024-08-28 | 8:02 | 49.947 | 211 | CDCL-1 | 291.5
2024-08-28 | 8:02 | 49.948 | 199 | STAY-2 | 413.125
2024-08-28 | 8:02 | 49.95 | 173 | CDCL-1 | 397.375
2024-08-28 | 8:02 | 49.952 | 248 | SEAB-2 | 361.25
2024-08-28 | 8:02 | 49.953 | 255 | FRANCE | 995.65
2024-08-28 | 8:02 | 49.954 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-08-28 | 8:02 | 49.954
2024-08-28 | 8:02 | 49.956
2024-08-28 | 8:02 | 49.957
2024-08-28 | 8:02 | 49.956
2024-08-28 | 8:02 | 49.956
2024-08-28 | 8:02 | 49.958
2024-08-28 | 8:02 | 49.96
2024-08-28 | 8:02 | 49.964
2024-08-28 | 8:02 | 49.967
2024-08-28 | 8:02 | 49.969
2024-08-28 | 8:02 | 49.967
2024-08-28 | 8:02 | 49.967
2024-08-28 | 8:02 | 49.965
2024-08-28 | 8:02 | 49.963
2024-08-28 | 8:02 | 49.958
2024-08-28 | 8:02 | 49.956
2024-08-28 | 8:02 | 49.953
2024-08-28 | 8:02 | 49.951
2024-08-28 | 8:02 | 49.951
2024-08-28 | 8:02 | 49.951
2024-08-28 | 8:02 | 49.949
2024-08-28 | 8:02 | 49.945
2024-08-28 | 8:02 | 49.943
2024-08-28 | 8:02 | 49.938
2024-08-28 | 8:02 | 49.936
2024-08-28 | 8:02 | 49.935
2024-08-28 | 8:02 | 49.937
2024-08-28 | 8:02 | 49.938
2024-08-28 | 8:02 | 49.939
2024-08-28 | 8:02 | 49.938
2024-08-28 | 8:02 | 49.937
2024-08-28 | 8:02 | 49.892
2024-08-28 | 8:02 | 49.783
2024-08-28 | 8:02 | 49.728
2024-08-28 | 8:02 | 49.711
2024-08-28 | 8:02 | 49.705
2024-08-28 | 8:02 | 49.707
2024-08-28 | 8:02 | 49.708
2024-08-28 | 8:02 | 49.71
2024-08-28 | 8:02 | 49.709
2024-08-28 | 8:02 | 49.71
2024-08-28 | 8:02 | 49.706
2024-08-28 | 8:02 | 49.706
2024-08-28 | 8:02 | 49.705
2024-08-28 | 8:02 | 49.708
2024-08-28 | 8:02 | 49.707
2024-08-28 | 8:02 | 49.709
2024-08-28 | 8:02 | 49.709
2024-08-28 | 8:02 | 49.707
2024-08-28 | 8:02 | 49.706
2024-08-28 | 8:02 | 49.704
2024-08-28 | 8:02 | 49.7
2024-08-28 | 8:02 | 49.7
2024-08-28 | 8:02 | 49.705
2024-08-28 | 8:02 | 49.711
2024-08-28 | 8:03 | 49.714
2024-08-28 | 8:03 | 49.717
2024-08-28 | 8:03 | 49.722
2024-08-28 | 8:03 | 49.726
2024-08-28 | 8:03 | 49.728
2024-08-28 | 8:03 | 49.73
2024-08-28 | 8:03 | 49.732
2024-08-28 | 8:03 | 49.732
2024-08-28 | 8:03 | 49.733
2024-08-28 | 8:03 | 49.731
2024-08-28 | 8:03 | 49.733
2024-08-28 | 8:03 | 49.733
2024-08-28 | 8:03 | 49.734
2024-08-28 | 8:03 | 49.731
2024-08-28 | 8:03 | 49.733
2024-08-28 | 8:03 | 49.734
2024-08-28 | 8:03 | 49.735
2024-08-28 | 8:03 | 49.733
2024-08-28 | 8:03 | 49.734
2024-08-28 | 8:03 | 49.735
2024-08-28 | 8:03 | 49.735
2024-08-28 | 8:03 | 49.731
2024-08-28 | 8:03 | 49.73
2024-08-28 | 8:03 | 49.733
2024-08-28 | 8:03 | 49.736
2024-08-28 | 8:03 | 49.736
2024-08-28 | 8:03 | 49.738
2024-08-28 | 8:03 | 49.738
2024-08-28 | 8:03 | 49.736
2024-08-28 | 8:03 | 49.735
2024-08-28 | 8:03 | 49.735
2024-08-28 | 8:03 | 49.737
2024-08-28 | 8:03 | 49.743
2024-08-28 | 8:03 | 49.748
2024-08-28 | 8:03 | 49.754
2024-08-28 | 8:03 | 49.762
2024-08-28 | 8:03 | 49.765
2024-08-28 | 8:03 | 49.765
2024-08-28 | 8:03 | 49.768
2024-08-28 | 8:03 | 49.771
2024-08-28 | 8:03 | 49.776
2024-08-28 | 8:03 | 49.781
2024-08-28 | 8:03 | 49.781
2024-08-28 | 8:03 | 49.779
2024-08-28 | 8:03 | 49.778
2024-08-28 | 8:03 | 49.778
2024-08-28 | 8:03 | 49.78
2024-08-28 | 8:03 | 49.784
2024-08-28 | 8:03 | 49.788
2024-08-28 | 8:03 | 49.792
2024-08-28 | 8:03 | 49.793
2024-08-28 | 8:03 | 49.795
2024-08-28 | 8:03 | 49.795
2024-08-28 | 8:03 | 49.796
2024-08-28 | 8:03 | 49.794
2024-08-28 | 8:03 | 49.796
2024-08-28 | 8:03 | 49.799
2024-08-28 | 8:03 | 49.801
2024-08-28 | 8:03 | 49.808
2024-08-28 | 8:04 | 49.812
2024-08-28 | 8:04 | 49.817
2024-08-28 | 8:04 | 49.821
2024-08-28 | 8:04 | 49.823
2024-08-28 | 8:04 | 49.826
2024-08-28 | 8:04 | 49.827
2024-08-28 | 8:04 | 49.828
2024-08-28 | 8:04 | 49.833
2024-08-28 | 8:04 | 49.838
2024-08-28 | 8:04 | 49.841
2024-08-28 | 8:04 | 49.841
2024-08-28 | 8:04 | 49.84
2024-08-28 | 8:04 | 49.839
2024-08-28 | 8:04 | 49.836
2024-08-28 | 8:04 | 49.836
2024-08-28 | 8:04 | 49.841
2024-08-28 | 8:04 | 49.845
2024-08-28 | 8:04 | 49.844
2024-08-28 | 8:04 | 49.846
2024-08-28 | 8:04 | 49.849
2024-08-28 | 8:04 | 49.849
2024-08-28 | 8:04 | 49.852
2024-08-28 | 8:04 | 49.851
2024-08-28 | 8:04 | 49.847
2024-08-28 | 8:04 | 49.848
2024-08-28 | 8:04 | 49.846
2024-08-28 | 8:04 | 49.843
2024-08-28 | 8:04 | 49.843
2024-08-28 | 8:04 | 49.843
2024-08-28 | 8:04 | 49.839
2024-08-28 | 8:04 | 49.836
2024-08-28 | 8:04 | 49.836
2024-08-28 | 8:04 | 49.835
2024-08-28 | 8:04 | 49.837
2024-08-28 | 8:04 | 49.838
2024-08-28 | 8:04 | 49.837
2024-08-28 | 8:04 | 49.836
2024-08-28 | 8:04 | 49.835
2024-08-28 | 8:04 | 49.834
2024-08-28 | 8:04 | 49.833
2024-08-28 | 8:04 | 49.833
2024-08-28 | 8:04 | 49.832
2024-08-28 | 8:04 | 49.831
2024-08-28 | 8:04 | 49.831
2024-08-28 | 8:04 | 49.832
2024-08-28 | 8:04 | 49.834
2024-08-28 | 8:04 | 49.837
2024-08-28 | 8:04 | 49.838
2024-08-28 | 8:04 | 49.836
2024-08-28 | 8:04 | 49.832
2024-08-28 | 8:04 | 49.83
2024-08-28 | 8:04 | 49.83
2024-08-28 | 8:04 | 49.836
2024-08-28 | 8:04 | 49.837
2024-08-28 | 8:04 | 49.839
2024-08-28 | 8:04 | 49.842
2024-08-28 | 8:04 | 49.842
2024-08-28 | 8:04 | 49.844
2024-08-28 | 8:04 | 49.843
2024-08-28 | 8:04 | 49.847
2024-08-28 | 8:04 | 49.847
2024-08-28 | 8:05 | 49.853
2024-08-28 | 8:05 | 49.856
2024-08-28 | 8:05 | 49.864
2024-08-28 | 8:05 | 49.866
2024-08-28 | 8:05 | 49.869
2024-08-28 | 8:05 | 49.87
2024-08-28 | 8:05 | 49.874
2024-08-28 | 8:05 | 49.875
2024-08-28 | 8:05 | 49.88
2024-08-28 | 8:05 | 49.881
2024-08-28 | 8:05 | 49.882
2024-08-28 | 8:05 | 49.884
2024-08-28 | 8:05 | 49.884
2024-08-28 | 8:05 | 49.886
2024-08-28 | 8:05 | 49.89
2024-08-28 | 8:05 | 49.892
2024-08-28 | 8:05 | 49.895
2024-08-28 | 8:05 | 49.895
2024-08-28 | 8:05 | 49.897
2024-08-28 | 8:05 | 49.896
2024-08-28 | 8:05 | 49.9
2024-08-28 | 8:05 | 49.899
2024-08-28 | 8:05 | 49.899
2024-08-28 | 8:05 | 49.902
2024-08-28 | 8:05 | 49.905
2024-08-28 | 8:05 | 49.903
2024-08-28 | 8:05 | 49.905
2024-08-28 | 8:05 | 49.903
2024-08-28 | 8:05 | 49.902
2024-08-28 | 8:05 | 49.903
2024-08-28 | 8:05 | 49.907
2024-08-28 | 8:05 | 49.915
2024-08-28 | 8:05 | 49.923
2024-08-28 | 8:05 | 49.926
2024-08-28 | 8:05 | 49.929
2024-08-28 | 8:05 | 49.93
2024-08-28 | 8:05 | 49.933
2024-08-28 | 8:05 | 49.934
2024-08-28 | 8:05 | 49.933
2024-08-28 | 8:05 | 49.932
2024-08-28 | 8:05 | 49.931
2024-08-28 | 8:05 | 49.934
2024-08-28 | 8:05 | 49.937
2024-08-28 | 8:05 | 49.937
2024-08-28 | 8:05 | 49.943
2024-08-28 | 8:05 | 49.948
2024-08-28 | 8:05 | 49.951
2024-08-28 | 8:05 | 49.955
2024-08-28 | 8:05 | 49.955
2024-08-28 | 8:05 | 49.954
2024-08-28 | 8:05 | 49.953
2024-08-28 | 8:05 | 49.952
2024-08-28 | 8:05 | 49.951
2024-08-28 | 8:05 | 49.949
2024-08-28 | 8:05 | 49.948
2024-08-28 | 8:05 | 49.953
2024-08-28 | 8:05 | 49.956
2024-08-28 | 8:05 | 49.958
2024-08-28 | 8:05 | 49.961
2024-08-28 | 8:06 | 49.961
2024-08-28 | 8:06 | 49.96
2024-08-28 | 8:06 | 49.96
2024-08-28 | 8:06 | 49.961
2024-08-28 | 8:06 | 49.961
2024-08-28 | 8:06 | 49.964
2024-08-28 | 8:06 | 49.967
2024-08-28 | 8:06 | 49.967
2024-08-28 | 8:06 | 49.968
2024-08-28 | 8:06 | 49.969
2024-08-28 | 8:06 | 49.968
2024-08-28 | 8:06 | 49.965
2024-08-28 | 8:06 | 49.966
2024-08-28 | 8:06 | 49.963
2024-08-28 | 8:06 | 49.962
2024-08-28 | 8:06 | 49.959
2024-08-28 | 8:06 | 49.958
2024-08-28 | 8:06 | 49.956
2024-08-28 | 8:06 | 49.954
2024-08-28 | 8:06 | 49.954
2024-08-28 | 8:06 | 49.954
2024-08-28 | 8:06 | 49.953
2024-08-28 | 8:06 | 49.956
2024-08-28 | 8:06 | 49.958
2024-08-28 | 8:06 | 49.957
2024-08-28 | 8:06 | 49.956
2024-08-28 | 8:06 | 49.959
2024-08-28 | 8:06 | 49.961
2024-08-28 | 8:06 | 49.963
2024-08-28 | 8:06 | 49.967
2024-08-28 | 8:06 | 49.973
2024-08-28 | 8:06 | 49.974
2024-08-28 | 8:06 | 49.975
2024-08-28 | 8:06 | 49.978
2024-08-28 | 8:06 | 49.983
2024-08-28 | 8:06 | 49.988
2024-08-28 | 8:06 | 49.991
2024-08-28 | 8:06 | 49.994
2024-08-28 | 8:06 | 49.993
2024-08-28 | 8:06 | 49.993
2024-08-28 | 8:06 | 49.991
2024-08-28 | 8:06 | 49.985
2024-08-28 | 8:06 | 49.981
2024-08-28 | 8:06 | 49.979
2024-08-28 | 8:06 | 49.975
2024-08-28 | 8:06 | 49.972
2024-08-28 | 8:06 | 49.969
2024-08-28 | 8:06 | 49.967
2024-08-28 | 8:06 | 49.963
2024-08-28 | 8:06 | 49.961
2024-08-28 | 8:06 | 49.958
2024-08-28 | 8:06 | 49.956
2024-08-28 | 8:06 | 49.958
2024-08-28 | 8:06 | 49.963
2024-08-28 | 8:06 | 49.963
2024-08-28 | 8:06 | 49.963
2024-08-28 | 8:06 | 49.964
2024-08-28 | 8:06 | 49.965
2024-08-28 | 8:06 | 49.968
2024-08-28 | 8:06 | 49.966
2024-08-28 | 8:06 | 49.967
2024-08-28 | 8:07 | 49.965
2024-08-28 | 8:07 | 49.964
2024-08-28 | 8:07 | 49.964
2024-08-28 | 8:07 | 49.96
2024-08-28 | 8:07 | 49.955
2024-08-28 | 8:07 | 49.952
2024-08-28 | 8:07 | 49.954
2024-08-28 | 8:07 | 49.961
2024-08-28 | 8:07 | 49.965
2024-08-28 | 8:07 | 49.97
2024-08-28 | 8:07 | 49.972
2024-08-28 | 8:07 | 49.982
2024-08-28 | 8:07 | 49.985
2024-08-28 | 8:07 | 49.984
2024-08-28 | 8:07 | 49.985
2024-08-28 | 8:07 | 49.987
2024-08-28 | 8:07 | 49.988
2024-08-28 | 8:07 | 49.988
2024-08-28 | 8:07 | 49.986
2024-08-28 | 8:07 | 49.985
2024-08-28 | 8:07 | 49.987
2024-08-28 | 8:07 | 49.985
2024-08-28 | 8:07 | 49.986
2024-08-28 | 8:07 | 49.988
2024-08-28 | 8:07 | 49.993
2024-08-28 | 8:07 | 49.996
2024-08-28 | 8:07 | 49.998
2024-08-28 | 8:07 | 49.999
2024-08-28 | 8:07 | 50.005
2024-08-28 | 8:07 | 50.012
2024-08-28 | 8:07 | 50.015
2024-08-28 | 8:07 | 50.017
2024-08-28 | 8:07 | 50.02
2024-08-28 | 8:07 | 50.022
2024-08-28 | 8:07 | 50.025
2024-08-28 | 8:07 | 50.026
2024-08-28 | 8:07 | 50.028
2024-08-28 | 8:07 | 50.03
2024-08-28 | 8:07 | 50.029
2024-08-28 | 8:07 | 50.029
2024-08-28 | 8:07 | 50.029
2024-08-28 | 8:07 | 50.029
2024-08-28 | 8:07 | 50.031
2024-08-28 | 8:07 | 50.03
2024-08-28 | 8:07 | 50.032
2024-08-28 | 8:07 | 50.034
2024-08-28 | 8:07 | 50.036
2024-08-28 | 8:07 | 50.037
2024-08-28 | 8:07 | 50.034
2024-08-28 | 8:07 | 50.033
2024-08-28 | 8:07 | 50.03
2024-08-28 | 8:07 | 50.028
2024-08-28 | 8:07 | 50.03
2024-08-28 | 8:07 | 50.028
2024-08-28 | 8:07 | 50.026
2024-08-28 | 8:07 | 50.02
2024-08-28 | 8:07 | 50.012
2024-08-28 | 8:07 | 50.01
2024-08-28 | 8:07 | 50.008
2024-08-28 | 8:08 | 50.004
2024-08-28 | 8:08 | 50.004
2024-08-28 | 8:08 | 50.005
2024-08-28 | 8:08 | 50.003
2024-08-28 | 8:08 | 49.995
2024-08-28 | 8:08 | 49.989
2024-08-28 | 8:08 | 49.985
2024-08-28 | 8:08 | 49.98
2024-08-28 | 8:08 | 49.977
2024-08-28 | 8:08 | 49.976
2024-08-28 | 8:08 | 49.974
2024-08-28 | 8:08 | 49.97
2024-08-28 | 8:08 | 49.97
2024-08-28 | 8:08 | 49.968
2024-08-28 | 8:08 | 49.963
2024-08-28 | 8:08 | 49.964
2024-08-28 | 8:08 | 49.965
2024-08-28 | 8:08 | 49.963
2024-08-28 | 8:08 | 49.965
2024-08-28 | 8:08 | 49.97
2024-08-28 | 8:08 | 49.973
2024-08-28 | 8:08 | 49.977
2024-08-28 | 8:08 | 49.981
2024-08-28 | 8:08 | 49.982
2024-08-28 | 8:08 | 49.985
2024-08-28 | 8:08 | 49.983
2024-08-28 | 8:08 | 49.984
2024-08-28 | 8:08 | 49.985
2024-08-28 | 8:08 | 49.986
2024-08-28 | 8:08 | 49.986
2024-08-28 | 8:08 | 49.983

## 20240828-2
In GMT
Date | Time | Freq
2024-08-28 | 19:56 | 49.982 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2024-08-28 | 19:56 | 49.983 | 222 | BRITNED | 676.211
2024-08-28 | 19:56 | 49.983 | 268 | WBURB-2 | 428.156
2024-08-28 | 19:56 | 49.979 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2024-08-28 | 19:56 | 49.977 |  | Viking Link | -648.9
2024-08-28 | 19:56 | 49.974 |  | Viking Link | 1398.96
2024-08-28 | 19:56 | 49.973 | 209 | DRAXX-3 | 626.95
2024-08-28 | 19:56 | 49.972 | 154 | CDCL-1 | 391.57
2024-08-28 | 19:56 | 49.972 | 268 | ROCK-1 | 468.495
2024-08-28 | 19:56 | 49.971 | 148 | IFA Bipole1 | 945.473
2024-08-28 | 19:56 | 49.971 | 132 | IFA Bipole1 | 999.1
2024-08-28 | 19:56 | 49.969 | 141 | IFA Bipole2 | 1000
2024-08-28 | 19:56 | 49.969 | 135 | IFA Bipole1 | 996.75
2024-08-28 | 19:56 | 49.969 |  | Viking Link | -780.3
2024-08-28 | 19:56 | 49.972
2024-08-28 | 19:56 | 49.974
2024-08-28 | 19:56 | 49.976
2024-08-28 | 19:56 | 49.976
2024-08-28 | 19:56 | 49.978
2024-08-28 | 19:56 | 49.978 | 130 | HEYM12 | 271.908
2024-08-28 | 19:56 | 49.979 | 228 | HUMR-1 | 303.75
2024-08-28 | 19:56 | 49.979
2024-08-28 | 19:56 | 49.979
2024-08-28 | 19:56 | 49.978
2024-08-28 | 19:56 | 49.981
2024-08-28 | 19:56 | 49.981
2024-08-28 | 19:56 | 49.982
2024-08-28 | 19:56 | 49.983
2024-08-28 | 19:56 | 49.984
2024-08-28 | 19:56 | 49.982
2024-08-28 | 19:56 | 49.98 | 211 | CDCL-1 | 291.5
2024-08-28 | 19:57 | 49.98 | 199 | STAY-2 | 413.125
2024-08-28 | 19:57 | 49.979 | 173 | CDCL-1 | 397.375
2024-08-28 | 19:57 | 49.978 | 248 | SEAB-2 | 361.25
2024-08-28 | 19:57 | 49.978 | 255 | FRANCE | 995.65
2024-08-28 | 19:57 | 49.979 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2024-08-28 | 19:57 | 49.98
2024-08-28 | 19:57 | 49.98
2024-08-28 | 19:57 | 49.981
2024-08-28 | 19:57 | 49.98
2024-08-28 | 19:57 | 49.98
2024-08-28 | 19:57 | 49.979
2024-08-28 | 19:57 | 49.98
2024-08-28 | 19:57 | 49.981
2024-08-28 | 19:57 | 49.982
2024-08-28 | 19:57 | 49.982
2024-08-28 | 19:57 | 49.976
2024-08-28 | 19:57 | 49.921
2024-08-28 | 19:57 | 49.875
2024-08-28 | 19:57 | 49.842
2024-08-28 | 19:57 | 49.823
2024-08-28 | 19:57 | 49.816
2024-08-28 | 19:57 | 49.814
2024-08-28 | 19:57 | 49.812
2024-08-28 | 19:57 | 49.812
2024-08-28 | 19:57 | 49.812
2024-08-28 | 19:57 | 49.812
2024-08-28 | 19:57 | 49.812
2024-08-28 | 19:57 | 49.813
2024-08-28 | 19:57 | 49.813
2024-08-28 | 19:57 | 49.813
2024-08-28 | 19:57 | 49.812
2024-08-28 | 19:57 | 49.814
2024-08-28 | 19:57 | 49.816
2024-08-28 | 19:57 | 49.814
2024-08-28 | 19:57 | 49.815
2024-08-28 | 19:57 | 49.814
2024-08-28 | 19:57 | 49.812
2024-08-28 | 19:57 | 49.811
2024-08-28 | 19:57 | 49.81
2024-08-28 | 19:57 | 49.81
2024-08-28 | 19:57 | 49.808
2024-08-28 | 19:57 | 49.807
2024-08-28 | 19:57 | 49.809
2024-08-28 | 19:57 | 49.809
2024-08-28 | 19:57 | 49.809
2024-08-28 | 19:57 | 49.81
2024-08-28 | 19:57 | 49.804
2024-08-28 | 19:57 | 49.806
2024-08-28 | 19:57 | 49.803
2024-08-28 | 19:57 | 49.803
2024-08-28 | 19:57 | 49.804
2024-08-28 | 19:57 | 49.803
2024-08-28 | 19:57 | 49.799
2024-08-28 | 19:57 | 49.796
2024-08-28 | 19:57 | 49.797
2024-08-28 | 19:57 | 49.797
2024-08-28 | 19:57 | 49.796
2024-08-28 | 19:57 | 49.796
2024-08-28 | 19:57 | 49.798
2024-08-28 | 19:58 | 49.8
2024-08-28 | 19:58 | 49.801
2024-08-28 | 19:58 | 49.802
2024-08-28 | 19:58 | 49.805
2024-08-28 | 19:58 | 49.805
2024-08-28 | 19:58 | 49.805
2024-08-28 | 19:58 | 49.808
2024-08-28 | 19:58 | 49.81
2024-08-28 | 19:58 | 49.81
2024-08-28 | 19:58 | 49.808
2024-08-28 | 19:58 | 49.808
2024-08-28 | 19:58 | 49.809
2024-08-28 | 19:58 | 49.808
2024-08-28 | 19:58 | 49.808
2024-08-28 | 19:58 | 49.811
2024-08-28 | 19:58 | 49.812
2024-08-28 | 19:58 | 49.813
2024-08-28 | 19:58 | 49.813
2024-08-28 | 19:58 | 49.813
2024-08-28 | 19:58 | 49.817
2024-08-28 | 19:58 | 49.814
2024-08-28 | 19:58 | 49.814
2024-08-28 | 19:58 | 49.811
2024-08-28 | 19:58 | 49.808
2024-08-28 | 19:58 | 49.805
2024-08-28 | 19:58 | 49.804
2024-08-28 | 19:58 | 49.802
2024-08-28 | 19:58 | 49.797
2024-08-28 | 19:58 | 49.795
2024-08-28 | 19:58 | 49.795
2024-08-28 | 19:58 | 49.797
2024-08-28 | 19:58 | 49.794
2024-08-28 | 19:58 | 49.793
2024-08-28 | 19:58 | 49.793
2024-08-28 | 19:58 | 49.793
2024-08-28 | 19:58 | 49.792
2024-08-28 | 19:58 | 49.792
2024-08-28 | 19:58 | 49.792
2024-08-28 | 19:58 | 49.792
2024-08-28 | 19:58 | 49.792
2024-08-28 | 19:58 | 49.79
2024-08-28 | 19:58 | 49.791
2024-08-28 | 19:58 | 49.794
2024-08-28 | 19:58 | 49.798
2024-08-28 | 19:58 | 49.8
2024-08-28 | 19:58 | 49.807
2024-08-28 | 19:58 | 49.817
2024-08-28 | 19:58 | 49.823
2024-08-28 | 19:58 | 49.832
2024-08-28 | 19:58 | 49.84
2024-08-28 | 19:58 | 49.85
2024-08-28 | 19:58 | 49.856
2024-08-28 | 19:58 | 49.864
2024-08-28 | 19:58 | 49.87
2024-08-28 | 19:58 | 49.873
2024-08-28 | 19:58 | 49.878
2024-08-28 | 19:58 | 49.882
2024-08-28 | 19:58 | 49.888
2024-08-28 | 19:58 | 49.893
2024-08-28 | 19:58 | 49.9
2024-08-28 | 19:59 | 49.904
2024-08-28 | 19:59 | 49.909
2024-08-28 | 19:59 | 49.914
2024-08-28 | 19:59 | 49.921
2024-08-28 | 19:59 | 49.927
2024-08-28 | 19:59 | 49.932
2024-08-28 | 19:59 | 49.937
2024-08-28 | 19:59 | 49.939
2024-08-28 | 19:59 | 49.943
2024-08-28 | 19:59 | 49.945
2024-08-28 | 19:59 | 49.947
2024-08-28 | 19:59 | 49.948
2024-08-28 | 19:59 | 49.946
2024-08-28 | 19:59 | 49.945
2024-08-28 | 19:59 | 49.943
2024-08-28 | 19:59 | 49.942
2024-08-28 | 19:59 | 49.942
2024-08-28 | 19:59 | 49.942
2024-08-28 | 19:59 | 49.942
2024-08-28 | 19:59 | 49.943
2024-08-28 | 19:59 | 49.944
2024-08-28 | 19:59 | 49.945
2024-08-28 | 19:59 | 49.944
2024-08-28 | 19:59 | 49.946
2024-08-28 | 19:59 | 49.946
2024-08-28 | 19:59 | 49.946
2024-08-28 | 19:59 | 49.946
2024-08-28 | 19:59 | 49.944
2024-08-28 | 19:59 | 49.943
2024-08-28 | 19:59 | 49.94
2024-08-28 | 19:59 | 49.937
2024-08-28 | 19:59 | 49.936
2024-08-28 | 19:59 | 49.932
2024-08-28 | 19:59 | 49.931
2024-08-28 | 19:59 | 49.926
2024-08-28 | 19:59 | 49.922
2024-08-28 | 19:59 | 49.92
2024-08-28 | 19:59 | 49.919
2024-08-28 | 19:59 | 49.92
2024-08-28 | 19:59 | 49.921
2024-08-28 | 19:59 | 49.925
2024-08-28 | 19:59 | 49.927
2024-08-28 | 19:59 | 49.927
2024-08-28 | 19:59 | 49.925
2024-08-28 | 19:59 | 49.923
2024-08-28 | 19:59 | 49.92
2024-08-28 | 19:59 | 49.919
2024-08-28 | 19:59 | 49.92
2024-08-28 | 19:59 | 49.918
2024-08-28 | 19:59 | 49.917
2024-08-28 | 19:59 | 49.915
2024-08-28 | 19:59 | 49.912
2024-08-28 | 19:59 | 49.91
2024-08-28 | 19:59 | 49.907
2024-08-28 | 19:59 | 49.904
2024-08-28 | 19:59 | 49.903
2024-08-28 | 19:59 | 49.903
2024-08-28 | 19:59 | 49.902
2024-08-28 | 19:59 | 49.902
2024-08-28 | 19:59 | 49.9
2024-08-28 | 20:00 | 49.899
2024-08-28 | 20:00 | 49.897
2024-08-28 | 20:00 | 49.898
2024-08-28 | 20:00 | 49.899
2024-08-28 | 20:00 | 49.9
2024-08-28 | 20:00 | 49.9
2024-08-28 | 20:00 | 49.901
2024-08-28 | 20:00 | 49.903
2024-08-28 | 20:00 | 49.901
2024-08-28 | 20:00 | 49.901
2024-08-28 | 20:00 | 49.902
2024-08-28 | 20:00 | 49.902
2024-08-28 | 20:00 | 49.902
2024-08-28 | 20:00 | 49.902
2024-08-28 | 20:00 | 49.901
2024-08-28 | 20:00 | 49.902
2024-08-28 | 20:00 | 49.901
2024-08-28 | 20:00 | 49.9
2024-08-28 | 20:00 | 49.901
2024-08-28 | 20:00 | 49.902
2024-08-28 | 20:00 | 49.902
2024-08-28 | 20:00 | 49.902
2024-08-28 | 20:00 | 49.903
2024-08-28 | 20:00 | 49.903
2024-08-28 | 20:00 | 49.905
2024-08-28 | 20:00 | 49.903
2024-08-28 | 20:00 | 49.903
2024-08-28 | 20:00 | 49.903
2024-08-28 | 20:00 | 49.899
2024-08-28 | 20:00 | 49.897
2024-08-28 | 20:00 | 49.895
2024-08-28 | 20:00 | 49.895
2024-08-28 | 20:00 | 49.894
2024-08-28 | 20:00 | 49.893
2024-08-28 | 20:00 | 49.892
2024-08-28 | 20:00 | 49.894
2024-08-28 | 20:00 | 49.894
2024-08-28 | 20:00 | 49.894
2024-08-28 | 20:00 | 49.89
2024-08-28 | 20:00 | 49.889
2024-08-28 | 20:00 | 49.884
2024-08-28 | 20:00 | 49.883
2024-08-28 | 20:00 | 49.885
2024-08-28 | 20:00 | 49.888
2024-08-28 | 20:00 | 49.889
2024-08-28 | 20:00 | 49.892
2024-08-28 | 20:00 | 49.891
2024-08-28 | 20:00 | 49.886
2024-08-28 | 20:00 | 49.884
2024-08-28 | 20:00 | 49.885
2024-08-28 | 20:00 | 49.886
2024-08-28 | 20:00 | 49.887
2024-08-28 | 20:00 | 49.887
2024-08-28 | 20:00 | 49.887
2024-08-28 | 20:00 | 49.888
2024-08-28 | 20:00 | 49.888
2024-08-28 | 20:00 | 49.888
2024-08-28 | 20:00 | 49.89
2024-08-28 | 20:00 | 49.89
2024-08-28 | 20:00 | 49.89
2024-08-28 | 20:00 | 49.888
2024-08-28 | 20:01 | 49.889
2024-08-28 | 20:01 | 49.887
2024-08-28 | 20:01 | 49.885
2024-08-28 | 20:01 | 49.887
2024-08-28 | 20:01 | 49.887
2024-08-28 | 20:01 | 49.887
2024-08-28 | 20:01 | 49.886
2024-08-28 | 20:01 | 49.886
2024-08-28 | 20:01 | 49.886
2024-08-28 | 20:01 | 49.885
2024-08-28 | 20:01 | 49.886
2024-08-28 | 20:01 | 49.886
2024-08-28 | 20:01 | 49.888
2024-08-28 | 20:01 | 49.89
2024-08-28 | 20:01 | 49.89
2024-08-28 | 20:01 | 49.89
2024-08-28 | 20:01 | 49.89
2024-08-28 | 20:01 | 49.889
2024-08-28 | 20:01 | 49.887
2024-08-28 | 20:01 | 49.886
2024-08-28 | 20:01 | 49.883
2024-08-28 | 20:01 | 49.881
2024-08-28 | 20:01 | 49.881
2024-08-28 | 20:01 | 49.88
2024-08-28 | 20:01 | 49.88
2024-08-28 | 20:01 | 49.88
2024-08-28 | 20:01 | 49.879
2024-08-28 | 20:01 | 49.881
2024-08-28 | 20:01 | 49.881
2024-08-28 | 20:01 | 49.881
2024-08-28 | 20:01 | 49.88
2024-08-28 | 20:01 | 49.879
2024-08-28 | 20:01 | 49.88
2024-08-28 | 20:01 | 49.876
2024-08-28 | 20:01 | 49.875
2024-08-28 | 20:01 | 49.873
2024-08-28 | 20:01 | 49.874
2024-08-28 | 20:01 | 49.873
2024-08-28 | 20:01 | 49.874
2024-08-28 | 20:01 | 49.874
2024-08-28 | 20:01 | 49.876
2024-08-28 | 20:01 | 49.872
2024-08-28 | 20:01 | 49.868
2024-08-28 | 20:01 | 49.866
2024-08-28 | 20:01 | 49.864
2024-08-28 | 20:01 | 49.863
2024-08-28 | 20:01 | 49.864
2024-08-28 | 20:01 | 49.866
2024-08-28 | 20:01 | 49.866
2024-08-28 | 20:01 | 49.868
2024-08-28 | 20:01 | 49.868
2024-08-28 | 20:01 | 49.87
2024-08-28 | 20:01 | 49.87
2024-08-28 | 20:01 | 49.87
2024-08-28 | 20:01 | 49.874
2024-08-28 | 20:01 | 49.878
2024-08-28 | 20:01 | 49.879
2024-08-28 | 20:01 | 49.882
2024-08-28 | 20:01 | 49.881
2024-08-28 | 20:02 | 49.882
2024-08-28 | 20:02 | 49.88
2024-08-28 | 20:02 | 49.882
2024-08-28 | 20:02 | 49.884
2024-08-28 | 20:02 | 49.888
2024-08-28 | 20:02 | 49.891
2024-08-28 | 20:02 | 49.89
2024-08-28 | 20:02 | 49.894
2024-08-28 | 20:02 | 49.892
2024-08-28 | 20:02 | 49.893
2024-08-28 | 20:02 | 49.899
2024-08-28 | 20:02 | 49.904
2024-08-28 | 20:02 | 49.91
2024-08-28 | 20:02 | 49.914
2024-08-28 | 20:02 | 49.92
2024-08-28 | 20:02 | 49.927
2024-08-28 | 20:02 | 49.928
2024-08-28 | 20:02 | 49.932
2024-08-28 | 20:02 | 49.932
2024-08-28 | 20:02 | 49.933
2024-08-28 | 20:02 | 49.932
2024-08-28 | 20:02 | 49.933
2024-08-28 | 20:02 | 49.933
2024-08-28 | 20:02 | 49.933
2024-08-28 | 20:02 | 49.934
2024-08-28 | 20:02 | 49.934
2024-08-28 | 20:02 | 49.935
2024-08-28 | 20:02 | 49.936
2024-08-28 | 20:02 | 49.935
2024-08-28 | 20:02 | 49.934
2024-08-28 | 20:02 | 49.934
2024-08-28 | 20:02 | 49.932
2024-08-28 | 20:02 | 49.933
2024-08-28 | 20:02 | 49.933
2024-08-28 | 20:02 | 49.933
2024-08-28 | 20:02 | 49.931
2024-08-28 | 20:02 | 49.931
2024-08-28 | 20:02 | 49.932
2024-08-28 | 20:02 | 49.935
2024-08-28 | 20:02 | 49.939
2024-08-28 | 20:02 | 49.942
2024-08-28 | 20:02 | 49.946
2024-08-28 | 20:02 | 49.95
2024-08-28 | 20:02 | 49.951
2024-08-28 | 20:02 | 49.951
2024-08-28 | 20:02 | 49.951
2024-08-28 | 20:02 | 49.953
2024-08-28 | 20:02 | 49.953
2024-08-28 | 20:02 | 49.954
2024-08-28 | 20:02 | 49.955
2024-08-28 | 20:02 | 49.959
2024-08-28 | 20:02 | 49.962
2024-08-28 | 20:02 | 49.962
2024-08-28 | 20:02 | 49.963
2024-08-28 | 20:02 | 49.965
2024-08-28 | 20:02 | 49.966
2024-08-28 | 20:02 | 49.965
2024-08-28 | 20:02 | 49.965
2024-08-28 | 20:02 | 49.965
2024-08-28 | 20:02 | 49.964
2024-08-28 | 20:03 | 49.962
2024-08-28 | 20:03 | 49.96
2024-08-28 | 20:03 | 49.961
2024-08-28 | 20:03 | 49.962
2024-08-28 | 20:03 | 49.962
2024-08-28 | 20:03 | 49.963
2024-08-28 | 20:03 | 49.963
2024-08-28 | 20:03 | 49.962
2024-08-28 | 20:03 | 49.961
2024-08-28 | 20:03 | 49.96
2024-08-28 | 20:03 | 49.959
2024-08-28 | 20:03 | 49.959
2024-08-28 | 20:03 | 49.96
2024-08-28 | 20:03 | 49.96
2024-08-28 | 20:03 | 49.962
2024-08-28 | 20:03 | 49.965
2024-08-28 | 20:03 | 49.967
2024-08-28 | 20:03 | 49.969
2024-08-28 | 20:03 | 49.973
2024-08-28 | 20:03 | 49.974
2024-08-28 | 20:03 | 49.977
2024-08-28 | 20:03 | 49.981
2024-08-28 | 20:03 | 49.982
2024-08-28 | 20:03 | 49.983
2024-08-28 | 20:03 | 49.985
2024-08-28 | 20:03 | 49.989
2024-08-28 | 20:03 | 49.995
2024-08-28 | 20:03 | 49.998
2024-08-28 | 20:03 | 50.003
2024-08-28 | 20:03 | 50.008
2024-08-28 | 20:03 | 50.012
2024-08-28 | 20:03 | 50.015
2024-08-28 | 20:03 | 50.018
2024-08-28 | 20:03 | 50.019
2024-08-28 | 20:03 | 50.018
2024-08-28 | 20:03 | 50.016
2024-08-28 | 20:03 | 50.016
2024-08-28 | 20:03 | 50.018
2024-08-28 | 20:03 | 50.017
2024-08-28 | 20:03 | 50.018
2024-08-28 | 20:03 | 50.02
2024-08-28 | 20:03 | 50.022
2024-08-28 | 20:03 | 50.022
2024-08-28 | 20:03 | 50.022
2024-08-28 | 20:03 | 50.023
2024-08-28 | 20:03 | 50.023
2024-08-28 | 20:03 | 50.023
2024-08-28 | 20:03 | 50.023
2024-08-28 | 20:03 | 50.022
2024-08-28 | 20:03 | 50.022
2024-08-28 | 20:03 | 50.022
2024-08-28 | 20:03 | 50.024
2024-08-28 | 20:03 | 50.023
2024-08-28 | 20:03 | 50.025
2024-08-28 | 20:03 | 50.028
2024-08-28 | 20:03 | 50.03
2024-08-28 | 20:03 | 50.035
2024-08-28 | 20:03 | 50.036
2024-08-28 | 20:03 | 50.036
2024-08-28 | 20:03 | 50.037
2024-08-28 | 20:04 | 50.039
2024-08-28 | 20:04 | 50.04
2024-08-28 | 20:04 | 50.039
2024-08-28 | 20:04 | 50.04
2024-08-28 | 20:04 | 50.044
2024-08-28 | 20:04 | 50.04
2024-08-28 | 20:04 | 50.038
2024-08-28 | 20:04 | 50.035
2024-08-28 | 20:04 | 50.036
2024-08-28 | 20:04 | 50.037
2024-08-28 | 20:04 | 50.033
2024-08-28 | 20:04 | 50.031
2024-08-28 | 20:04 | 50.03
2024-08-28 | 20:04 | 50.028
2024-08-28 | 20:04 | 50.03
2024-08-28 | 20:04 | 50.028
2024-08-28 | 20:04 | 50.028
2024-08-28 | 20:04 | 50.03
2024-08-28 | 20:04 | 50.029
2024-08-28 | 20:04 | 50.032
2024-08-28 | 20:04 | 50.034
2024-08-28 | 20:04 | 50.037
2024-08-28 | 20:04 | 50.037
2024-08-28 | 20:04 | 50.038
2024-08-28 | 20:04 | 50.04
2024-08-28 | 20:04 | 50.038
2024-08-28 | 20:04 | 50.042
2024-08-28 | 20:04 | 50.04
2024-08-28 | 20:04 | 50.039
2024-08-28 | 20:04 | 50.038
2024-08-28 | 20:04 | 50.038

## V20240820-1
Date | Time | Va PU | Vb PU | Vc PU
08/20/2024 | 22:07 | 1.0004 | 1.0116 | 1.0089
08/20/2024 | 22:07 | 1.0007 | 1.0116 | 1.0085
08/20/2024 | 22:07 | 1.0011 | 1.0114 | 1.0082
08/20/2024 | 22:07 | 1.0013 | 1.011 | 1.0082
08/20/2024 | 22:07 | 1.0014 | 1.0106 | 1.0085
08/20/2024 | 22:07 | 1.0012 | 1.0103 | 1.0088
08/20/2024 | 22:07 | 1.0009 | 1.0102 | 1.0091
08/20/2024 | 22:07 | 1.0004 | 1.0104 | 1.0093
08/20/2024 | 22:07 | 1.0001 | 1.0107 | 1.0092
08/20/2024 | 22:07 | 0.99991 | 1.011 | 1.0089
08/20/2024 | 22:07 | 1 | 1.0113 | 1.0085
08/20/2024 | 22:07 | 1.0003 | 1.0113 | 1.0081
08/20/2024 | 22:07 | 1.0007 | 1.011 | 1.0078
08/20/2024 | 22:07 | 1.001 | 1.0106 | 1.0078
08/20/2024 | 22:07 | 1.001 | 1.0101 | 1.0081
08/20/2024 | 22:07 | 1.0009 | 1.0099 | 1.0085
08/20/2024 | 22:07 | 1.0005 | 1.0098 | 1.0088
08/20/2024 | 22:07 | 1.0001 | 1.01 | 1.009
08/20/2024 | 22:07 | 0.9997 | 1.0103 | 1.0089
08/20/2024 | 22:07 | 0.99952 | 1.0107 | 1.0086
08/20/2024 | 22:07 | 0.99959 | 1.0109 | 1.0081
08/20/2024 | 22:07 | 0.99994 | 1.0109 | 1.0077
08/20/2024 | 22:07 | 1.0003 | 1.0107 | 1.0075
08/20/2024 | 22:07 | 1.0006 | 1.0102 | 1.0075
08/20/2024 | 22:07 | 1.0007 | 1.0098 | 1.0078
08/20/2024 | 22:07 | 1.0005 | 1.0095 | 1.0082
08/20/2024 | 22:07 | 1.0002 | 1.0095 | 1.0085
08/20/2024 | 22:07 | 0.99975 | 1.0097 | 1.0087
08/20/2024 | 22:07 | 0.99941 | 1.0101 | 1.0086
08/20/2024 | 22:07 | 0.99925 | 1.0104 | 1.0083
08/20/2024 | 22:07 | 0.99936 | 1.0106 | 1.0078
08/20/2024 | 22:07 | 0.99969 | 1.0106 | 1.0075
08/20/2024 | 22:07 | 1.0001 | 1.0104 | 1.0073
08/20/2024 | 22:07 | 1.0003 | 1.0096 | 1.0074
08/20/2024 | 22:07 | 1.0002 | 0.99978 | 1.0095
08/20/2024 | 22:07 | 0.99972 | 0.97186 | 1.0095
08/20/2024 | 22:07 | 0.99545 | 0.93553 | 1.0066
08/20/2024 | 22:07 | 0.98726 | 0.89916 | 1.0051
08/20/2024 | 22:07 | 0.97751 | 0.87192 | 1.0068
08/20/2024 | 22:07 | 0.96854 | 0.8574 | 1.0106
08/20/2024 | 22:07 | 0.9612 | 0.85344 | 1.0139
08/20/2024 | 22:07 | 0.95758 | 0.85347 | 1.0136
08/20/2024 | 22:07 | 0.95691 | 0.84901 | 1.01
08/20/2024 | 22:07 | 0.95877 | 0.83294 | 1.0032
08/20/2024 | 22:07 | 0.96072 | 0.80061 | 0.99613
08/20/2024 | 22:07 | 0.95867 | 0.75406 | 0.9904
08/20/2024 | 22:07 | 0.95055 | 0.69755 | 0.98645
08/20/2024 | 22:07 | 0.9366 | 0.64108 | 0.98486
08/20/2024 | 22:07 | 0.92072 | 0.59755 | 0.98617
08/20/2024 | 22:07 | 0.90589 | 0.57309 | 0.98963
08/20/2024 | 22:07 | 0.89557 | 0.56555 | 0.99311
08/20/2024 | 22:07 | 0.89158 | 0.56558 | 0.99305
08/20/2024 | 22:07 | 0.89336 | 0.55969 | 0.98845
08/20/2024 | 22:07 | 0.89785 | 0.53626 | 0.9795
08/20/2024 | 22:07 | 0.90125 | 0.5043 | 0.96879
08/20/2024 | 22:07 | 0.8995 | 0.48792 | 0.96391
08/20/2024 | 22:07 | 0.89461 | 0.47843 | 0.96464
08/20/2024 | 22:07 | 0.88787 | 0.47403 | 0.96536
08/20/2024 | 22:07 | 0.88165 | 0.47252 | 0.96427
08/20/2024 | 22:07 | 0.87721 | 0.47189 | 0.96237
08/20/2024 | 22:07 | 0.87537 | 0.47154 | 0.96092
08/20/2024 | 22:07 | 0.87546 | 0.47154 | 0.95967
08/20/2024 | 22:07 | 0.87818 | 0.47105 | 0.95766
08/20/2024 | 22:07 | 0.88143 | 0.46865 | 0.95602
08/20/2024 | 22:07 | 0.8833 | 0.46508 | 0.95546
08/20/2024 | 22:07 | 0.88327 | 0.46214 | 0.95687
08/20/2024 | 22:07 | 0.88232 | 0.46221 | 0.95867
08/20/2024 | 22:07 | 0.88117 | 0.4646 | 0.95952
08/20/2024 | 22:07 | 0.88031 | 0.46747 | 0.95867
08/20/2024 | 22:07 | 0.88097 | 0.46949 | 0.95687
08/20/2024 | 22:07 | 0.88218 | 0.47046 | 0.9547
08/20/2024 | 22:07 | 0.88371 | 0.47046 | 0.95235
08/20/2024 | 22:07 | 0.88503 | 0.46929 | 0.95009
08/20/2024 | 22:07 | 0.88641 | 0.46687 | 0.94859
08/20/2024 | 22:07 | 0.88753 | 0.46352 | 0.9487
08/20/2024 | 22:07 | 0.88762 | 0.46026 | 0.94985
08/20/2024 | 22:07 | 0.88708 | 0.45864 | 0.95097
08/20/2024 | 22:07 | 0.88686 | 0.45841 | 0.95139
08/20/2024 | 22:07 | 0.88778 | 0.45885 | 0.9509
08/20/2024 | 22:07 | 0.88907 | 0.45959 | 0.94921
08/20/2024 | 22:07 | 0.88966 | 0.46 | 0.94659
08/20/2024 | 22:07 | 0.88956 | 0.46006 | 0.94291
08/20/2024 | 22:07 | 0.88929 | 0.4597 | 0.93822
08/20/2024 | 22:07 | 0.88893 | 0.45877 | 0.93456
08/20/2024 | 22:07 | 0.88937 | 0.45768 | 0.93366
08/20/2024 | 22:07 | 0.88957 | 0.45691 | 0.93523
08/20/2024 | 22:07 | 0.88826 | 0.45947 | 0.93651
08/20/2024 | 22:07 | 0.8865 | 0.4815 | 0.93694
08/20/2024 | 22:07 | 0.88995 | 0.51563 | 0.93623
08/20/2024 | 22:07 | 0.89696 | 0.5398 | 0.93233
08/20/2024 | 22:07 | 0.90212 | 0.55072 | 0.92469
08/20/2024 | 22:07 | 0.9067 | 0.5526 | 0.91634
08/20/2024 | 22:07 | 0.9097 | 0.55225 | 0.91029
08/20/2024 | 22:07 | 0.90993 | 0.55783 | 0.90758
08/20/2024 | 22:07 | 0.90903 | 0.57612 | 0.90879
08/20/2024 | 22:07 | 0.90896 | 0.60999 | 0.91188
08/20/2024 | 22:07 | 0.91119 | 0.65367 | 0.91635
08/20/2024 | 22:07 | 0.91386 | 0.69788 | 0.92048
08/20/2024 | 22:07 | 0.91571 | 0.73462 | 0.92002
08/20/2024 | 22:07 | 0.9169 | 0.7591 | 0.91316
08/20/2024 | 22:07 | 0.92143 | 0.77168 | 0.90093
08/20/2024 | 22:07 | 0.93051 | 0.77448 | 0.89188
08/20/2024 | 22:07 | 0.93952 | 0.77437 | 0.89241
08/20/2024 | 22:07 | 0.9446 | 0.7802 | 0.90069
08/20/2024 | 22:07 | 0.94544 | 0.79874 | 0.91267
08/20/2024 | 22:07 | 0.94522 | 0.83108 | 0.92332
08/20/2024 | 22:07 | 0.94778 | 0.87086 | 0.93182
08/20/2024 | 22:07 | 0.95373 | 0.90349 | 0.93752
08/20/2024 | 22:07 | 0.95743 | 0.92259 | 0.93766
08/20/2024 | 22:07 | 0.95782 | 0.93305 | 0.93366
08/20/2024 | 22:07 | 0.96078 | 0.93835 | 0.92885
08/20/2024 | 22:07 | 0.96524 | 0.93942 | 0.92848
08/20/2024 | 22:07 | 0.96884 | 0.9395 | 0.93395
08/20/2024 | 22:07 | 0.97189 | 0.94123 | 0.94435
08/20/2024 | 22:07 | 0.97316 | 0.94647 | 0.95655
08/20/2024 | 22:07 | 0.97313 | 0.95367 | 0.96642
08/20/2024 | 22:07 | 0.97266 | 0.96086 | 0.97214
08/20/2024 | 22:07 | 0.9739 | 0.96906 | 0.97454
08/20/2024 | 22:07 | 0.97744 | 0.97641 | 0.97486
08/20/2024 | 22:07 | 0.98257 | 0.98059 | 0.97473
08/20/2024 | 22:07 | 0.98708 | 0.98165 | 0.97559
08/20/2024 | 22:07 | 0.98966 | 0.98162 | 0.97752
08/20/2024 | 22:07 | 0.99009 | 0.98179 | 0.98019
08/20/2024 | 22:07 | 0.98957 | 0.98343 | 0.98396
08/20/2024 | 22:07 | 0.98921 | 0.98689 | 0.98821
08/20/2024 | 22:07 | 0.98921 | 0.99085 | 0.99197
08/20/2024 | 22:07 | 0.98917 | 0.9944 | 0.99459
08/20/2024 | 22:07 | 0.98915 | 0.99687 | 0.99565
08/20/2024 | 22:07 | 0.98993 | 0.99858 | 0.99578
08/20/2024 | 22:07 | 0.99217 | 1.0001 | 0.99581
08/20/2024 | 22:07 | 0.99439 | 1.0006 | 0.99627
08/20/2024 | 22:07 | 0.99595 | 1.0006 | 0.99737
08/20/2024 | 22:07 | 0.9968 | 1.0007 | 0.99853
08/20/2024 | 22:07 | 0.99677 | 1.0012 | 0.99961
08/20/2024 | 22:07 | 0.99655 | 1.0026 | 1.0011
08/20/2024 | 22:07 | 0.99655 | 1.005 | 1.0028
08/20/2024 | 22:07 | 0.99677 | 1.0072 | 1.0036
08/20/2024 | 22:07 | 0.99716 | 1.0083 | 1.0036