## Response raw data (hidden)
ID | Start time | Completion time | Email | Name | Last modified time | Company Name | Respondent name and contact details | Does this response contain confidential information? If yes, please specify. | Please provide any specific comments relating to the proposed Phased Delivery Approach, Provider Eligibility, and Registration and Prequalification process for Phase 1 of the Quick Reserve service. | Please provide any specific comments relating to the proposed Service Utilisation & Dispatch Mechanism for Phase 1 of the Quick Reserve service. | Please provide any specific comments relating to proposed Quick Reserve Service Design Parameters including Notice to Start Ramping, Time to Full Delivery, Cease Time, Activation Periods, Recovery… | Please provide any specific comments relating to proposed Quick Reserve Metering including Operational Metering and Performance Metering. | Please provide any specific comments relating to proposed Quick Reserve Provider Availability, including Baselining, Energy Requirements, Cross-overs, Aggregation and Availability Declarations. | Please provide any specific comments relating to the proposed Quick Reserve Delivery Assessment including Settlement, ABSVD, and Performance Monitoring. | Please provide any specific comments relating to the proposed Procurement Approach including Maximum Bid Size, Service Windows and Locationality. | Please provide any specific comments relating to the proposed Auction Process including Timings, Bid submissions, and Auction Results. | Please provide any specific comments relating to the proposed Quick Reserve Market Design including Sell order structure (e.g. baskets, parent orders, child orders), overholding, and clearing algo... | Please share your feedback on ESO’s overall strategy to move to a single, simultaneous, co-optimised auction for the procurement of Frequency Response and Quick Reserve. | Please share any additional feedback on ESO’s proposed delivery of Quick Reserve that may fall outside of the questions above. | MCD Comments | SME | Draft response (due 09/08)
1 | 2024-07-04 13:10 | 2024-07-04 13:50 | anonymous |  |  | NGED | Luke Harker (lharker@nationalgrid.co.uk) | [7 empty] | Different terminology has been used in this document to that from the Stacking Technical Working Group – ‘Stacking’ is akin to the TWG’s ‘Co-Delivery’. It would be useful to align on terminology moving forward to avoid any potential confusion. |  |  |  | To facilitate the implementation of Primacy Rules a certain amount of data pertaining to the providers/assets involved in flexibility services needs to be exchanged with DNOs. For certain services in the past such data has not been collected/stored appropriately which has created blockers for the Primacy TWG. It would be useful to understand what data is being collected by the ESO in order for providers to access QR.
2 | 2024-07-22 09:03 | 2024-07-22 09:28 | anonymous |  |  | Peak Gen Top Co Limited | Nick Sillito | No |  | We think the proposed solution is sensible | The proposed contract from does not explicitly state the run down rate at the end of the delivery. We infer that it is meant to be identical to the run up rate. It would be helpful if this was made explicit | No further comments beyond our discussion on clarifying if distribution network line loss factors should be included for distribution connected providers | No additional comments | Para 9.2 of the contract is unclear regarding ABSVD. It would be clearer if it stated that there will be no ABSVD adjustments when the service is delivered via BOAs in the BM | We are generally supportive of the proposal. We note that when NGESO expects to procure around 300 MW of service, allowing units up to 300 MW to participate risks an outcome where a single failure will result in the loss of all service. A smaller size may be more appropriate It is important to be explicit how a unit is sized. A 50 MW storage unit is able to deliver 100 MW of service by moving from 50 MW of input to 50 MW of export. | We are supportive of the proposal | We have not reviewed the detail of the proposal but we are supportive based on our initial assessment | We are supportive | We are concerned by the potential penalty for non delivery of the service. See para 14.3 and the definition of "Incremental Volume Cost Amount" We do not see how the cost of the most expensive offer accepted relates to the cost of replacing quick reserve (for example we would expect the value of a bid to be subtracted along with the avoided payment to the failed provider). A more justifiable method for calculating the cost of the replacement service would be to rerun the auction, without the failed unit and charge the failed provider the different between the new and the old clearing price. | The penalty regime is consistent across all new Reserve Services. If the volume that a provider is not going to deliver despite being contracted, we may need to seek to replace such volume through Balancing Mechanism. This is the reason why we are proposing this penalty mechanism. We expect there to be an interchangeability between Quick Reserve and Balancing Reserve, as many of the BR units we have seen have been QR capable, and so we may find that in real time the optimal cost option is to run QR in merit (if cheaper than BR) and hold our QR requirement on BR assets. Because of this we feel that it is appropriate that the services have consistent penalty structure to avoid either the market or the ESO having an incentive to prefer one market over another. The cost of replacing the volume may not be the same as the cost of new clearing price deriving from reruning the auction therefore we feel this may not be the most practical approach and would leave ESO exposed to higher cost for end consumer.
3 | 2024-07-25 15:58 | 2024-07-25 16:25 | anonymous |  |  | SSEN Distribution, trading name of Southern Electric Power Distribution plc | Brian Wann Contact details : Brian.Wann@sse.com M: 0777 660 3535 T: 441738341036 | No | We consider the proposed Phased Delivery Approach to be inherently unfair and anti-competitive as it excludes non-BM providers from participating during Phase 1. ESO's justification for this approach is not based on any inherent benefit of BM providers over non-BMs, but simply their own systems' inability to accommodate non-BMs into the new market before summer 2025. Furthermore, the ESO’s stated plan to procure 100% of its requirement from the day-ahead Quick Reserve market from November 2024, and as little as possible from the existing within-day Fast Reserve market, is discriminatory to non-BM Fast Reserve providers, who will be immediately excluded from participating in this market. The ESO’s suggested mitigation is for non-BM Fast Reserve providers to join the BM, but this is not feasible for some providers, such as those delivering reserve services using CLASS solutions. Timescales do not allow a large, aggregated CLASS provider time to develop a solution to achieve the more technically onerous requirements of Quick Reserve between now and November 2024. ESO and Ofgem have both actively encouraged and supported CLASS providers to enter this market, and this change in procurement strategy is contrary to previous communications from ESO. We suggest alternative approaches which ESO could implement: either postpone the launch of the Quick Reserve (QR) market until it is open to both BM and non-BM participants alike; or adopt a gradual cutover between the FR and QR markets, for example by initially procuring 10% of required volumes from QR and increasing that by a further 10% each month during the transition period. Such a gradual cutover would also support ESO’s aim for cross-market competition, as outlined below. These approaches both provide volume in the non-BM OFR market until participants are allowed to join the replacement non-BM QR market, maximizing market liquidity and ensuring ESO can maintain system security at the lowest possible cost. ESO has stated that it wants to use the existing Optional Fast Reserve (OFR) market to provide cross-market price competition to QR during Phase 1, despite its clearly stated intention to procure as little as possible OFR from day one of QR. This seems contradictory, because as the expected OFR volume falls immediately to near zero, so does the commercial incentive for SSEN to continue its investment to provide a solution suitable to participate in OFR, and subsequently submit competitive offers to the OFR market. Cross-market competition only works if both markets are active and liquid. In fact, given the very low expected procured volumes, as well as ESO’s stated intention to only buy OFR in emergencies, OFR participants will be inclined to offer higher market prices to reflect both the limited opportunities for revenue and the knowledge that ESO will only ever approach them as a distressed buyer. A gradual cutover from the OFR to the QR market would both maintain price competition within the residual OFR market and provide genuine price signals to the growing QR market. Broadly, we are disappointed with ESO’s approach and timing to publishing the revised proposed strategy. The proposed changes to procurement strategy are contrary to those that ESO has shared with us previously and are a prohibitive factor in our ability to justify participating in the market from November 2024. There is also a risk for the ESO there will be a lack of confidence in future developments and market signalling with this pivot at such a late stage, resulting in a wariness from participants to invest in the infrastructure needed to offer services in the future. | No comments | Several of the Quick Reserve technical parameters are more onerous than their Fast Reserve equivalents, and some have an impact on our ability to offer and deliver a Quick Reserve service due to our CLASS asset type. Time to Full Delivery is proposed to be a maximum of 1 minute from dispatch, as opposed to 2 minutes for OFR. ESO estimates that only “around 30% of the non-BM OFR capacity… can achieve the 1-minute time to full delivery,” (quote from the Quick Reserve Summary document, p9) and we (SSEN) would fall into the 70% of capacity which cannot. Our “unit” is an aggregated and geographically dispersed group of assets. Reducing the “time to full delivery” from 2 minutes to 1 minute will require significant design, investment and implementation of an improved solution. This is not achievable by November 2024. The maximum Recovery Period for Quick Reserve is proposed to be 3 minutes, whereas for the OFR service recovery period is 15 minutes. Again, meeting this change to requirements would significantly restrict our offering to a small proportion of our available capacity at any time, keeping volume in reserve to be available for dispatch 3 minutes later while the previously dispatched assets recover. Furthermore, delivering even this diminished volume would require significant investment in scheduling and dispatch systems to cycle through available aggregated assets in a way that is not necessary for our OFR service, and therefore not in place. At this point, we would not be able to provide a service with this requirement. The cumulative effect of these changes is to diminish the volume of OFR capacity that will be available to offer QR, which would be disadvantageous for ESO and for market competition generally. However, given that the ESO (i) already accepts that 70% of that capacity will be ineligible for QR, and (ii) is confident that it will be able to meet 100% of its QR needs without any OFR volume, it appears that this market competition is not considered by the ESO to be of significant value. We feel there is a risk ESO is focused on this approach to ‘Standardise’ products; we support the standardisation of products across the industry. However, the approach taken risks increasing rather than reducing barriers to entry. | As a non-BM OFR provider, the “Meter Data” we provide for both operational and settlement purposes is derived from our own operational data using a methodology and formula that has been agreed with the ESO. We would use the methodology outlined in our Data Approach (v2.0 as previously shared with ESO on 1st May 2024 and formally approved by ESO on 18th July 2024), to generate the equivalent data for Quick Reserve (with 1-second granularity, as opposed to 15 seconds for operational data and 1 minute for settlement data as required under OFR). | As with the proposed technical parameters, several of these requirements vary from their OFR equivalents and some have an impact on our ability to deliver the new service. Baselining is a new requirement for QR that does not apply to OFR. The requirement to submit Physical Notifications (PN) 24 hours ahead and Final Physical Notifications (FPN) 1 hour ahead is an achievable technical upgrade, subject to our currently agreed position with the ESO on baselining continuing to apply, i.e. that our PNs and FPNs will always be zero, and that there is no declarable activity from our assets unless and until we are dispatched to deliver the service. The proposed Energy Requirement for QR is that providers must be able to sustain their contracted capacity continuously for a full 30-minute QR Window (or for multiples of 30 minutes if offered as linked windows). The requirement for OFR is, and until recently the draft requirement for QR was, to be able to sustain delivery for 15 minutes. Meeting this latest and adjusted requirement would mean only offering a proportion of our total available capacity at any time, keeping assets in reserve to be available later in the period when the previously dispatched assets reach the limit of their physical capability. Furthermore, delivering even this diminished volume would require significant investment in scheduling and dispatch systems to cycle through available assets and coordinate between them, in a way that is not necessary for the existing OFR service, and therefore not in place. At this point we would not be able to provide this service. The requirement for the Firm (day ahead) QR service is to submit day-ahead Availability Declarations for every half-hour period in the following day. This is obviously not applicable to the within-day OFR service. For the Optional (within day) QR service, the requirement is for non-BM providers to submit Availability Declarations no later than 90 minutes ahead of the relevant delivery window, as opposed to 60 minutes ahead for BM providers of Optional QR and for OFR. It’s not clear why this requirement has been made more onerous for non-BM providers than for BM providers of the same service in the within-day market. This seems unnecessarily discriminatory against non-BM providers for no apparent reason. As with the technical parameters, the cumulative effect of these changes is to diminish the volume of OFR capacity that participants will be available to offer as QR, which would be worse for ESO and for market competition generally. | Firm QR participants will be subject to performance monitoring, with penalties applied for non-delivery and for availability deviating from their day-ahead offer. The current proposal only includes details of how this monitoring would be implemented for BM Units, so as a non-BM provider it is unclear whether we would be able to meet the monitoring requirement. Thus, assuming it is technically possible, this requirement would necessitate offering a capacity that is lower than our forecast volumes to avoid penalties for actual availability turning out lower than forecast. These performance monitoring requirements will diminish the volume of OFR capacity that participants will be available to offer QR, which would have a negative outcome for ESO and for market competition generally. | No comment | No comment | No comment | No comment | We are alarmed by the ESO’s stated intention to procure 100% of its expected need from the day-ahead Firm Quick Reserve Market as soon as it is launched in November 2024, as it undermines not just the existing Optional Fast Reserve market (as outlined in our response to Question 1) but also the forthcoming Optional Quick Reserve market before it has even opened. It is a dramatic change from ESO’s stated aim to encourage competition between the day-ahead and within-day markets and consider offers from both markets on their own merits, to ESO explicitly stating it plans and expects to fulfil 100% of its needs from the day-ahead market alone, and to use the within-day market only in emergencies. The latter is a clear statement of intent which serves only to undermine the liquidity and therefore the viability of the within-day markets. This is also contrary to the work and position that Ofgem has historically supported. The expectation of near-zero market volume makes entry into the OQR market difficult to justify commercially for potential participants. SSEN anticipates it will also have a perverse impact on the prices offered by those who do participate which is quite different from that anticipated by the ESO. Under the stated procurement strategy, within-day participants will know that the ESO will only ever approach them as a distressed buyer and participants are likely to set their prices accordingly. Consequently, OQR prices may turn out to be significantly higher than today’s OFR prices, where participants compete for “normal” daily volume. This is not in the best interests of GB energy customers. To make the OQR market liquid and viable, and to keep within-day prices low for both normal and emergency use, it would be better to always procure a proportion of the expected volume through that route, incentivising within-day sellers to remain competitive. We strongly encourage ESO to reconsider its commercial strategy in this regard. As a non-BM provider, we are also struck by several aspects of the proposal, including the exclusion of non-BM providers from the QR market during Phase 1, the acceptance of 70% of non-BM capacity being excluded indefinitely, and the seemingly arbitrary requirement for non-BMs to submit within-day offers 30 minutes ahead of BMs. ESO’s suggestion that non-BMs can simply join the BM is unfeasible for some providers, including those offering services using CLASS who have been encouraged to add liquidity to the market by both the ESO and Ofgem. The cumulative impression given is that Quick Reserve has been designed around and for BM participants, and non-BMs are at best an afterthought whose services are not needed, and at worst unwanted. This seems unnecessarily discriminatory, and as an organisation currently trying to build a business case to justify joining the market and investment in the infrastructure required, entirely counterproductive. Broadly, we are disappointed with ESO’s approach and timing to publishing the revised proposed strategy. The proposed changes, particularly the intention to procure 100% of need from QR and 0% from OFR as soon as the QR market opens, are contrary to those that ESO has shared with us previously, and are a prohibitive factor in our ability to justify participating in the market from November 2024.
4 | 2024-07-26 09:50 | 2024-07-26 09:53 | anonymous |  |  | Statera Energy | James Bolland. jbolland@stateraenergy.co.uk | No | Statera appreciates the Phased Delivery Approach, which will give BM participants the opportunity to deliver this service in a faster timeframe while ESO develops its systems to enable full market participation. The availability of Wider Access as a pathway to the service for non-BM units does help to provide fair access. The Registration and Prequalification processes is handled by our optimiser so Statera has no specific comments. | The use of existing processes/systems is welcome. | The Notice to Start Ramping being 0 minutes suggests that ESO expects providers to instantly process instructions – however, there are certain communications that providers may have set up with third-party systems, which this parameter currently doesn’t facilitate. In practice this may be fine given that Time to Full Delivery is 1 minute from instruction, but in theory it could exclude technologies that take a full minute to ramp but require additional time to process the dispatch instruction. Statera welcomes that there is no restriction on ramp up/down rates, meaning that batteries can respond without having to stagger their response. | Submission of Operational Metering at a frequency of once per second (1 Hz) with a latency of no greater than five (5) seconds, including active power and system frequency data, will require some changes to our current systems, working with third party providers to achieve those within the provided timelines for Phase 1 delivery. Using the 30-minute settlement metering data from Elexon to evaluate Availability, Time to Full Delivery, and Utilisation is welcome, but further clarification would be required in terms of Phase II performance monitoring. Is 1-second data expected? How will it be shared? And further communication on requirements for non-BM is still required, how will the performance metering data be shared? | Using existing BM processes for defining Availability and Baselining is welcome. Statera agrees with ESO’s approach to dealing with unwanted behaviours associated with State of Energy Management and Bid/Offer prices, but would appreciate clarity and precision in defining ‘excessively high or excessively low’ prices. This would ensure that all participants are assessed on a fair and transparent basis. | The hard cliff-edge whereby availability payments are foregone if a provider fails to deliver 95% of the instructed volume of energy is excessively punitive in Statera’s view. A more merciful approach, such as a sliding-scale penalty below 95% down to some value (for example 80%), would be less harmful for assets which have the occasional trip or fault during a Settlement Period while still achieving the same result for assets which are outright unavailable from the start of a Settlement Period. (Note: Statera holds the same view for Balancing Reserve, which is a similar service to the proposed Quick Reserve). Statera agrees with the principle of penalising over-delivery of energy. No comments on ABSVD as this makes use of an existing methodology. | Statera agrees with the Maximum Bid Size. Aligning Service Windows to match other Balancing Services, in terms of Settlement Periods, is welcome. | What is the reasoning behind proposing to move the auction to D-1 at 09:00 in Phase II? Would all Ancillary Services move towards D-1 09:00 auction (including DFR) in order to allow for co-optimisation of response and reserve auctions? Further clarity on defining the scope and methodology of Linked Buy-Orders would be appreciated, given it is a new mechanism that can impact volumes and prices being bid into the market. | No comment as Statera’s optimiser oversees bidding into the market on our behalf. | Statera welcomes ESO’s overall strategy in this regard, and encourages ESO to publish further details regarding timelines and mechanisms by which the co-optimised auction will operate. | None.
5 | 2024-07-26 10:11 | 2024-07-26 10:14 | anonymous |  |  | Flexitricity Limited | Lisa Perrin; Lisa.perrin@flexitricity.com | No | Flexitricity is a registered service provider for multiple asset types and has already fully registered in ESO’s Single Market Platform for registration and prequalification. We have no concerns over the proposal to utilise SMP for the BM-QR phase 1 registration and prequalification. ESO should engage with industry as soon as possible should there be any requirements for testing for BM-QR qualification, especially if this requires external validation via an Independent Technical Expert. | No comments on this for phase 1. We would encourage early engagement with industry on phase 2, non-BM, and the transition away from ASDP into OBP for non-BM assets | Recovery Periods: Whilst we appreciate that the ESO has relaxed the requirement for recovery periods from 1 minute to 3 minutes, this will still not enable I&C load to participate and will create a barrier to entry. The service should be designed to be technology agnostic and whilst the ESO is not explicitly restricting assets from participating, the recovery period parameter does make participation from assets, other than battery storage, particularly challenging. ESO should proactively engage with flexibility providers and I&C load participants before moving forward. Ramp Rates: We welcome the ESO’s proposed update on removing ramp rate restrictions for the QR service and for acknowledging the constraints this puts on providers in Dx response service delivery | Operational Metering: We understand the ESO intends to retain the 1Hz granularity of metering for QR which we believe to be overly restrictive for non-BM asset classes in Phase 2. We appreciate that ESO is undergoing an independent review of metering standards and currently conducting a 300MW small assets in the BM test case which may show that operational integrity can remain whilst relaxing metering standards. We look forward to the outcome of the independent review, but emphasise that the substantial delay in ESO’s timeline for this review should not necessitate the application of unnecessarily strict metering requirements for QR metering. Our expectation is that the learnings from the review and trial, both of which are well underway, should be incorporated into the QR product design as early as possible, so that metering standards for products not yet launched should be aligned so as not introduce unnecessary barriers to entry. | As these remain consistent with the current requirements for Balancing Mechanism participation, we see no issues with these and have no comments on the proposal. | We support the proposal for availability payments to be made based on pay-as-clear, and utilisation payments to be based on Bid-Offer Data provided in the Balancing Mechanism and paid for energy delivered volumes. We noted from the webinar on the 8th July that there will be additional terms applied for uneconomic pricing. We would hope that this is clear in the terms as failure could lead to ambiguity among providers. The ESO should provide some further guidance on this and advise providers whether any further information should be provided to the ESO to justify pricing parameters. No comments on ABSVD, but this should be applied to all assets (BM and non-BM) once we approach phase 2 implementation. | Service Windows: We welcome the 30-minute service windows and would encourage ESO to consider this service window sizing for all reserve and response products. This will support stacking/splitting in later phases of the Reserve reform and Response Reform releases. Furthermore, it will help with the economics if all services align with a 30-minute service window. Currently, bidders into QR at 30-minute service windows that are also bidding into Dx services for EFA block service windows, will need to account for the opportunity cost in QR to account for the risk of only being awarded a single service window, and being unable to provide Dx for the rest of the EFA. This could have the effect of increasing the QR pricing and therefore will not offer the lowest cost to consumers. This also creates an unnecessary barrier to stacking, which was identified as a priority in the draft Flexibility Market Strategy. We would like to see ESO make progress in the coming months to improving stacking opportunities for providers. Maximum Bid Size: 300MW for Phase 1 is a large percentage of the anticipated market size (at the Balancing Programme Event in June, it was suggested the full market size for Phase 1 will be ~500MW PQR and ~300MW NQR). This could result in a saturated market early in its implementation. Could the ESO provide some rationale to how this maximum bid size was decided? | Flexitricity is in support of a co-optimised auction at 2pm alongside the Response (Dx) services. We would encourage early engagement with industry before Phase 2 of the QR service design is finalised as we understand there is a proposal to move QR auctions to the morning for a single co-optimised Reserve Auction, alongside BR and SR (in 2025). Auction results for Phase 1 make sense given the timing of the auction. No comments here. No specific comments on Bid Submissions. | No specific comments on these points – this has been made clear in the consultation documents. | Feedback has been provided in Q8 on this point. However, we would like to reiterate and argue that all products should be run as a single co-optimised auction. This would include all products, across both Response and Reserve. The consultation outlines that Phase 2 approach is to split this into a Reserve (am) and Response (pm) auction, which we do not believe to be an optimised approach to ensuring all products are procured at the lowest possible cost to the end consumer. We would encourage ESO to consider this in phase 2 and provide industry with early engagement. | No additional comments.
6 | 2024-07-26 12:27 | 2024-07-26 12:32 | anonymous |  |  | Sembcorp Energy (UK) Limited | Mark Field (mark.field@sembcorp.com) | No | We believe it would be preferable from a non-discriminatory perspective to launch the service when all units, both BM and non-BM, are able to fully participate. This would provide greater competition and ensure a level playing field, as well as likely be most cost-effective for ESO. | No Comment | The 1-minute time to full delivery and maximum 3-minute recovery time could severely limit the participation of most technologies including our flexible reciprocating engines. We believe the market will be restricted to storage assets and thus limit the competitive offering. | We have reservations about the metering requirements and would appreciate further discussion to understand them better. | We would like to have further information on how crossovers will work in practice. | No Comment | No Comment | We are of the view that the auction should take place at 14:00 in conjunction with the Frequency Response services auction in order to allow as much market information as possible to be taken into consideration in bidding. This will enable the procurement to be as cost-effective as possible. | We would like orders to be of similar structure to those for the Dynamic suite of products including Linked Orders, to facilitate consistent submission. | We agree with the decision to have Quick Reserve procurement co-optimised with that of Frequency Response services. In that context, it seems strange to propose consideration in Phase 2 of moving the auction to the morning in line with the Balancing Reserve auction. We are of the view that the auction should remain later in the day in order to allow as much market information as possible to be taken into consideration in bidding. This will enable the procurement to be as cost-effective as possible. | Clause 5.11: While we agree with the spirit behind this clause, we do not believe it is within the remit of NGESO to determine what is “excessively” high or low pricing. We believe it is fair for NGESO to refer such instances to the Authority as per 5.11.1, but not with 5.11.2-5.11.4. There needs to be a clear, objective procedure for actions such as deregistering a unit or provider.
7 | 2024-07-26 14:59 | 2024-07-26 15:04 | anonymous |  |  | Drax Group | kamila.nugumanova@drax.com | no | The proposed phased approach is sensible given that the necessary technical and IT capability to integrate NBM participants will not be available until Summer 2025. In the meantime, we welcome the introduction of Phase 1 for BM participants and the use of existing industry processes for baselining, availability confirmations and performance monitoring. | We agree with the proposed service utilisation and dispatch mechanism requirements for Phase 1. Specifically, we agree with the Time to Full Delivery, Ramp Up and Ramp Down requirements, as well as the proposed Recovery window of 3 min. | We believe the proposed 3 min recovery period is an optimal threshold which maximises participation from available capacity, thus delivering market liquidity and cost benefits. Reducing this recovery period will significantly limit participation, and implicitly introduces discriminatory treatment for non-critical reasons by making delivery of the service suitable for one type of technology only. This may not be in line with the technology and size agnostic approach the ESO typically strives for. More importantly, this will increase the risk of over-reliance on one type of asset and jeopardises the efficiency of the service and security of meeting system needs. Moving forward, we would welcome an indication from the ESO on whether the Maximum Recovery Period study and analysis will continue exploring a move to a 2 min or lower recovery period in the future. If a shorter recovery period remains an option, we are keen to see timely engagement with industry stakeholders in any future technical or commercial studies. With regards to baselining, we agree with the acceptable baseline being either zero or non-zero. This allows PSH units to deliver from spin mode and enhance their participation in the market, hence improving liquidity and flexibility of the service. | We support the approach of using existing BM processes to submit operational metering. We also welcome the use of existing 30-minute average settlement metering data of BM units for performance monitoring purposes. This streamlines the process and creates a consistent and efficient approach which utilises existing standards and industry mechanisms. With regards to NBM performance and operational metering, we would welcome timely updates on the development of the ESO’s Performance monitoring capability and integration of operational metering in OBP. | We agree with the proposed terms, specifically we agree with baselining from zero or non-zero PN, as well as the ability to submit user-defined bid curtailment. We also support the introduction of new State of Charge rules for energy limited assets. We believe that these new rules coupled with similar requirements in the Dynamic Response service terms and GC0166 proposals will address the issue with insufficient energy or unavailability of energy limited assets for commercial reasons. We are, however, concerned that the legal text of the service terms specifically refers to ‘excessive pricing’ without providing a reference or a clear definition of what constitutes ‘excessive’. There is no generally accepted definition of ‘excessive pricing’ in either the licencing regime (such as the Transmission Constraint Licence Condition) or network codes. Therefore, we are concerned that this reference to ‘excessive pricing’, without any substantive regulatory or legislative grounding, may add additional complications to the Ofgem approval process and may cause a delay in the implementation of Quick Reserve. We also note that internal monitoring of instances of ‘excessive pricing’ will require substantial administrative and resource requirements from the relevant ESO teams and may create an unnecessary need for a dedicated investigation and dispute team. In order to avoid the risk of delays to the introduction of Quick reserve, we suggest the ESO expands on the legal standing and clear methodology applied to the identification of ‘excessive prices’ or defers the solution to technical requirements only, such as the new State of Charge rules and GC0166 (subject to approval). | We agree with the proposed Quick Reserve delivery assessment. We welcome the approach to performance monitoring, whereby service delivery of a unit is assessed over a greater period than the individual service day in order to establish overall delivery against the 95% performance measure. | The proposed procurement approach is largely consistent with the Balancing Reserve service and procurement terms. Locationality - We note that while the proposed approach for Phase 1 and Phase 2 is based on national procurement, the ESO has explored the option of locational procurement which proved to be complex and not achievable within the accelerated delivery time. However, it is not clear from the consultation whether the ESO will continue the analysis and may in the future introduce locational procurement. We would welcome some indication on the next steps and future studies on the option of locational procurement. Service windows - With regards to NBM providers and specific telephony requirements, it is not clear whether NBM units can bid into any available windows or are limited to only participate in windows where they have Control telephony available as was previously discussed in the Balancing Reserve service terms | We do not have any immediate concerns with the specific service terms in relation to auctions. However, it would be useful to see some clearer explanation of the Splitting/ Stacking principles, such as why splitting is not allowed between Quick reserve and Dynamic services in Phase 1 and similar decisions. It would also be useful to have a practical walkthrough of what a co-optimised procurement with Dynamic Response may look like and what are the commercial implications on the participation pool and/or system needs. | We don’t have any views or concerns with the Market design proposals. We welcome the ability to secondary trade between the pre-qualified units of the same parent company. | We understand the rationale and benefits of moving to a co-optimised procurement with Response services. We would welcome an example walkthrough of how this would work in practice and what it means for Quick Reserve volumes and participation. | No response
8 | 2024-07-26 15:35 | 2024-07-26 15:37 | anonymous |  |  | Zenobe Energy | Shantanu Jha <shantanu.jha@zenobe.com> | No | No comments | No comments | No comments | No comments | No comments | ABSVD Zenobe agree with the principle that energy volumes dispatched to meet a QR contract should lead to adjustments in the imbalance position of the relevant party, such that all providers can be compared on utilisation price alone when dispatch decisions are made. We note that for Primary BMUs, dispatch will be via the BM, included in QBS via QAO/QAB and therefore no further adjustment via QAS is necessary. Similarly, we note that for secondary (VLP) BMUs, dispatch via the BM will lead to adjustments in energy position via P-flows, therefore no further adjustment to QAS is necessary. For Phase 2 non-BM QR dispatch, ABSVD should be calculated and included for those units. Interactions with Spin-Gen/Pump Spin-Gen/Pump contracts are used by the ESO to make pump storage units available for dispatch from zero MW with shorter notice/commitment times than would otherwise be possible. These units then receive an availability payment for providing the additional flexibility. Zenobe believe that Spin-Gen/Pump should not be commercially “stackable” with QR. Where a unit has a PQR/NQR contract and an overlapping Spin-Gen/Pump instruction, we believe no Spin Gen/Pump availability payment should be made. Failure to preclude overlapping Spin Gen/Pump payments is, in effect, a technology specific subsidy in order to provide the same flexibility as the QR contract, and hence would distort QR prices and inhibit fair competition in QR. Zenobe recognise that Spin Gen/Pump can be instructed within-day and hence provides flexibility beyond the DAH procurement of QR. We believe that while in the short term there is a case for the continuation of Spin Gen/Pump payments (when not contracted for QR), ESO should move to introduce within-day QR procurement with a view to retiring the Spin Gen/Pump service in the medium term. Rule 5.11 Zenobe recognise that the BR service design has driven a need to enhance consideration of how energy limited assets are incentivised to bid in reserve services. In our response to the recent BR consultation we stated that the current incentives to place a high utilisation price in BR in order to discourage dispatch could be resolved by applying the penalty rate (based on highest BM offer acceptance) for non-delivery of the BR contract due to low state of energy following a BM dispatch. By applying this higher penalty rate, the risk of not providing the contract rises significantly since: a) The highest offer acceptance (exposure) is not readily forecastable at the time of bid submission. b) As dispatch of MW procured through the reserve service increases, the “strategy” of placing a high offer acceptance to discourage use and hence application of the penalty in the subsequent period becomes unstable since high offer price dispatch becomes more likely. We believe the application of the higher penalty rate in a period of non-delivery following a BM dispatch is sufficient to discourage energy-limited participants from offering volumes they are not certain they can deliver. Further, we can imagine simple penalty mechanisms where by non-delivery penalties in one settlement period is linked to the utilisation price in the preceding period(s) such that it is always the case that a provider who submits a high utilisation price to discourage use, net loses after penalties if volumes are offered which cannot be delivered. We note that Rules 14.1.3, through 14.3 in the QR service terms apply the Incremental Offer Volume Cost to non delivery as a result of delivery of the QR contract as a consequence of delivery of energy in a preceding period, analogous to our BR proposal. We do not believe rule 5.11 is necessary in light of rules 14.1.3 – 14.3 and further that rule 5.11 in effect is a proposal for an arbitrary price cap on QR utilisation price. Rule 5.11 makes no provision for any process for determining what utilisation price the ESO might consider “excessive” and is open to discretionary and prejudicial | Zenobe note that 30 minute QR service windows and inability to split with D* in the first instance means that providers of D* services will need to forgo a full block D* revenue to provide QR in a short window. While we agree that the 30 minute QR window is appropriate for the QR service, we believe ESO should set a pathway to aligning reserve and response service windows such that best use can be made of the flexibility afforded by response and reserve providers
9 | 2024-07-26 15:36 | 2024-07-26 15:57 | anonymous |  |  | Centrica | Maria Popova, maria.popova@centrica.com | No. | We are fine with the proposals and understand that a phased approach is required for technical reasons. There have been delays in launching this new product and we appreciate the current efforts to launch it in November. We hope there would be no further delays. We would appreciate more clarity on the distinction between Balancing Reserve and Quick Reserve. In our view, the ESO should increase the performance granularity to support service stacking from Phase 1. | We are fine with the proposals. | Our preference remains for a shorter maximum recovery period than 3 min. A 2 min period would be appropriate. | We are fine with the proposals. | With respect to Service Availability, in our view, the rules may be more restrictive than necessary and not favourable for batteries, as we get closer to the end of the service window. The current rules (even for BR), require service providers to make sure that they can support a full 30 min activation even at the end of their service window. So, they need to have a dropping profile of MEL/MIL, otherwise they end up keeping more energy buffer than required to deliver the service. | Overall, we are fine with the proposals. In relation to ABSVD, in our view, it is important to ensure a level playing field among battery storage providers. This means applying ABSVD not only to BMUs, but also to non-BMUs. Alternatively, removing ABSVD for BMUs and not applying it to non-BMUs could also be a solution, as currently, the time it takes to receive accurate imbalance volumes with ABSVD applied (up to 5 months) significantly reduces the potential benefits. In the context of the Quick Reserve Phase 1, this is not an issue, but it will become of relevance when we enter Phase 2, which will include non-BMUs. | In relation to maximum bid size, we would recommend having a limit on maximum non-divisible size per asset. The current system, along with increasing the maximum sell size, creates risks of exploitation of the system by bigger participates. They can make sure that their products add up to the exact requirement for grid and push out other participants. For context, DM is 170MW in low and 200 in high, if one participant decides to submit 2 bids of 100MW each, both non-divisible, they can push everyone out. We have already seen this happen in DRH. | We are fine with the proposals. However, and this goes back to our initial question about the distinction between the Balancing Reserve and Quick Reserve services, it seems to us that the auction could take place earlier. We would like to understand the requirement to procure this service together with the DC/DM/DR auction and if it would have an impact on the clearing of those products. | We are fine with the proposals. | We are fine with the proposals. | With respect to the provisions around high pricing set out in 5.11 of the Service Terms, we support the objective and would call for effective implementation. We would highlight, however, that to ensure a level playing field in the interpretation of the requirements, which would also increase their effectiveness, more clarity is needed. To provide more clarity and certainty as to the interpretation of “excessively high or excessively low” prices, the ESO should provide further guidance, for example, on what can be included in the pricing (e.g., opportunity costs plus acceptable margin).
10 | 2024-07-26 15:07 | 2024-07-26 16:23 | anonymous |  |  | RWE | Ross Haywood | No | The phased approach for rolling out Quick Reserve seems to make sense and seemingly contingent upon the rollout of the relevant ESO I.T systems, in any case. | This is in line with expectations. | Many of these proposed technical parameters prevent all flexible technology types from participating, except batteries. This is arguably in contrast with the self-styled “technology-agnostic” approach of the ESO. | In respect of the metering requirements, this is a continuation of the status quo and appropriate for Quick Reserve. | In line with expectations. | No comments | No comments | No comments | No comments | No comments | Planned retirement of ASDP In reference to the planned retirement of ASDP in December 2025, and the rollout of the OBP from Spring 2025, this raises a question with regards to the ability of Non-BM assets to participate in the STOR market – could ESO please clarify and reassure non-BM STOR providers that they will not be disadvantaged as a result of this I.T transition. Flexibility Services Standard Agreement Whilst it’s recognised that the Flexibility Services Standard Agreement is not an ESO document; by referencing its content within ESO documentation; it means that ESO have the responsibility of ensuring that any amendments, and any consequential impact, are clearly communicated. For example, Balancing Reserve references version 0.4 of the Flexibility Services Terms, and yet Quick Reserve references version 3.0. Contract Formation Participants are required to sign Form B, however this is not defined or referenced in the Service Terms, Procurement Guidelines or the Glossary. We would therefore request that it is made clearer in the procurement documentation that it’s the signing of Form B by the Provider & Form C by the ESO, that binds the parties to the procurement documentation.
11 | 2024-07-26 16:48 | 2024-07-26 17:09 | anonymous |  |  | EDF Energy | Edward.Bryan@edfenergy.com | [11 empty] | 1. The ESO needs to be clearer on when the incremental volume cost amount will be applied to assets which do not retain the contracted headroom when holding a QR contract. This hasn’t been applied consistently for BR and applying the penalty “at the ESO’s discretion” creates an environment where some optimisers are following the rules as written and others are not. The ESO should clarify that this rule will always apply and develop a robust process for monitoring it. 2. ESO should provide greater clarity on how they define “excessive” Bid-Offer prices under 5.11 when providers submit prices through the BM for utilisation which in the ESO’s opinion are designed to be rejected. We agree that this should be addressed, although would also request clarity as to which regulations or license conditions a provider could be in breach of if submitting prices (particularly offer prices) which are deemed to be excessive, e.g. in the case of bids a provider could be in breach of TCLC if the asset sits behind a transmission constraint, and the instances when each of 5.11.1, 5.11.2, 5.11.3, & 5.11.4 may be applied.
12 | 2024-07-28 18:00 | 2024-07-28 18:05 | anonymous |  |  | Shell | Melanie Ellis mel.ellis@shell.com | No | We are supportive of the two phased approach to prevent duplication of work and to leverage the OBP. We are keen that the ESO keep to their planned phase out of the Fast Reserve and don’t change this target as was the case with phasing out the old Response product. | Supportive of the planned dispatch mechanism. | We are supportive of the design parameters for Quick Reserve. We note that there has been much discussion around the proposed 3-minute recovery period. We believe that the ESO should base the recovery time on the required system needs. If the system would operate more efficiently with a faster recovery period, then we recommend the ESO stipulate a shorter recovery period or a date by which they want to revisit a review of the response time. We would also welcome an overview from the ESO, as to why they need the Balancing and Quick Reserve and whether they can be rationalized. Having two Reserve products which are both procured at day ahead and served by the same technology type may lead to inefficiencies and costs for consumers. | We are supportive of the 1 hz operational metering and that for phase 1 no additional data will be required for performance monitoring as 30-minute average settlement metering data will be used. When data submission moves to daily we ask that sufficient time is allowed for participants to adjust their processes to accommodate this. | Please provide details of how state of charge should be managed for linked-buy orders. | No additional comments. | We are supportive of the maximum bid size, 30-minute service window and excluding a locational dynamic. If the later is considered in the future, then we request a consultation and feasibility study is conducted. | We are supportive of the timing of the auction and believe that it is practical and will lead to the optimum result by co-optimising Fast Reserve with the Response auctions at 14:00. As the auction is held after the day ahead power auctions there is less uncertainty which needs to be factored into the submissions. We note that the guidance document says that the ESO may consider holding the Quick Reserve auction at the same time as the Balancing Reserve auction which we do not support. There would need to be significant opportunity cost priced into the Quick Reserve if it were to move to the same time as the Balancing Reserve which is unlikely to lead to the best price for consumers. | No additional comments. | As per our answer to question 8 we are supportive of the co-optimised proposal. We are keen for the ESO to introduce stacking of Quick Reserve and the Dynamic Response markets for phase 2. | We understand that the ESO is looking to introduce terms which address the operational challenges experienced with the Balancing Reserve. Whilst we are supportive of this in principle, we have some concerns with the practicalities of managing ‘excessive pricing’ as this is not defined and can be subjective. We note that OFGEM found it difficult to define excessive profit under the TCLC rules, leading to the need for a comprehensive guidance to support it. It would also require resource to monitor and deal with complaints. We believe this issue needs to be considered further. The introduction of the new SoC rules under GC0166 will help in monitoring if the unit is technically available so could be used to monitor whether an asset is trying to signal it does not want to receive a BOA even though it is available.
13 | 2024-07-28 18:30 | 2024-07-28 18:34 | anonymous |  |  | SSE Plc | Michael-Allan Millar, ancillaryservices@sse.com | no | We have no comments on this, as the requirements align with current BM requirements so cannot foresee any difficulty with this. We have no comments on the phased approach. |  | We have reviewed the service requirements against technical capabilities of common technologies (e.g. hydro, CCGT/OCGT, wind, solar, battery etc.). The service seems to only cater for technologies which can provide rapid response. Relaxing some of the time requirements (e.g. time to full delivery) would support non-energy limited assets to participate. | [7 empty] | Version 3 of the ENA Flexibility Services Standard Agreement has introduced caps on liabilities (except for death & personal injury due to negligence). Para 10.1 of the ENA Agreement carves out any indemnities under the Service Terms and Procurement Rules (e.g. Third Party claims, Modern Slavery & Anti-Bribery, IPR, etc). Was this intended or should the liabilities under the Service Terms and Procurement Rules be capped as well? In addition, could you please check references to the ENA Agreement in the QR Service Terms and Procurement Rules, e.g.: QR Procurement Rules 10.1 & 10.2 refer to the ENA Agreement 11.1 & 11.3. Should this be 10.1 & 10.3? The QR Service Terms 16.1 refers to the ENA Agreement 8.1 & 8.3. Should this be 7.1 & 7.3? Equally, 16.3 refers to 8.5 & 8.7. Should this be 7.5 & 7.7?
14 | 2024-07-28 21:25 | 2024-07-28 21:47 | anonymous |  |  | ENWL | Tom Ridgway. Tom.ridgway@enwl.co.uk | This is a confidential response throughout and should not be published. This response should be read alongside recent ENWL responses to the NESO on Quick Reserve (QR) design and Flexibility Markets, including NESO Quick Reserve Survey Response from ENWL (18/04/24), Flexibility Markets Strategy Call for Input ENWL Response (28/06/24), Routes to Market Review for Demand Side Flexibility ENWL Response (28/06/24), and ENWL Letter to the NESO on Market Reform (25/01/24). Additional examples of early engagement from ENWL are engagement in QR webinars, bilateral meetings and the email to Mike Coldwell and Steve Dugmore on QR technical requirements (01/03/24). This response includes key comments (in addition to our comments in our previous letters and responses) based on our current understanding of draft proposals. We expect to add further comments in future as the information available and our understanding of how the proposals are expected to apply to demand side flexibility develops. The NESO has acknowledged that it is not clear how current proposals would apply to demand side flexibility in the response to ENWL question one point f. in the pre article 18 survey for QR. There needs to be clarity on how rules would apply to demand side flexibility providers for Phase 1 Quick Reserve (as ENWL have been asking for over 6 months), and it needs to be consulted on properly, firstly because demand side flexibility providers may want to enter the Quick Reserve market in future as a BM unit, and secondly because NESO have noted that they expect alignment across requirements in BM and non-BM Quick Reserve. | Phased Delivery Approach and Provider Eligibility: ENWL appreciates the dialogue opened with NESO on this but is still very concerned Quick Reserve implementation plans risk damaging customer interests by not allowing Non-BM units to compete on a level playing field for a year or more when the new BM Quick Reserve is running alongside Non-BM Optional Fast Reserve, therefore reducing competition. Key concerns with the proposed delivery timeline are as follows: a. NESO implementation plans exclude Non-BM units in the interim Quick Reserve market which will reduce competition Current NESO Implementation plans exclude non-BM units from the Quick Reserve Market for at least nine months. This will disadvantage customers through higher bills and higher carbon footprint of balancing services during this period. This decision would also strongly disincentivise investment in new green technologies such as CLASS in the non-BM market. The majority of Fast Reserve capacity is currently provided by non-BM units based on price merit order. If non-BM units are excluded from Quick Reserve then prices are likely to be higher than necessary for customers and investment and development of non-BM technologies will be inhibited. There is also a significant risk that less capacity is available to dispatch when required by the NESO. We believe the NESO should launch BM Quick Reserve at the same time as Non-BM Quick Reserve to facilitate competition and ensure the lowest cost and lowest carbon solutions can compete and are not inhibited to the detriment of customers. The current plan to have a new NESO IT system to bring in non-BM Quick Reserve 12 months later appears very challenging particularly based on the track record of IT projects not delivering on time. We suggested that Non-BM units enter Quick Reserve using systems and adapted processes being proposed for BM Quick Reserve while remaining Non BM units. It has been noted by the NESO that this is not considered feasible with current NESO systems. We suggest that the timelines for the introduction of Slow Reserve should be brought forward to boost competition for customers. We welcome the discussions held so far and appreciate the NESO’s verbal commitment to fair competition between the Optional Fast Reserve market and BM Quick Reserve on price alone (to help mitigate the impact on non-BM providers), but we are keen to see that this commitment is formally documented. Competition between markets (with the NESO procuring capacity based on which market was cheaper recently, as suggested by the NESO) would help mitigate but would not eliminate the negative impact of the proposed two-phase approach. To avoid damaging customer interests we think the NESO should urgently clarify and document steps that are being taken to ensure Non-BM units can compete on a level playing field with BM units at the launch of new markets. b. Implementation timescales insufficient The NESO initiated the Quick Reserve project in October 2020 with the project ongoing over several years. The NESO is proposing significant changes which are likely to require complex IT changes for non-traditional suppliers such as CLASS. These requirements will only be finalised after the consultation periods. The NESO is then proposing go-live one to two months after consultation periods. This is not sufficient time to deliver and implement complex IT change as the NESO will understand from the experience of developing Quick Reserve IT solutions. The NESO draft plan is likely to exclude or severely inhibit providers such as CLASS from the market until complex IT projects can be delivered. It was suggested that as part of synchronising the launch of BM and non-BM Quick Reserve the consultations could be run concurrently (as soon as possible), with a 6-month period after the consultation results are announced before go-live. NOT ENOUGH SPACE TO ADD THE REMAINDER OF THIS ANSWER. FULL ANSWER WILL BE EMAILED TO STEVE DUGMORE. | We do not currently have any specific feedback on this point. There are elements of the Quick Reserve technical design where the NESO have noted that further clarification will be provided for how requirements will be adapted/applied for demand side flexibility providers. We expect to add further comments in future as the information available and our understanding of how the proposals are expected to apply to demand side flexibility develops. | ENWL Position Summary on Recovery Period: The maximum recovery period rules should be set based on what is in the best interests of consumers. Issues with NESO’s current analysis are highlighted below. The maximum recovery period that is in the best interests of consumers should be supported by a robust cost benefit analysis. This appears to be a gap in NESO analysis performed to date, as highlighted in previous ENWL responses. It is asked that the issues highlighted below with assumptions used in NESO analysis are reviewed, and NESO analysis is reperformed using updated assumptions and with highlighted gaps in analysis addressed. It is suggested that the maximum recovery time for Quick Reserve is set to ten minutes while NESO update market analysis based on the issues highlighted in this response and earlier correspondence. ENWL are happy to continue to work with NESO to help ensure that the analysis performed is robust. Note that ten minutes is the minimum recovery time that CLASS sites can operate at per consultation with hardware manufacturers and internal subject matter experts. Alongside working with NESO to establish a robust cost benefit analysis, ENWL is looking to commission an independent review on the optimal recovery time for Quick Reserve from a customer perspective, and the expected costs/savings for customers of different maximum recovery times. ENWL are hoping to commission the independent review to deliver a report in September or early October 2024. It appears that the current QR proposals do not align with NESO’s mission, NESO’s recent Strategy consultations and NESO’s Market Design Framework for establishing new markets. It is asked that alignment of Quick Reserve proposals with NESO’s mission, strategy and Market Design Framework are urgently reviewed and actions established to realign current proposals. NOT ENOUGH SPACE TO ADD THE DETAIL FOR THIS ANSWER. FULL ANSWER WILL BE EMAILED TO STEVE DUGMORE. | Second by second Operational reporting requirement: Second by second operational reporting requirements could exclude technologies such as CLASS and V2G from operating in Quick Reserve given it is much more difficult and data intensive for data to be gathered across hundreds of sites every second compared to more standard providers that would only have one or a small number of data points to collect every second. It is understood that more detailed operational data points are useful for the ESO control room. The ESO feedback in the February QA response document to ENWL noted that second by second operational reporting was required so the ESO could know that sites had fully responded within a minute. However, we do not think that a granularity of 1 second data would be required to prove sites responded consistently within a minute. CLASS very consistently achieves full response in 30 seconds. It is suggested that it should be considered if operational metering requirements could be moved to a lesser granularity, for example once every 15 seconds (settlement data could be required at a more granular level if necessary), while still meeting ESO control room requirements. The lower the frequency the operational performance data that is required the less likely it is that non-standard technologies such as CLASS are excluded from the market due to this data heavy requirement. ESO concerns noted: The ESO have noted repeatedly that their control room colleagues do not understand the presentation of current CLASS RTM in their dispatch system and have questioned the accuracy of load data they receive for CLASS, although no examples of issues with agreed RTM data have been provided to ENWL. The accuracy and format of the data sent has been explained on previous occasions, but we are always happy to engage further to help resolve any confusion. Real Time Operational Data Requirements: It is very difficult to respond on this point as it has not been stated what would be required of demand side flexibility providers who may operate in BM or non-BM Quick Reserve Markets (although ENWL has been asking for detail on this for over 6 months). It is asked that detail on this is published and consulted on prior to the launch of Quick Reserve. As previously noted demand side flexibility may want to join BM Quick Reserve, and NESO has noted the expectation of consistent rules across BM and non-BM Quick Reserve. It is therefore very important that this is consulted on prior to the launch of Phase 1 QR. In the response below we are assuming the format of data required for CLASS type providers stays the same as is currently agreed for Fast Reserve. A requirement for operational data to match settlement data within 1% could inhibit CLASS type provision and other demand side flexibility providers operating in Quick Reserve and Slow Reserve markets. The ESO has informally noted that CLASS is a highly reliable provider on the basis of the settlement data provided. There are challenges given the nature of CLASS technology (a wide network of units simultaneously sending significant amounts of data over an operational network) in providing highly granular real time operational data. These challenges have been discussed in detail between ESO and ENWL previously and the ESO has accepted current arrangements for Fast Reserve operational reporting. The operational data currently provided is an accurate representation of performance for the purpose of checking that CLASS has activated successfully, and the ESO can check that the initial response is in line with the procurement level as soon as it receives the real time metering data. We believe this should be sufficient to deliver the benefits NESO is looking to obtain. We ask that the ESO relaxes this requirement to a level that is in line with operational need (for example 2% or 3% could be considered) against the damage to consumer interest. INSUFFICIENT SPACE - ANSWER EMAILED TO STEVE DUGMORE. | There are elements of the Quick Reserve technical design including baselining where the NESO have noted that further clarification will be provided for how requirements will be adapted/applied for demand side flexibility providers. We expect to add further comments in future as the information available and our understanding of how the proposals are expected to apply to demand side flexibility develops. | Penalties for over (>120%) and under (95%) deliveries Penalties (the loss of availability revenue for the 30-minute block) are proposed for over 120% delivery and under 95% delivery. Due to the nature of CLASS there can be a small difference in delivery based on weather and load patterns being different to expectation. We think that loss of availability revenue outside of a 120% to 90% window would be more proportionate than a 120% to 95% window. This would help ensure over delivery is not incentivised for all providers in the market. Lack of clarity for Demand Side flexibility providers on several requirements It is not clear how some elements of proposed service requirements for Quick Reserve would be applied for demand side flexibility providers, for example baselining, PN notification, performance reporting requirements, and performance measurement methodology. It appears that the inclusion of demand side flexibility providers has not yet been fully considered when designing Quick and Slow Reserve Requirements. It has been discussed how some of these elements may be managed between ENWL and the ESO, but it is important that this is documented by the ESO as soon as possible so this can be consulted on effectively and planning performed for any required system changes. If demand side flexibility providers are not considered in requirement design this makes it less likely that demand side flexibility units can compete in these markets. This risks reducing competition with higher prices (and a higher carbon footprint) than necessary for customers. We believe that protocols/approaches used for CLASS in Non-BM Fast Reserve should be retained/preserved. Given the current absence of documented detail it is presumed that performance measurement methodology for CLASS is intended to stay the same. | Treatment of activations running across two successive 30-minute blocks if two different levels of MWs are offered Feedback from the ESO in the February QA response noted that ‘Feedback from participants that has been received with regards to current implementation through ASDP will be taken forward and considered as part of the design process’. We have been told informally that auto-denomination issues that we have highlighted in the Fast Reserve market would no longer be an issue in the Quick Reserve market, but we are not aware of any documented clarification of proposed treatment of activations running across two successive 30-minute blocks if two different levels of MWs are offered (for example it is not clarified if an activation be stopped even if there was a relatively small change of under 5% moving in line with demand patterns nationally). If auto-denomination issues are set up in the new Quick Reserve market this would ensure existing costs for the ESO and customers in not procuring the lowest cost provider available could be perpetuated. If the NESO links a significant number of service windows we believe it should be allowed for providers to make small amendments to MWs offered between blocks (for example up to 5% change). | There are elements of the Quick Reserve technical design (and therefore performance monitoring) where the NESO have noted that further clarification will be provided for how requirements will be adapted/applied for demand side flexibility providers. We expect to add further comments in future as the information available and our understanding of how the proposals are expected to apply to demand side flexibility develops. | It is important that there is transparency in how the clearing algorithm works and how each set of results are reached to ensure the market operates as efficiently as possible. | No comments noted. We expect to add further comments in future as the information available and our understanding of how the proposals are expected to apply to demand side flexibility develops. | Elements of the proposed service design should be amended to ensure that all DNOs could operate CLASS type provision in the Quick Reserve market to ensure liquidity and optimal competition for consumers. This could facilitate the inclusion of 3GWs of cheap, reliable, low-cost flexibility in the market. ENWL led the development of CLASS. Other DNOs have expressed an intention to roll out CLASS nationally which has massive potential for multiplying the significant benefits to customers that CLASS provides, but these huge potential benefits would be prevented by Quick Reserve requirements as currently drafted. Ofgem noted in its impact assessment from December 2022 that it considers CLASS ‘one of the many low cost, low carbon and reliable technologies that will be needed to meet the ESO’s future balancing service requirements’ It noted that if CLASS is rolled out more widely across GB it could unlock consumer benefits of £1.8bn with a potential 3GWs of additional capacity for flexible demand side flexibility. We are very concerned that draft requirements have been set primarily in line with the ESO’s expectation that batteries will dominate this market, and established innovative green technologies such as CLASS will be excluded or severely inhibited. Many of the key concerns raised in this response in relation to the potential exclusion of CLASS are also likely to exclude other innovative clean technologies in development that utilise demand side flexibility or call on a large, distributed network of units (for example EVs). This survey response includes key comments (in addition to our comments in our previous letters) based on our current understanding of draft proposals. We expect to add further comments in future as the information available develops. The proposed service design risks excluding or severely inhibiting CLASS type provision which is not in consumer interests when CLASS has and continues to provide very significant benefits to customers through its consistent operation in the optional Fast Reserve Market in recent years. The ESO have said CLASS is one of the most reliable providers for the ESO, and the operation of CLASS has consistently reduced prices in the Fast Reserve market in addition to reducing customer bills for ENWL customers by over £13.5m. The setting of Quick Reserve Requirements that exclude CLASS from the market is clearly not in customer interests. There have been very large barriers to investment in CLASS type services to date which appears to have stopped provision developing significantly. Providing certainty as soon as possible that CLASS type provision can compete in the Quick Reserve market has the potential to ensure these barriers are removed in future. Primarily it could help provide certainty for investment which has made business cases for investment difficult previously. Future change As the markets evolve and new providers join, as well as the ESO’s needs change, adaptions to market rules may be required. We think the ESO should document the framework for adapting market rules in future. We also suggest that there could be set review points established for new/existing markets where market rules can be reconsidered if in the best interests of the customer. The ESO’s assessment of how any reforms it makes deliver against this strategy and value for customers should be undertaken and published. We suggest this is done for the reforms leading to Quick Reserve.
15 | 2024-07-25 11:48 | 2024-07-29 07:56 | anonymous |  |  | Statkraft UK Ltd | Mitchell Tyse, mitchell.tyse@statkraft.com, +47 920 33 945 | No | The reasons behind the phased delivery approach, transition plan and timelines are well understood and have been sufficiently communicated. Perhaps, some of the details on the proposed changes for BM Quick Reserve in Phase II could be further highlighted (updates to the QR service design); such as the proposal to change the performance monitoring data to 1 second as opposed to the average 30-minute settlement metering or proposal to change the auction timings from T-1 at 14:00 to T-1 at 09:00 AM. Further clarification on the future possibilities for stacking QR with other ancillary services could also be outlined in further detail. The registration and prequalification process via the SMP is also understood. However, the there are some points in the registration process that are proving at times tricky/time consuming. This applied to general SMP asset onboarding process rather than being service specific. For example, an account holder with multiple entities, is not able to register the different entities under the same account (same email address) and multiple accounts are having to be requested via the SMP team as a backend process/workaround. This should be changed as it is quite common for the same individual to be involved with multiple assets. The request for Agents and registration of assets as an Agent should be more streamlined. | There are no comments on the above as dispatch mechanism is via EDL/EDT systems – already existing and embedded processes. | The recently made changes to some of the technical parameters under the service design may prevent/limit participation, specifically the Notice to Start Ramping and Time to full delivery require an instantaneous processing time for QR instructions to be delivered in accordance with the notice period of 0 minutes and response time of 1 minute. Although, majority of assets can respond to an instruction quick enough, the current service design does not allow for much processing time or communications latency between the communication of third-party systems. The proposal is also not in line with other services (such as Balancing Reserve). Having to forgo the availability payment for the whole Settlement Period due to response time longer than 1 minute may prevent participation and it should take into consideration the asset response as well as the processing time and communications latency of the instruction. As the recommendation sits on two separate analyses, have those analyses taken into consideration all technology types such as energy limited assets or gas peaking assets? As only pump hydro storage is currently quoted in the summary document. We would prefer that the response time is 2 minutes to allow for variable processing time and communications latency and to maximise assets which can participate. As the ramp rates will not be required, would NG be able to share timelines of when this will put in place (and will this also be implemented for DFR services)? | Using the 30-minute settlement metering data from Elexon to evaluate Availability, time to full delivery and utilisation is welcomed but further clarification would be required in terms of Phase II performance monitoring – is 1 second data expected? How will it be shared? And further communication on requirements for non-BM is still required, how will the performance metering data be shared? Performance monitoring with payment penalties for over and under delivery are clear and understood. | Additional state of energy management guidance / rules for energy limited assets would be welcome to ensure NGESO is receiving the service it expects and fair competition between providers. For example, is the expectation to maintain energy sufficient for a 60 minute instruction in each direction? | Answered in question 4 – further information on Performance Monitoring requirements for BM QR in Phase II and NBM QR to be shared in advance to allow for implementation. Where dispatch is through the BM no separate ABSVD adjustment is required, since BM volumes will adjust the lead party’s traded position. For NBM QR ABSVD should be implemented in order to ensure a level playing field between BM and NBM QR participants. | When can we expect the minimum volume management for QR to be set dynamically (similarly to QR)? How much volume will be procured via OFR ? The maximum bid volume is limited to 300 MW which is good. | What is the reasoning behind proposing to move the auction to D-1 at 09:00 in Phase II? Would all Ancillary Services move towards D-1 09:00 auction (including DFR) in order to allow for co-optimisation of response and reserve auctions? When will co-optimisation of response and reserve auctions become available? Are there plans for allowing stacking of QR with other response/reserve services (such as DFR)? When and how will the ‘’linked buy-orders’’ be communicated? How are key crossover periods decided? Is it dynamic? It would be preferable to not be stuck with the MW consistency across periods. | Having non-curtailable Child Orders would be a useful option for providers. Additional bidding baskets will be useful when the market moves towards a combined procurement of Frequency Response and Quick Reserve. NGESO should allow for Overholding in all Frequency Response and Reserve products where doing so results in a lower overall cost to consumers. | Would it be possible for National Grid to share timelines and details of the co-optimised auction? How will the co-optimisation algorithm decide on accepted baskets? | Increased monitoring in terms of increased penalties for units running out energy and preventing pricing units out of the market during contracted periods are welcome as this will level the playing field.
16 | 2024-07-29 08:46 | 2024-07-29 08:46 | anonymous |  |  | Kraken | Euan Killengray, euan.killengray@krakenflex.com | Yes | Agree with phased approach in order to get QR for BMUs launched sooner whilst IT changes for nBMU are completed Kraken is happy with the communicated timelines, but would push the ESO to communicate an accurate go-live date from the moment of the Ofgem approval. This helps guide that Day-1 go live for service providers, and to prioritise workload on building out the capabilities Kraken also wondered if mock auctions will be held? Kraken found this particularly useful with BR as it allows us to run simulated assets with the mock results to ensure our optimisation and control software is working as expected for a range of scenarios and edge cases | No concerns | Kraken agrees with all the proposed parameters and believes it fits the purpose of QR for system stability. Kraken do have some confusion over what asset types the ESO was envisaging participating in the service outside of BESS assets given the parameters likely still only allow for BESS participation The no notice of ramping is a change in how providers will be scheduling/ controlling assets, but we have no concerns | Although we agree that bringing QR sooner without 1Hz performance monitoring is the better choice, the use of 30-minute settlement metering data from Elexon to evaluate performance does raise some potential concerns around accuracy of monitoring participant performance. Especially in the context of the ESO trying to put into force more stringent performance monitoring in the Response and Reserve setting Kraken would appreciate frequent updates from ESO after QR go-live to understand if the proposed approach for performance metering is providing enough granularity to properly penalise underperformance and remove availability payments when applicable. We are mostly interested in knowing if this process can be suitable for seeing if an asset met the time to full delivery/minimum ramping requirements, or would operational metering cover this type of monitoring? | Kraken agrees with the additional wording around SoE management being added to the Service Terms. However, as mentioned in multiple streams, we would wish to ensure these new terms are properly enforced and that the enforcement is being mentioned back to industry, likely in the OTF meetings | Kraken agrees with deterring assets from pricing BOAs too high to avoid utilisation, however, it still seems to form a grey area for what would be regarded as a “too high price”. Kraken would like some further clarification around this, i.e., does the price need to be within a certain % of the prevailing market prices or accepted BOAs of similar asset types. ESO will need to tread with caution here, as it should not be indicating to the market what the appropriate BOA price should be, nor should any fixed caps be considered. Overall, we would just wish for further clarification on this point as to what will be regarded as a high price Kraken are also unclear on the point around being penalised for BOAs before a QR period - from previous conversations with ESO around BR, we were under impression this was fine as the ESO wished for still the same amount of availability for BOAs in the earlier SPs to that reserved for QR, and that QR units should just price the risk of misdelivery in QR into the preceding BOAs that might be provided before the QR period. Can ESO clarify if this is still the case, or not the case across both QR and BR? Also to confirm on the penalties, does “in line with other balancing services” mean the same as in BR where it's the most expensive BOA for that period? | Happy with all proposed parameters for this QR release, but would like to reiterate the enablement of locational procurement should remain a priority for the ESO after initial QR/SR release | Due to the number of different customers we have, Kraken pulls auction results to schedule assets via the data portal. Kraken would therefore greatly benefit from results being published in an identical format to BR as it makes the scheduling process more efficient for market participants. Equally, we seek clarifications on if the results will be published in the same file as the Dx services it is being co-optimised with? We would support and assume results being published at the same time as Dx, especially seeing they are co-optimised auctions | No comments | Agree that is the right procedure, allows for assets unsuccessful in QR to be successful in Dx, as well as simplifying auction processes and driving better market welfare | Kraken wants to raise concerns over the running of OFR (Optional Fast Reserve) alongside QR. Kraken understands the use case, but would like to understand the process ESO will go through to utilise OFR prices to guide QR buy-orders. Could the ESO provide a worked example of OFR and QR auctions running alongside each other and show how the prices could feed into each other? Kraken would also question if there are any gaming risks to providers in OFR and QR? Has the ESO thought through scenarios where providers price a specific way in OFR to benefit in QR? As a software provider to many service providers across the market, we ensure all services are available to our customers on day 1, and with OFR being kept open, it does put a risk on software providers like ourselves of having to keep/or build out capabilities of providing a service that is not enduring. As a general rule we urge the ESO to resign services when they are no longer needed, which the ESO seems to hint to with OFR just being there for emergencies. In a growing market with a range of services, resigning legacy services that are superseded should be a priority of ESO to remove complexity in operating in the market, reduce costs to consumers and avoid over-purchasing.
17 | 7/29/24 19:43:27 | 7/29/24 23:05:53 | anonymous |  |  | Arenko Group | Meziane Benmaamar, meziane.benmaamar@arenko.group | No | The Phased Delivery Approach is sensible given the lack of supporting market IT infrastructure in place such as performance monitoring for nBMUs. We think it is a pragmatic solution to do Phase 1 via the BM first to avoid further delays. | We are supportive of measure to implement solutions on the back of our Balancing Reserve CFI response. However, we are concerned about the lack of a scientific approach to defining excessing pricing in the chosen solution and the absence of a clear penalty structure as seen in the new Dynamic Response service terms. We are concerned that precedent from Ofgem's ruling on the Inflexible Offer License Condition (~aversion to defining 'excessive' given uncertainty over market participant information) could suggest additional regulatory risk that participating in QR could represent for participants. We think 'chatham house' in-person sessions with industry participants, particularly those offering expertise in engineering and trading roles, could present an opportunity for ESO to constructively explore the solution space, including via the procurement of digital tools to deliver performance monitoring outcomes. We note that the deterrent of retrospective penalties/nominal fines based on historic data that indicates gaming at system-risk activity should be explored in our response to Dynamic Response Release 3 feedback. This could ensure provide an added incentive to ensure reserves exist in QR, providing time for clear and scientific penalty regime gets introduced. Finally, we support continued clarity and defined penalty structure for mis-delivery over and above imbalance prices or BM non-delivery charges, especially as NBM units come on to the system. | We support the proposed 3 minute recovery period and appreciated the supplementary analysis made available by the ESO. We agree that the maximum recovery period should continue to be reviewed and reduced to two minutes when possible as this will present the best cost to the consumer and utility to the system operator. |  | Regarding linked buy-orders, we would appreciate any further market information that could inform pricing strategies at the day ahead, and learning more about what indicators ESO will use to evaluate when crossover periods drop off will become significant to require this. | We would appreciate clarity on what further information is needed by ESO before deciding performance monitoring capability for Phase 2. We would prefer a delay and ironed out rules than non-delay and 'gaming' from day 1, as it reinforces a set of misaligned market incentives, compounding a structural lack of trusted governance and fundamentally undermines system security. |  | Regarding auction timings, our core preference is that Reserve and Response services all clear at same time and co-optimised, subsequent to EPEX DA wholesale market (3:30 pm) clearing. This would enable better price discovery as we can more optimally price the counterfactual use of our flexibility. |  | We are supportive of the move to single, simultaneous, co-optimised auction for procurement. However we note the preference for Phase 2 to explore moving QR clearing time to the Balancing Reserve 08:30 am time, instead of in the afternoon after the EPEX DA wholesale market clearing. We note that the ESO proposed timing is intentionally before the I/C markets, guaranteeing national reserve for ENCC, however at the expense of better cost-reflective pricing by other market participants. As raised in ESO's consultation webinar, we do not fully understand the rationale as to why participants can’t stack two-sided with D* especially as you can do this in BR. As a result we would need a significantly higher price going into QR. We are supportive of exploring stacking as part of Phase 2 should involve stacking as per webinar.
18 | [5 empty] | Energy UK | Naomi Baker | No | Whilst we would prefer the whole service to be accessible for all participants this year, we accept that the delay as necessary given the IT and technical constraints. |  | Maximum recovery period – Energy UK supports the proposed 3 minute recovery period. Whilst, in general, a shorter recovery period can reduce competition in the market, we think it is unlikely to have a significant impact in this case as the service requirements in general (speed of delivery, ramping and notice period) mean that the service is unlikely to be both feasible and commercial attractive for other plant such as CCGTs and OCGTs. We appreciate the ESO perspective that the maximum recovery period would be as close to zero as possible because that enables the greater the maximum coverage of like the frequency deviations that the service aims to deal with. We would welcome some clarity or indication of whether the 3-min will be a confirmed parameter for the near future or whether the ESO will keep exploring the option of moving to a 2 min recovery. If a move to a shorter recovery is considered, this should be supported by evidence and stakeholder engagement with a timely notice for all stakeholders. | [7 empty] | Stacking: Members felt that there is lack of clarity over the level of stacking that is permitted in Phase 1 and Phase 2 for example, whether the non-stacking provision just applies to other ESO services (for example to DC,DM, DR) or further, to arbitrage / wholesale markets. Clarity here would be welcome (especially given the proposed penalty for non-delivery). High pricing: Whilst members are supportive of the service and service terms, there is concern at the proposed provisions around high pricing set out in 5.11 -where ‘NGESO reasonably considers that the Service Provider has submitted Bid-Offer Prices into the Balancing Mechanism… which by virtue of being excessively high or excessively low,… have as their sole or primary objective to discourage NGESO from issuing Bid-Offer Acceptance(s)… then NGESO may at its discretion (but with reasonable grounds):- 5.11.1 refer such prices to the Authority for consideration; and/or 5.11.2 declare Quick Reserve as unavailable from that QR Unit for the entire affected Contracted Service Period(s); and/or 5.11.3 Deregister the relevant QR Unit(s) or any of them; and/or 5.11.4 Deregister the Service Provider as a Registered Auction Participant /Provider’. Whilst we support the outcome that the ESO are looking to achieve, we are concerned at the additional regulatory risk this could represent for participants if ‘excessive’ cannot clearly defined. Given the potential difficulties with definition (set out in the paragraph below), we urge the ESO to explore alternative means to manage the perceived risk. Defining ‘excessive pricing’ This concern is centralised on the difficulty of defining what constitutes ‘excessively’ high (or low) pricing. If participants are going to be judged on it, it will be necessary to be able to define it or participants could be inadvertently caught out (especially given the difficulty of pricing at day-ahead stage and the changes that can materialise after this time). Members note that Ofgem did not define this in the Inflexible Offer License Condition (IOLC) for this reason. Members highlight the complexity that assessing this could involve, especially with an ex ante assessment. It will be hard to ascertain the level of market information the participants had when placing the BOA (for example, of potential constraints, weather change, actions of other assets on the system). Members felt that defining this would be difficult whether it was based on a percentage deviation from average pricing or via a fixed utilisation fee approach. Without an shared understanding of how ‘excessively high’ would be defined, members agree it will introduce risk (and therefore cost) for participants. Members expressed concern that what constitutes ‘excessively’ high pricing could be defined elsewhere (for example, by extending IOLC Transmission Constraint Licence Condition [TCLC]) and then backdated to apply to services including Quick Reserve. If the ESO were to proceed with this approach, implementation would require sufficient administrative resource to manage it, including a dispute investigation team to addresses the queries as well as further guidance (for example, on what can be included in the pricing - e.g., opportunity costs plus acceptable margin). Is it necessary/ can the perceived risk be managed in another way? Members think that the new State of Charge (SoC) rules and stricter performance monitoring would be a more appropriate way of means of managing the perceived risk (the SoC rules should address the root cause). If the unit is technically available and has enough SoC to meet its contracted volume, this should be sufficient. Members noted GC166 as a further development in this space. Members think the excessive pricing terms introduces additional risk and complexity into the market where the risk has been covered off by changes elsewhere. Members note that the proposed performance monitoring for Quick Reserve is light - the ESO could retain the option to bolster this if the initial period of the service brings to light any concerns. In summary, members do not agree that the excessive pricing terms are justified –they introduce regulatory risk which could increase the costs of provision (ultimately born by the end consumer). We support the outcome that the ESO is seeking to achieve but urge the ESO to look to more proportionate means to achieve this. At this stage, members expect the current rules around State of Charge (and general direction of travel in this area) to be sufficient. We would welcome the ESO monitoring the market for a period and then revising the penalty regime if there is sufficient evidence that this is necessary.
19 | [5 empty] | ADE | Natasha Mills | No | We agree with the laid out phased delivery approach and that it makes sense to wait for the full implementation of OBP to allow access to non-BMUs. However, we don’t agree that this will facilitate ‘fair access for all market participants’ due to the issues laid out above that are required of assets to participate in Quick Reserve. We would also emphasise the importance of a co-optimised auction with Reserve and Response services as we eventually move into Phase 2 of implementation. |  | A recovery period of 3 minutes, despite being decided as the optimum recovery time from ESO analysis, still causes all flexible assets apart from batteries to be excluded from participating in Quick Reserve. As above, we are disappointed in the design of yet another battery exclusive ancillary service, the fifth to be implemented throughout RIIO-2. This places further emphasis on the need for the service to be technology agnostic in reality rather than just a lack of explicit restrictions. Industrial and Commercial load is the main group of assets to be excluded as a result of this requirement, leading us to question the alignment between ESO’s message of inclusivity and delivery in service design. We would also like to see additional information regarding the analysis that has been undertaken by ESO to get to this result, specifically the significance between the effect of the recovery time and the ability for assets to participate. On the time to full delivery, for many flexible assets to get up to what is required within 1 minute is either unachievable or will have large impacts on the health of the asset being used, again apart from batteries. To say that any load unable to participate in QR to just participate in Slow Reserve is not an adequate solution. | The ADE has long advocated for relaxed operational metering requirements as without an immediate steer, consumers will continue to invest in assets which do not have the ability to enable them to participate in flexibility markets. Given that ESO are currently undertaking a review of metering requirements, it is disappointing to see the 1Hz granularity being retained for Quick Reserve. With the current trial attempting to increase access to the Balancing Mechanism (BM) for 300MW of small-scale assets underway, the use case of relaxed operational metering requirements is made clear. We look forward to the outcome of the independent review but would like to flag to the ESO that metering standards should be aligned to the small assets in the BM test-case in order to not introduce unnecessary barriers to entry – particularly for BM assets being grandfathered as part of the small assets in the BM test case. This will be particularly problematic for Phase 2 when non-BM assets are able to participate through the use of the fully established Open Balancing Platform which should be a massive advancement, but only if it has the assets to dispatch. Present operational metering requirements will limit the return on investment that such IT investments will realise. |  |  |  | See question 10 | There will need to be consideration into the length of Linked Buy-Orders when these are implemented and how realistic this would be for assets to dispatch for the entire linked QR window. | We consider having a co-optimised auction as vital for the implementation of QR, so are in support of having the auction at 2pm, at the same time as the Dynamic Response Services. We are however concerned with proposals to move the QR auction timing to the morning during phase 2, alongside Balancing Reserve. Not only does this make less sense for flexible assets able to participate (explicitly batteries as above) but could have a large effect on overall balancing costs.
20 | 2024-07-30 10:52 | 2024-07-30 10:57 | anonymous |  |  | Tesla Motors Limited | Giulio Beseghi (gbeseghi@tesla.com), Andrew Lam (andrlam@tesla.com) | No | We agree with the proposal | We agree with the proposal | We agree with the proposal In particular, we agree that with there being no maximum ramp up or ramp down rates for baselines. This will ensure QR is consistent with the new rules for DC,DM and DR and consistent with the rationale for removing the maximum ramp rate for response. | We agree with the proposal | **Energy Requirement** We agree with this proposal, but want to point out that this rule combined with Gate Closure will naturally incentivise bidders to bid in QR at high prices: 1. Due to Gate Closure, we have no control on the SOE in the hour before the contracted period start 2. Therefore, we'll have to reflect our availability / awarded volume in other markets (BR, DC/DM/DR, BM) in a way that under an extreme activation we can still enter the QR contracted period with an acceptable SOE We note that as a result of having to respect the Energy Requirement, QR providers may be driven to factor in the opportunity cost for missing opportunities in these other markets, which will have an upward effect on the price of QR bids. **Cross overs** We agree with the proposal - we think this is a neat solution; we encourage the ESO to use linked buy orders only to cover the required volume at the boundary, and use regular orders for the remainder. We think this will produce a more efficient clearing outcome that should help keep the overall costs of the service down. **Everything else** We agree with the proposal | We agree with the proposal | We agree with the proposal | We agree with the proposal | We agree with the proposal | We agree with the proposal. We note clearing for one settlement period in QR, means providers would miss out on four hours (a whole EFA block) of DC/DM/DR. As mentioned above, this creates a large opportunity cost for bidding for one settlement period in QR - similar to what currently happens in BR. Per our previous feedback to NGESO, we think this problem of having high opportunity costs being factor into QR bids could be mitigated by shifting DC/DM/DR to per settlement period procurement (rather than the current arrangement for per EFA block procurement). | We agree with the proposal

## Q1 Phased Delivery
Company Name | Please provide any specific comments relating to the proposed Phased Delivery Approach, Provider Eligibility, and Registration and Prequalification process for Phase 1 of the Quick Reserve service. | ESO Response
SSEN Distribution, trading name of Southern Electric Power Distribution plc | We consider the proposed Phased Delivery Approach to be inherently unfair and anti-competitive as it excludes non-BM providers from participating during Phase 1. ESO's justification for this approach is not based on any inherent benefit of BM providers over non-BMs, but simply their own systems' inability to accommodate non-BMs into the new market before summer 2025. Furthermore, the ESO’s stated plan to procure 100% of its requirement from the day-ahead Quick Reserve market from November 2024, and as little as possible from the existing within-day Fast Reserve market, is discriminatory to non-BM Fast Reserve providers, who will be immediately excluded from participating in this market. The ESO’s suggested mitigation is for non-BM Fast Reserve providers to join the BM, but this is not feasible for some providers, such as those delivering reserve services using CLASS solutions. | Thank you for the feedback. We consider our overall approach to be compliant with our legal and regulatory obligations, and in particular to be non-discriminatory, and in this respect we have sought to ensure that the QR service is designed in such a way that all parameters are properly justified, proportionate, and based on system need. Where we have identified a requirement which potentially acts as a barrier to market entry, we have sought to mitigate any ‘first mover’ advantage, and as a service which (like balancing reserve) will, initially, be dependent on BM systems, we are able to utilise the BM wider access route so that QR is accessible in phase 1 by the widest possible range of flexible providers. There is benefit in terms of value to the consumer (see below) in pursuing the phased approach compared to waiting until OBP is fully functioning, and on a cost benefit analysis, other mitigation options specifically accelerating OBP development or adapting existing ASDP/PAS are similarly sub-optimal. Whilst we are unable to launch the Quick Reserve market to non-BM parties until 2025 when our OBP functionality will allow, we have identified an opportunity to bring forward consumer value and deliver the service in winter 2024, utilising our existing BM systems in combination with the new Open Balancing Platform (OBP) multi-dispatch. This means that in Phase 1 access to Quick Reserve will be through our existing BM systems and parties would need to register their units in the BM. We believe the majority of existing market participants and new providers of flexible energy, that meet the Quick Reserve requirements, have the opportunity and necessary lead-time to register in the BM and access Quick Reserve from day one. Aside from existing BM parties and those able to join as Primary BMUs, we believe through the BM Wider Access route there is a clear cost effective and efficient route to market for smaller non-traditional providers, aggregators and providers of flexibility, which allows them to access the Quick Reserve service in Phase 1. In order to maintain a route to market for the provision of faster-acting reserve from any party, either unable to or not wishing to access the BM, we will be retaining the existing Optional Fast Reserve service until the end of 2025. Where any market participant feels there are barriers that make it unfeasible for their technology to access our balancing services or the BM then we are keen to discuss these with you and to work with industry and the regulator to look at how these can be overcome. After thorough consideration, ESO firmly believe that our decision to implement the new Quick Reserve service directly on the new OBP system with a phased approach during 2024 and 2025 is the right approach that provides an opportunity to bring forward (by circa 7 months) increased competition and a more competitive market (compared to the existing Optional Fast Reserve and Spin Gen market) that realises increased consumer value, estimated in the region of £29.3m - £32.7m. For the new Quick Reserve service, our analysis suggests that there is over 5.5 GW of market capacity available (aided by our ability to co-optimise procurement with Dynamic Response services) against an estimated typical requirement of 300-500MW, ensuring sufficient competition. Therefore, by establishing a firm market we expect the benefit of a reduced availability clearing price, against the alternative costs of Optional Fast Reserve and Spin Gen/ Spin Pump, to outweigh the additional cost of not having full participation in the market on day 1. Based on this analysis, we expect to be able to procure 100% of the requirement via the new day ahead Quick Reserve auction, however we cannot guarantee this and we will turn to the existing reserve (Optional Fast Reserve and Spin Gen/ Spin Pump) to make up any shortfall. Whilst we will submit a buy-order for 100% of our Quick Reserve requirement, the pricing of the buy-order will be driven by the range of available alternatives. For example, if Optional Fast Reserve is priced competitively to Quick Reserve, this will lead to some (or all) of the buy-order not being filled, as Optional Fast Reserve has met the need. This means that there's no benefit to artificially limiting the volume of our buy-order, as the market will in practice determine where the limit should be. If there is reliable volume in the Optional Fast Reserve market routinely pricing for availability at a lower price than Quick Reserve, then the ESO may reduce the price of the Quick Reserve buy-order and turn to cheaper Optional Fast Reserve.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | Timescales do not allow a large, aggregated CLASS provider time to develop a solution to achieve the more technically onerous requirements of Quick Reserve between now and November 2024. ESO and Ofgem have both actively encouraged and supported CLASS providers to enter this market, and this change in procurement strategy is contrary to previous communications from ESO. | The ESO first shared the details of the final proposed Quick Reserve service design during industry webinars in December 2023, followed by another in February 2024 and a final proposed design 'request for feedback' in early spring 2024 - as published on our website (https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/quick-reserve#Events). There have also been many communications with industry prior to the delivery of the final designs which outlined many of the requirements as they stand today. Procuring 100% of the firm Quick Reserve capacity at day-ahead is one of the drivers to reducing costs of the expensive pump storage and Optional Fast Reserve we currently have access to. Although non-BM providers won't be able to participate in the Quick Reserve market (unless they decide to join the BM), they will still be able to compete during Phase 1 of Quick Reserve via Optional Fast Reserve. As long as they are priced competitively then there is no reason why these units would not be instructed. CLASS services may not be a best fit for the Quick Reserve service but ESO are happy to work with SSEN and the wider industry/Ofgem to look at how the CLASS service best fits within the ESO future balancing service requirements.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | We suggest alternative approaches which ESO could implement: either postpone the launch of the Quick Reserve (QR) market until it is open to both BM and non-BM participants alike; or adopt a gradual cutover between the FR and QR markets, for example by initially procuring 10% of required volumes from QR and increasing that by a further 10% each month during the transition period. Such a gradual cutover would also support ESO’s aim for cross-market competition, as outlined below. These approaches both provide volume in the non-BM Optional Fast Reserve market until participants are allowed to join the replacement non-BM QR market, maximizing market liquidity and ensuring ESO can maintain system security at the lowest possible cost. | We firmly believe that our decision to implement the new Quick Reserve service with a phased delivery during 2024 and 2025 is the right approach that provides an opportunity to bring forward (by circa 7 months) increased competition (compared to the existing Optional Fast Reserve and Spin Gen market) that realises increased consumer value, estimated in the region of £29.3m - £32.7m. To clarify our procurement strategy, while we will submit a buy-order for 100% of our Quick Reserve requirement, the pricing of the buy-order will be driven by the range of available alternatives. If Optional Fast Reserve is priced competitively to Quick Reserve, this will lead to some (or all) of the buy-order not being filled, as Optional Fast Reserve can meet the requirement. This also means that there's no benefit to artificially limiting the volume of our buy-order, as the market will in practice determine where the limit should be. To be clear, we will not buy 100% of our volume at any cost through Quick Reserve. We will only procure it if we can fill the need more economically compared with other options.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | ESO has stated that it wants to use the existing Optional Fast Reserve (Optional Fast Reserve) market to provide cross-market price competition to QR during Phase 1, despite its clearly stated intention to procure as little as possible Optional Fast Reserve from day one of QR. This seems contradictory, because as the expected Optional Fast Reserve volume falls immediately to near zero, so does the commercial incentive for SSEN to continue its investment to provide a solution suitable to participate in Optional Fast Reserve, and subsequently submit competitive offers to the Optional Fast Reserve market. Cross-market competition only works if both markets are active and liquid. In fact, given the very low expected procured volumes, as well as ESO’s stated intention to only buy Optional Fast Reserve in emergencies, Optional Fast Reserve participants will be inclined to offer higher market prices to reflect both the limited opportunities for revenue and the knowledge that ESO will only ever approach them as a distressed buyer. A gradual cutover from the Optional Fast Reserve to the QR market would both maintain price competition within the residual Optional Fast Reserve market and provide genuine price signals to the growing QR market. Broadly, we are disappointed with ESO’s approach and timing to publishing the revised proposed strategy. The proposed changes to procurement strategy are contrary to those that ESO has shared with us previously and are a prohibitive factor in our ability to justify participating in the market from November 2024. There is also a risk for the ESO there will be a lack of confidence in future developments and market signalling with this pivot at such a late stage, resulting in a wariness from participants to invest in the infrastructure needed to offer services in the future. | We have not changed our proposed procurement strategy for Quick Reserve. To clarify, while we will submit a buy-order for 100% of our Quick Reserve requirement, the pricing of the buy-order will be driven by the range of available alternatives. If Optional Fast Reserve is priced competitively to Quick Reserve, this will lead to some or all of the buy-order not being filled, as Optional Fast Reserve can meet the requirement. This also means that there's no benefit to artificially limiting the volume of our buy-order, as the market will in practice determine where the limit should be. To be clear, we will not buy 100% of our volume at any cost through Quick Reserve. We will only procure it if we can fill the need more economically compared with other options. We hope this addresses the concern around the benefits, if not we are happy to discuss this further.
Statkraft UK Ltd | The reasons behind the phased delivery approach, transition plan and timelines are well understood and have been sufficiently communicated. Perhaps, some of the details on the proposed changes for BM Quick Reserve in Phase II could be further highlighted (updates to the QR service design); such as the proposal to change the performance monitoring data to 1 second as opposed to the average 30-minute settlement metering or proposal to change the auction timings from T-1 at 14:00 to T-1 at 09:00 AM. Further clarification on the future possibilities for stacking QR with other ancillary services could also be outlined in further detail. | Thanks for the feedback. We plan to share details of the enduring service and procurement design for Quick Reserve and Slow Reserve in September 2024. We will ensure that the points raised here are addressed in that material.
Statkraft UK Ltd | The registration and prequalification process via the SMP is also understood. However, the there are some points in the registration process that are proving at times tricky/time consuming. This applied to general SMP asset onboarding process rather than being service specific. For example, an account holder with multiple entities, is not able to register the different entities under the same account (same email address) and multiple accounts are having to be requested via the SMP team as a backend process/workaround. This should be changed as it is quite common for the same individual to be involved with multiple assets. The request for Agents and registration of assets as an Agent should be more streamlined. | Thanks for the feedback. We are planning to implement the Single Sign-on in Q3 financial year 2025 where a provider with one email address will be able to access multiple accounts if they have the permissions. As discussed, you have agreed to provide specific feedback on the email template with examples so that our SMP team can review and enchance the email template as necessary.
Flexitricity Limited | ESO should engage with industry as soon as possible should there be any requirements for testing for BM-QR qualification, especially if this requires external validation via an Independent Technical Expert. | Thank you for the feedback. We won't require independent validation of units.
Sembcorp Energy (UK) Limited | We believe it would be preferable from a non-discriminatory perspective to launch the service when all units, both BM and non-BM, are able to fully participate. This would provide greater competition and ensure a level playing field, as well as likely be most cost-effective for ESO. | Thank you for you feedback. We consider our overall approach to be compliant with our legal and regulatory obligations, and in particular to be non-discriminatory, and in this respect we have sought to ensure that the QR service is designed in such a way that all parameters are properly justified, proportionate, and based on system need. Where we have identified a requirement which potentially acts as a barrier to market entry, we have sought to mitigate any ‘first mover’ advantage, and as a service which (like balancing reserve) will, initially, be dependent on BM systems, we are able to utilise the BM wider access route so that QR is accessible in phase 1 by the widest possible range of flexible providers. There is benefit in terms of value to the consumer (see below) in pursuing the phased approach compared to waiting until OBP is fully functioning, and on a cost benefit analysis, other mitigation options specifically accelerating OBP development or adapting existing ASDP/PAS are similarly sub-optimal. Whilst we are unable to launch the Quick Reserve market to non-BM parties until 2025 when our OBP functionality will allow, we have identified an opportunity to bring forward consumer value and deliver the service in winter 2024, utilising our existing BM systems in combination with the new Open Balancing Platform (OBP) multi-dispatch. This means that in Phase 1 access to Quick Reserve will be through our existing BM systems and parties would need to register their units in the BM. We believe the majority of existing market participants and new providers of flexible energy, that meet the Quick Reserve requirements have the opportunity and necessary lead-time to register in the BM and access Quick Reserve from day one. Aside from existing BM parties and those able to join as Primary BMUs, we believe through the BM Wider Access route there is a clear cost effective and efficient route to market for smaller non-traditional providers, aggregators and providers of flexibility, which allows them to access the Quick Reserve service in Phase 1. After thorough consideration, ESO firmly believe that our decision to implement the new Quick Reserve service directly on the new OBP system with a phased approach during 2024 and 2025 is the right approach that provides an opportunity to bring forward (by circa 7 months) increased competition and a more competitive market (compared to the existing Optional Fast Reserve and Spin Gen market) that realises increased consumer value, estimated in the region of £29.3m - £32.7m. For the new Quick Reserve service, our analysis suggests that there is over 5.5 GW of market capacity available (aided by our ability to co-optimise procurement with Dynamic Response services) against an estimated typical requirement of 300-500MW, ensuring sufficient competition. Therefore, by establishing a firm market we expect the benefit of a reduced availability clearing price (against the alternative costs of Optional Fast Reserve and Spin gen/ Spin Pump) to outweigh the additional cost of not having full participation in the market on day 1.
Centrica | We would appreciate more clarity on the distinction between Balancing Reserve and Quick Reserve. In our view, the ESO should increase the performance granularity to support service stacking from Phase 1. | Balancing Reserve is a service by which the ESO can procure Regulating Reserve at day-ahead, effectively reducing the overall cost of any relatively large amounts of volume used for many different types of pre-fault (and sometimes post-fault) actions, but crucially, for known changes to either demand or generation. Quick Reserve, on the other hand, is designed to react to smaller, fast-acting and unknown system impetuses. It is designed to keep frequency within normal operational conditions by injecting relatively small amounts of fast-acting MWs on the system. Regarding service stacking, we appreciate that this is a desired capability. However, our internal systems are currently unable to handle this resolution of data. We are working to develop this capability, with the vision that it will be available for Phase 2.
Shell | We are keen that the ESO keep to their planned phase out of the Fast Reserve and don’t change this target as was the case with phasing out the old Response product. | Thank you for the feedback.
ADE | We agree with the laid out phased delivery approach and that it makes sense to wait for the full implementation of OBP to allow access to non-BMUs. However, we don’t agree that this will facilitate ‘fair access for all market participants’ due to the issues laid out above that are required of assets to participate in Quick Reserve. We would also emphasise the importance of a co-optimised auction with Reserve and Response services as we eventually move into Phase 2 of implementation. | We understand that the parameters for Quick Reserve are somewhat more onerous than our other services, but they are reflective of a system need which the ESO requires in order to efficiently manage the network. We have conducted a full market analysis and believe that batteries, pump storage, small BMUs, wind and some gas reciprocating engines will be able to participate, generating a minimum estimated 5.5GWs of capacity for a typical estimated requirement of 500MW +ve/300MW -ve, ensuring sufficient competition. We are still reviewing the timings of the Reserve services for Phase 2, with our final decision yet to be published. We appreciate the feedback and will take this into consideration.

## Q2 Service Utilis & Dispatch
Company Name | Please provide any specific comments relating to the proposed Service Utilisation & Dispatch Mechanism for Phase 1 of the Quick Reserve service. | ESO Response
Arenko Group | We are supportive of measure to implement solutions on the back of our Balancing Reserve CFI response. However, we are concerned about the lack of a scientific approach to defining excessing pricing in the chosen solution and the absence of a clear penalty structure as seen in the new Dynamic Response service terms. We are concerned that precedent from Ofgem's ruling on the Inflexible Offer License Condition (~aversion to defining 'excessive' given uncertainty over market participant information) could suggest additional regulatory risk that participating in QR could represent for participants. We think 'chatham house' in-person sessions with industry participants, particularly those offering expertise in engineering and trading roles, could present an opportunity for ESO to constructively explore the solution space, including via the procurement of digital tools to deliver performance monitoring outcomes. We note that the deterrent of retrospective penalties/nominal fines based on historic data that indicates gaming at system-risk activity should be explored in our response to Dynamic Response Release 3 feedback. This could ensure provide an added incentive to ensure reserves exist in QR, providing time for clear and scientific penalty regime gets introduced. Finally, we support continued clarity and defined penalty structure for mis-delivery over and above imbalance prices or BM non-delivery charges, especially as NBM units come on to the system. | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we are proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances. We considered a penalty based structure, such as that proposed for the Dynamic Response services, but felt that these were not necessary given the new state of energy controls we have included in the service terms along with the shorter window lengths and the fact that this is a brand new service. We will be reviewing this decision and engaging with industry for feedback through Phase 1, just as we have done with Balancing Reserve, in order to assess Quick Reserve market behaviours. We will also continue to monitor the penalties outlined in the Response services and share any proposed design changes with industry as appropriate.
Flexitricity Limited | No comments on this for phase 1. We would encourage early engagement with industry on phase 2, non-BM, and the transition away from ASDP into OBP for non-BM assets | Thanks for the feedback. We plan to share details of the enduring service and procurement design for Quick Reserve and Slow Reserve in September 2024. On 13 August 2024 we held the first webinar on the proposed transition away from ASDP and we have opened this up to industry for feedback until 10 September 2024. https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/future-reserve-services#Events

## Q3 QR Service Design
Column1 | Column2 | Column3
Company Name | Please provide any specific comments relating to the proposed Quick Reserve Service Design Parameters including Notice to Start Ramping, Time to Full Delivery, Cease Time, Activation Periods, Recovery Period, Ramping Envelope, Ramp rates for Baselines for energy limited assets. | ESO Response
Peak Gen Top Co Limited | The proposed contract form does not explicitly state the Run Down Rate at the end of the delivery. We infer that it is meant to be identical to the Run Up Rate. It would be helpful if this was made explicit | Thank you for pointing this out. Our expectation initially was to make this symmetrical, however we realised with the Ramp Up requirements, and the requirement on Minimum Activation Time at 5-minutes, that the Ramp Down Time was already limited to a maximum of 3-minutes. We felt that not defining a requirement here would allow providers some additional flexibility. We will monitor how this performs and whether any changes are necessary in future.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | Several of the Quick Reserve technical parameters are more onerous than their Fast Reserve equivalents, and some have an impact on our ability to offer and deliver a Quick Reserve service due to our CLASS asset type. Time to Full Delivery is proposed to be a maximum of 1 minute from dispatch, as opposed to 2 minutes for OFR. ESO estimates that only “around 30% of the non-BM OFR capacity… can achieve the 1-minute time to full delivery,” (quote from the Quick Reserve Summary document, p9) and we (SSEN) would fall into the 70% of capacity which cannot. Our “unit” is an aggregated and geographically dispersed group of assets. Reducing the “time to full delivery” from 2 minutes to 1 minute will require significant design, investment and implementation of an improved solution. This is not achievable by November 2024. | We understand that the parameters for Quick Reserve are somewhat more onerous than our other services, but they are reflective of a system need which the ESO requires in order to efficiently manage the network. The 1-minute Time to Full Delivery has been consistently set out since 2022. To clarify on the 70% reference in our Quick Reserve Summary Document, we state that "It is estimated that around 30% of the non-BM OFR capacity (close to 320 MW) can achieve the 1-minute time to full delivery". This does not reflect any of the other existing units which may be working towards this capablity in order to participate in Quick Reserve.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | The maximum Recovery Period for Quick Reserve is proposed to be 3 minutes, whereas for the OFR service recovery period is 15 minutes. Again, meeting this change to requirements would significantly restrict our offering to a small proportion of our available capacity at any time, keeping volume in reserve to be available for dispatch 3 minutes later while the previously dispatched assets recover. Furthermore, delivering even this diminished volume would require significant investment in scheduling and dispatch systems to cycle through available aggregated assets in a way that is not necessary for our OFR service, and therefore not in place. At this point, we would not be able to provide a service with this requirement. | Thank you for the feedback. The Recovery Period parameter was initially determined through a detailed analysis of historic frequency deviations and is therefore directly tied to a system need. This parameter was then relaxed (from 1-minute to 3-minutes) in order to maximise participation (and consequently competition) in the market. We recognise that the 3-minute Recovery Period in particular has generated lots of feedback and this has been an area of detailed study and as such we are not planning to change this parameter for the foreseeable future. We have explained our reasoning in the published '3-minute Recovery Period' justification paper which was uploaded to our website alongside the A18 documentation. You can find this justification paper under the supporting documents tab, here: https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/quick-reserve#Document-library
SSEN Distribution, trading name of Southern Electric Power Distribution plc | The cumulative effect of these changes is to diminish the volume of OFR capacity that will be available to offer Quick Reserve, which would be disadvantageous for ESO and for market competition generally. However, given that the ESO (i) already accepts that 70% of that capacity will be ineligible for Quick Reserve, and (ii) is confident that it will be able to meet 100% of its Quick Reserve needs without any OFR volume, it appears that this market competition is not considered by the ESO to be of significant value. We feel there is a risk ESO is focused on this approach to ‘Standardise’ products; we support the standardisation of products across the industry. However, the approach taken risks increasing rather than reducing barriers to entry. | We have assessed the impact of any additional barriers to entry on levels of competition and are satisfied that they represent the best compromise available between liquidity, price and system security. To clarify on the 70% reference in our Quick Reserve Summary Document, we state that "It is estimated that around 30% of the non-BM OFR capacity (close to 320 MW) can achieve the 1-minute time to full delivery". This does not reflect any of the other existing units which may be working towards this capablity in order to participate in Quick Reserve.
Statera Energy | The Notice to Start Ramping being 0 minutes suggests that ESO expects providers to instantly process instructions – however, there are certain communications that providers may have set up with third-party systems, which this parameter currently doesn’t facilitate. In practice this may be fine given that Time to Full Delivery is 1 minute from instruction, but in theory it could exclude technologies that take a full minute to ramp but require additional time to process the dispatch instruction. Statera welcomes that there is no restriction on ramp up/down rates, meaning that batteries can respond without having to stagger their response. | In principle, the ESO are happy to accept that providers response times may not be 0 (although, we would still require that they are submitted as such, as our systems can only handle integers and a 1-minute NTO/NTB would fail availability checks). As long as the unit is able to reach it's Time to Full Delivery within 1-minute from instruction, then the actual response time can be non-zero. That is, if it takes 10-seconds for instructions to be processed and accepted, and the unit is able to reach full output in the next 50-seconds, then this is acceptable.
Flexitricity Limited | Recovery Periods: Whilst we appreciate that the ESO has relaxed the requirement for recovery periods from 1 minute to 3 minutes, this will still not enable I&C load to participate and will create a barrier to entry. The service should be designed to be technology agnostic and whilst the ESO is not explicitly restricting assets from participating, the recovery period parameter does make participation from assets, other than battery storage, particularly challenging. ESO should proactively engage with flexibility providers and I&C load participants before moving forward. Ramp Rates: We welcome the ESO’s proposed update on removing ramp rate restrictions for the QR service and for acknowledging the constraints this puts on providers in Dx response service delivery | We appreciate that some technology types may not be able to participate in the market. Our requirements for the Quick Reserve service have been driven by our system needs, and we have tried to open this up where possible to as many technology types as we can. We understand that the 3-minute recovery period in particular has generated lots of feedback. This has been an area of detailed study, and we have published a full '3-minute Recovery Period' justification paper along with the A18 documentation which you can find on our website here: https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/quick-reserve#Document-library We appreciate that this requirement may be more onerous than in other services, but it is a direct reflection of the needs of the system. Whilst this has been an area of detailed study, however we are not able to make this parameter more flexible for the foreseeable future. Thank you for the feedback on the Ramp Rate restrictions. We have worked to be consistent with the Response team as they have also been removed in the recent response consultation, and we agreed that this was an area we could compromise to increase participation.
Sembcorp Energy (UK) Limited | The 1-minute time to full delivery and maximum 3-minute recovery time could severely limit the participation of most technologies including our flexible reciprocating engines. We believe the market will be restricted to storage assets and thus limit the competitive offering. | We appreciate that some technology types may not be able to participate in the market. Our requirements for the Quick Reserve service have been driven by our system needs, and we have tried to open this up where possible to as many technology types as we can. We will continuously monitor the service as it matures over Phase 1 and, if required and not to the detriment of the system, may relax certain requirements for greater access for the market where possible. We recognise that the 3-minute recovery period in particular has generated feedback. This has been an area of detailed study, however we are not able to make this parameter more flexible for the foreseeable future. We have published a full '3-minute Recovery Period' justification paper along with the A18 documentation which you can find on our website here: https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/quick-reserve#Document-library We have conducted a full market analysis and believe that batteries, pump storage, small BMUs, wind and some gas reciprocating engines will be able to participate, generating a minimum estimated 5.5GWs of capacity for a typical estimated requirement of 500MW +ve/300MW -ve, ensuring sufficient competition.
Drax Group | We believe the proposed 3 min recovery period is an optimal threshold which maximises participation from available capacity, thus delivering market liquidity and cost benefits. Reducing this recovery period will significantly limit participation, and implicitly introduces discriminatory treatment for non-critical reasons by making delivery of the service suitable for one type of technology only. This may not be in line with the technology and size agnostic approach the ESO typically strives for. More importantly, this will increase the risk of over-reliance on one type of asset and jeopardises the efficiency of the service and security of meeting system needs. Moving forward, we would welcome an indication from the ESO on whether the Maximum Recovery Period study and analysis will continue exploring a move to a 2 min or lower recovery period in the future. If a shorter recovery period remains an option, we are keen to see timely engagement with industry stakeholders in any future technical or commercial studies. With regards to baselining, we agree with the acceptable baseline being either zero or non-zero. This allows PSH units to deliver from spin mode and enhance their participation in the market, hence improving liquidity and flexibility of the service. | We appreciate that some technology types may not be able to participate in the market. Our requirements for the Quick Reserve service have been driven by our system needs, and we have tried to open this up where possible to as many technology types as we can. We have explained this in the published 3-minute Recovery period justification paper which was uploaded to our website alongside the A18 documentation. You can find this justification paper under the supporting documents tab, here: https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/quick-reserve#Document-library. We will continuously monitor the service as it matures over Phase 1 and, if required and not to the detriment of the system, may relax certain requirements for greater access for the market where possible.
RWE | Many of these proposed technical parameters prevent all flexible technology types from participating, except batteries. This is arguably in contrast with the self-styled “technology-agnostic” approach of the ESO. | We believe that there are enough different asset types in the available market who can participate, which include batteries, pump storage, small BMUs, wind and some gas reciprocating engines, which constitute over 5.5GW as a low estimate. We are comfortable in our market analysis and have made as many concessions on the service as possible without materially reducing it's effectiveness at meeting the specific needs of the system from which it was designed. You can find this analysis in our published justification paper on our wevsite under the supporting documents tab, here: https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/quick-reserve#Document-library. We would like to stress that we are technology agnostic. Our new suite of Reserve services are a reflection of an evolving system need, which is largely dictated by a reduced demand and increase in low inertia and renewable generation. Technology agnostic does not mean that all technologies will be able to participate in all services, but that we do not introduce rules for the sole purpose of including or excluding a particular technology type.
Shell | We would also welcome an overview from the ESO, as to why they need the Balancing and Quick Reserve and whether they can be rationalized. Having two Reserve products which are both procured at day ahead and served by the same technology type may lead to inefficiencies and costs for consumers. | Balancing Reserve is a service by which the ESO can procure Regulating Reserve at day-ahead, effectively reducing the overall cost of any relatively large amounts of volume used for many different types of pre-fault (and sometimes post-fault) actions, but crucially, for known changes to either demand or generation. Quick Reserve, on the other hand, is designed to react to smaller, fast-acting and unknown system impetuses. It is designed to keep frequency within normal operational conditions by injecting relatively small amounts of fast-acting MWs on the system. That said, separately defined services such as Balancing Reserve and Quick Reserve can be used interchangeably, depending on the system needs at the time, and can therefore contribute towards our total pre-fault Reserve requirements. In general, we try to create a balance between different products which allow different assets' value to be realised in operation of the system, verses reducing and standardising the products to maximise competition in each market and lower prices, as well as setting clear investment signals for the flexibility that the ESO values. We have committed to exploring whether the Balancing Reserve auction should move to be part of the same co-optimised auction, which we believe would address your concern. If this does not occur, we expect price signals to drive more flexible assets towards more flexible services.
Statkraft UK Ltd | The recently made changes to some of the technical parameters under the service design may prevent/limit participation, specifically the Notice to Start Ramping and Time to full delivery require an instantaneous processing time for Quick Reserve instructions to be delivered in accordance with the notice period of 0 minutes and response time of 1 minute. Although, majority of assets can respond to an instruction quick enough, the current service design does not allow for much processing time or communications latency between the communication of third-party systems. The proposal is also not in line with other services (such as Balancing Reserve). Having to forgo the availability payment for the whole Settlement Period due to response time longer than 1 minute may prevent participation and it should take into consideration the asset response as well as the processing time and communications latency of the instruction. As the recommendation sits on two separate analyses, have those analyses taken into consideration all technology types such as energy limited assets or gas peaking assets? As only pump hydro storage is currently quoted in the summary document. We would prefer that the response time is 2 minutes to allow for variable processing time and communications latency and to maximise assets which can participate. As the ramp rates will not be required, would NG be able to share timelines of when this will put in place (and will this also be implemented for DFR services)? | Whilst we appreciate that the Quick Reserve parameters are somewhat more onerous than other services, they are a reflection of the needs of the system. Although we do state that NTO/NTB needs to be zero (because our systems can only handle integer values and anything >0 would be an automatic availability failure) we are willing to accept that some providers may still be able to reach full delivery within a minute, even if their notice period is non-zero. That is, if it takes 10-seconds to process and receive an instruction, and the unit can still reach it's contracted capacity within the next 50-seconds (i.e. total of 60-seconds from instruction receipt) then NGESO will consider that acceptable.
Statkraft UK Ltd | We would prefer that the response time is 2 minutes to allow for variable processing time and communications latency and to maximise assets which can participate. As the ramp rates will not be required, would NG be able to share timelines of when this will put in place (and will this also be implemented for DFR services)? | Thanks for the feedback. We have designed the Quick Reserve service around a system need. Unfortunately, extending the response time out to 2-minutes isn't possible, as this will undermine the fast-nature of the product and reduce it's value to the ESO. We assume you are referring here to Ramp Rates for Baselines. They are going to be aligned with the Dynamic Response markets and we intend that the removal of the Maximum Ramp Rate shall be in effect as soon as we publish revised Service Terms subject to and following Ofgem approval of our proposals, which we expect to be late October or early November 2024. Before this date we do not intend to enforce the prevailing service terms around the Maximum Ramp Rate. We set this out in our ‘2024 Roadshow slides’ and 'Consultation Webinar slides - 11 June 2024', both available in the document library of our Dynamic Services web page (under Market Engagement 2024).
Energy UK | Maximum recovery period – Energy UK supports the proposed 3 minute recovery period. Whilst, in general, a shorter recovery period can reduce competition in the market, we think it is unlikely to have a significant impact in this case as the service requirements in general (speed of delivery, ramping and notice period) mean that the service is unlikely to be both feasible and commercial attractive for other plant such as CCGTs and OCGTs. We appreciate the ESO perspective that the maximum recovery period would be as close to zero as possible because that enables the greater the maximum coverage of like the frequency deviations that the service aims to deal with. We would welcome some clarity or indication of whether the 3-min will be a confirmed parameter for the near future or whether the ESO will keep exploring the option of moving to a 2 min recovery. If a move to a shorter recovery is considered, this should be supported by evidence and stakeholder engagement with a timely notice for all stakeholders. | We recognise that the 3-minute Recovery Period in particular has generated a lot of feedback as this parameter is somewhat more onerous than in other services. The 3-minute Recovery Period is a direct reflection of a system need, and we have explained this in the published 3-minute Recovery period justification paper which was uploaded to our website alongside the A18 documentation. You can find this justification paper under the supporting documents tab, here: https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/quick-reserve#Document-library This is a confirmed parameter which we do not currently intend to change. However, we will monitor key required parameters throughout Phase 1 and, if required, will update industry with any potential changes to the design along with any relevant justification.
ADE | A recovery period of 3 minutes, despite being decided as the optimum recovery time from ESO analysis, still causes all flexible assets apart from batteries to be excluded from participating in Quick Reserve. As above, we are disappointed in the design of yet another battery exclusive ancillary service, the fifth to be implemented throughout RIIO-2. This places further emphasis on the need for the service to be technology agnostic in reality rather than just a lack of explicit restrictions. Industrial and Commercial load is the main group of assets to be excluded as a result of this requirement, leading us to question the alignment between ESO’s message of inclusivity and delivery in service design. We would also like to see additional information regarding the analysis that has been undertaken by ESO to get to this result, specifically the significance between the effect of the recovery time and the ability for assets to participate. On the time to full delivery, for many flexible assets to get up to what is required within 1 minute is either unachievable or will have large impacts on the health of the asset being used, again apart from batteries. To say that any load unable to participate in Quick Reserve to just participate in Slow Reserve is not an adequate solution. | We believe there are many asset types which can participate in the Quick Reserve service that match the requirements. Batteries, pump storage, small BMUs, CCGT and possibly wind units are all expected to participate, helped in some part by the allowance of non-zero baselines. Due to the fast-acting and flexible nature of the requirement, the service does lend itself to more flexible and fast-acting units and is a direct reflection of the needs of the system to manage an ever-more volatile frequency profile. Whilst we are technology agnostic that does not mean we can make all services accessible to all providers. The services we design are merely a reflection of what is required in order to economically and efficiently manage the network, and we have no bias on particular technology types. We do aim to have a variety of services which allow a variety of asset types to have routes to market and achieve value from their capabilities. We have published a supplementary '3-minute Recovery Period' justification paper which you can find on our website under the consultation section (https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/quick-reserve#Document-library). We have analysed the market and found that there is around 5.5GW (minimum) of potential capacity that is eligible for the Quick Reserve market, of which would be competing for a typical 500MW +ve/300MW -ve volume. This includes many technology types, not just batteries. Slowing the Time to Full Delivery or increasing the Recovery Period drastically undermines the aim of the Quick Reserve service, which is aimed to be fast-acting, quick to recover and cost-effective. Relaxing the parameters above will dramatically increase costs and lower the service's value. Our justification for this can be found in the above linked '3-minute Recovery Period' document.
Centrica | Our preference remains for a shorter maximum recovery period than 3 min. A 2 min period would be appropriate. | We recognise that the 3-minute recovery period in particular has generated lots of feedback. This has been an area of detailed study and as such we are not planning to change this parameter for the foreseeable future. The 3-minute Recovery Period is a direct reflection of a system need, and we have explained this in the published '3-minute Recovery Period' justification paper which was uploaded to our website alongside the A18 documentation. You can find this justification paper under the supporting documents tab, here: https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/quick-reserve#Document-library
Shell | We are supportive of the design parameters for Quick Reserve. We note that there has been much discussion around the proposed 3-minute recovery period. We believe that the ESO should base the recovery time on the required system needs. If the system would operate more efficiently with a faster recovery period, then we recommend the ESO stipulate a shorter recovery period or a date by which they want to revisit a review of the response time. | Thank you for the feedback. The Recovery Period parameter was initially determined through a detailed analysis of historic frequency deviations and is therefore directly tied to a system need. This parameter was then relaxed (from 1-minute to 3-minutes) in order to maximise participation (and consequently competition) in the market. We recognise that the 3-minute Recovery Period in particular has generated lots of feedback and this has been an area of detailed study and as such we are not planning to change this parameter for the foreseeable future. We have explained our reasoning in the published '3-minute Recovery Period' justification paper which was uploaded to our website alongside the A18 documentation. You can find this justification paper under the supporting documents tab, here: https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/quick-reserve#Document-library
SSE Plc | We have reviewed the service requirements against technical capabilities of common technologies (e.g. hydro, CCGT/OCGT, wind, solar, battery etc.). The service seems to only cater for technologies which can provide rapid response. Relaxing some of the time requirements (e.g. time to full delivery) would support non-energy limited assets to participate. | Although the Quick Reserve service is technology agnostic, it does lend itself to fast-acting technologies. The service requirements are somewhat more onerous than other Ancillary Services, and this is a direct reflection of our need for a fast-acting, flexible service in order to help manage an ever-increasingly volatile system. ESO has done lots of work and engagement with providers to enable the maximum possible participation. The Quick Reserve requirements will be kept under review during Phase 1, but we are hopeful that participation from non-zero baselines should allow all Secondary Response capable generators (i.e. BM units which provide mandatory Response) to be technically capable of providing Quick Reserve (as Secondary Response has a much quicker delivery time of 30-seconds).
Arenko Group | We support the proposed 3 minute recovery period and appreciated the supplementary analysis made available by the ESO. We agree that the maximum recovery period should continue to be reviewed and reduced to two minutes when possible as this will present the best cost to the consumer and utility to the system operator. | Thank you for the positive feedback.

## Q4 QR Metering
Company Name | Please provide any specific comments relating to proposed Quick Reserve Metering including Operational Metering and Performance Metering. | ESO Response
SSEN Distribution, trading name of Southern Electric Power Distribution plc | As a non-BM OFR provider, the “Meter Data” we provide for both operational and settlement purposes is derived from our own operational data using a methodology and formula that has been agreed with the ESO. We would use the methodology outlined in our Data Approach (v2.0 as previously shared with ESO on 1st May 2024 and formally approved by ESO on 18th July 2024), to generate the equivalent data for Quick Reserve (with 1-second granularity, as opposed to 15 seconds for operational data and 1 minute for settlement data as required under OFR). | We are still finalising the details of the non-BM metering rules, but we expect this will align with the proposal we discussed with you. We are planning to update industry on our proposal for Quick Reserve Phase 2 (and also Slow Reserve) in September 2024 and we are very happy to have a 1-2-1 to agree how your technology can best deliver against the requirement if necessary.
Statera Energy | Submission of Operational Metering at a frequency of once per second (1 Hz) with a latency of no greater than five (5) seconds, including active power and system frequency data, will require some changes to our current systems, working with third party providers to achieve those within the provided timelines for Phase 1 delivery. Using the 30-minute settlement metering data from Elexon to evaluate Availability, Time to Full Delivery, and Utilisation is welcome, but further clarification would be required in terms of Phase II performance monitoring. Is 1-second data expected? How will it be shared? And further communication on requirements for non-BM is still required, how will the performance metering data be shared? | For Phase 2, we will require the submission of 1-second Operational Metering. Quick Reserve is a fast-acting service which therefore requires a high-precision of unit output for control room visibility. This metering will also be used for performance monitoring during Phase 2, so we again need accurate and high-frequency data to assess a units performance and it's effect on the system. We are still developing the non-BM solution as it will be integrated into the new Open Balancing Platform (OBP) and these details are yet to be finalised. We are planning to update industry on our proposal for Quick Reserve Phase 2 (and also Slow Reserve) in September 2024.
Flexitricity Limited | Operational Metering: We understand the ESO intends to retain the 1Hz granularity of metering for QR which we believe to be overly restrictive for non-BM asset classes in Phase 2. We appreciate that ESO is undergoing an independent review of metering standards and currently conducting a 300MW small assets in the BM test case which may show that operational integrity can remain whilst relaxing metering standards. We look forward to the outcome of the independent review, but emphasise that the substantial delay in ESO’s timeline for this review should not necessitate the application of unnecessarily strict metering requirements for QR metering. Our expectation is that the learnings from the review and trial, both of which are well underway, should be incorporated into the QR product design as early as possible, so that metering standards for products not yet launched should be aligned so as not introduce unnecessary barriers to entry. | Thanks for the feedback - our colleagues in the Metering Review are closely looped into the further development of Quick Reserve metering standards. Any outcome of the investigation will apply to general BM units. However the 1Hz requirement is still applicable for any Quick Reserve participating units and we expect this to continue to be true due to the fast-acting nature of the service.
Sembcorp Energy (UK) Limited | We have reservations about the metering requirements and would appreciate further discussion to understand them better. | Our proposed metering requirements are yet to be finalised but our intention is that they will stay the same from Phase 1 to Phase 2, and we are happy to discuss the current proposals with providers, either through 1-2-1's or as feedback on our planned update to industry on Quick Reserve Phase 2 (and also Slow Reserve) in September 2024.
Statkraft UK Ltd | Using the 30-minute settlement metering data from Elexon to evaluate Availability, time to full delivery and utilisation is welcomed but further clarification would be required in terms of Phase II performance monitoring – is 1 second data expected? How will it be shared? And further communication on requirements for non-BM is still required, how will the performance metering data be shared? Performance monitoring with payment penalties for over and under delivery are clear and understood. | 1-second data will be expected from Phase 2. We will utilise submitted Operational Metering (at 1Hz granularity) for Performance Monitoring. We are planning to update industry on our proposal for Quick Reserve Phase 2 (and Slow Reserve) in September 2024.
ADE | The ADE has long advocated for relaxed operational metering requirements as without an immediate steer, consumers will continue to invest in assets which do not have the ability to enable them to participate in flexibility markets. Given that ESO are currently undertaking a review of metering requirements, it is disappointing to see the 1Hz granularity being retained for Quick Reserve. With the current trial attempting to increase access to the Balancing Mechanism (BM) for 300MW of small-scale assets underway, the use case of relaxed operational metering requirements is made clear. We look forward to the outcome of the independent review but would like to flag to the ESO that metering standards should be aligned to the small assets in the BM test-case in order to not introduce unnecessary barriers to entry – particularly for BM assets being grandfathered as part of the small assets in the BM test case. This will be particularly problematic for Phase 2 when non-BM assets are able to participate through the use of the fully established Open Balancing Platform which should be a massive advancement, but only if it has the assets to dispatch. Present operational metering requirements will limit the return on investment that such IT investments will realise. | We appreciate the challenges that the proposed 1Hz Operational Metering proposal presents to certain technologies, and we are keen to work closely with you and other industry parties to understand your specific challenges better and what is possible, so that we can agree how these requirements can be achieved. This is in line with the current Grid Code standard, although there is a review of Operational Metering standards underway for the BM. We would note that we require the central signal to ESO to be at 1 second granularity, but it is possible to construct a signal from distributed sites that have a less frequent update through methods such as staggering polling of the data (e.g. each sub-meter reports at 10-second granularity but staggered so that 1/10 give an update each second.) The granularity required from the sub-meters depends on the number of them (as it is a statistical method) so the more meters there are, the more the granularity can be relaxed. As well as the proof of delivery, during the periods where Quick Reserve is likely to be used, rapid confirmation of delivery with low lag is important for the ESO to correlate frequency changes with delivery of services to ensure that operational awareness is maintained in rapidly changing scenarios (e.g. has the Quick Reserve delivered, or has there been a coincident change in demand, and the Quick Reserve activation risks overdelivering against the requirement). It also aids confidence in delivery. It is much more obvious to see the effect of more granular metered services on the frequency as it can be observed in real time, and so operators can then trust and model the effect on the power system at that point in time. While there may be opportunities to change this for the wider BM, and for Slow Reserve, the timescales of Quick Reserve mean we are retaining 1Hz as a requirement.
Drax Group | We support the approach of using existing BM processes to submit operational metering. We also welcome the use of existing 30-minute average settlement metering data of BM units for performance monitoring purposes. This streamlines the process and creates a consistent and efficient approach which utilises existing standards and industry mechanisms. With regards to NBM performance and operational metering, we would welcome timely updates on the development of the ESO’s Performance monitoring capability and integration of operational metering in OBP. | Thank you for the feedback. We are planning to update industry on our proposal for Quick Reserve Phase 2 (and Slow Reserve) in September 2024.
Shell | We are supportive of the 1 hz operational metering and that for phase 1 no additional data will be required for performance monitoring as 30-minute average settlement metering data will be used. When data submission moves to daily we ask that sufficient time is allowed for participants to adjust their processes to accommodate this. | Thank you for the feedback. We are planning to update industry on our proposal for Quick Reserve Phase 2 (and Slow Reserve) in September 2024.

## Q5 QR Provider Availability
Company Name | Please provide any specific comments relating to proposed Quick Reserve Provider Availability, including Baselining, Energy Requirements, Cross-overs, Aggregation and Availability Declarations. | ESO Response
SSEN Distribution, trading name of Southern Electric Power Distribution plc | As with the proposed technical parameters, several of these requirements vary from their Optional Fast Reserve equivalents and some have an impact on our ability to deliver the new service. | Whilst we understand that the Quick Reserve requirements are more onerous than the Optional Fast Reserve service, these are a direct reflection of a system need which has driven the key parameters of this service. Where possible we have tried to relax requirements (e.g. 3-minute Recovery Period rather than 1-minute, and the allowance of non-zero baselines, etc) such that we can maximise market participation without adding any unnecessary hinderance to the main aims of the service.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | Baselining is a new requirement for QR that does not apply to Optional Fast Reserve. The requirement to submit Physical Notifications (PN) 24 hours ahead and Final Physical Notifications (FPN) 1 hour ahead is an achievable technical upgrade, subject to our currently agreed position with the ESO on baselining continuing to apply, i.e. that our PNs and FPNs will always be zero, and that there is no declarable activity from our assets unless and until we are dispatched to deliver the service. | We are planning to update industry on our proposal for Quick Reserve Phase 2 (and also Slow Reserve) in September 2024 and we will be very happy to engage with any provider to discuss the specific requirements, but we expect this will align with the proposal we discussed with you previously.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | The proposed Energy Requirement for QR is that providers must be able to sustain their contracted capacity continuously for a full 30-minute QR Window (or for multiples of 30 minutes if offered as linked windows). The requirement for Optional Fast Reserve is, and until recently the draft requirement for QR was, to be able to sustain delivery for 15 minutes. Meeting this latest and adjusted requirement would mean only offering a proportion of our total available capacity at any time, keeping assets in reserve to be available later in the period when the previously dispatched assets reach the limit of their physical capability. Furthermore, delivering even this diminished volume would require significant investment in scheduling and dispatch systems to cycle through available assets and coordinate between them, in a way that is not necessary for the existing Optional Fast Reserve service, and therefore not in place. At this point we would not be able to provide this service. | The ESO has communicated it's position on the Quick Reserve energy requirements since December 2023. We did previously require at least 1 activation at full contracted capacity per Settlement Period when the Service Window was 2 hours. Moving to a 30-minute Settlement Period granularity eased this requirement, with no complex performance monitoring/activation requirements therefore required. ESO are more than happy to discuss with SSEN other future balancing services which may be a better fit for CLASS services.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | The requirement for the Firm (day ahead) QR service is to submit day-ahead Availability Declarations for every half-hour period in the following day. This is obviously not applicable to the within-day Optional Fast Reserve service. | Availability Declarations for Phase 1 will be in accordance with the BM. We are planning to update industry on our proposal for Quick Reserve Phase 2 (and also Slow Reserve) in September 2024, but in line with our Response services we are planning on requiring additional data submissions from non-BM providers to aid visibility.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | For the Optional (within day) QR service, the requirement is for non-BM providers to submit Availability Declarations no later than 90 minutes ahead of the relevant delivery window, as opposed to 60 minutes ahead for BM providers of Optional QR and for Optional Fast Reserve. It’s not clear why this requirement has been made more onerous for non-BM providers than for BM providers of the same service in the within-day market. This seems unnecessarily discriminatory against non-BM providers for no apparent reason. | Thank you for pointing this out. This is a typo, and both the BM and non-BM declarations should be 60-minutes ahead of the relevant Settlement Period.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | As with the technical parameters, the cumulative effect of these changes is to diminish the volume of Optional Fast Reserve capacity that participants will be available to offer as QR, which would be worse for ESO and for market competition generally. | As we have previously stated, the Quick Reserve design has been driven by a system need, which is to have a fast-acting and responsive Reserve service. We have tried to balance the needs of the system with the capabilities of the market, and we believe that the current requirements best reflect this compromise. We are open to reviewing key parameters in the future as the Quick Reserve service develops and we have a better understanding of how it behaves when operational. We expect Optional Fast Reserve providers to either move into Quick Reserve, or other markets where they can be valued, such as Static FFR and Slow Reserve, and still deliver benefit to consumers.
Statera Energy | Using existing BM processes for defining Availability and Baselining is welcome. Statera agrees with ESO’s approach to dealing with unwanted behaviours associated with State of Energy Management and Bid/Offer prices, but would appreciate clarity and precision in defining ‘excessively high or excessively low’ prices. This would ensure that all participants are assessed on a fair and transparent basis. | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances.
Sembcorp Energy (UK) Limited | We would like to have further information on how crossovers will work in practice. | In practice, for Phase 1, crossovers will be managed as normal through the BM. So, control-room engineers will have forward visibility of a unit's availability and can then send instructions appropriately. For Phase 2, we will require that participating units must be able to continue delivering MWs for any subsequent Settlement Period following the end of a Quick Reserve contract. The maximum this could be is in line with the unit's defined Minimum Activation Period. These requirements will be clarified when we update industry on our proposal for Quick Reserve Phase 2 (and also Slow Reserve) in September 2024.
Drax Group | We are, however, concerned that the legal text of the service terms specifically refers to ‘excessive pricing’ without providing a reference or a clear definition of what constitutes ‘excessive’. There is no generally accepted definition of ‘excessive pricing’ in either the licencing regime (such as the Transmission Constraint Licence Condition) or network codes. Therefore, we are concerned that this reference to ‘excessive pricing’, without any substantive regulatory or legislative grounding, may add additional complications to the Ofgem approval process and may cause a delay in the implementation of Quick Reserve. | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances.
Drax Group | We also note that internal monitoring of instances of ‘excessive pricing’ will require substantial administrative and resource requirements from the relevant ESO teams and may create an unnecessary need for a dedicated investigation and dispute team. | Thank you for the feedback on this. We are happy that we have the necessary resources in place to monitor the requirements of section 5.11 of the Service Terms.
Drax Group | In order to avoid the risk of delays to the introduction of Quick reserve, we suggest the ESO expands on the legal standing and clear methodology applied to the identification of ‘excessive prices’ or defers the solution to technical requirements only, such as the new State of Charge rules and GC0166 (subject to approval). | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances.
Shell | Please provide details of how state of charge should be managed for linked-buy orders. | For linked buy-orders, the ESO require that a unit's state of charge is managed the same as for individual Service Windows. Linked Service Windows are treated as individual contracts, and all requirements apply for each individual window. A unit must therefore be able to deliver it's contracted volume for a full 30-minutes for each linked window. In the case of two linked Service Windows, a unit must therefore be able to deliver for 60 minutes, as an example.
Statkraft UK Ltd | Additional state of energy management guidance / rules for energy limited assets would be welcome to ensure NGESO is receiving the service it expects and fair competition between providers. For example, is the expectation to maintain energy sufficient for a 60 minute instruction in each direction? | Energy requirements state that a unit should be able to deliver it's full contracted capacity per Service Window/Settlement Period. This should apply to both positive and negative services.
Arenko Group | Regarding linked buy-orders, we would appreciate any further market information that could inform pricing strategies at the day ahead, and learning more about what indicators ESO will use to evaluate when crossover periods drop off will become significant to require this. | We would look to link buy-orders if points in time emerge where the set of units in merit for Quick Reserve consistently completely change from one period to the next. We do not currently have much insight into whether this will happen at all, but if it does, we'll be as transparent as possible about our understanding of the drivers and how we'll structure our buy-orders to mitigate it.
Tesla Motors Limited | **Energy Requirement** We agree with this proposal, but want to point out that this rule combined with Gate Closure will naturally incentivise bidders to bid in QR at high prices: 1. Due to Gate Closure, we have no control on the SOE in the hour before the contracted period start 2. Therefore, we'll have to reflect our availability / awarded volume in other markets (BR, DC/DM/DR, BM) in a way that under an extreme activation we can still enter the QR contracted period with an acceptable SOE We note that as a result of having to respect the Energy Requirement, QR providers may be driven to factor in the opportunity cost for missing opportunities in these other markets, which will have an upward effect on the price of QR bids. | We agree that the energy requirement as expressed may put some upwards pressure on the price of the service at times of scarcity. We expect this will be more than mitigated by the value derived from the increased reliability achieved by the energy requirement.
Tesla Motors Limited | **Cross overs** We agree with the proposal - we think this is a neat solution; we encourage the ESO to use linked buy orders only to cover the required volume at the boundary, and use regular orders for the remainder. We think this will produce a more efficient clearing outcome that should help keep the overall costs of the service down. | Thank you. We fully agree that linked buy-orders should be kept to a minimum and will be endeavouring to do so, depending of course on what market behaviour is observed in practice.
Centrica | With respect to Service Availability, in our view, the rules may be more restrictive than necessary and not favourable for batteries, as we get closer to the end of the service window. The current rules (even for BR), require service providers to make sure that they can support a full 30 min activation even at the end of their service window. So, they need to have a dropping profile of MEL/MIL, otherwise they end up keeping more energy buffer than required to deliver the service. | We understand that the service availability requirement may increase operational complexity for some providers, however we are confident that the required level of reliability is appropriate for a premium energy security service. It appears that this feedback covers the interaction with the "30-minute" rule in general BM operation. If so, then we expect this interaction to be improved by the new storage parameters available through Grid Code modification GC0166.

## Q6 QR Delivery Assess
Company Name | Please provide any specific comments relating to the proposed Quick Reserve Delivery Assessment including Settlement, ABSVD, and Performance Monitoring. | ESO Response
Peak Gen Top Co Limited | Para 9.2 of the contract is unclear regarding ABSVD. It would be clearer if it stated that there will be no ABSVD adjustments when the service is delivered via BOAs in the BM | This is intentionally left high-level as the definitive approach is specified in the ABSVD methodology.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | Firm QR participants will be subject to performance monitoring, with penalties applied for non-delivery and for availability deviating from their day-ahead offer. The current proposal only includes details of how this monitoring would be implemented for BM Units, so as a non-BM provider it is unclear whether we would be able to meet the monitoring requirement. | We are planning to update industry on our proposal for Quick Reserve Phase 2 (and also Slow Reserve) in September 2024 and we will be very happy to engage with any provider to discuss any specific requirements. The same requirements, where appropriate, will be applicable to all units (including BM).
SSEN Distribution, trading name of Southern Electric Power Distribution plc | Thus, assuming it is technically possible, this requirement would necessitate offering a capacity that is lower than our forecast volumes to avoid penalties for actual availability turning out lower than forecast. | Correct. We have allowed a sufficient over-delivery window to incentivise over-delivery rather than under-delivery, as this is much easier to manage in the control room, but this tolerance can be used for availability uncertainty management.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | These performance monitoring requirements will diminish the volume of Optional Fast Reserve capacity that participants will be available to offer QR, which would have a negative outcome for ESO and for market competition generally. | We believe that the available Quick Reserve market will be large enough to meet 100% of the required volumes. We are still keen to work with SSEN and CLASS assets as a whole to ensure that their capacity is still made available to us through other services.
Statera Energy | The hard cliff-edge whereby availability payments are foregone if a provider fails to deliver 95% of the instructed volume of energy is excessively punitive in Statera’s view. A more merciful approach, such as a sliding-scale penalty below 95% down to some value (for example 80%), would be less harmful for assets which have the occasional trip or fault during a Settlement Period while still achieving the same result for assets which are outright unavailable from the start of a Settlement Period. (Note: Statera holds the same view for Balancing Reserve, which is a similar service to the proposed Quick Reserve). Statera agrees with the principle of penalising over-delivery of energy. No comments on ABSVD as this makes use of an existing methodology. | The availability payment tolerances are designed to be less onerous for over-delivery, rather than under-delivery, as this is much easier for control-room engineers to manage in real-time if and when they occur. Control-room engineers will need to be able to rely on the Quick Reserve service. If we were to extend the delivery tolerances too far, then there is a great deal of uncertainty in the outputs of each unit, which may then cause distrust of the service and additional MWs to be procured, further increasing the cost of the service (a direct contradiction of the purpose of the service). Particularly with Quick Reserve we anticipate the service being used when the frequency has already deviated, and so under delivery increases the risk of exceeding our frequency standards. A 'more merciful' sliding scale would also require the need to develop new tools within our settlements systems/processes which would not be feasible for Phase 1.
Zenobe Energy | ABSVD Zenobe agree with the principle that energy volumes dispatched to meet a QR contract should lead to adjustments in the imbalance position of the relevant party, such that all providers can be compared on utilisation price alone when dispatch decisions are made. We note that for Primary BMUs, dispatch will be via the BM, included in QBS via QAO/QAB and therefore no further adjustment via QAS is necessary. Similarly, we note that for secondary (VLP) BMUs, dispatch via the BM will lead to adjustments in energy position via P-flows, therefore no further adjustment to QAS is necessary. For Phase 2 non-BM QR dispatch, ABSVD should be calculated and included for those units. | Thank you, we agree with these statements.
Zenobe Energy | Interactions with Spin-Gen/Pump Spin-Gen/Pump contracts are used by the ESO to make pump storage units available for dispatch from zero MW with shorter notice/commitment times than would otherwise be possible. These units then receive an availability payment for providing the additional flexibility. Zenobe believe that Spin-Gen/Pump should not be commercially “stackable” with QR. Where a unit has a PQR/NQR contract and an overlapping Spin-Gen/Pump instruction, we believe no Spin Gen/Pump availability payment should be made. Failure to preclude overlapping Spin Gen/Pump payments is, in effect, a technology specific subsidy in order to provide the same flexibility as the QR contract, and hence would distort QR prices and inhibit fair competition in QR. Zenobe recognise that Spin Gen/Pump can be instructed within-day and hence provides flexibility beyond the DAH procurement of QR. We believe that while in the short term there is a case for the continuation of Spin Gen/Pump payments (when not contracted for QR), ESO should move to introduce within-day QR procurement with a view to retiring the Spin Gen/Pump service in the medium term. | We are reviewing the status of Spin Gen/Pump post Quick Reserve, but do not currently believe there is a case for retiring them in the medium term. If we’ve sent a Spin Gen instruction in a Settlement Period immediately preceding the Quick Reserve contracted window, then the applicable bilateral agreement rules around payment would apply and we would either send a shutdown instruction before the Quick Reserve contract starts or deal with it through settlement (when not to pay them). During any Quick Reserve contract window, if a unit stays in Spin Gen (if appropriate for the Quick Reserve contract they have) we would not be paying them for the Spin Gen availability.
Zenobe Energy | Rule 5.11 Zenobe recognise that the BR service design has driven a need to enhance consideration of how energy limited assets are incentivised to bid in reserve services. In our response to the recent BR consultation we stated that the current incentives to place a high utilisation price in BR in order to discourage dispatch could be resolved by applying the penalty rate (based on highest BM offer acceptance) for non-delivery of the BR contract due to low state of energy following a BM dispatch. By applying this higher penalty rate, the risk of not providing the contract rises significantly since: a) The highest offer acceptance (exposure) is not readily forecastable at the time of bid submission. b) As dispatch of MW procured through the reserve service increases, the “strategy” of placing a high offer acceptance to discourage use and hence application of the penalty in the subsequent period becomes unstable since high offer price dispatch becomes more likely. We believe the application of the higher penalty rate in a period of non-delivery following a BM dispatch is sufficient to discourage energy-limited participants from offering volumes they are not certain they can deliver. Further, we can imagine simple penalty mechanisms where by non-delivery penalties in one settlement period is linked to the utilisation price in the preceding period(s) such that it is always the case that a provider who submits a high utilisation price to discourage use, net loses after penalties if volumes are offered which cannot be delivered. We note that Rules 14.1.3, through 14.3 in the QR service terms apply the Incremental Offer Volume Cost to non delivery as a result of delivery of the QR contract as a consequence of delivery of energy in a preceding period, analogous to our BR proposal. We do not believe rule 5.11 is necessary in light of rules 14.1.3 – 14.3 and further that rule 5.11 in effect is a proposal for an arbitrary price cap on QR utilisation price. Rule 5.11 makes no provision for any process for determining what utilisation price the ESO might consider “excessive” and is open to discretionary and prejudicial | We have looked at a range of ways to monitor and address state of energy, giving consideration to the penalty based structure proposed for the Dynamic Response services, and feedback from Balancing Reserve. As Quick Reserve is a new service we believe the current proposed penalties associated with 'excessive' prices are sufficient and justified given the evidence obtained from the Balancing Reserve market. However, we will monitor and review this decision and engage with industry for feedback through Phase 1, just as we have done with Balancing Reserve. We will also continue to monitor the penalties outlined in the Dynamic Response services and share any proposed design changes with industry as appropriate. The value of a firm service lies in its reliability to be available in real-time, and so it is important to prevent behaviour that jeopardises this, otherwise the service may not deliver value.
Arenko Group | We would appreciate clarity on what further information is needed by ESO before deciding performance monitoring capability for Phase 2. We would prefer a delay and ironed out rules than non-delay and 'gaming' from day 1, as it reinforces a set of misaligned market incentives, compounding a structural lack of trusted governance and fundamentally undermines system security. | We are planning to update industry on our proposal for Quick Reserve Phase 2 (and Slow Reserve) in September 2024 and we will have clearly defined performance monitoring rules in place for service go live.
Flexitricity Limited | We support the proposal for availability payments to be made based on pay-as-clear, and utilisation payments to be based on Bid-Offer Data provided in the Balancing Mechanism and paid for energy delivered volumes. We noted from the webinar on the 8th July that there will be additional terms applied for uneconomic pricing. We would hope that this is clear in the terms as failure could lead to ambiguity among providers. The ESO should provide some further guidance on this and advise providers whether any further information should be provided to the ESO to justify pricing parameters. No comments on ABSVD, but this should be applied to all assets (BM and non-BM) once we approach phase 2 implementation. | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances. While we do expect to apply ABSVD to both BMUs and non-BMU's in phase 2, non-BMU's will have the entire volume offset, and BMU's a smaller volume to mitigate ramping imbalance. We believe this is the best way to create a level playing field, as BMU's already incur QAS as part of a BOA instruction, which is what ABSVD simulates for non-BMU's.
Centrica | Overall, we are fine with the proposals. In relation to ABSVD, in our view, it is important to ensure a level playing field among battery storage providers. This means applying ABSVD not only to BMUs, but also to non-BMUs. Alternatively, removing ABSVD for BMUs and not applying it to non-BMUs could also be a solution, as currently, the time it takes to receive accurate imbalance volumes with ABSVD applied (up to 5 months) significantly reduces the potential benefits. In the context of the Quick Reserve Phase 1, this is not an issue, but it will become of relevance when we enter Phase 2, which will include non-BMUs. | In phase 2, we expect that ABSVD will be applied to non-BMU's, and to BMU's only to mitigate ramping imbalance. We believe this is the best way to create a level playing field, as BMU's already incur QAS as part of a BOA instruction, which is what ABSVD simulates for non-BMU's.
Statkraft UK Ltd | Answered in question 4 – further information on Performance Monitoring requirements for BM QR in Phase II and non-BM QR to be shared in advance to allow for implementation. Where dispatch is through the BM no separate ABSVD adjustment is required, since BM volumes will adjust the lead party’s traded position. For non-BM QR ABSVD should be implemented in order to ensure a level playing field between BM and non-BM QR participants. | We are planning to update industry on our proposal for Quick Reserve Phase 2 (and also Slow Reserve) in September 2024 and this will include details of ABSVD for 'non-BM' parties.

## Q7 Approach
Company Name | Please provide any specific comments relating to the proposed Procurement Approach including Maximum Bid Size, Service Windows and Locationality. | ESO Response
NGED | Different terminology has been used in this document to that from the Stacking Technical Working Group – ‘Stacking’ is akin to the TWG’s ‘Co-Delivery’. It would be useful to align on terminology moving forward to avoid any potential confusion. | Thank you for pointing this out. We are aware of a difference in the terminology used around stacking in our published documentation. We are working on a coherent strategy internally and once finalised we will communicate this with industry as appropriate.
Peak Gen Top Co Limited | We are generally supportive of the proposal. We note that when NGESO expects to procure around 300 MW of service, allowing units up to 300 MW to participate risks an outcome where a single failure will result in the loss of all service. A smaller size may be more appropriate It is important to be explicit how a unit is sized. A 50 MW storage unit is able to deliver 100 MW of service by moving from 50 MW of input to 50 MW of export. | We have tried to ensure that as many technology types as possible can participate in the Quick Reserve service without adding any undue risk to the value or security of the service. Opening up the maximum bid size to 300MW allows for maximum participation and competition in the market, particularly if there are occasions that we have a higher requirement, therefore lowering overall costs. We believe the potential benefits of opening up the service in this way outweigh the small risk of losing a single unit if contracted for the full 300MW. The limitation is on the bid size, not the asset size.
Flexitricity Limited | Service Windows: We welcome the 30-minute service windows and would encourage ESO to consider this service window sizing for all reserve and response products. This will support stacking/splitting in later phases of the Reserve reform and Response Reform releases. Furthermore, it will help with the economics if all services align with a 30-minute service window. Currently, bidders into QR at 30-minute service windows that are also bidding into Dx services for EFA block service windows, will need to account for the opportunity cost in QR to account for the risk of only being awarded a single service window, and being unable to provide Dx for the rest of the EFA. This could have the effect of increasing the QR pricing and therefore will not offer the lowest cost to consumers. This also creates an unnecessary barrier to stacking, which was identified as a priority in the draft Flexibility Market Strategy. We would like to see ESO make progress in the coming months to improving stacking opportunities for providers. | Thank you for the feedback. We shall be considering shorter windows in Response but this is still under review. Slow Reserve will have a 2-hour commitment as it's primary function is to restore imbalances post-fault and return frequency back to operational limits whilst other actions are taken to replace it, therefore requiring a sustained delivery period. However, these commitment periods will be based on 30-minute settlement period blocks, thus giving providers more flexibility in when they can offer their Slow Reserve MWs. The ability to co-optimise multiple options from providers in our auction platform also limits the cost exposure, as the capacity from different providers at different times can be used to fill the requirement effectively.
Flexitricity Limited | Maximum Bid Size: 300MW for Phase 1 is a large percentage of the anticipated market size (at the Balancing Programme Event in June, it was suggested the full market size for Phase 1 will be ~500MW PQR and ~300MW NQR). This could result in a saturated market early in its implementation. Could the ESO provide some rationale to how this maximum bid size was decided? | We have tried to ensure that as many technology types as possible can participate in the Quick Reserve service without adding any undue risk to the value or security of the service. Opening up the max bid size to 300MW allows for maximum participation and competition in the market, therefore lowering overall costs. We believe the potential benefits of opening up the service in this way outweigh the small risk of losing a single unit if contracted for the full 300MW. The maximum was set based on the largest instantaneous ramp that we would be comfortable operationally instructing. We believe instructing a unit larger than 300MW with the speed of Quick Reserve would add too much operational risk.
Drax Group | The proposed procurement approach is largely consistent with the Balancing Reserve service and procurement terms. Locationality - We note that while the proposed approach for Phase 1 and Phase 2 is based on national procurement, the ESO has explored the option of locational procurement which proved to be complex and not achievable within the accelerated delivery time. However, it is not clear from the consultation whether the ESO will continue the analysis and may in the future introduce locational procurement. We would welcome some indication on the next steps and future studies on the option of locational procurement. | Work has started that looks at developing a locational procurement methodology. As this work applies across many Ancillary Services, involving various stakeholders, it is outside the scope of Quick or Slow Reserve. We have no official timelines for the completion of this work as of yet, but any developments will be communicated with industry appropriately.
Drax Group | Service windows - With regards to NBM providers and specific telephony requirements, it is not clear whether NBM units can bid into any available windows or are limited to only participate in windows where they have Control telephony available as was previously discussed in the Balancing Reserve service terms | As with BM participants, non-BM units will only be able to bid in for Settlement Periods/Service Windows where they have System/Control Telephony available. The requirement is there to give the ESO control-room access to units in case of any system interruptions. This requirement can be filled simply by having a mobile phone available to call and does not require any expensive installation of dedicated phone lines.
Zenobe Energy | Zenobe note that 30 minute QR service windows and inability to split with D* in the first instance means that providers of D* services will need to forgo a full block D* revenue to provide QR in a short window. While we agree that the 30 minute QR window is appropriate for the QR service, we believe ESO should set a pathway to aligning reserve and response service windows such that best use can be made of the flexibility afforded by response and reserve providers | Thank you for the feedback. We are aiming to improve stacking opportunities for Phase 2. We are looking at whether we can move the Response services to a shorter window length and will update industry where appropriate.
Centrica | In relation to maximum bid size, we would recommend having a limit on maximum non-divisible size per asset. The current system, along with increasing the maximum sell size, creates risks of exploitation of the system by bigger participates. They can make sure that their products add up to the exact requirement for grid and push out other participants. For context, DM is 170MW in low and 200 in high, if one participant decides to submit 2 bids of 100MW each, both non-divisible, they can push everyone out. We have already seen this happen in DRH. | Thank you for your feedback. The EAC auction allows overholding which enables the auction to clear more than ESO's firm requirement. The algorithm selects the sell-orders and buy-orders that optimise the market welfare and treats different order sizes equally. We are keen to ensure the auction design is technology agnostic and provides a level-playing field for all participants. We will assess the value of introducing a limit on maximum non-divisible size per asset.
Statkraft UK Ltd | When can we expect the minimum volume management for QR to be set dynamically (similarly to QR)? How much volume will be procured via OFR ? The maximum bid volume is limited to 300 MW which is good. | The current minimum requirement for Quick Reserve is 500MW for positive and 300MW negative. This may change as the Quick Reserve service matures through Phase 1. We don't currently procure any Optional Fast Reserve volume, as it is purely optional. We are keen to keep the Optional Fast Reserve market open during Phase 1 to allow non-BM providers to compete with the Quick Reserve service, ultimately helping to drive competition, and also allowing non-BM providers to still participate in a fast-acting reserve service until the roll-out of Phase 2 Quick Reserve.
Shell | We are supportive of the maximum bid size, 30-minute service window and excluding a locational dynamic. If the later is considered in the future, then we request a consultation and feasibility study is conducted. | Thank you for your feedback. Locational procurement is high on our agenda and we hope to announce a consultation on this topic in the near future.

## Q8 Proposed Auction Process
Company Name | Please provide any specific comments relating to the proposed Auction Process including Timings, Bid submissions, and Auction Results. | ESO Response
Statera Energy | What is the reasoning behind proposing to move the auction to D-1 at 09:00 in Phase II? Would all Ancillary Services move towards D-1 09:00 auction (including DFR) in order to allow for co-optimisation of response and reserve auctions? Further clarity on defining the scope and methodology of Linked Buy-Orders would be appreciated, given it is a new mechanism that can impact volumes and prices being bid into the market. | The reasoning for this proposal is to align all the Reserve products, which has the potential to reduce costs via competition and co-optimisation. We are still reviewing this requirement and will communicate with industry as appropriate. Response will remain in the afternoon at 14:00. The logic behind linked buy-orders is to secure common units across certain crossover boundaries. For example, ESO may see consistent challenges around the EFA 2 - EFA 3 boundary, requiring lots of actions to be taken in order to secure this crossover. ESO could issue a consistent linked buy-order for this time period for every day, with the requirement issued ahead of auction opening (D-14). Any providers then bidding into these two Settlement Periods would have to link both SP 16 - 17 (06:30-07:00 and 07:00-07:30). The ESO control-room can then use these units across this boundary to better manage any frequency deviations with consistent units.
Drax Group | We do not have any immediate concerns with the specific service terms in relation to auctions. However, it would be useful to see some clearer explanation of the Splitting/ Stacking principles, such as why splitting is not allowed between Quick reserve and Dynamic services in Phase 1 and similar decisions. It would also be useful to have a practical walkthrough of what a co-optimised procurement with Dynamic Response may look like and what are the commercial implications on the participation pool and/or system needs. | Splitting is not allowed with Dynamic services in Phase 1 as our internal IT solution isn't able to performance monitor both Quick Reserve and the Response services to a great enough accuracy. Once 1-second performance monitoring is available during Phase 2, then we will allow participants to stack Quick Reserve (or Slow Reserve) with our Response services. We will update the Market Design Explainer Document (https://www.nationalgrideso.com/document/277671/download) with co-optimisation examples soon.
Centrica | We are fine with the proposals. However, and this goes back to our initial question about the distinction between the Balancing Reserve and Quick Reserve services, it seems to us that the auction could take place earlier. We would like to understand the requirement to procure this service together with the DC/DM/DR auction and if it would have an impact on the clearing of those products. | We believe that co-optimising Quick Reserve with Response in the afternoon should provide greater competition and more efficient clearing for both services as we would expect similar asset types to be participating in both. We will also be considering the Balancing Reserve auction timing based on recent feedback.
Statkraft UK Ltd | What is the reasoning behind proposing to move the auction to D-1 at 09:00 in Phase II? Would all Ancillary Services move towards D-1 09:00 auction (including DFR) in order to allow for co-optimisation of response and reserve auctions? | The ESO have proposed moving Quick Reserve to the morning auction such that there is a combined Balancing Reserve, Quick Reserve and Slow Reserve auction. Therefore, effectively a co-optimised Reserve auction. We are still investigating the pro's and con's of this approach and will communicate any decisions with industry where appropriate. We will also be considering the Balancing Reserve auction time based on recent feedback.
Statkraft UK Ltd | When will co-optimisation of response and reserve auctions become available? Are there plans for allowing stacking of QR with other response/reserve services (such as DFR)? | We will be co-optimising Response with Quick Reserve in Phase 1. Once 1-second performance monitoring is available in Phase 2, we are planning on allowing stacking of Quick Reserve and Slow Reserve with the Response market.
Statkraft UK Ltd | When and how will the ‘’linked buy-orders’’ be communicated? How are key crossover periods decided? Is it dynamic? It would be preferable to not be stuck with the MW consistency across periods. | The linked buy-orders are currently envisaged to be communicated with industry ahead of gate opening. Key crossover periods will be decided by internal teams, but initially from control-room engineers. These linked buy-orders only signify that a unit is available for 2 (or more) consecutive Service Windows/Settlement Periods, such that control-room engineers have access to a consistent number of units across a particular EFA/Settlement Period boundary. Procured MWs will typically be a static value across both windows.
Flexitricity Limited | Flexitricity is in support of a co-optimised auction at 2pm alongside the Response (Dx) services. We would encourage early engagement with industry before Phase 2 of the QR service design is finalised as we understand there is a proposal to move QR auctions to the morning for a single co-optimised Reserve Auction, alongside BR and SR (in 2025). | Thank you for the feedback. The timing of the Phase 2 Quick Reserve (and Slow Reserve) auctions are still under review. Any updates will be clearly communicated with industry as appropriate.
Sembcorp Energy (UK) Limited | We are of the view that the auction should take place at 14:00 in conjunction with the Frequency Response services auction in order to allow as much market information as possible to be taken into consideration in bidding. This will enable the procurement to be as cost-effective as possible. | Thank you for the feedback. We will take this into consideration when deciding on the auction timing.
Shell | We are supportive of the timing of the auction and believe that it is practical and will lead to the optimum result by co-optimising Fast Reserve with the Response auctions at 14:00. As the auction is held after the day ahead power auctions there is less uncertainty which needs to be factored into the submissions. We note that the guidance document says that the ESO may consider holding the Quick Reserve auction at the same time as the Balancing Reserve auction which we do not support. There would need to be significant opportunity cost priced into the Quick Reserve if it were to move to the same time as the Balancing Reserve which is unlikely to lead to the best price for consumers. | Thank you for the positive feedback. Moving the Quick Reserve auction to the morning is a possibility, however we would need to see significant benefit to doing so. This is still under review, and we will of course update industry on any developments appropriately. We are also considering the timing of the Balancing Reserve auction based on recent feedback.
Arenko Group | Regarding auction timings, our core preference is that Reserve and Response services all clear at same time and co-optimised, subsequent to EPEX DA wholesale market (3:30 pm) clearing. This would enable better price discovery as we can more optimally price the counterfactual use of our flexibility. | Thank you for the positive feedback. We are still reviewing the timing of the Reserve auctions and will communicate our decision to industry appropriately ahead of Phase 2.

## Q9 QR Market Design
Column1 | Column2 | Column3
Company Name | Please provide any specific comments relating to the proposed Quick Reserve Market Design including Sell order structure (e.g. baskets, parent orders, child orders), overholding, and clearing algorithm. | ESO Response
Sembcorp Energy (UK) Limited | We would like orders to be of similar structure to those for the Dynamic suite of products including Linked Orders, to facilitate consistent submission. | Thank you for the feedback. We aim to have a consistent auction design for Response, Quick Reserve and Balancing Reserve. The Quick Reserve auction design (e.g., buy-order structure, sell order structure) will be of similar structure to those for Dynamic Containment, Dynamic Moderation, and Dynamic Regulation.
Drax Group | We don’t have any views or concerns with the Market design proposals. We welcome the ability to secondary trade between the pre-qualified units of the same parent company. | Thank you for your comments
Statkraft UK Ltd | Having non-curtailable Child Orders would be a useful option for providers. Additional bidding baskets will be useful when the market moves towards a combined procurement of Frequency Response and Quick Reserve. NGESO should allow for Overholding in all Frequency Response and Reserve products where doing so results in a lower overall cost to consumers. | Thank you for the feedback. We will assess the value of introducing non-curtailability to non-parent orders. We are planning to set the maximum number of baskets to 100 (per unit per auction) for units which are only qualified for Quick Reserce, and to 125 for units which are qualified for both Quick Reserve and Response. We allow overholding in Response and Balancing Reserve auctions. Overholding will also be allowed in Quick Reserve to achieve a more efficient market clearing and also to maintain consistency in our procurement strategies. The overholding volume will be reflected in post auction buy-order result files.
ADE | There will need to be consideration into the length of Linked Buy-Orders when these are implemented and how realistic this would be for assets to dispatch for the entire linked QR window. | Thank you for the feedback. We will of course aim to minimise the disruption to industry by keeping linked buy-orders to a minimum and by giving the market adequate notice, aiming to notify participants by at latest auction opening, except for any potential exceptional circumstances. The need for linked buy-orders will be assessed during Phase 1 of the Quick Reserve service.

## Q10 Overall Strategy
Company Name | Please share your feedback on ESO’s overall strategy to move to a single, simultaneous, co-optimised auction for the procurement of Frequency Response and Quick Reserve. | ESO Response
Drax Group | We understand the rationale and benefits of moving to a co-optimised procurement with Response services. We would welcome an example walkthrough of how this would work in practice and what it means for Quick Reserve volumes and participation. | Thank you for the response. We will update the Market Design Explainer document (https://www.nationalgrideso.com/document/277671/download) with co-optimisation examples soon.
Statkraft UK Ltd | Would it be possible for National Grid to share timelines and details of the co-optimised auction? How will the co-optimisation algorithm decide on accepted baskets? | For the co-optimised Quick Reserve and Response auction, gate opening is 8:00 D-15, gate closure is 14:00 D-1, and the publication of auction results on the auction platform is 14:30 D-1 (note: D is the delivery date). The clearing algorithm is explained in detail in Appendix A of the EAC Market Design Report (https://www.nationalgrideso.com/document/282401/download) published by N-SIDE. The clearing algorithm seeks to find the optimal acceptance of buy-orders and sell-orders that maximise total market welfare within a time limit. The welfare maximisation problem is a Mixed Integer Linear Program (MILP) and is solved by the branch and bound (B&B) method. Note: "Market Welfare" is a defined term in the Glossary of the Procurement Rules. An explanation of market welfare is provided in Chapter 3 (Objective Function) of the EAC Market Design Report published by N-SIDE. Definitions and examples of market welfare can be found in the 'Market Fundamentals' section of the Market Design Explainer document (https://www.nationalgrideso.com/document/277671/download) published by ESO.
Arenko Group | We are supportive of the move to single, simultaneous, co-optimised auction for procurement. However we note the preference for Phase 2 to explore moving QR clearing time to the Balancing Reserve 08:30 am time, instead of in the afternoon after the EPEX DA wholesale market clearing. We note that the ESO proposed timing is intentionally before the I/C markets, guaranteeing national reserve for ENCC, however at the expense of better cost-reflective pricing by other market participants. | Thanks for the response. We will consider this in our decision making process for Phase 2 timings.
Arenko Group | As raised in ESO's consultation webinar, we do not fully understand the rationale as to why participants can’t stack two-sided with D* especially as you can do this in BR. As a result we would need a significantly higher price going into QR. We are supportive of exploring stacking as part of Phase 2 should involve stacking as per webinar. | Stacking with other Ancillary Services won’t be allowed during Phase 1 due to a limited capability in Performance Monitoring granularity. We do plan on allowing stacking with the Dynamic Response services in Phase 2 once 1-second Performance Monitoring capability is available. With Balancing Reserve, because it was a slower service, it wasn’t co-optimised directly with Response and, given the fact we were able to implement some changes to performance assessment, we decided the risk of enabling stacking in the opposite direction was justified. With Quick Reserve being faster delivery and co-optimised directly with Response, then the Performance Monitoring becomes somewhat more onerous so we are working hard to enable this for Phase 2.
ADE | We consider having a co-optimised auction as vital for the implementation of QR, so are in support of having the auction at 2pm, at the same time as the Dynamic Response Services. We are however concerned with proposals to move the QR auction timing to the morning during phase 2, alongside Balancing Reserve. Not only does this make less sense for flexible assets able to participate (explicitly batteries as above) but could have a large effect on overall balancing costs. | Thank you for the response. We will consider this in our decision making process for Phase 2 timings.
Tesla Motors Limited | We agree with the proposal. We note clearing for one settlement period in QR, means providers would miss out on four hours (a whole EFA block) of DC/DM/DR. As mentioned above, this creates a large opportunity cost for bidding for one settlement period in QR - similar to what currently happens in BR. Per our previous feedback to NGESO, we think this problem of having high opportunity costs being factor into QR bids could be mitigated by shifting DC/DM/DR to per settlement period procurement (rather than the current arrangement for per EFA block procurement). | Thanks for the feedback. This is something NGESO are currently looking at internally and we will take this feedback into consideration. Any decisions made will be communicated with industry where appropriate.
Statera Energy | Statera welcomes ESO’s overall strategy in this regard, and encourages ESO to publish further details regarding timelines and mechanisms by which the co-optimised auction will operate. | For the co-optimised Quick Reserve and Response auction, gate opening is 8:00 D-15, gate closure is 14:00 D-1, and the publication of auction results on the auction platform is 14:30 D-1 (note: D is the delivery date). The clearing algorithm is explained in detail in Appendix A of the EAC Market Design Report (https://www.nationalgrideso.com/document/282401/download) published by N-SIDE. The clearing algorithm seeks to find the optimal acceptance of buy-orders and sell-orders that maximise total market welfare within a time limit. The welfare maximisation problem is a Mixed Integer Linear Program (MILP) and is solved by the branch and bound (B&B) method. Note: "Market Welfare" is a defined term in the Glossary of the Procurement Rules. An explanation of market welfare is provided in Chapter 3 (Objective Function) of the EAC Market Design Report published by N-SIDE. Definitions and examples of market welfare can be found in the 'Market Fundamentals' section of the Market Design Explainer document (https://www.nationalgrideso.com/document/277671/download) published by ESO.
Flexitricity Limited | Feedback has been provided in Q8 on this point. However, we would like to reiterate and argue that all products should be run as a single co-optimised auction. This would include all products, across both Response and Reserve. The consultation outlines that Phase 2 approach is to split this into a Reserve (am) and Response (pm) auction, which we do not believe to be an optimised approach to ensuring all products are procured at the lowest possible cost to the end consumer. We would encourage ESO to consider this in phase 2 and provide industry with early engagement. | Thank you for the feedback. We are looking at the timing of the auctions internally and will communicate any decisions with industry appropriately. We are keen to make sure the timings of these service auctions are best for both market participants and also for the end consumer, where we should be seeking to bring the lowest total cost for procuring these services.
Sembcorp Energy (UK) Limited | We agree with the decision to have Quick Reserve procurement co-optimised with that of Frequency Response services. In that context, it seems strange to propose consideration in Phase 2 of moving the auction to the morning in line with the Balancing Reserve auction. We are of the view that the auction should remain later in the day in order to allow as much market information as possible to be taken into consideration in bidding. This will enable the procurement to be as cost-effective as possible. | Thank you for the feedback. The plan for Phase 2 is still under discussion, and we will communicate any decisions on auction timing where arppropriate.

## Q11 Additional feedback
Company Name | Please share any additional feedback on ESO’s proposed delivery of Quick Reserve that may fall outside of the questions above. | ESO Response
NGED | To facilitate the implementation of Primacy Rules a certain amount of data pertaining to the providers/assets involved in flexibility services needs to be exchanged with DNOs. For certain services in the past such data has not been collected/stored appropriately which has created blockers for the Primacy TWG. It would be useful to understand what data is being collected by the ESO in order for providers to access QR. | During Phase 1, we expect to have the unit data relevant to BM units. We would value specific requests for data (whether for Primacy or otherwise) from DNOs to input into our engagement into the Phase 2 work, which will be in September. This will allow us to ensure that we have any relevant data items captured in the terms for the Phase 2 consultation.
Peak Gen Top Co Limited | We are concerned by the potential penalty for non delivery of the service. See para 14.3 and the definition of "Incremental Volume Cost Amount" We do not see how the cost of the most expensive offer accepted relates to the cost of replacing quick reserve (for example we would expect the value of a bid to be subtracted along with the avoided payment to the failed provider). A more justifiable method for calculating the cost of the replacement service would be to rerun the auction, without the failed unit and charge the failed provider the different between the new and the old clearing price. | The rationale for using the highest offer price is that by the time the non-delivery is observed, it is too late to replace the unit at auction, and instead the energy which would have been delivered by the unit must be procured from a different unit. By definition, the most expensive MW procured at that point in time is the MW which could have been avoided had the unit delivered correctly. We note that this penalty applies for where the provider has pursued other commercial opportunities (and so is avoidable). The IVC (Incremental Volume Cost) does subtract the availability payment as part of the calculation.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | We are alarmed by the ESO’s stated intention to procure 100% of its expected need from the day-ahead Firm Quick Reserve Market as soon as it is launched in November 2024, as it undermines not just the existing Optional Fast Reserve market (as outlined in our response to Question 1) but also the forthcoming Optional Quick Reserve market before it has even opened. | To clarify our procurement strategy, while we will submit a buy-order for 100% of our Quick Reserve requirement, the pricing of the buy-order will be driven by the range of available alternatives. If Optional Fast Reserve is priced competitively to Quick Reserve, this will lead to some or all of the buy-order not being filled, as Optional Fast Reserve can meet the need. This also means that there's no benefit to artificially limiting the volume of our buy-order, as the market will in practice determine where the limit should be. To be clear, we will not buy 100% of our volume at any cost through Quick Reserve. We will only procure it if we can fill the need more economically compared with other options.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | It is a dramatic change from ESO’s stated aim to encourage competition between the day-ahead and within-day markets and consider offers from both markets on their own merits, to ESO explicitly stating it plans and expects to fulfil 100% of its needs from the day-ahead market alone, and to use the within-day market only in emergencies. The latter is a clear statement of intent which serves only to undermine the liquidity and therefore the viability of the within-day markets. This is also contrary to the work and position that Ofgem has historically supported. | The transition period will allow Optional Fast Reserve units to participate in competition with the firm Quick Reserve market. Volume is only secured by the way of day-ahead contracts, and therefore the Optional Fast Reserve market is able to compete and, if cheaper than Quick Reserve, will be utilised - it is not only limited to emergency actions. To clarify our procurement strategy, while we will submit a buy-order for 100% of our Quick Reserve requirement, the pricing of the buy-order will be driven by the range of available alternatives. If Optional Fast Reserve is priced competitively to Quick Reserve, this will lead to some or all of the buy-order not being filled, as Optional Fast Reserve can meet the need. This also means that there's no benefit to artificially limiting the volume of our buy-order, as the market will in practice determine where the limit should be. To be clear, we will not buy 100% of our volume at any cost through Quick Reserve. We will only procure it if we can fill the need more economically compared with other options.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | The expectation of near-zero market volume makes entry into the OQR market difficult to justify commercially for potential participants. SSEN anticipates it will also have a perverse impact on the prices offered by those who do participate which is quite different from that anticipated by the ESO. Under the stated procurement strategy, within-day participants will know that the ESO will only ever approach them as a distressed buyer and participants are likely to set their prices accordingly. Consequently, OQR prices may turn out to be significantly higher than today’s OFR prices, where participants compete for “normal” daily volume. This is not in the best interests of GB energy customers. | Optional services are not there for emergencies only. As stated above, optional units have the same opportunities to bid in their capacity competitively as firm units, and will be utilised appropriately through merit order. If we are able to procure firm Quick Reserve at day-ahead, then this will increase the volume available to compete with Optional Quick Reserve (or Optional Fast Reserve in Phase 1) on utilisation price for any given time, therefore logically this should lead to increased competition, rather than reduced competition in real-time.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | To make the OQR market liquid and viable, and to keep within-day prices low for both normal and emergency use, it would be better to always procure a proportion of the expected volume through that route, incentivising within-day sellers to remain competitive. We strongly encourage ESO to reconsider its commercial strategy in this regard. | The ESO plan to procure 100% of the Quick Reserve requirement at day ahead. This only ensures that this capacity is then available during those contracted hours. If Optional Fast Reserve units are competitive during that time, then there is no preference from the ESO on which units are chosen (if requirements are similar). If these Optional Fast Reserve units are priced competitively, then they will be instructed in merit order. When setting our requirements, we do not set them so high as to avoid the need for Optional Fast Reserve under any circumstances, as buying that quantity firm would lead to excess procurement at most times. We aim to procure our minimum requirement at all times (if economic), and can procure more than that firm if we have specific knowledge of system risk, or we believe that it would be economic to do so.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | As a non-BM provider, we are also struck by several aspects of the proposal, including the exclusion of non-BM providers from the QR market during Phase 1, the acceptance of 70% of non-BM capacity being excluded indefinitely, and the seemingly arbitrary requirement for non-BMs to submit within-day offers 30 minutes ahead of BMs. ESO’s suggestion that non-BMs can simply join the BM is unfeasible for some providers, including those offering services using CLASS who have been encouraged to add liquidity to the market by both the ESO and Ofgem. The cumulative impression given is that Quick Reserve has been designed around and for BM participants, and non-BMs are at best an afterthought whose services are not needed, and at worst unwanted. This seems unnecessarily discriminatory, and as an organisation currently trying to build a business case to justify joining the market and investment in the infrastructure required, entirely counterproductive. | Thank you for you feedback. We consider our overall approach to be compliant with our legal and regulatory obligations, and in particular to be non-discriminatory, and in this respect we have sought to ensure that the QR service is designed in such a way that all parameters are properly justified, proportionate, and based on system need. Where we have identified a requirement which potentially acts as a barrier to market entry, we have sought to mitigate any ‘first mover’ advantage, and as a service which (like balancing reserve) will, initially, be dependent on BM systems, we are able to utilise the BM wider access route so that QR is accessible in phase 1 by the widest possible range of flexible providers. There is benefit in terms of value to the consumer (see below) in pursuing the phased approach compared to waiting until OBP is fully functioning, and on a cost benefit analysis, other mitigation options specifically accelerating OBP development or adapting existing ASDP/PAS are similarly sub-optimal. The Quick Reserve service has been designed for both the BM and non-BM markets. Whilst we are unable to launch the Quick Reserve market to non-BM parties until 2025 when our OBP functionality will allow, we have identified an opportunity to bring forward consumer value and deliver the service in winter 2024, utilising our existing BM systems in combination with the new Open Balancing Platform (OBP) multi-dispatch. This means that in Phase 1 access to Quick Reserve will be through our existing BM systems and parties would need to register their units in the BM. We believe the majority of existing market participants and new providers of flexible energy, that meet the Quick Reserve requirements, have the opportunity and necessary lead-time to register in the BM and access Quick Reserve from day one. Aside from existing BM parties and those able to join as Primary BMUs, we believe through the BM Wider Access route there is a clear cost effective and efficient route to market for smaller non-traditional providers, aggregators and providers of flexibility, which allows them to access the Quick Reserve service in Phase 1. We have assessed the impact of any additional barriers to entry on levels of competition and are satisfied that they represent the best compromise available between liquidity, price and system security. To clarify on the 70% reference in our Quick Reserve Summary Document, we state that "It is estimated that around 30% of the non-BM OFR capacity (close to 320 MW) can achieve the 1-minute time to full delivery". This does not reflect any of the other existing units which may be working towards this capablity in order to participate in Quick Reserve. Any non-BM providers that do not wish to access the BM can participate in Quick Reserve from June 2025. In order to maintain a route to market for the provision of faster-acting reserve from any party, either unable to or not wishing to access the BM, we will be retaining the existing Optional Fast Reserve service until the end of 2025. Where any market participant feels there are barriers that make it unfeasible for their technology to access our Balancing Services or the BM then we are keen to discuss these with you and to work with industry and the regulator to look at how these can be overcome. After thorough consideration, ESO firmly believe that our decision to implement the new Quick Reserve service directly on the new OBP system with a phased approach during 2024 and 2025 is the right approach that provides an opportunity to bring forward (by circa 7 months) increased competition via a more competitive market (compared to the existing Optional Fast Reserve and Spin Gen market) and deliver increased consumer value, estimated in the region of £29.3m - £32.7m. Please note that the reference to non-BM Availability Declarations being required ‘no later than ninety (90) minutes prior to each Quick Reserve Window’ (page 20 ‘Availability Declarations’ in the Quick Reserve Summary Document) is incorrect and should read 60-minutes. We will shortly be publishing an updated summary document to incorporate all the requirements for the enduring ‘Phase 2’ Quick Reserve service where we will correct this error.
SSEN Distribution, trading name of Southern Electric Power Distribution plc | Broadly, we are disappointed with ESO’s approach and timing to publishing the revised proposed strategy. The proposed changes, particularly the intention to procure 100% of need from QR and 0% from OFR as soon as the QR market opens, are contrary to those that ESO has shared with us previously, and are a prohibitive factor in our ability to justify participating in the market from November 2024. | We are sorry to hear of your disappointment in our strategy. Our aim with Quick Reserve has always been to replace the legacy Optional Fast Reserve service, with it's main objective of reducing balancing costs by procuring fast-acting Reserve firm at day-ahead. Procuring 100% of the Quick Reserve requirement is how we hope to reduce the high spend on Pump Storage and Optional Fast Reserve, ultimately passing savings on to the end-consumer. By securing 100% of the requirement at day-ahead, we are only securing that capacity. Optional Fast Reserve units are still able to bid in for utilisation on the day and, as long as they are within merit, control room engineers will send instructions to units in merit order. As mentioned, we will only look to procure Quick Reserve if it is more economic than other options, and Optional Fast Reserve will therefore be considered as another option, which may mean that it is economic to procure less Quick Reserve than our requirement.
Sembcorp Energy (UK) Limited | Clause 5.11: While we agree with the spirit behind this clause, we do not believe it is within the remit of NGESO to determine what is “excessively” high or low pricing. We believe it is fair for NGESO to refer such instances to the Authority as per 5.11.1, but not with 5.11.2-5.11.4. There needs to be a clear, objective procedure for actions such as deregistering a unit or provider. | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances.
Centrica | With respect to the provisions around high pricing set out in 5.11 of the Service Terms, we support the objective and would call for effective implementation. We would highlight, however, that to ensure a level playing field in the interpretation of the requirements, which would also increase their effectiveness, more clarity is needed. To provide more clarity and certainty as to the interpretation of “excessively high or excessively low” prices, the ESO should provide further guidance, for example, on what can be included in the pricing (e.g., opportunity costs plus acceptable margin). | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances.
RWE | Planned retirement of ASDP In reference to the planned retirement of ASDP in December 2025, and the rollout of the OBP from Spring 2025, this raises a question with regards to the ability of Non-BM assets to participate in the STOR market – could ESO please clarify and reassure non-BM STOR providers that they will not be disadvantaged as a result of this I.T transition. | The STOR service will be ending along with the ASDP platform in Dec 2025. Non-BM STOR providers are encouraged to transition over to either Slow Reserve or any other service they are qualified for before that date. On 13 August 2024 we held the first webinar on the proposed transition away from ASDP and we have opened this up to industry for feedback until 10 September 2024 (https://www.nationalgrideso.com/industry-information/balancing-services/reserve-services/future-reserve-services#Events).
RWE | Flexibility Services Standard Agreement Whilst it’s recognised that the Flexibility Services Standard Agreement is not an ESO document; by referencing its content within ESO documentation; it means that ESO have the responsibility of ensuring that any amendments, and any consequential impact, are clearly communicated. For example, Balancing Reserve references version 0.4 of the Flexibility Services Terms, and yet Quick Reserve references version 3.0. | The intention was to reference the Flexibility Services Standard Agreement (Version 3.0) of April 2024. As Balancing Reserve was published when a previous iteration of this document was available the version numbers on those documents were different. We appreciate we have not referenced these documents in a consistent manner across services and the use of these documents in ESO Terms and Conditions is under review and will be updated accordingly.
RWE | Contract Formation Participants are required to sign Form B, however this is not defined or referenced in the Service Terms, Procurement Guidelines or the Glossary. We would therefore request that it is made clearer in the procurement documentation that it’s the signing of Form B by the Provider & Form C by the ESO, that binds the parties to the procurement documentation. | Please note, Form B is referenced in the Schedule 2 of the Quick Reserve (Phase 1) Procurement Rules.
EDF Energy | The ESO needs to be clearer on when the incremental volume cost amount will be applied to assets which do not retain the contracted headroom when holding a QR contract. This hasn’t been applied consistently for BR and applying the penalty “at the ESO’s discretion” creates an environment where some optimisers are following the rules as written and others are not. The ESO should clarify that this rule will always apply and develop a robust process for monitoring it. | We intend to have the necessary monitoring tools ready for the start of Phase 1 and that we will be closely monitoring any performance failures that require further investigation, as set out in section 14 'Provision of Other Services' of the Quick Reserve Service Terms.
EDF Energy | ESO should provide greater clarity on how they define “excessive” Bid-Offer prices under 5.11 when providers submit prices through the BM for utilisation which in the ESO’s opinion are designed to be rejected. We agree that this should be addressed, although would also request clarity as to which regulations or license conditions a provider could be in breach of if submitting prices (particularly offer prices) which are deemed to be excessive, e.g. in the case of bids a provider could be in breach of TCLC if the asset sits behind a transmission constraint, and the instances when each of 5.11.1, 5.11.2, 5.11.3, & 5.11.4 may be applied. | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances. The purpose of this section 5.11 is not to enforce compliance by providers with their various legal or regulatory obligations. Instead, it seeks to provide some recourse for the ESO if it assesses that, having regard to market conditions and prevailing circumstances etc, prices have been set by a provider at levels [outside of market norms and] which appear designed solely (or primarily) to deprive ESO (and hence consumers) of the benefit of a contract under which availability fees have been paid. We accept that prices in competitive markets are influenced by the interplay of supply and demand, and for that reason have not sought to attempt to define an ‘excessive price’, but rather to facilitate a dialogue with the relevant provider so that ESO can seek to understand the rationale for particular prices before assessing whether it is appropriate in all the circumstances for it to invoke the further provisions of the clause.
Shell | We understand that the ESO is looking to introduce terms which address the operational challenges experienced with the Balancing Reserve. Whilst we are supportive of this in principle, we have some concerns with the practicalities of managing ‘excessive pricing’ as this is not defined and can be subjective. We note that OFGEM found it difficult to define excessive profit under the TCLC rules, leading to the need for a comprehensive guidance to support it. It would also require resource to monitor and deal with complaints. We believe this issue needs to be considered further. The introduction of the new SoC rules under GC0166 will help in monitoring if the unit is technically available so could be used to monitor whether an asset is trying to signal it does not want to receive a BOA even though it is available. | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances.
SSE Plc | Version 3 of the ENA Flexibility Services Standard Agreement has introduced caps on liabilities (except for death & personal injury due to negligence). Para 10.1 of the ENA Agreement carves out any indemnities under the Service Terms and Procurement Rules (e.g. Third Party claims, Modern Slavery & Anti-Bribery, IPR, etc). Was this intended or should the liabilities under the Service Terms and Procurement Rules be capped as well? | Liabilities under 10.1 of the ENA terms are capped at the Distribution Limit and the Transmission Limit which are defined in the Balancing Services Glossary and the ENA Agreement respectively. The carve out relating to indemnities in 10.1 of the ENA Agreement is kept under review but this matches the approach taken across other balancing services. We have therefore attempted to remain consistent here. We have also attempted to remain consistent with paragraph 6.12 of the Connection and Use of System Code (CUSC).
SSE Plc | In addition, could you please check references to the ENA Agreement in the QR Service Terms and Procurement Rules, e.g.: QR Procurement Rules 10.1 & 10.2 refer to the ENA Agreement 11.1 & 11.3. Should this be 10.1 & 10.3? The QR Service Terms 16.1 refers to the ENA Agreement 8.1 & 8.3. Should this be 7.1 & 7.3? Equally, 16.3 refers to 8.5 & 8.7. Should this be 7.5 & 7.7? | Thank you. These references are to be updated.
Energy UK | Stacking: Members felt that there is lack of clarity over the level of stacking that is permitted in Phase 1 and Phase 2 for example, whether the non-stacking provision just applies to other ESO services (for example to DC,DM, DR) or further, to arbitrage / wholesale markets. Clarity here would be welcome (especially given the proposed penalty for non-delivery). | For Phase 1, providers are only allowed to stack positive and negative Quick Reserve, along with the Capacity market, stability and voltage services, and in the BM. We regard stacking with the wholesale market as an implied necessity for providers to have their energy positions in a place to provide the service. For Phase 2, this stacking capability will be extended to the Dynamic Response market and the opposite directions for Reserve services.
Energy UK | High pricing: Whilst members are supportive of the service and service terms, there is concern at the proposed provisions around high pricing set out in 5.11 -where ‘NGESO reasonably considers that the Service Provider has submitted Bid-Offer Prices into the Balancing Mechanism… which by virtue of being excessively high or excessively low,… have as their sole or primary objective to discourage NGESO from issuing Bid-Offer Acceptance(s)… then NGESO may at its discretion (but with reasonable grounds):- 5.11.1 refer such prices to the Authority for consideration; and/or 5.11.2 declare Quick Reserve as unavailable from that QR Unit for the entire affected Contracted Service Period(s); and/or 5.11.3 Deregister the relevant QR Unit(s) or any of them; and/or 5.11.4 Deregister the Service Provider as a Registered Auction Participant /Provider’. Whilst we support the outcome that the ESO are looking to achieve, we are concerned at the additional regulatory risk this could represent for participants if ‘excessive’ cannot clearly defined. Given the potential difficulties with definition (set out in the paragraph below), we urge the ESO to explore alternative means to manage the perceived risk. | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances.
Energy UK | Defining ‘excessive pricing’ - This concern is centralised on the difficulty of defining what constitutes ‘excessively’ high (or low) pricing. If participants are going to be judged on it, it will be necessary to be able to define it or participants could be inadvertently caught out (especially given the difficulty of pricing at day-ahead stage and the changes that can materialise after this time). Members note that Ofgem did not define this in the Inflexible Offer License Condition (IOLC) for this reason. | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances.
Energy UK | Members highlight the complexity that assessing this could involve, especially with an ex ante assessment. It will be hard to ascertain the level of market information the participants had when placing the BOA (for example, of potential constraints, weather change, actions of other assets on the system). Members felt that defining this would be difficult whether it was based on a percentage deviation from average pricing or via a fixed utilisation fee approach. Without an shared understanding of how ‘excessively high’ would be defined, members agree it will introduce risk (and therefore cost) for participants. Members expressed concern that what constitutes ‘excessively’ high pricing could be defined elsewhere (for example, by extending IOLC Transmission Constraint Licence Condition [TCLC]) and then backdated to apply to services including Quick Reserve. | The ESO acknowledges the absence of an industry standard or otherwise obvious definition of “excessive pricing” which as the service terms had been written, left it to the ESO to make a subjective decision. However, it is not the assessment that the price is ‘excessive’ that constitutes the trigger to invoke the contractual remedies (including making a referral to Ofgem) – rather, the trigger is that the pricing has as its sole or primary purpose been submitted to discourage the ESO from issuing a BOA and ESO’s judgment that prices are ‘excessive’ will be treated as evidence of that. On this basis, we have reviewed the relevant section of the Service Terms and added an additional step in the process whereby the ESO shall request an explanation from the provider in reasonable detail of the rationale for such pricing, and on receipt of such explanation the ESO will then make its judgement (acting reasonably) on the motivation behind the pricing. In seeking that explanation, the ESO will be trying to assess if the prices are genuine in the sense of representing a real interest in being despatched or instead appear designed to do the opposite by influencing the ESO to despatch someone else instead. We have also included the right to refer to Ofgem and/or pursue the other remedies if a provider fails to provide such explanation after a reasonable period following request, and we proposing this as 14 days. We believe a clause which links to motivation behind the price setting, rather than solely focusing on the numerical value of those prices, is appropriate in these circumstances.
Energy UK | If the ESO were to proceed with this approach, implementation would require sufficient administrative resource to manage it, including a dispute investigation team to addresses the queries as well as further guidance (for example, on what can be included in the pricing - e.g., opportunity costs plus acceptable margin). Is it necessary/ can the perceived risk be managed in another way? Members think that the new State of Charge (SoC) rules and stricter performance monitoring would be a more appropriate way of means of managing the perceived risk (the SoC rules should address the root cause). If the unit is technically available and has enough SoC to meet its contracted volume, this should be sufficient. Members noted GC166 as a further development in this space. | Thank you for the feedback on this. We are happy that we have the necessary resources in place to monitor the requirements of section 5.11 of the service terms.
Energy UK | Members think the excessive pricing terms introduces additional risk and complexity into the market where the risk has been covered off by changes elsewhere. Members note that the proposed performance monitoring for Quick Reserve is light - the ESO could retain the option to bolster this if the initial period of the service brings to light any concerns. In summary, members do not agree that the excessive pricing terms are justified –they introduce regulatory risk which could increase the costs of provision (ultimately born by the end consumer). We support the outcome that the ESO is seeking to achieve but urge the ESO to look to more proportionate means to achieve this. At this stage, members expect the current rules around State of Charge (and general direction of travel in this area) to be sufficient. We would welcome the ESO monitoring the market for a period and then revising the penalty regime if there is sufficient evidence that this is necessary. | We have looked at a range of ways to monitor and address state of energy, giving consideration to the penalty based structure proposed for the Dynamic Response services, and feedback from Balancing Reserve. As Quick Reserve is a new service we believe the current proposed penalties associated with 'excessive' prices are sufficient and justified given the evidence obtained from the Balancing Reserve market, but we will monitor and review this decision and engage with industry for feedback through Phase 1, just as we have done with Balancing Reserve. We will also continue to monitor the penalties outlined in the Dynamic Response services and share any proposed design changes with industry as appropriate. The value of a firm service lies in its reliability to be available in real-time, and so ensuring that behaviour which jeopardises that is prevented is important, otherwise the service may not deliver value.