## Webinar 13.11.24
# | Webinar Question | NESO Response
1 | Are you looking for more Synchronous Condensers to be added to the network? Is this a technology that would benefit NESO? | Our markets are desgined to be technology agnostic, however, all participating solutions will be expected to meet technical requirements. For reactive power markets, synchronous condensors and other technolgies which can provide reactive power services and meet our market eligibility criteria will be able to participate.
2 | How does this Mid-Term market sit alongside a Mandatory Services Agreement that a CCGT may have? could a CCGT exit their MSA to agree to a Mid Term contract? | All generators covered by the requirements of the Grid Code are required to have the capability to provide reactive power. Mandatory Services Agreements are a requirement to connect to the system and the future reactive power markets will not remove that requirement for MSAs. Providers with additional capability over and above what is mandated could be eligible to participate, providing they meet the other necessary tender criteria. Once the market is further developed, guidance on "stacking" would be provided.
3 | Would the results of any 'direct award' contracts be published? (in the public domain) | To date we have published the results of contract awards through our voltage pathfinders and directly awarded voltage contracts on our NESO web pages. The intention would be that the results of any contract awards through the mid-term market would also be published based on this practice. What level of detail we would publish about contract awards is still to be determined.
4 | A 2 week turnaround on the RFI is quite tight. can this be extended? | Following last week’s webinar, please be aware that we have extended the response deadline for our market engagement voluntary RFI by two-weeks, the extended deadline is now 5pm on Friday 13 December 2024.
5 | Often reactive power capability (MVAr) is limited to the minimum required to meet grid code compliance requirements when a generator is operating at Rated MW. It might be an idea to allow us to prioritise reactive power over active power in this scenario - assuming we will be compensated appropriately? | Prioritisation of MVAr over MW is certainly a possibility. If a provider's connection agreement enables them to provide MVAr in excess of the minimum grid code requirements, it is certainly possible for this to be bid into a mid-term reactive power market (noting any bids would be assessed in line with market provisions). However, the MVAr would need to be delivered independently of the MW output.
6 | Appreciate its still early days but can NESO advise how much benefit CM085 Decision has provided and is expected to provide? Has this reduced the need for new reactive power compensation? | We welcome code modifications such as CM085 as this will allow NESO to access additional reactive power services from existing units. Whilst a positive development, it does not diminish the importance of a competitive mid-term reactive power market to procure at economically cheaper prices than the counterfactual.
7 | Are transmission connected assets at 132Kv, Grid Parks and tertiaries excluded? Are they not effective? They have Grid Code mandatory reactive obligations | We expect all transmission connected assets to be able to participate in this market subject to market eligibility criteria. We have included a question on this topic in our market engagement voluntary RFI, if you have any views, please provide them through this engagement mechanism.
8 | What are the expectations regarding stacking of this service? | We have not developed the stacking rules at this time, however if you have thoughts on this please submit these through the market engagement voluntary RFI.
9 | You have been working on these d-1, yearly and y-4 Reactive mkt for some time and it seems it will take another 6-8months before any tenders. Is this correct or will you do some more pathfinders in the meantime? | At this time we have not published any future long-term Y-4 tenders which we previously referred to as Pathfinders. If a need is identified for further requirements we would publish this through our usual mechanisms of the NESO website and the newsletters.
10 | Would multi quadrant operation be accepted? E.g. active power import with reactive power injection. | The intention with the mid-term market design is that any technology that is proposed should be able to provide reactive power services without the need for MW export to the system, with the exception of any intrinsic losses. For example, a synchronous compenstor which usually requires small amount of MW import all the time will be acceptable. In addition to the need to be able to provide MVAr at 0MW, it is proposed that we would accept multi-quadrant operation, though the provision of MVAr needs to be wholly independent of MW provision, i.e. the device/provider doesn't need to change MW output to achieve a change in MVAr output.
11 | I'm interested in predominantly distribution connected BESS in the 10s-100s MW range. Just confirming that the NESO reactive power services would not be suitable for this (as it was mentioned that it is transmission connected only)? Why is this? | A number of technical, regulatory and commercial blockers have been identified through various projects and shared with the relevant parties across the energy landscape, some of which we are starting to see changes on. For example, the Mersey and Pennine Pathfinder projects identified technical restrictions on DNO circuit breakers, which could impact the ability of DER to participate at zero, or low, MW outputs, and may require significant upgrades to DNO networks. Further work with the relevant parties including Ofgem and the DNO's is being pursued where required.
12 | For resources whose availability is weather dependent, what is the plan for the short term (~day ahead) market? Alternatively is there a non-firm option available under this process? | On the short-term market, further analysis is required to determine the value of a day ahead service. This work will also consider the output from the review of the Obligatory Reactive Power Service (ORPS). Earlier this year we advised that this work needs to be completed before we can continue with the development of the day-ahead market. But please continue to monitor the future of reactive power webpage and our newsletters for updates on the day-ahead market.
13 | What do you see as the role of interconnectors in providing reactive power under this new reform? | Our markets are designed to be technology agnostic, however, all participating solutions will be expected to meet technical requirements. For reactive power markets, interconnectors and other technolgies which can provide reactive power services and meet our tender criteria will be able to participate.
14 | If a mid-term reactive power market becomes the preferred route for NESO to procure reactive power, does this mean future NSPs for inertia or SCL may not value or ask for reactive power above the mandatory required levels? Or the NSPs may expect solutions to contract their reactive power separately into the mid-term market? | In our development work for reactive power markets, we closely align our work with the work on stability markets and Network Services Procurement (NSP). We still expect the two markets to define technical requirements separately however, we will take account of solutions provided under both markets to determine our technical requirements. For stability markets, at this time, we still expect solutions to provide minimum reactive power capability as per Grid Code requirements and will be compensated via ORPS. Please note, we have included a question related to this in the market engagement voluntary RFI and we'd welcome your input and feedback - we'll use the feedback received to shape this as well.
15 | Under the mid-term market, is payment for availability to be complemented by ORPS payments for any MVAh delivery? | Our current position is that this mid-term market would be compensated thorugh an availability payment only. Nonetheless, we are keen to hear from you on this and would encourage you to express any views via the voluntary RFI.
16 | I presume you plan to procure locationally within the year ahead/within year so will be locational and direct award really to manage location priorities? | Reactive power is a locational service so the intention is we would procure locationally through this market through one of processes outlined and as appropriate based on the requirements, including the duration of requirements.
17 | Is NESO considering the potential for distribution connected reactive power solutions? Are there any clear technical or regulatory barriers to such solutions? | Currently we are looking at transmission connected solutions only. To access reactive power from Distributed Energy Resources (DER), more work with Distribution Network Operators (DNOs) is required to understand the implications on individual DNO networks and coordination with Distribution Ssystem Operators (DSOs) on voltage management within their networks.
18 | Are you going to publish a heat map identifying where the reactive power is most needed / valued on the network? | Thank you for the question. As part of the Clean Power 2030 advice to government, NESO has produced an indicative heat map within Annex 3, Figure 2 on page 6. https://www.neso.energy/document/346801/download More information on requirements for specific tenders would be communicated as part of any mid-term reactive power market process.
19 | Is the power factor requirement as current ORPS states : rated power output (MW) at any point between the limits 0.85 power factor lagging and 0.95 power factor leading at the BMU terminals still going to be applied for Mid-Term market? | The mid-term market will be targeting the reactive power requirements in MVAr, rather than targetting specific provision at MW output levels. Any solution would need to be capable of providing the MVAr capability independently of MW output.
20 | The generator who is in the Mid Term Market are they considered as Clean Power Plan 2030 or designation project? | Mid term market providers will be required to deliver the reactive power service independently from their active power MW output, which should aid clean power operation. Whether a project is considered to be "designated" or as a technology within the Clean Power 2030 Plan as part of Connections Reform would be determined by the Connections Reform designation methodology rather than by the mid-term market. For more info on Connections Reform, see https://www.neso.energy/industry-information/connections/connections-reform. There is also a webinar recording on the methodologies deep dive with an explanation of CP30 and project designation https://www.neso.energy/industry-information/connections/customer-connection-events#Other-webinars-and-slides
21 | Follow up on Q16: Sorry to clarify - so in the year ahead tender, you will procure multiple locational requirements at the same time. Or will you do one location in each year ahead tender focussed on one location as with the pathfinders. | In short, we'd tender when / where we identify a requirement. This might be based on single locations or multiple locations of need depending on the requirements identified and the most appropriate way to meet those requirements. To clarify, locational requirement could be tendered at Y-1, or at other points through mini tenders. Please note, previous pathfinders have included multiple locations of need.
22 | To clarify, are the published Clean Power 2030 heatmaps a view of need from 2025 onwards or from 2029/2030 onwards? As was stated earlier, based on current thinking there is no clear need for a reactive power Y-4 market until 2029 earliest. | The heatmaps published in CP30 publication are a view of our needs for clean power operation in 2030 as known at this stage: https://www.neso.energy/document/346801/download. At this time we have not published any further long-term Y-4 tenders but may do so in the future based on identified requirements. Meanwhile, this mid-term market is being developed to access reactive power capability from existing connections to help with any closer to real time operational voltage management requirements.