## Webinar 1 - Framework and Metho
Question | Answer
Will FRCR 2025 consider frequency risks associated with sub synchronous oscillations which have been seen in the GB system? Based on recent NESO presentations these appear not to be directly related to low levels of inertia. | From previous investigation following SSO events we concluded no correlation between lower national system inertia and the initiation of the SSO events although local inertia reduction can have a negative impact on SSO, as a secondary effect of reducing the Short Circuit Level and damping provided from inertia providing synchronous machines at local levels. FRCR 2025 will continue to look at minimum inertia policy at a national level and will closely collaborate with NESO operability workstreams to ensure further reduction of national inertia will not cause other operability issues like the sub synchronous oscillation when the policy is implemented.
Will NESO use the units of MW.s which is specified in the GB Grid Code and cease using MVA.s which risks conversion uncertainty and which cannot be used to measure inertia. Eg a flywheel is a factory acceptance test | Different parts of the NESO have used MW.s or MVA.s and unfortunately we have not been very consistent between the two. For the tenders we generally use MVA.s but caveat that for the tender so we consider 1 MW.s = 1 MVA.s. As part of the GB Grid Forming Expert Group work we think it would be useful to clarify this definition to ensure some consistency going forwards.
In the introduction past simultaneous event review= past tense. Would argue this deserves review as since 2022 we see greater short term storage reliance (energy exhaustion/ replenishment risk), different set freq services, & lower SCL= greater impact across network area from combined F &V events. | Thank you for your comment and feedback. If you joined our recent Operational Transparency Forum (OTF), we mentioned that in FRCR 2025, past system events were reviewed and updated into the model. Particularly to the simultaneous events we reviewed system cascading or simultaneous events between January 2019 and October 2024 in line with GC105 and GC151 reporting and OC3 requirement updates. The updated failure rate of system events are codified into FRCR 2025 model. We will cover more details in next webinar.
When you refer to vector shift please can you clarify that you are only referring to VS protection on DER to avoid islanding during loss of mains (which is no longer permitted), rather than simultaneous tripping events cause by failure ride though large vector shifts? | The vector shift we are talking about is exclusively referred to the VS protection on DER. We are aware that Vector shift is increasingly used in the industry to describe the fault ride through large vector shifts. We will make clear of our VS definition in our FRCR report to avoid any confusion.
Would also suggest regional estimation of df/dt important within first 1sec to correctly identify areas both RoCoF & power electronic device control may be compromised immediate to event. Related to this, monitoring of phase angle movement over same period across different areas of Tx network. | This issue has been raised as part of the GB Grid Forming Expert Group and will be addressed through that forum. We have graphs showing the effect of regional RoCoF events which is an important part of this work. We don’t model regional RoCoF in current FRCR and plan to consider that in future version. The challenges are that we have limited direct measurement or monitoring of locational RoCoF or inertia, and we do not have a policy for locational RoCoF or inertia. We manage the risk in operation timescales. We note that compliant RoCoF relays has a time delay of 500ms. We doubt that local RoCoF would be sustained at 1Hz/s or more for longer than this time delay (i.e. 1s). Non-compliant RoCoF relays that would trip due to this is less than the total RoCoF loss which we consider in the FRCR policy, i.e. securing all BMU losses with its consequential RoCoF loss.
Why is the starting point for FRCR reducing inertia to 102 GW.s? Should the process not be to access the risks, benefits and costs; and determine the optimum minimum inertia? The process seems back to front - do you agree? | In FRCR 2025 report we will include the review of system performance when running at 120 GVA.s minimum inertia policy, that includes residual risks, and benefits based on operational data. From history of FRCR assessment, we understand inertia reduction is the main policy development trajectory to achieve zero carbon operation and present huge cost savings for GB consumers. Particularly in FRCR 2024 we already looked into the benefits and cost when running the system at 102 GVA.s so we are going to continue onto this direction this year to confirm the benefits. The inertia policy in FRCR is the minimal operational requirement for inertia which is driven by the largest tolerable RoCoF and it is not a parameter in economic operation. For example, we need to meet min inertia requirement first, then if we still need more controls, it is an economic question for increasing 1 GVA.s of inertia or 1 MW of response From modelling point of view we could assess a more "appropriate, dynamic and time-varying" system inertia based on changing system conditions, response market capacity and price. As a consequence, if a time-varying inertia is proposed in operational pracitice, a changing, uncertain and unstable response or inertia market could be introduced which would not be welcomed by the industry and could further introduce operational risks to NESO. This is not the purpose of FRCR policy development or appropriate for NESO operation.
In methodology- not just the model&data but predictability/ accuracy that are important- e.g.need to ensure we are factoring in hard to determine distribution system dynamics and inertia contribution-or identify measures to generate confidence in these. What margins are we/ should we be assuming? | As we mentioned in the presentation. FRCR analysis is not intended to do a forecasting or prediction for the future. Our main objective is to identify the most appropriate frequency policies that suits the current energy landscape and system conditions. For the system dynamics such as inertia contribution from distribution network, this is include in our inertia data, which is derived from the historically system outturn inertia. And the inertia contribution from distribution network is part of it. In operation practice NESO has a process to periodically review the inertia factor contributed from distribution networks and update to our operational tools.
Can you clarify the meaning of Simultaneous Event. Does this include a rapid sequence of events over a few seconds to a minute could for a cascade event rather than "An event that disconnects two BMUs at the same instant" as stated in the presentation? | Simultaneous events or cascading events are not easy to model. So, In the FRCR analysis, we use the profile of two BMUs disconnected at the same time, e.g. instantaneously, to represent the worst-case scenario. Sequence of events over a certain period or cascading events within a short period time can be modelled and tested but the impact is smaller compared to the simultaneous event. In FRCR 2025, we have reviewed the recent simultaneous and cascading events between January 2019 to October 2024 in line with GC105, GC151 and OC3, and calibrated our assumptions in the analysis.
On simultaneous events- are we receiving information on non GB disturbance risks present that would potentially impact a collective import of power into GB more severely than the host EU TSO- E.g. a NW france fault near/ at sellindge? how does reduction in inertia effect these risk considerations? | If there is a fault in Europe this would be behind an HVDC System so we would not see the AC effects of the fault on the European side but we would see the effect of the loss of import to GB which would be the same as the loss of a generator. In this regard the loss of an interconnector is slightly less of an issue when compared to loosing a synchronous or Grid Forming plant where you loose the MW output and inertia. The only issue we need to be careful of is if Grid Forming is installed on both ends of an interconnector (eg where one synchronous area is used to provide inertia (ie MW support) to the other). This situation poses additional risks of faults on the european system which increases the risk seen to the GB System. We are aware of these types of issues and are looking into them within the NESO.
Should fault ride though be added to the list of controls on slide 17, to emphasise this is a critical control measure. | Fault ride through is a Grid Code requirement. It is a very critical requirement however, It is not a service we procure to ensure frequency remains within limits.
How can you compare costs to risks except qualitatively? Surely you should make a quantitative comparison of the operational costs with the costs of LFDD events taking into account relevant probabilities. Do you agree? | FRCR is a qualitative analysis to determine which policy combinations give better cost vs risk pairs by identifying the trend, and this trend is valid qualitatively and quantitatively. The challenge for using the cost of LFDD events is there is not a definitive value for the Value of Lost Load (VoLL). The FRCR Methodology 2021 explained why VoLL is not suitable for frequency control policy assessment. Our current understanding remains that VoLL is not appropriate. FRCR analysis evaluates system security and benefits by considering balancing costs, including frequency response, inertia, and BM actions. Thus, FRCR is using Cost Per Avoided Event to determine the value of securing events.
What is the risk of a Cyberattack on a class or portfolio of assets causing a simultaneous event with a loss of demand or infeed greater than the largest single infeed loss? | Thanks for your feedback. All the risks in the FRCR analysis are the events. In addition it is a requirement in the Grid Code for User’s to ensure the Critical Tools and Facilities installed on their plant is cyber secure to NIS Standards.
Please confirm that your answer to my previous question on Cybersecurity, is that there is no risk, because of grid code requirements. Correct? | Cybersecurity and its impact to power system is a big risk topic which is under discussion with the industry led by DESNZ. NESO’s input into this work is to ensure all the directions we are going to would not deteriorate existing system performance or security. For FRCR, we will consider this risk into future model once it is well clarified and structured. Out of FRCR cycle, if we see a risk becomes materialised NESO will introduce appropriate operational measures to mitigate before a proper policy is developed.
There's things we can do in FRCR 2025& probably quite a lot on time& resource reasons we can't. good to "get ahead of the game" for FRCR 2026, 27.. especially 2029&2030. What's the inertia trajectory, FRCR risk evaluations& frequency & grid forming services that complement? what should we start now? | Thanks for sharing your thoughts. The current FRCR methodology use immediate historical dataset including system outturns and market prices and adjust for expected changes for upcoming 2 years. The data is not a good representation for future system or market development. Therefore, FRCR recommendation does not forecast or indicate any long-term operation policies. However, the concerns are aware by us. NESO teams, e.g. longer term operability, zero carbon operation, market strategy who are collaborating to seek a better approach to address future challenges and create the framework that the whole industry can work together to tackle the challenges.
What were stakeholder questions and feedback in previous years and what were the NESO responses ? Have these feedbacks been reviewed again to ensure that any issues have been considered and addressed?. | Thanks for the question. Since 2024 FRCR project following running the consultation we published all the feedbacks and NESO responses on NESO website. We will continue publishing them this year and be transparent with industry. Before 2024 although we did not publish the full details of feedback from consultation, we had individual engagement following their comments and updated the FRCR report based on the feedback. The comments which might not need immediate modelling consideration we would include them into future work that is in the end of the report. When starting a new FRCR process, we would review the feedback in the backlog to form the project scope. The scope is also shared with SQSS panel, Ofgem and industry via OTF.
Can you share the slides before the meeting so we can review and undestand whether to attend? Thanks | Thanks for your feedback. For this webinar we will share the slide and recording onto our website after the webinar. In the future, we will share the content as early as possible. Thank you.
Where will you get more inertia from if you don't want to run CCGTs and you haven't brought forward your T-4 and daily inertia mkts? | We need to meet the minimum inertia requirement which is set in the policy. That mean we need to run CCGTs to meet this requirements if necessary. The long-term and short-term inertia markets, i.e. T-4 market, and intra day or day-ahead market are under developing aiming for bring more certainties to real-time operation and eventually reducing cost.
Could there be any impact on SQSS due to this reduction in inertia | Regarding the governance process, the policy recommendation will be shared with SQSS panel for their approval and recommendation before we can submit to Ofgem for final approval according to Appendix H SQSS. During the engagement the impact will be fully discussed with SQSS panel.
Can you share the analysis of simultaneous events (GC0151 and GC0105) ahead of the next webinar to allow time for analysis to prepare questions? | Thanks for the question. We are improving the transparency of FRCR process. This will be included in the guidance document aimed to be published by end of January 2025.
FRCR focuses on cost reductions, what about carbon? Inertia decrease could lead to large carbon emission reductions despite a small cost reduction for the ESO. Could you provide metrics on that? | Carbon reduction is not a direct measure in FRCR policy. Running system at lower inertia level significantly reduces carbon emission as well as cost benefits. Practically the issue is addressed by the introduction of the stability path-finder work, Stability market and the development of Grid Forming techniques which are already part of the GB Grid Code and is being reviewed on a regular basis. Grid Forming enables converter-based plant (a lot of which are used in renewable technologies) to contribute system strength and inertia which will prevent the need to run carbon based plant.
Can you better explain why you don't give much importance to DM/DR response in the analysis? Higher DM/DR response surely has an impact on the RoCoF | We do value DR and DM for pre-fault frequency and are currently reviewing the requirements. As the frequency can vary from 49.8 to 50.2 within the operational limit, FRCR considers a worst-case scenario where an event occurs at 49.85 (current prefault frequency assumption), as FRCR is essentially a post-fault analysis. In this situation, the majority of DR and half of DM are already delivered. Therefore, DC is the main variable in FRCR analysis. While DM/DR indeed can deliver a response to mitigate system events, they are primarily designed to manage frequency fluctuations within the operational limit. This requires more energy, more frequent utilization, and therefore a higher cost. Conversely, DC is designed for large events, triggered less frequently, resulting in a more cost-effective solution.
How will you desite to make Grid Forming now mandatory for all Type D generators (Renewables) from Jan.2026? how will this impact FRCR going forward as all a-sync. assets will have stability parameters? | This issue is being addressed through the GB Grid Forming Best Practice Group, part of which is to consider the requirement for a mandate. If you are interested in joining this group please use contact Hazem Karbouj (Hazem.Karbouj@uk.nationalenergyso.com) and we will be happy to add you to the group. It should also be noted that in Europe (ENTSO-E) they are also proposing to mandate Grid Forming on any plant of 10 MW and above or connected via a feeder of 110 kV or above. Changes following the mandating will be considered into future FRCR work.
GC0155 relating to FRT clarification remains un-concluded. Do we have a clear understanding for how much generation would be at risk of post fault overvoltage trip relating to this current uncertainty, and whether this risk is growing over time? again a question of margins in the model assumed. | Our interpretation of the Grid Code is that the oscillations arising due to a fault is covered by fault ride through requirements even when it includes a temporary overvoltage. So far, we have not seen limited cases when a PPM response to a fault has caused an overvoltage at the turbine terminals and caused the turbines to deload. This has not been a widespread issue and the risk associated with it is managed through the compliance process.
In the methodology, has FSM response from renewable generation and battery energy storage has been considered? | As part of the modelling LFSM-O operation has been considered. FSM or MFR is not considered in the model. Commercial response services like DC, DR, and DM are the main sources for frequency control. When providing DC, DR and DM services, FSM response is overridden by fast-acting dynamic response.
How is inertia measured in real-time? | In NESO’s current operation practice we do not directly measure inertia. In real-time operation, system inertia is composed of the inertia from synchronising plants, the inertia contribution from synchronising elements on demand side and the inertia from pathfinder units. A synchronising plant’s inertia is calculated based on its running mode in real time and the inertia factor that is submitted to NESO via compliance process. The demand inertia is estimated by a demand inertia factor that is derived based on historical frequency events. We continue monitoring system inertia following frequency events and update the demand inertia factor to ensure it best represents system condition. We are also running innovation projects to validate our assumptions on demand side inertia. We will be able to measure system inertia in real-time and use the data for operation decisions once we have confidence on the outcomes from the innovation projects.

## Webinar 2 - Data and Model
Question | Answer
Frequency recovery dynamics; been noticing slower post event recovery across number of events recently-suspect represents in part decline in total of inertial & response supporting recovery & that IBR don't give >linear voltage/power, particularly if volts low; can this be included in FRCR thinking? | FRCR policy is to ensure securable events are compliant to SQSS requirements in frequency control that includes frequency nadir to be no less than 49.2Hz and can return to 49.5 Hz within 60 seconds. Frequency recovered is considered into the model when we applying DC control via static FFR. We will make sure the holdings of those services are sufficient to meet the frequency restoration requirements. We are also reviewing the system need to a static recovery service. Regarding the potential reason of reduced inertia, less inertia means faster frequency recovery, because inertia resist frequency movement in any direction, hence less inertia means faster frequency recovery.
Will FRCR consider interconnector reversal as a potential worst case single BMU fault? | Interconnector reversal is not considered into current BMU profile as the reversing behaviour does not happen in operational practice. When an interconnector trips it should return to its PN position pre to the trip or to be agreed between two TSOs if it is different to its original position. If the original position is at a reversing direction we will manage according to the planned operation envelop. We are aware some of the interconnectors have the function to recover their output following a trip or fault event. NESO works with the interconnectors and the neighbouring TSOs to clarify the recovering capacity and speed of those interconnectors so we can manage the risk in real-time operation.
Also on same theme of post event frequency dynamics- how confident are we of the dynamics of DER embedded within the net transmission demand which have limited code obligations to provide same MW across a freq disturbance. how doesG past (event) monitoring inform forecasting effect of DER growth? | From a Code perspective, all plants which are directly connected to the transmission system are required to comply with the requirements of the Grid Code and any Large Power Stations are required to meet the requirements of the Grid Code. For any plants which are not CUSC Parties (excluding Licence Exempt Embedded Medium Power Stations) they would be caught by the requirements of the Distribution Code and G59 / G99. For any plants which are caught by G99 (which came in through the introduction of the EU Requirements for Generators which applies to any generator which connected to the System on or after 27 April 2019 and concluded contracts for main plant and apparatus on or after 17th May 2018) has to meet very similar requirements to those in the Grid Code such as frequency range, fault ride through, reactive capability, frequency response etc. Limited Frequency Response Mode Over frequency (LFSM-O) applies to all units of any size and FSM/LFSM applies to all generators which are either connected at or above 110kV or 10MW or above. A condition of RfG which is coded in Grid Code and G99 requires Generators of 10MW and above or connected at or above 110kV to install monitoring eg Dynamic System Monitoring, fault recording etc. There are however very limited requirements on pre RfG embedded plant caught by the requirements of G59. Common mode failures affecting a multiple small embedded power stations not covered by the above requirements are identified through analysis of past events. If such risks are identified, depending on materiality, and provided that there are no other mechanisms to manage the risk, we would look at introducing them into the operational guidance and into FRCR assessment.
Does FRCR consider the importance of regional RoCoF? A national RoCoF less than 1Hz/s may lead to a regional RoCoF over 1Hz/s causing loss of mains tripping for some DER.. | We don’t model regional RoCoF in current FRCR and we plan to consider that in future version. The challenges are that we have limited direct measurement or monitoring of locational RoCoF or inertia, and we do not have a policy for locational RoCoF or inertia. We manage the risk in operation timescales. We note that complaint RoCoF relays has a time delay of 500ms. We doubt that local RoCoF would be sustained at 1Hz/s or more for longer than this time delay. Non-compliant RoCoF relays that would trip and this is less than the total RoCoF loss which we consider for BMU + RoCoF volumes.
On interconnectors-fault @les mandarin, france=volt zero= max 3GW instant loss of interconnector capability there + potl loss 1GW permanent+RTE voltage depression influencing various interconnectors doing similar things?adds a vector shift to GB system?a big loss& HVDC recovery to consider. Others? | In the FRCR analysis, we include all known risks based on their historical occurrence. Its worth noting that under the HVDC Network Code, HVDC Systems which are caught by the requirements of the Code (generally plants connected from September 2019) are required to have a fault ride through capability which would apply to all HVDC Systems installed in EU Member States. We also welcome any feedback on the modelling solutions for the new and emerging risks.
Can your share the detail of the analysis of simultaneous events January 2019 – October 2024? Including for example how many simultaneous events where there and how many involved more than two BMUs, or 1 BMU and some DER? | Events detail from 2020 to 2024 are published via GC105 and GC151 monthly reports that are available on our website. There are detailed infeed and outfeed losses for more than 250MW as per GC OC3. Events in 2019 are not included in those reports as those requirements were in place since November 2020 and it is difficult for us to re run all the thorough investigations. However we will include the total MW and duration and high level causes when we publish the FRCR guidance document in January 2025.
Simultaneous events-should go though few tests before making a call: 1) coincident or consequential relationship wt each other? 2) likelihood vs contain-able? 3) predictable vs low visibility? 4) proximity to "cliff edges"of perform vs confidence of edges? 5) known vulnerabilities related to events? | I think we all agree modelling and testing simultaneous events are difficult. Consequential events would be modelled based on the mechanism that causes them and we can see if they are simultaneous events. I hope Yuankai’s slides in P29-30 give you some clues to your questions. For FRCR purposes we are interested in the total volume and duration of the events. In our model we consider the worst case scenario that is, the cascading or simultaneous events happen instantaneously to quantify their impacts.
Is there a risk that considering only 5 years of information for 1 in 10,20,30yr events is less informative than a larger time sample for simultaneous events? i appreciate there's alot of change going on in that 5 year period to inform near term, but there's a danger we are also missing things too. | From statistical point of view the larger the sample size is the better representative for analysis. We understand GB power system and markets have changed significantly especially in recent years. Data from more than 5 years back might not represent current system dynamics and risks. Also the data requisition and recording requirements have changed significantly which make our review back to more than 5 years difficult. For simultaneous events analysis if the calibrated risk is higher than our previous assumptions, we will update the risks in the model to ensure that the assumptions we used in the model reflect the recent system conditions. We will continue reviewing this in future FRCR assessment and update the statics and volume in the model.
Looking forward, what are the risks of operating a lower inertia clean power system? Will these risks be covered via grid forming, pathfinders and more dcrm procurement? | Running system at a lower inertia will bring challenges bigger than frequency control, and they are being addressed indeed by things like the Stability Pathfinders (including grid forming technology and new synch comps being introduce in the system) and other technologies under zero carbon operation. Within NESO we have teams and expertise in those operability workstreams working on understanding the risks and proposing approaches to tackle them.
The analysis of BMU losses appears to have used half hourly data only. Would this mis any events where the plant trips and returns to service in less than half an hour? Is there any automated analysis of operational metering data looking for short duration trips and coincident tripping? | A quick trip-return would not affect BMU profiles, as they are based on the average PN during a Settlement Period (SP). The quick trip-return events within a SP or adjacent SPs may not be reflected in the MEL in the operational data or REMIT reports from which we derive BMU failure rates, so there could be a gap, but this is the most available data we have. It's also worth mentioning that FRCR policy always recommends covering all BMU faults, and the residual risks are from BMU+VS and simultaneous events. The gap from per SP profile does not affect the system risk and the policy direction.