## Sheet1
|  | Existing |  | Requested |  | TIA Required?
| Example Scenario | Installed Capacity | Export Capacity | Installed Capacity | Export Capacity | Installed capacity as criteria | Export capacity as criteria | Outcome check
New projects | New DG connection eg 4MW | 0 | 0 | <5MW | <5MW | No | No | same
| New DG connection eg 6MW | 0 | 0 | ≥5MW | ≥5MW | Yes | Yes | same
| New DG connection with reduced export eg 6MW installed but 3MW export | 0 | 0 | ≥5MW | <5MW | Yes | No | different
Changes to existing projects currently under both thresholds | Existing project 2MW to increase to 4MW for both | <5MW | <5MW | <5MW | <5MW | No | No | same
| Existing project 2MW to increase to 6MW for both | <5MW | <5MW | ≥5MW | ≥5MW | Yes | Yes | same
| Existing project 2MW to increase to 6MW installed but 4MW export | <5MW | <5MW | ≥5MW | <5MW | Yes | No | different
Changes to existing projects currently over both thresholds | Existing project of 6MW for both | ≥5MW | ≥5MW | ≥5MW | ≥5MW | Yes | Yes | same
Changes to existing projects currently over installed only | Existing project 6MW installed but 2MW export, no new installed but export increasing to 4MW | ≥5MW | <5MW | ≥5MW | <5MW | Yes | No | different
| Existing project 6MW installed but 2MW export, increasing installed to 8MW and export increasing to 4MW | ≥5MW | <5MW | ≥5MW | <5MW | Yes | No | different
| Existing project 6MW installed but 2MW export, increasing installed to 8MW and export increasing to 6MW | ≥5MW | <5MW | ≥5MW | ≥5MW | Yes | Yes | same
Notes.
Existing projects would cover already connected or changes to contracted not yet connected
These are the options assuming no fault level issues at GSP
These situations would also apply to existing demand connections adding generation