## Sheet1
Category | Example Scenarios |  | Existing |  | New |  | TIA Required? |  | Outcome check
|  |  | Installed Capacity | Export Capacity | Installed Capacity | Export Capacity | Installed capacity | Export capacity
A new generation connection | 1 | New generation connection with 4MW export capacity | N/A | N/A | 4MW | 4MW | No | No | Same
| 2 | New generation connection with 6MW export capacity | N/A | N/A | 6MW | 6MW | Yes | Yes | Same
| 3 | New generation connection with 6MW installed capacity but only 3MW export | N/A | N/A | 6MW | 3MW | Yes | No | Different
Changes to an existing connection with both export and installed capacities below the 5MW threshold | 4 | Existing connection with 2MW export capacity increasing to 4MW | 2MW | 2MW | 4MW | 4MW | No | No | Same
| 5 | Existing connection with 2MW export capacity to increasing to 6MW | 2MW | 2MW | 6MW | 6MW | Yes | Yes | Same
| 6 | Existing connection with 2MW export capacity increasing to 6MW installed capacity and 4MW export capacity | 2MW | 2MW | 6MW | 4MW | Yes | No | Different
Changes to an existing connection with both export and installed capacities above the 5MW threshold | 7 | Existing connection with 6MW of export increasing to 8MW | 6MW | 6MW | 6MW | 8MW | Yes | Yes | Same
Changes to an existing connection with installed capacity only above the 5MW threshold | 8 | Existing connection with 6MW installed capacity but only 2MW export increasing to 4MW export | 6MW | 2MW | 6MW | 4MW | Yes | No | Different
| 9 | Existing connection with 6MW installed capacity with 2MW export increasing installed capacity to 8MW and export capacity to 4MW | 6MW | 2MW | 8MW | 4MW | Yes | No | Different
| 10 | Existing connection with 6MW installed capacity with 2MW export, increasing installed capacity to 8MW and export capacity to 6MW | 6MW | 2MW | 8MW | 6MW | Yes | Yes | Same
Changes to an existing connection wanting to reduce capacity | 11 | Existing connection with 6MW of export capacity reducing to 4MW of export capacity | 6MW | 6MW | 4MW | 4MW | No | No | Same
| 12 | Existing connection with 6MW of both export and installed capacity reducing export capacity to 4MW | 6MW | 6MW | 6MW | 4MW | Yes | No | Different
Assumptions:
The term "existing connection" means sites which are already energised or are have a contracted DNO connection offer but not yet energised
All of the scenarios listed assume that there are no fault level issues at GSP, where fault level issues are known the connection can not be energised until such time as rectified
All of the scenarios listed also apply to existing demand connections seeking to add generation