## Sheet1
Category | Example Scenarios |  | Existing |  | New |  | TIA Required? |  | Outcome check
|  |  | Installed Capacity | Export Capacity | Installed Capacity | Export Capacity | Installed capacity | Export capacity
A new generation connection | 1 | New generation connection with 0MW export capacity | N/A | N/A | 4MW | 0MW* | No | No | Same
| 2 | New generation connection with 6MW installed capacity and 0 MW export capacity | N/A | N/A | 6MW | 0MW* | Yes | No | Different
Changes to an existing connection with 0 MW export and installed capacity below the 5MW threshold | 3 | Existing connection with 2MW installed capacity increasing to 4MW | 2MW | 0MW* | 4MW | 0MW* | No | No | Same
| 4 | Existing connection with 2MW installed capacity increasing to 6MW | 2MW | 0MW* | 6MW | 0MW* | Yes | No | Different
Changes to an existing connection with 0 MW export capacity and installed capacity above the 5MW threshold | 5 | Existing connection with 6MW installed capacity increasing to 12MW | 6MW | 0MW* | 12MW | 0MW* | Yes | No | Different
NOTE: * An ENA Engineering Recommendation G100 (EREC G100) Export Limiting Scheme will be installed to limit the export from customer's site to 0 MW.
Assumptions:
The term "existing connection" means sites which are already energised or are have a contracted DNO connection offer but not yet energised
All of the scenarios listed assume that there are no fault level issues at GSP, where fault level issues are known the connection cannot be energised until such time as rectified
All of the scenarios listed also apply to existing demand connections seeking to add generation