## Slide 1: Interconnector Ramping CBA
28 04 2023
NG - ESO
Report Presentation

## Slide 2: Agenda
Agenda Items |  | Items to share
 | Introduction | Team introductions - Ronan Project background and Scope - Ronan
 | Background | Review of Project Plan - Ronan High Level overview of methodologies utilised - Meerav Options and Shortlisting - Ronan
 | Methodologies utilised | Ramp Management Balancing Costs - Meerav PLEXOS modelling - Josh Cost Benefit Analysis (CBA) – Josh/Alex
 | Project conclusions | Results and conclusions – Alex/Ronan Q&A - All

## Slide 3: Project Purpose

## Slide 4: Project Background and Scope
Background | Ofgem has requested the ESO raise a Grid Code modification to include interconnector ramping within GB frameworks to be fully compliant to SOGL Article 119 after EU-Exit Current arrangements allow interconnectors to ramp at 100MW/min. The combined swing size and ramp rate of these interconnectors may be causing operational costs and difficulties for the control room to manage efficient consumer cost and system security GB has five interconnectors connected between UK and Continental Europe today. With up to 8 continental interconnectors are expected by 2035 The ESO wish to review interconnector ramping arrangements before submitting their Grid Code modifications to ensuring a safe and secure transmission system whilst delivering consumer value
Scope | Overall scope: conduct a Cost-Benefit Analysis to indicate which option the ESO should opt to include in their Grid Code modification Step 1: Confirm our overall methodology and socialise with the ESO and industry stakeholders Step 2: Shortlist options using a structured methodology with the ESO and WG Step 3: Utilise PLEXOS and other bespoke modelling to determine I/C flows, ramp rates, costs to various defined parties (inc. Ramp Management) Step 4: Combine and evaluate costs in our CBA framework, with the following groups considered: interconnectors, consumers, ESO
We conducted an independent Cost-Benefit Analysis to assist an upcoming Grid Code modification

## Slide 5: Project Plan

## Slide 6: Project Timeline
Our independent CBA engaged stakeholders across the ESO and industry (via Working Group 0154)
04/01- 22/01
Develop and finalise CBA methodology
Shortlisting
Modelling + CBA Analysis
Prepare + Present Report
23/01- 03/02
03/02 – 21/04
21-28 /04
Actions | Engagement
Worked with the ESO to confirm the core components of each option Identified publicly available data sources to support our assessment Determined our data driven approach on how to quantify the costs and benefits of the option | Internal ESO methodology update (11/01) ESO data workshop (16/01) Methodological approach presented at Working Group 7 (18/01)
Developed a list of criteria to shortlist options Iterated shortlisting criteria with the ESO in a series of workshops Conducted an internal scoring session to evaluate options using expert judgement and other qualitative evidence to shortlist c.3 options Held a review and challenge session on our scoring with the ESO Co-created alternative options based on feedback from ESO and WG (see slide 11) | ESO shortlisting criteria workshops (19 + 26/01) Baringa shortlisting session (26/01) ESO challenge + review session (31/01) Shortlisting outcomes review held with Working Group and facilitated their feedback and input to final Options Working Group 8 (09/02)
Agreed key balancing cost modelling assumptions with ESO, including the price scenarios and interconnector connections to use in our PLEXOS model Conducted analysis detailing the average ramp rate, frequency of high ramp events and impacts on balancing costs on the different options Conducted PLEXOS modelling on the different options over a set time horizon Estimated interconnector revenues (with no imbalance costs provided) Conducted qualitative analysis on implementation and operational costs Determine CBA results based on monetised and non-monetised costs and benefits | ESO CBA + ramp mgmt. cost workshop (22/02) Discussion on alternative options at Working Group 9 (23/02) ESO ramp mgmt. balancing cost workshop (21/03) Presented proposed options to model at Working Group 10 (22/03) Working Group feedback incorporated into final option design
Finalise the report and present our findings to ESO and the Working Group | ESO + Ofgem Internal Report (28/04) Working Group Session 11 (09/05)
Note: Weekly project management update calls were held with the ESO

## Slide 7: Methodology Overview

## Slide 8: Methodology Overview
  To model interconnector flows we used our internal PLEXOS Pan-European Day Ahead model at 15 minute granularity
  This model is regularly used by industry and uses a set of base assumptions (see appendix C)
  This was used to determine:
    IC flow volumes (MW)
    IC Revenues (£)
    Social Economic Welfare (£)
    Wholesale prices (£/MWh)
    Carbon impact (gCO2/MW)
  Created a bespoke approach to model balancing costs
  This accounted for Reserve, Repositioning, Response and Frequency Control actions
  We used 2022 data to determine volume of average action per given swing magnitude, noting costs would be distorted by market effects
  We found a strong non-linear correlation (0.98) between I/C swings and volume (MW) of BOAs + ASDP instructions
  We used a line of best fit to extrapolate volume required
  To calculate ramp management balancing costs, we multiplied projected wholesale price * VOL Balancing Services required based on swing projection
Pan-European Day Ahead Model
Ramp Management Balancing Costs
Our CBA used inputs from PLEXOS and bespoke Ramp Management Balancing cost modelling
Cost Benefit Analysis
  We designed a CBA tool to evaluate costs from PLEXOS and Ramp Management Balancing
  Qualitative non-monetised costs were added from additional analysis
Refine Options
  From our shortlist, we defined our options in further detail

## Slide 9: Refine Options
The following options were agreed – noting implementation method is out of scope in this analysis
Baseline: Keep current ramp rate (100MW/min)
2C
Use existing ramp rate for continental I/Cs (100MW/min). All other interconnectors use their default rates (e.g., EWIC, Moyle, NSL).
Ramp Management
(Curtail Ramp Rate based on Swing Size)
1A
Use existing ramp rates for continental I/Cs (100MW/min) with a reduction of ramping rates at anticipated points of system stress. For modelling this is defined by a 3500MW+ total swing. All other interconnectors use their default rates (e.g., EWIC, Moyle, NSL).
Static Lower Ramp Rate
(50MW/min)
2B
Change continental interconnector base rate ramp limit to match generators (50MW/min). All other interconnectors use their default rates (e.g., EWIC, Moyle, NSL).
Dynamic Ramp Rate Periods
(100MW/min <-> 50MW/min)
3.1
Ramp rate changes to meet system needs. Base ramp rate set at 50MW/min with increased ramp rates made available when system conditions allow for this (raised to 100MW/min at certain time periods for import or export based on anticipated demand movement). All other I/Cs use their default rates (e.g., EWIC, Moyle, NSL).

## Slide 10: Options and Shortlisting

## Slide 11: Options Considered for Shortlisting
We refined options developed by the Working Group which were subsequently presented for shortlisting
Ramp Mgmt Tools
Ramping arrangements
Market Based Solutions
1
2
3
a) TSO Ramp Management
b) TSO-TSO arrangements
a) Dynamic ramp rate
b) Static ramp rate
c) Static ramp rate (status quo)
a) Procure increased Frequency response
b) Base rate set for all IC and a market would be created for IC to participate
c) Create a ramping market
Option
Overarching Options
Use the existing ramp rates in Interconnector agreements and add to the Grid Code. Use Ramp Management agreements that are in tripartite agreements (not necessarily in all current agreements)
Use the existing ramp rates in Interconnector agreements and add to the Grid Code. Utilise European balancing platforms to allow for optimisation of products in the market when simultaneous fast ramping requires counteraction. Additional trading would be informed by day-ahead reference programmes.
Base ramp rate of 50MW allocated to all Interconnectors. Additional ramping to be made available based on day ahead forecasting of up to 250MW with a max ramp rate of 100MW. The additional ramping is based on the rate of change of demand forecast.
Change interconnector base rate ramp limit to match generators (50MW/min). Evaluate and then further compare effect of alternative rates.
Interconnectors currently connected to the system have a ramping maximum of 100MW - continue with this rate. This represents our proposed baseline.
ESO to hold sufficient Frequency Response to facilitate up to 100MW/min interconnector ramping. This will take into account FRCR policy.
Each IC gets a ‘banked’ 50 MW, and the extra 50 MW is multiplied across the number of ICs, then a market is run for this availability. The IC to choose if they wanted to be in that market. As this is a variant of 2a+2b, this option will require further analysis.
ESO to set up a “ramping market” where, based on the day ahead position of trade and risks estimated across ramping transition a volume dependent escalating ramping price is identified reflecting the costs incurred in operating the GB system, which allows the benefits of offsetting that position to be reflected by those offering flexibility to mitigate it whether interconnectors or other providers
Description

## Slide 12: Our Shortlisting Process
An initial long list of shortlisting criteria was presented to the WG, this was then iterated and further refined based on feedback provided (see right for final criteria)
Baringa conducted an internal scoring session followed by a challenge and review session with the ESO
The outcome of both these sessions was presented back to the WG
During this session we indicated our provisional recommendations for options that should be modelled further in detail:
  Option 2C – keeping ramp rates at 100MW/min as the base case for other options to be compared against as this is the status quo
  Two other options for detailed analysis emerged from the scoring undertaken i.e., Option 2B and Option 3A
Following feedback from the Working Group, additional time was taken to enable the WG to select its preferred options. The WG preference was for Option 1A and 3A.
Following additional refinement and reflection of Option 3 (on further analysis Option 3A was deemed out of scope) elements of 3A/B/C were combined to create Option 3.1
Therefore, Option 1A, 2B, 2C (becomes base case), and 3.1 were taken into the analysis stage
We conducted a structured process to shortlist 3 options to review against the base case

## Slide 13: Balancing Costs for IC Ramp Management

## Slide 14: Ramp management actions
Typical ESO actions to manage anticipated ramping within the system
IC ramp
Only required if normal actions are insufficient
Frequency control actions
Short duration
Potentially high cost
Re-positioning BOAs
Ramps against ramp
Cover energy imbalance
Additional regulating reserve
Uncertainty
Additional Response
Normal
actions
Additional actions
Additional balancing costs
Potentially set Settlement Period £/MWH
ESO Actions
Impacts
Interconnectors
Additional voltage support
Requirement during certain system conditions (typically in SE England)
System security cost
Additional balancing costs
System security cost
Additional balancing costs
We mapped various ESO actions to manage interconnector ramping and their associated impacts

## Slide 15: Balancing Costs Methodology
To assess affect of ramping on Balancing actions we explored the existing relationship between high ramp rates and volume of Balancing actions required to manage the ramp
Using public data, we developed an approach to calculate the volume of Repositioning, Response, Frequency Control and other short term energy actions needed for a given average cumulative ramp rate
We found a statistically significant relationship exists based on reviewing actions +/- 15 mins to each hour compared to actions taken outside that time
We further developed a methodology to calculate long-term reserve (where actions needed to be taken between 15-45 mins before an I/C swing) using operational experience
Our methodology is described in further detail in Appendix A
Note: We have used datasets which can be publicly sourced in our analysis (e.g., ESO Data Portal, ElecLink, RNP)
We used various public datasets to assess the relationship between I/C Ramping and Balancing actions
Calculate the volume of Balancing actions required for Ramp Management in 2022 using public data and operational insights
Assess whether a relationship exists between volume required and I/C average ramp rate
Apply this relationship to our DA I/C modelled flows 2023-2030
Input estimated Balancing Costs into CBA
A statistically significant correlation was found

## Slide 16: Two analytical concepts used
Highlighting two key methodological concepts used to calculate Ramp Management Balancing Costs
Sub-settlement periods |  | To determine affect of I/C swings on Response, Frequency Control and other short-term actions we divided each hour into four sub-settlement periods 15-minute granularity has been chosen to capture difference between GREEN periods where we expect little cost affect of I/C swings and BLUE periods where we expect costs to be affected by swings
Average Total Ramp Rate |  | Interconnectors over 2022 ramp at different times e.g. IFA2 and ElecLink ramped evenly over +/- 10 mins compared to NEMO and Britned that ramped at 100 MW/min for a certain duration. All can spill if ramping over 1000MW across 10 mins We need to determine the total average ramp rate to assess how costs across sub-settlement periods differed based on ramp rate Using contractual principles and operational experience we calculated an average ramp rate that would be experienced over 10 mins (+/- 5 mins to each hour) This method incorporates swing size and duration – as such we believe it is the best estimate we can use however it may dampen the affect I/Cs could have on Balancing Costs
Avg ramp rate
I/C 1
I/C 2
I/C 3
- 5mins
+ 5mins
MW/min

## Slide 17: Our Methodology
We used both historical data and operational experience to determine Balancing actions required
Outputs
Analysis
BOA Data
(Categorised based on instruction time across 96 sub-SPs)
ASDP Data
(Categorised based on instruction time across 96 sub-SPs)
Inputs
Determine average cost for each sub-settlement period
Calculate repositioning cost for each action
Repositioning
Filter BOAs for repositioning bids (excluding “Response”, “System”, “Constrained Loss”)
Response
Filter BOAs for “Response” bids. Exclude any actions <5 mins
Determine average cost for each sub-settlement period
Calculate response cost for each action
Freq Control
Filter BOAs for <5 mins duration
Determine average cost for each sub-settlement period
Calculate cost for each action
Filter ASDP for “Fast Response” and “STOR”
Determine average cost for each sub-settlement period
Calculate cost for each action
Reserve
Establish with operation teams how much reserve would be required for a given swing size and ramp rate. Note the duration of time reserve is required varies on swing size
Design equation to calculate this Reserve required.
Average cost of reserve per given I/C swing
Operational expertise
Average volume of balancing services per sub-settlement period in 2022 based on swing intervals of 400MW
Average volume of balancing services per average ramp rate experienced in 2022

## Slide 18: Relationships existed for Repositioning, Response and Frequency Control Actions
Balancing service procurement costs and volumes were correlated to the average total ramp rate
Volume
Cost
Total Ramp Rate (MW/min)
Total Ramp Rate (MW/min)
Balancing Actions (MW)
Balancing Costs (£)
*Note only 13 swings occurred over 300-450MW/min. As such these results have been removed from analysis to ensure data reliability

## Slide 19: Reserve Calculation
Due to the complexity of ramp management, it is not always possible to untangle the reserve requirement due to interconnectors from other activities
Therefore, we have reviewed the theoretical basis for requiring reserve to cover uncertainties (inc. energy imbalance)
For any 700MW swing across continental I/Cs, this additional reserve would be procured within +/- 15 mins of a swing and last less than 30 mins. As such it would be captured by our existing methodology
However, for overall swing sizes between 700MW – 4000MW additional reserve would be required
All swings above 4000MW would follow the same calculation as 4000 MW
This would match the total I/C ramp rate, as this would be the anticipated reserve volume requirement
Operational experience helped informed the way we calculated Reserve requirements
700MW Swing | 
2350MW Swing | 
4000MW Swing | 

## Slide 20: Balancing Cost Analysis
Repositioning, Response, Frequency Control + Short-term energy actions
Reserve
Applying our methodology to an example interconnector swing
Example swing
Time | IFA | NEMO | BritNED | IFA2 | Eleclink | Total
00:00 | -1000 | -500 | 700 | 1200 | 0 | 400
01:00 | 2000 | 500 | 0 | 1500 | 650 | 4500
Swing | +3000 | +1000 | -700 | +300 | +650 | 4100
Avg Ramp Rate (+/- 5 ms) | 100 MW/min | 100 MW/min | -70MW/min | 30 MW/min | 65MW/min | 225 MW /min
4000MW +
Swing
Overall Balancing Volume Required = 569 MW |Wholesale Price £200/MW | Overall Cost £113,800
Total volume
289 MW
Total volume
Balancing Actions = Time * Ramp Rate = 1.25hrs * 225 MW/mins = 281 MW
See detailed methodology in appendix
Balancing action volume calculated from relationship seen in 2022 between average total ramp rate and balancing actions taken.
Swing <700MW: Additional reserve would be procured within +/- 15 mins and be captured in “other energy actions” on left
Swing 700 – 4000 MW: additional plant needs to be procured at a longer timescale. Linear relationship between procuring 15 mins before and after to 25 mins before and 30 mins after
Swing 4000 MW+: Control room seek to procure reserve for max time

## Slide 21: Balancing Actions Baseline Results
 |  | 2023 | 2030
Ramp Rate (MW/mins) | 0 | 1806 | 2585
 | 0 – 50 | 2332 | 1785
 | 50 – 100 | 1688 | 1339
 | 100 – 150 | 1087 | 754
 | 150 – 200 | 713 | 634
 | 200 – 250 | 421 | 432
 | 250 – 300 | 278 | 409
 | 300 – 350 | 151 | 233
 | 350 – 400 | 146 | 216
 | 400 – 450 | 49 | 134
 | 450 – 500 | 89 | 88
Summary Stats | Avg Ramp Rate | 89 | 104
 | Avg Price (£/MW) | £221 | £60
 | Overall Cost (£) | £388m | £168m
Our analysis shows that the average cumulative ramp rate increases from 2023 to 2030
We find that the spread of interconnector ramp rates increases in 2030:
ICs more 50% more likely to have higher ramp rates above 250MW/mins
Yet simultaneously the overall probability ICs do not swing increases by 9%
Smaller ramp rate probability decreases
Whilst the average cumulative ramp rates increases, the overall Balancing costs fall due to the wholesale price of energy

## Slide 22: Applying ESO Ramp Management Costs to Modelled Flows
Calculate the Total Ramp Rate and Swing Size for each hour (2023-2030)
Determine volume of Balancing actions required
Apply Wholesale GB Price to calculated volume
1
2
3
Using PLEXOS modelled I/C hourly positions we determine the total swing size of continental I/Cs and the total ramp rate (using same methodology outlined in “Our Methodology” slide)
Response, Frequency Control and Repositioning Reserve: we use a cost lookup table based on total ramp rate intervals of 50MW
Reserve: apply our formula to determine the length of time Balancing actions need to be procured
We apply modelled PLEXOS wholesale GB prices to Balancing actions volumes
These are the best estimated prices that are likely to be experienced
We acknowledge this may not fully reflect the premium paid to procure energy closer to real-time (based on experience this could be up to 10%)

## Slide 23: PLEXOS Modelling of Options

## Slide 24: Capacity and generation mix – Reference Case
Our modelling scenario is underpinned by our assumptions on new generation capacity build and retirement
Chart: 
 | 39227.356 | 28795.7095 | 24193.596 | 24504.674 | 24954.909 | 13644.5125 | 21882.559 | 33051.664
 | 10685.6882 | 6101.0816 | 0 | 0 | 0 | 0 | 0 | 0
 | 75867.3632 | 65656.3845 | 65906.5167 | 73282.9841 | 68261.5374 | 71131.2373 | 59798.4576 | 56561.8475
 | 62.2272 | 50.976 | 13.6138 | 5.3941 | 2.566 | 3.1308 | 5.3167 | 11.8272
 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
 | 6422.0851 | 6474.3383 | 6484.0082 | 6502.0995 | 6514.9527 | 6549.8703 | 6509.5071 | 6516.084
 | 54665.0359 | 55849.4536 | 55837.3428 | 55632.006 | 40682.1403 | 32744.1481 | 32201.4579 | 32583.8325
 | 33819.2195 | 37707.7712 | 43299.5451 | 49563.3807 | 52665.8361 | 54157.1684 | 54467.249 | 55774.5162
 | 57925.1473 | 69351.4006 | 81263.825 | 95610.6102 | 111678.5806 | 131435.8958 | 143039.0899 | 148659.4747
 | 13734.0494 | 15300.8132 | 17148.5648 | 19627.5435 | 20730.7543 | 21456.6154 | 22168.9809 | 22922.3335
 | 354.7903 | 484.4959 | 608.0758 | 710.5365 | 824.0451 | 911.5503 | 974.6663 | 1044.3864
 | 2890.2315 | 3163.6585 | 3433.3962 | 3401.7523 | 3564.8076 | 3633.0847 | 4452.0595 | 5972.1133
Chart: 
 | 5873 | 5873 | 3538 | 3538 | 3538 | 3538 | 2798 | 4398
 | 3764 | 1500 | 0 | 0 | 0 | 0 | 0 | 0
 | 35927.4079 | 35803.1899 | 36628.3499 | 34914.8997 | 33532.3499 | 33632.3499 | 32327.0686 | 30086.9686
 | 1471.94 | 1506.47 | 1480.49 | 1103.8 | 877.8 | 877.8 | 877.8 | 877.8
 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
 | 2016.7 | 2026.7 | 2036.7 | 2046.7 | 2056.7 | 2066.7 | 2076.7 | 2086.7
 | 7263.1 | 7688.7 | 7788.7 | 7888.7 | 7988.7 | 5200 | 4655 | 4755
 | 13518.79 | 14793.78 | 16730.01 | 19041.81 | 20241.8 | 20916.8 | 21441.79 | 21966.79
 | 14302.39 | 16780.79 | 19476.79 | 22737.39 | 26405.39 | 30895.4 | 33851.39 | 35251.39
 | 14241.72 | 15841.73 | 17791.72 | 20391.72 | 21591.74 | 22366.75 | 23266.08 | 24165.42
 | 124.5 | 169.5 | 214.5 | 259.5 | 304.5 | 349.5 | 394.5 | 439.5
 | 2827.6 | 2827.6 | 2827.6 | 2827.6 | 3127.6 | 3127.6 | 3127.6 | 3827.6
0
50
100
150
  200
Capacity (GW)
Capacity mix (Reference Case)
Generation mix (Reference Case)
0
100
200
500
300
400
2030
2023
Generation (TWh)
2024
Biomass CCS
Gas CCS
Hydrogen
Battery Storage
Pumped Storage
Wind Onshore
Solar
Wind Offshore
Hydro
Oil
Gas
Coal
Nuclear
2025
2026
2027
2028
2029
2030
2023
2024
2025
2026
2027
2028
2029
The charts opposite show annual capacity and generation mix in GB in the Reference Case.
Investment and closure decisions drive changes in the capacity mix and in our modelling are based on a combination of national policy ambition or decisions, and the economics of individual units and generators in the market (i.e. a generator will close where it can no longer cover its costs from market revenues).
In GB, wind and solar capacity increases significantly due to CfD support for offshore wind in the near term. We project wind capacity (onshore and offshore) to more than double from 27 GW in 2023 to 57 GW in 2030. Solar capacity also increases significantly, from 14 GW in 2023 to 24 GW in 2030.
Coal-fired generation is phased out by the end of 2024 despite some short-term delay to closures. There are also significant closures of existing gas capacity leading to a downward trend in the contribution of gas to both the capacity mix and generation. This, combined with increasing peak demand, is projected to lead to lower capacity margins.
A range of technologies are built in the Reference Case, including gas CCS, gas engines and batteries, to meet the target capacity margin of approximately 3% to 5% in the medium to long term. Some existing biomass capacity is converted with the addition of CCS in the late 2020s and nuclear capacity also increases from the late 2020s.
By 2030, 75% of generation comes from wind, solar, biomass, biowaste and hydro.

## Slide 25: Interconnector capacity – Reference Case
GB interconnection capacity is assumed to increase from 8.4 GW in 2023 to 13.1 GW by 2030
  In the short-term, new capacity build in the Baringa model is based on information on project status and progress, and profitability of each project over the assumed lifetime (in the long-term we rely on economic assessment alone). Our view is developed based on iteration of capacity build on each border. Where price differentials, and the resulting revenue for a new interconnector are sufficiently large to incentivise investment, we take this as a market signal for new investment.
  Great Britain currently has an import and export capacity of 8.4 GW.
  The capacity of interconnection is expected to increase in the future as existing projects in the pipeline come online supported by positive economics due to the hourly price differentials between markets.
  Export and import capacity is assumed to increase to 13.1 GW by 2030 in the Reference Case. This is due to additional interconnection capacity with France and adding new interconnection capacity with Denmark and Germany. The NeuConnect interconnector with Germany is now projected to become operational by 2028.
  We note that there are a number of additional projects that may come forward in Ofgem’s Cap and Floor window 3 which have not been modelled explicitly in this study. Our approach to date has been to consider medium-term projects based on project economics rather than picking winners from the range of projects currently in the pipeline.
Chart: 
| 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
FR | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5.4
IE | 0.95 | 0.95 | 0.95 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45 | 1.45
BE | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
DE | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 1.4 | 1.4
DK | 0 | 0 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
NL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NO | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Reference Case – GB export capacity
Reference Case – GB import capacity
Cross-border capacity (GW)
Chart: 
| 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
FR | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5.4
IE | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
BE | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
DE | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 1.4 | 1.4
DK | 0 | 0 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
NL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NO | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4

## Slide 26: Our reference case
We use the yearly base assumptions below

## Slide 27: New interconnectors between 2023 – 2030 (study horizon)
Interconnector | Capacity (MW) | Connection Date in Model
Denmark | 1400 | 2024
Ireland | 500 | 2025
Germany | 1400 | 2028
France | 1400 | 2030
We make the following assumptions on new interconnector additions to GB
Please note this is based on our experience and does not reflect that we believe others will not be build and connected

## Slide 28: Modelling Outputs | Price results
New ramp rate options have very little impact on annual average wholesale prices across Europe
Dynamic Ramp Rate Option (3.1) vs status quo
TSO Ramp Management Option (1A) vs status quo
Country | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
BE | 0.00 | -0.01 | 0.02 | 0.01 | 0.01 | 0.03 | 0.02 | -0.01
DE | -0.01 | 0.00 | 0.02 | 0.01 | 0.00 | 0.03 | 0.02 | -0.01
DK W | -0.01 | 0.00 | 0.02 | 0.02 | 0.01 | 0.03 | 0.02 | -0.01
FR | 0.00 | -0.02 | 0.00 | 0.01 | 0.00 | 0.02 | 0.01 | -0.01
GB | -0.04 | -0.05 | -0.04 | -0.02 | -0.02 | 0.00 | 0.02 | -0.01
NL | -0.01 | 0.00 | 0.02 | 0.01 | 0.01 | 0.03 | 0.02 | -0.01
Static Ramp Rate Option (2B) vs status quo
Country | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
BE | 0.00 | -0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.01 | 0.00
DE | 0.00 | 0.02 | 0.05 | 0.00 | 0.07 | 0.02 | 0.01 | 0.00
DK W | -0.09 | 0.04 | 0.05 | 0.00 | 0.06 | 0.03 | 0.01 | -0.01
FR | 0.03 | -0.01 | 0.00 | -0.01 | 0.01 | 0.01 | 0.01 | -0.02
GB | 0.03 | -0.01 | 0.00 | -0.04 | -0.01 | 0.02 | -0.01 | -0.05
NL | 0.05 | 0.01 | 0.04 | 0.00 | 0.02 | 0.02 | 0.01 | -0.01
Country | 2023 | 2024* | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
BE | -0.02 |  | 0.03 | 0.01 | 0.01 | -0.04 | 0.01 | 0.01
DE | -0.01 |  | -0.01 | 0.00 | -0.03 | -0.03 | 0.01 | 0.00
DK W | 0.02 |  | 0.00 | 0.02 | -0.02 | -0.06 | 0.02 | 0.01
FR | 0.00 |  | -0.01 | 0.02 | 0.01 | -0.07 | 0.03 | 0.00
GB | -0.13 |  | -0.23 | -0.14 | -0.05 | -0.44 | 0.01 | 0.03
NL | -0.03 |  | 0.00 | 0.00 | 0.01 | -0.03 | 0.02 | 0.01
Static Ramp Rate Option (2C) – status quo
Country | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
BE | 213.71 | 165.45 | 130.02 | 95.08 | 90.60 | 81.53 | 73.33 | 67.33
DE | 187.86 | 157.54 | 126.47 | 94.74 | 90.58 | 82.67 | 74.60 | 67.90
DK W | 179.30 | 154.88 | 124.15 | 90.71 | 86.98 | 79.37 | 70.58 | 63.97
FR | 213.87 | 162.66 | 127.77 | 92.29 | 86.37 | 77.98 | 69.76 | 64.95
GB | 221.26 | 174.25 | 134.31 | 91.69 | 87.25 | 78.59 | 66.62 | 59.94
NL | 200.09 | 159.57 | 126.47 | 93.99 | 89.89 | 81.96 | 73.45 | 67.25

## Slide 29: Cost Benefit Analysis (CBA)

## Slide 30: CBA Framework
Our CBA framework combines various tools and datasets to capture a wide range of impacts on the ESO, GB and EU consumers, interconnectors and generators
Cost or benefit | Approach | Source
Consumer impacts | Difference in wholesale spot market prices in a given market under the baseline (e.g. 100 MW/min) and alternative option multiplied by total demand | PLEXOS modelling for consumer welfare, qualitative analysis for impact of options on interconnector investment
Producer impacts | Difference in wholesale spot market prices in a given market under the baseline (e.g. 100 MW/min) and alternative option, minus generation costs and multiplied by total generation | PLEXOS modelling for producer welfare
Interconnector impacts | Difference in net revenues realised by interconnectors, taking into account direct changes in revenue from ramp constraints and indirect changes from changes in market participant views of the value of interconnector capacity | PLEXOS modelling for interconnector welfare, qualitative analysis for impact on capacity value
Balancing costs | Additional costs incurred by the ESO associated with repositioning, frequency control actions and other response actions | Analysis of ESO costs
Implementation costs | Additional costs to the ESO and industry from the set up and ongoing costs of the alternative options relative to the baseline | Estimated implementation costs from ESO and interconnectors
Other quantified impacts | Broader impacts, for example from changes in emissions (MtCO2/yr) measured at the social cost of carbon | PLEXOS modelling plus HMG Green Book carbon values
Other non-quantified impacts | A range of potential costs and benefits, including impacts on security of supply and on connecting TSO market etc. | Qualitative review and analysis
Monetised, quantified and qualitative impacts for all options, with ranking/scoring of combined impact for each option
Identification of best performing option taking into account monetised, quantified and qualitative evidence, and proposals for refining the evidence base
Switching analysis – are the qualitative impacts sufficiently material to outweigh the quantified impacts?
Costs and benefits included in the CBA
Sensitivity analysis – how sensitive is the best performing option to changes in high impact assumptions?

## Slide 31: Modelling Outputs | Flow impacts
Changes in interconnector flows as a result of new ramping options are small
In the chart on the right imports are denoted as negative and exports are denoted as positive. Negative net flows indicate GB is net importer whilst positive net flows indicate GB is a net exporter.
The data labels show the differences between the 50MW/min option (2C) and the base 100MW/min option (2B). There are very small changes in flows between modelled options.
GB is a net importer in the first half of the modelled timeframe then switches to net exporter.
The modelling shows that the total flow volume increases with time across all ramping options. This is due to the increased price volatility induced by growth in renewable capacity over time.
We see that in the majority of years, the average impact of the new ramping rate enhances the net flow position i.e. GB becomes a stronger net importer in net importing years, and a stronger net exporter in net exporting years.
As shown previously, interconnectors can ramp both early and late in response to new ramp rate. As these behaviours are complex, the ultimate impact on import and export volumes is not a simple relationship.
Interconnector revenues can both gain and lose as a result of the new ramping characteristics. On an annual basis, sometimes gains cancel losses (and vice versa).
Interconnector revenues are driven by price differentials and flow volumes. As we see marginal changes across both metrics between the modelled options, the resulting impact on interconnector welfare in the CBA is very low.
Chart: Option 2C vs 2B: Flows
| 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
GB Imports | -28.1657 | -39.4232 | -38.0591 | -25.5568 | -27.0883 | -28.6962 | -24.8984 | -25.0535
GB Exports | 16.1397 | 14.1232 | 17.0598 | 28.9419 | 26.5955 | 32.31 | 39.8513 | 47.1995
GB Net Flows | -12.026 | -25.3 | -20.9993 | 3.3851 | -0.49271 | 3.6138 | 14.9529 | 22.146

## Slide 32: Modelling Outputs | Price impacts
Wholesale electricity price differentials are the key driver in producer and consumer welfare impacts
Compared to the baseline 100MW/min ramp rate, reducing the ramping rate to 50MW/min results in lower prices in GB in the majority of years across the modelled time frame.
It is important to recognise that the change in wholesale price is very small. Therefore on a relative basis, this has a low impact on overall welfare costs and benefits for producers and consumers.
When comparing the modelled options, if prices fall then consumers will benefit, however if prices rise then producers will benefit.
We can see in the modelling that prices in GB are lower in the first half of the modelled horizon, which means GB consumers gain. GB producers lose out as they are not able to earn as much per MWh of electricity sold.
In years 2028 and 2029, this dynamic changes temporarily, whereby GB experiences an increase in prices with the lower ramp rate. This benefits producers whilst consumers lose out.
In the early years, GB is a net importer. Reducing the ramp rate results in a larger volume of lower cost imports from surrounding markets due to the additional time taken to ramp up/down. This causes the GB wholesale price to fall.
Later in the horizon, GB becomes a net exporter and we see the same behaviour but in the opposite direction, therefore raising the GB wholesale price and switching the benefits from consumer to producer.
Chart: Option 2C vs 2B: Prices and Welfare
Price Differential GB | -0.040203 | -0.043166 | -0.037933 | -0.019418 | -0.015107 | 0.0017642 | 0.016753 | -0.0068648
Producer Welfare GB | -11.1391 | -9.3537 | -8.7337 | -1.8616 | -5.9252 | 2.5951 | 5.1572 | -4.1749
Consumer Welfare GB | 12.0341 | 9.6579 | 4.6627 | 0.87203 | 5.7978 | -2.929 | -6.2752 | 2.3322
Interconnector Welfare GB | 0.5081 | 0.43356 | 2.0999 | 0.41107 | 0.19835 | -0.057413 | 0.55279 | 0.12534

## Slide 33: CBA Outputs | Monetised impacts
Chart: Present value impacts (€m)
| Option 1A* | Option 2B | Option 3.1
GB consumer welfare | 221.3741 | 25 | 13
GB producer welfare | -268.3107 | -31 | -22
GB IC welfare | 9.6011 | 4 | 2
RoE consumer welfare | -129.3191 | -89 | -164
RoE producer welfare | -11.206 | 68 | 141
RoE IC welfare | 89.5545 | -2 | 24
Balancing cost savings | 582 | 989 | 911
NPV | 493.6938 | 964 | 905
All options analysed would deliver an overall net benefit to society over an 8-year horizon
NPV of options relative to Option 2C
Reducing the ramp rate provides and overall net benefit relative to maintaining the current 100 MW/min ramp rate. Moving to a 50 MW/min ramp rate (2B) results in a net benefit of €964m , introducing a dynamic ramp rate (3.1) results in a net benefit of €905m and moving to a ramp management option (1A) results in a net benefit of €494m*.
The main driver of the overall results is the balancing cost savings in both options. The net welfare impacts are close to zero when balancing costs are excluded from the monetised impacts.
In GB, consumer welfare increases over the modelling horizon as a result of the small reduction in GB prices under the 50 MW/min and ramp management options relative to the 100 MW/min option. Producer welfare moves in the opposite direction as the reduction in prices negatively affects generator revenues. The impacts are however marginal, with producer welfare impacts for example being equivalent to around 0.01-0.03% of overall producer welfare.
Interconnector welfare appears to increase slightly over the modelling horizon as the divergence in prices caused by a lower ramp rate outweigh any reduction in flows seen in some years.
This analysis only captures the costs and benefits that it has been possible to monetise through the PLEXOS modelling and balancing cost analysis. Other qualitative impacts need to be considered to get a complete picture on the CBA. In the following slides we show the overall impacts as a RAG assessment to combine both monetized, quantified and qualitative impacts.
*Results for option 1A to be finalised

## Slide 34: CBA Outputs
Key: | <£5m | £5-10m | >£10m | Minimal impact
Qualitative impact assessment
Qualitative | Description | Option 1A | Option 2B | Option 3.1
Security of Supply | A varied and technically diverse range of energy sources are required to ensure a high level of security of supply for the UK. The utilisation and growth of interconnectors are important part of the UK policy in this space, therefore any potential option proposed must ensure that this is not put this growth at risk. This growth needs to be balanced against its impact on the operability and security of the system from multiple Interconnectors ramping in the same operational envelope. This should also include any potential increase in the number of actions required to be taken by the System Operator to mange these ramps. |  |  | 
 |  | Small reduction on Operability Risks due to ability to request reduced ramp rate | Large reduction in Operability Risks by reducing the combined ramp rate | Reduction in Operability Risks due to SO ability to define periods of increased ramp rate
Implementation Cost | All options should be considered against any requirements that change the current process, system, therefore this cost of implementation need to be considered as part of the overall costs |  |  | 
 |  | Minor IT system changes to all parties | No change to current IT systems | Major IT systems changes to all parties
Impact on Interconnector investment | The ability to create a robust business case for investment in the growth of interconnector needs to be considered as part of this CBA. The chosen options need to consider the impact on the revenue that an Interconnector can make when analyzing the different options. If there is a significant fall in revenue then this may impact on any business case to invest in new interconnectors, this need to be balanced by ensuring that interconnectors do not make excessive profits at the expense of the end consumer. |  |  | 
 |  | Largest positive impact on GB IC revenues | Positive impact on GB IC revenues | Very slight positive impact on GB IC revenues
Note: Key for “Security of Supply and “Impact on Interconnector investment” are based on CBA results
“Implementation Costs” will benefit from additional analysis in the future based on further details on any implementation approach adopted

## Slide 35: CBA Outputs | Sensitivities
Due to the number of variables within any modelling technique when simulating over a long time horizon and allowing potential data inaccuracies it is normal to test the results over a range, for the purpose of this analysis a range of 80% to 120% was chosen. The range of results can be seen below. Even when allowing for this wide range
Balancing costs remain the main driver of the overall NPV
Small changes in assumptions on balancing costs could lead to material impacts
A reasonable low scenario would be 20% reduction, and there would still be a large net-benefit from reducing the ramp rate e.g., Option 2B
To allow for potential modelling and data inaccuracies
 | Option 2C 100MW €m | Option 1A Ramp Management €m | Option 2B 50MW €m | Option 3.1 Dynamic Ramping Periods €m |  | 1A vs. 2C (saving) €m | 2B vs. 2C (saving) €m | 3.1 vs. 2C (saving) €m
 | 1, 671 – 2,507 | 1,032 – 1,548 | 768 – 1,151 | 842 – 1,264 |  | 640 – 959 | 904 – 1,356 | 829 – 1,243
Note – see Appendix D for full Balancing Cost results

## Slide 36: Results and conclusions

## Slide 37: CBA Results
The qualitative costs and benefits are unlikely to be sufficiently large enough to outweigh the balancing cost savings from reducing the ramp rate or dynamic ramp rate periods
Cost or benefit | 1A | 2B | 3.1 | Comment
GB consumer, producer and IC welfare | -€37m* | -€2m | -€6m | GB consumer welfare increases under both 2B and 3.1 as a result of GB power prices falling slightly. The reduction in prices leads to a small reduction in producer welfare in both options. Interconnector welfare increases marginally as the reduction in interconnector flows is outweighed by changes in price differentials between GB and connected markets.
GB balancing cost savings | +€582m* | +€989m | +€911m | GB balancing costs fall significantly under both 2B and 3.1, and are the main driver of the positive net-benefit overall.
Rest of Europe consumer, producer and IC welfare | -€51m* | -€24m | €1m | Changing the ramp rate via the Options considered have a very small negative effect on EU consumer, producers and IC. Option 2B has a slightly worse effect than Option 3.1.
Implementation costs | Major IT changes required* | Negligible | Major IT changes required | There could be additional costs to the ESO, interconnector owners and other market participants from setting up and operating IT systems and processes. These costs are likely to be highest under 3.1. Under 2B on the other hand, there would be no implementation costs. Further analysis could be undertaken to quantify these costs if 3.1 is adopted.
Security of supply |  |  |  | Operability Risks are associate with the ability to manage and control large rapid system changes in a very short timescale on the Transmission system. The SO has a responsibility to ensure that system can accommodate a wide rage of different sources of energy and balance these Operability Risks against facilitating these energy sources.
Impact on interconnector investment | Limited* | Limited | Limited | The quantitative analysis suggests interconnector revenues could increase slightly with a lower ramp rate. This analysis does not capture the costs of imbalance. However, based on the evidence provided, this is not expected to materially affect investment decisions.
GB CO2 emissions savings | -231,000 tCO2* | -10,000 tCO2 | 28,000 tCO2 | GB carbon emissions increase slightly in 2B and decrease slightly in 3.1 as a result of changes in the generation mix. These changes in carbon emissions are captured at market prices within the estimates of Socio-Economic Welfare. Under the Governments social cost of carbon, these emissions impacts are equivalent to -£2m (2B) and £7m (3.1).
Cost £0-10m
Cost £10-100m
Cost >£100m
Benefit £0-10m
Benefit £10-100m
Benefit >£100m
Note: Slide has been updated

## Slide 38
This document: (a) is proprietary and confidential to Baringa Partners LLP (“Baringa”) and should not be disclosed to third parties without Baringa's consent; (b) is subject to contract and shall not form part of any contract nor constitute an offer capable of acceptance or an acceptance; (c) excludes all conditions and warranties whether express or implied by statute, law or otherwise; (d) places no responsibility on Baringa or its group companies for any inaccuracy or error herein as a result of following instructions and information provided by the requesting party; (e) places no responsibility for accuracy and completeness on Baringa or its group companies for any comments on, or opinions regarding, the functional and technical capabilities of any software or other products mentioned where based on information provided by the software or product vendors; and (f) may be withdrawn by Baringa or its group companies within the timeframe specified by the requesting party and if none upon written notice. Where specific clients of Baringa or its group companies are mentioned by name, please do not contact them without Baringa's prior written approval. If any of these terms are invalid or unenforceable, the continuation in full force and effect of the remainder will not be prejudiced. Copyright © Baringa Partners LLP 2023. All rights reserved.

## Slide 39: Modelling Outputs | Flow Characteristics
Chart: 
| 47485.291666666657 | 47485.302083333343 | 47485.3125 | 47485.322916666657 | 47485.333333333343 | 47485.34375 | 47485.354166666657
100 MW/min | 1000 | 1000 | 1000 | 1000 | 0 | 0 | 0
50 MW/min | 1000 | 1000 | 1000 | 1000 | 250 | 53.1214 | 52.5019
Chart: Time of day
Ramping rates lag changes in flows, but summary flows don’t change significantly
A constrained event
Most events are observed at the beginning of an hour when the model presumes change in demand and renewable profiles
One day example of GB – NL interconnector flows
Possible options to meet the required constraint on GB side
Coupling time periods
Ramping event connects two time periods – the beginning and the end of the event
At the begining
Generators on GB side decrease their output and increase import
GB price falls
At the end
Generators on GB side increase their output and decrease import
GB price raises
Possible options to meet the required constraint on NL side
At the begining
Generators on NL side increase their output and decrease import
NL price raises
At the end
Generators on NL side decrease their output and increase import
NL price falls
Flow stops at 250 MW due to ramp rate

## Slide 40: Modelling Outputs | Price Characteristics
Chart: Time of day
Chart: 
| 47485.291666666657 | 47485.302083333343 | 47485.3125 | 47485.322916666657 | 47485.333333333343 | 47485.34375 | 47485.354166666657
100 MW/min | 113.5133 | 109.4548 | 107.5452 | 107.1942 | 107.2156 | 108.3123 | 108.4484
50 MW/min | 113.5133 | 109.4548 | 107.4358 | 99.0291 | 120.8702 | 106.8177 | 106.952
Prices form cardiogram curves, but average prices don’t change significantly
Prices
In most cases GB price is affected. In the ramping event from 07:45 to 8:00 GB price decreases at the beginning of the first time period increases at the end of the second time period
Impact on interconnectors
In Option 2B, Interconnectors are affected during both import and export directions In Option 3.1, Interconnectors are mostly affected in export directions The influence is expressed in terms of when a flow takes place, not in terms of what magnitude the flow has. It results in comparatively same flows between options. Ыame prices give overall insiginificant changes in interconnectors’ revenues.
One day example of GB prices

## Slide 41: Balancing Actions Baseline Results
 |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Ramp Rate (MW/mins) | 0 | 1806 | 1900 | 2187 | 1967 | 1981 | 2094 | 2393 | 2585
 | 0 – 50 | 2332 | 2184 | 1868 | 2120 | 1995 | 1742 | 1787 | 1785
 | 50 – 100 | 1688 | 1533 | 1505 | 1544 | 1489 | 1382 | 1324 | 1339
 | 100 – 150 | 1087 | 1015 | 973 | 953 | 915 | 909 | 826 | 754
 | 150 – 200 | 713 | 732 | 746 | 692 | 687 | 734 | 638 | 634
 | 200 – 250 | 421 | 474 | 512 | 465 | 492 | 530 | 474 | 432
 | 250 – 300 | 278 | 352 | 362 | 370 | 448 | 431 | 425 | 409
 | 300 – 350 | 151 | 226 | 221 | 233 | 267 | 284 | 256 | 233
 | 350 – 400 | 146 | 128 | 155 | 152 | 183 | 216 | 212 | 216
 | 400 – 450 | 49 | 83 | 78 | 90 | 95 | 135 | 148 | 134
 | 450 – 500 | 89 | 69 | 78 | 90 | 93 | 119 | 115 | 88
Summary Stats | Avg Ramp Rate | 89 | 97 | 99 | 100 | 106 | 117 | 109 | 104
 | Avg Price (£/MW) | £221 | £175 | £134 | £92 | £87 | £79 | £67 | £60
 | Overall Cost (£) | £388m | £359m | £ 286m | £212m | £228m | £244m | £203m | £168m
Our analysis shows that the average cumulative ramp rate increases year-on-year

## Slide 42: CBA Outputs | Quantitative
Changing GB interconnector ramp rates can be felt across the EU, with changing Carbon emissions
Total Reduction in CO2 emissions, 000 tonnes | Option 2C vs 2B | Option 2C vs 3.1 | Option 2C vs 1A*
GB | -10 | 28 | -231
FR | 2 | -17 | -6
BE | -10 | -13 | -15
DE | -3 | -97 | -30
DK | 0 | -1 | -5
NL | -15 | -33 | -20
Rest of Europe | 36 | -67 | -69
Total | 0 | -201 | -377