## Data Required from Unit
Data Source | Data | Data Format | Granularity | Data Range | Update Frequency | NESO Systems Use As | Note
Registration | Capacity | MWh | Static
| Charging Efficiency | % (0-100) | Static
| Discharge Efficiency | % (0-100) | Static
| SOC limit Positive | % (0-100) | Static
| SOC limit Negative | % (0-100) | Static
| Daily Cycle Limit | whole number | Static
| MWh Cycle Limit | MWh | Static
IEMS | SOC/SOE | % (0-100) | Static |  | sub minute
| MW Meter | MW | Static |  | sub minute
EDL/EDT | MEL | MW | 1 min | to D+1 05:00 | as required
| MIL | MW | 1 min | to D+1 05:00 | as required
| SEL | MW | 1 min | to D+1 05:00 | as required
| SIL | MW | 1 min | to D+1 05:00 | as required
| PN | MW | 1 min | to D+1 05:00 | as required
| Offer Price Bands | MW from-to | 1 min | to D+1 05:00 | as required
| Bid Price Bands | MW from-to | 1 min | to D+1 05:00 | as required
| RUR | MW/min (3 break points) | Static |  | as required
| RDR | MW/min (3 break points) | Static |  | as required
| MDO | MWh | 1 min | to D+1 05:00 | as required
| MDB | MWh | 1 min | to D+1 05:00 | as required
| NTO | min (0-2) | Static |  | as required
| NTB | min (0-2) | Static |  | as required
| NDZ | min (0-999) | Static |  | as required
Derived from tool given by Chris McLeod (Habitat)
Changed from 30 min SPs to mimute values
Calculation of Declared MDO/MDB added

## 1 - No BOA or PN
| BMU |  |  |  |  | Explanation
|  |  | Site: | EXAMPLE BESS |  | PN is zero throughout and no BOA has been accepted | [15 empty] | Input | --> user can configure Battery physical parameters, dispatch profile, BM acceptance, DFR contract commitment
|  |  | MW | MWh | [17 empty] | Calc | --> calculated fields such as expected SoC, DFR SoE envelope, MW headroom/footroom
|  |  | 100 | 50 | [17 empty] | Output | --> MWh MDVO/B profile
|  |  | Min SoC | Max SoC
|  |  | 0% | 100% | [12 empty] | 25 | [5 empty] | Delivery period / Real time
|  |  | Imp_eff | Exp_eff | [18 empty] | Gate Closure
|  |  | 95% | 95%
|  | SoC Limit: | Ok
Energy
| Date | [10 empty] | 30 min rule | 30 min rule | SoC | Day Ahead | Day Ahead | Change |  |  |  | Dynamic Response Contracts
| 2025-02-24 | [6 empty] | Instant | Instant | Declared | Declared | Battery | Battery | before | Declared | Declared | From | Cumulative | ESO Derived | ESO Derived | Low Service |  |  |  |  | Check | High Service
| Time |  |  |  | Battery MW (PN) | ESO MW (BOA) | SoC | MDB (MWh) | MDO (MWh) | MDB (MWh) | MDO (MWh) | MIL (MW) | MEL (MW) | BOAs | MDVB | MDVO | BOA | Change | MDB | MDO | DFR -LF MW | DFR MinSOC | DFR MWh | MW Headroom | Service | Flag | DFR-HF MW | DFR MaxSoC | DFR MWh | MW Footroom | Service
0:00 | 0:01 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:02 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:03 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:04 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:05 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:06 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:07 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:08 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:09 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:10 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:11 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:12 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:13 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:14 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:15 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:16 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:17 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:18 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:19 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:20 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:21 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:22 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:23 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:24 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:25 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:26 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:27 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:28 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:29 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:30 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:31 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:32 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:33 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:34 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:35 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:36 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:37 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:38 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:39 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:40 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:41 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:42 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:43 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:44 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:45 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:46 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:47 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:48 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:49 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:50 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:51 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:52 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:53 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:54 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:55 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:56 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:57 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:58 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:59 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:00 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:01 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:02 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:03 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:04 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:05 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:06 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:07 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:08 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:09 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:10 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:11 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:12 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:13 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:14 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:15 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:16 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:17 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:18 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:19 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:20 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:21 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:22 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:23 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:24 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:25 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:26 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:27 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:28 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:29 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:30 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:31 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:32 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:33 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:34 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:35 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:36 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:37 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:38 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:39 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:40 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:41 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:42 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:43 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:44 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:45 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:46 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:47 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:48 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:49 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:50 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:51 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:52 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:53 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:54 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:55 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:56 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:57 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:58 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:59 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:00 |  | SP4 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:01 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:02 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:03 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:04 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:05 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:06 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:07 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:08 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:09 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:10 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:11 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:12 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:13 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:14 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:15 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:16 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:17 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:18 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:19 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:20 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:21 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:22 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:23 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:24 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:25 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:26 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:27 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:28 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:29 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:30 |  | SP5 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:31 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:32 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:33 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:34 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:35 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:36 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:37 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:38 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:39 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:40 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:41 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:42 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:43 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:44 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:45 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:46 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:47 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:48 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:49 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:50 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:51 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:52 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:53 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:54 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:55 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:56 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:57 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:58 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:59 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:00 |  | SP6 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:01 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:02 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:03 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:04 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:05 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:06 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:07 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:08 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:09 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:10 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:11 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:12 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:13 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:14 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:15 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:16 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:17 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:18 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:19 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:20 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:21 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:22 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:23 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:24 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:25 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:26 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:27 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:28 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:29 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:30 |  | SP7 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:31 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:32 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:33 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:34 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:35 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:36 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:37 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:38 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:39 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:40 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:41 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:42 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:43 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:44 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:45 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:46 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:47 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:48 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:49 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:50 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:51 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:52 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:53 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:54 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:55 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:56 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:57 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:58 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:59 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 4:00 |  | SP8 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 47.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100

## 2- PN SP4
| BMU |  |  |  |  | Explanation
|  |  | Site: | EXAMPLE BESS | [17 empty] | Input | --> user can configure Battery physical parameters, dispatch profile, BM acceptance, DFR contract commitment
|  |  | MW | MWh |  | PN submitted in SP 4 | [15 empty] | Calc | --> calculated fields such as expected SoC, DFR SoE envelope, MW headroom/footroom
|  |  | 100 | 50 |  | MDB/MDO redeclared | [15 empty] | Output | --> MWh MDVO/B profile
|  |  | Min SoC | Max SoC
|  |  | 0% | 100% | [12 empty] | 25 | [5 empty] | Delivery period / Real time
|  |  | Imp_eff | Exp_eff | [18 empty] | Gate Closure
|  |  | 95% | 95%
|  | SoC Limit: | Ok
Energy
| Date | [10 empty] | 30 min rule | 30 min rule | SoC | Day Ahead | Day Ahead | Change |  |  |  | Dynamic Response Contracts
| 2025-02-24 | [6 empty] | Instant | Instant | Declared | Declared | Battery | Battery | before | Declared | Declared | From | Cumulative | ESO Derived | ESO Derived | Low Service |  |  |  |  | Check | High Service
| Time |  |  |  | Battery MW (PN) | ESO MW (BOA) | SoC | MDB (MWh) | MDO (MWh) | MDB (MWh) | MDO (MWh) | MIL (MW) | MEL (MW) | BOAs | MDVB | MDVO | BOA | Change | MDB | MDO | DFR -LF MW | DFR MinSOC | DFR MWh | MW Headroom | Service | Flag | DFR-HF MW | DFR MaxSoC | DFR MWh | MW Footroom | Service
0:00 | 0:01 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:02 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:03 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:04 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:05 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:06 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:07 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:08 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:09 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:10 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:11 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:12 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:13 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:14 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:15 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:16 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:17 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:18 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:19 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:20 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:21 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:22 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:23 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:24 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:25 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:26 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:27 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:28 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:29 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:30 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:31 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:32 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:33 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:34 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:35 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:36 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:37 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:38 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:39 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:40 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:41 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:42 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:43 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:44 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:45 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:46 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:47 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:48 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:49 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:50 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:51 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:52 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:53 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:54 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:55 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:56 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:57 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:58 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:59 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:00 |  | SP2 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:01 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:02 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:03 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:04 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:05 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:06 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:07 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:08 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:09 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:10 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:11 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:12 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:13 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:14 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:15 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:16 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:17 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:18 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:19 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:20 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:21 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:22 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:23 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:24 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:25 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:26 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:27 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:28 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:29 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:30 |  | SP3 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:31 |  | SP4 |  | 100 | 0 | 100% | 0 | 47.5 | 0 | 22.5 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:32 |  | SP4 |  | 100 | 0 | 96.49% | 1.8467 | 45.8333 | 1.8467 | 22.5 | -3.6934 | 91.6667 | 96.49% | 1.8467 | 45.8333 | 0 | 0 | 1.8467 | 45.8333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:33 |  | SP4 |  | 100 | 0 | 92.98% | 3.6934 | 44.1667 | 3.6934 | 22.5 | -7.3869 | 88.3333 | 92.98% | 3.6934 | 44.1667 | 0 | 0 | 3.6934 | 44.1667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:34 |  | SP4 |  | 100 | 0 | 89.47% | 5.5402 | 42.5 | 5.5402 | 22.5 | -11.0803 | 85 | 89.47% | 5.5402 | 42.5 | 0 | 0 | 5.5402 | 42.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:35 |  | SP4 |  | 100 | 0 | 85.96% | 7.3869 | 40.8333 | 7.3869 | 22.5 | -14.7738 | 81.6667 | 85.96% | 7.3869 | 40.8333 | 0 | 0 | 7.3869 | 40.8333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:36 |  | SP4 |  | 100 | 0 | 82.46% | 9.2336 | 39.1667 | 9.2336 | 22.5 | -18.4672 | 78.3333 | 82.46% | 9.2336 | 39.1667 | 0 | 0 | 9.2336 | 39.1667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:37 |  | SP4 |  | 100 | 0 | 78.95% | 11.0803 | 37.5 | 11.0803 | 22.5 | -22.1607 | 75 | 78.95% | 11.0803 | 37.5 | 0 | 0 | 11.0803 | 37.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:38 |  | SP4 |  | 100 | 0 | 75.44% | 12.9271 | 35.8333 | 12.9271 | 22.5 | -25.8541 | 71.6667 | 75.44% | 12.9271 | 35.8333 | 0 | 0 | 12.9271 | 35.8333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:39 |  | SP4 |  | 100 | 0 | 71.93% | 14.7738 | 34.1667 | 14.7738 | 22.5 | -29.5476 | 68.3333 | 71.93% | 14.7738 | 34.1667 | 0 | 0 | 14.7738 | 34.1667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:40 |  | SP4 |  | 100 | 0 | 68.42% | 16.6205 | 32.5 | 16.6205 | 22.5 | -33.241 | 65 | 68.42% | 16.6205 | 32.5 | 0 | 0 | 16.6205 | 32.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:41 |  | SP4 |  | 100 | 0 | 64.91% | 18.4672 | 30.8333 | 18.4672 | 22.5 | -36.9344 | 61.6667 | 64.91% | 18.4672 | 30.8333 | 0 | 0 | 18.4672 | 30.8333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:42 |  | SP4 |  | 100 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 22.5 | -40.6279 | 58.3333 | 61.4% | 20.3139 | 29.1667 | 0 | 0 | 20.3139 | 29.1667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:43 |  | SP4 |  | 100 | 0 | 57.89% | 22.1607 | 27.5 | 22.1607 | 22.5 | -44.3213 | 55 | 57.89% | 22.1607 | 27.5 | 0 | 0 | 22.1607 | 27.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:44 |  | SP4 |  | 100 | 0 | 54.39% | 24.0074 | 25.8333 | 24.0074 | 22.5 | -48.0148 | 51.6667 | 54.39% | 24.0074 | 25.8333 | 0 | 0 | 24.0074 | 25.8333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:45 |  | SP4 |  | 100 | 0 | 50.88% | 25.8541 | 24.1667 | 25.8541 | 22.5 | -51.7082 | 48.3333 | 50.88% | 25.8541 | 24.1667 | 0 | 0 | 25.8541 | 24.1667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:46 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:47 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:48 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:49 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:50 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:51 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:52 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:53 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:54 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:55 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:56 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:57 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:58 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:59 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:00 |  | SP4 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:01 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:02 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:03 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:04 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:05 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:06 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:07 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:08 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:09 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:10 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:11 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:12 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:13 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:14 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:15 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:16 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:17 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:18 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:19 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:20 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:21 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:22 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:23 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:24 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:25 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:26 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:27 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:28 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:29 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:30 |  | SP5 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:31 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:32 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:33 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:34 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:35 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:36 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:37 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:38 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:39 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:40 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:41 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:42 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:43 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:44 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:45 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:46 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:47 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:48 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:49 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:50 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:51 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:52 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:53 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:54 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:55 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:56 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:57 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:58 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:59 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:00 |  | SP6 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:01 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:02 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:03 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:04 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:05 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:06 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:07 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:08 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:09 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:10 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:11 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:12 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:13 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:14 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:15 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:16 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:17 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:18 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:19 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:20 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:21 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:22 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:23 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:24 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:25 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:26 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:27 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:28 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:29 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:30 |  | SP7 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:31 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:32 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:33 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:34 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:35 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:36 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:37 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:38 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:39 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:40 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:41 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:42 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:43 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:44 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:45 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:46 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:47 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:48 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:49 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:50 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:51 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:52 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:53 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:54 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:55 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:56 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:57 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:58 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:59 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 4:00 |  | SP8 |  | 0 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 22.5 | -55.4017 | 45 | 47.37% | 27.7008 | 22.5 | 0 | 0 | 27.7008 | 22.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100

## 3- BOA accepted
| BMU |  |  |  |  | Explanation
|  |  | Site: | EXAMPLE BESS | [17 empty] | Input | --> user can configure Battery physical parameters, dispatch profile, BM acceptance, DFR contract commitment
|  |  | MW | MWh |  | BOA accepted 00:10 to 00:20 | [15 empty] | Calc | --> calculated fields such as expected SoC, DFR SoE envelope, MW headroom/footroom
|  |  | 100 | 50 |  | MDB/MDO redeclared | [15 empty] | Output | --> MWh MDVO/B profile
|  |  | Min SoC | Max SoC
|  |  | 0% | 100% | [12 empty] | 25 | [5 empty] | Delivery period / Real time
|  |  | Imp_eff | Exp_eff | [18 empty] | Gate Closure
|  |  | 95% | 95%
|  | SoC Limit: | Ok
Energy
| Date | [10 empty] | 30 min rule | 30 min rule | SoC | Day Ahead | Day Ahead | Change |  |  |  | Dynamic Response Contracts
| 2025-02-24 | [6 empty] | Instant | Instant | Declared | Declared | Battery | Battery | before | Declared | Declared | From | Cumulative | ESO Derived | ESO Derived | Low Service |  |  |  |  | Check | High Service
| Time |  |  |  | Battery MW (PN) | ESO MW (BOA) | SoC | MDB (MWh) | MDO (MWh) | MDB (MWh) | MDO (MWh) | MIL (MW) | MEL (MW) | BOAs | MDVB | MDVO | BOA | Change | MDB | MDO | DFR -LF MW | DFR MinSOC | DFR MWh | MW Headroom | Service | Flag | DFR-HF MW | DFR MaxSoC | DFR MWh | MW Footroom | Service
0:00 | 0:01 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 4.1667 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:02 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 4.1667 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:03 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 4.1667 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:04 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 4.1667 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:05 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 4.1667 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:06 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 4.1667 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:07 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 4.1667 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:08 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 4.1667 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:09 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 4.1667 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:10 |  | SP1 |  | 0 | 100 | 100% | 0 | 47.5 | 0 | 4.1667 | 0 | 95 | 100% | 0 | 47.5 | 1.5833 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:11 |  | SP1 |  | 0 | 100 | 96.49% | 1.8467 | 45.8333 | 1.8467 | 4.1667 | -3.6934 | 91.6667 | 100% | 0 | 47.5 | 1.5833 | 1.5833 | 1.5833 | 45.9167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:12 |  | SP1 |  | 0 | 100 | 92.98% | 3.6934 | 44.1667 | 3.6934 | 4.1667 | -7.3869 | 88.3333 | 100% | 0 | 47.5 | 1.5833 | 3.1667 | 3.1667 | 44.3333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:13 |  | SP1 |  | 0 | 100 | 89.47% | 5.5402 | 42.5 | 5.5402 | 4.1667 | -11.0803 | 85 | 100% | 0 | 47.5 | 1.5833 | 4.75 | 4.75 | 42.75 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:14 |  | SP1 |  | 0 | 100 | 85.96% | 7.3869 | 40.8333 | 7.3869 | 4.1667 | -14.7738 | 81.6667 | 100% | 0 | 47.5 | 1.5833 | 6.3333 | 6.3333 | 41.1667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:15 |  | SP1 |  | 0 | 100 | 82.46% | 9.2336 | 39.1667 | 9.2336 | 4.1667 | -18.4672 | 78.3333 | 100% | 0 | 47.5 | 1.5833 | 7.9167 | 7.9167 | 39.5833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:16 |  | SP1 |  | 0 | 100 | 78.95% | 11.0803 | 37.5 | 11.0803 | 4.1667 | -22.1607 | 75 | 100% | 0 | 47.5 | 1.5833 | 9.5 | 9.5 | 38 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:17 |  | SP1 |  | 0 | 100 | 75.44% | 12.9271 | 35.8333 | 12.9271 | 4.1667 | -25.8541 | 71.6667 | 100% | 0 | 47.5 | 1.5833 | 11.0833 | 11.0833 | 36.4167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:18 |  | SP1 |  | 0 | 100 | 71.93% | 14.7738 | 34.1667 | 14.7738 | 4.1667 | -29.5476 | 68.3333 | 100% | 0 | 47.5 | 1.5833 | 12.6667 | 12.6667 | 34.8333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:19 |  | SP1 |  | 0 | 100 | 68.42% | 16.6205 | 32.5 | 16.6205 | 4.1667 | -33.241 | 65 | 100% | 0 | 47.5 | 1.5833 | 14.25 | 14.25 | 33.25 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:20 |  | SP1 |  | 0 | 100 | 64.91% | 18.4672 | 30.8333 | 18.4672 | 4.1667 | -36.9344 | 61.6667 | 100% | 0 | 47.5 | 1.5833 | 15.8333 | 15.8333 | 31.6667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:21 |  | SP1 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:22 |  | SP1 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:23 |  | SP1 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:24 |  | SP1 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:25 |  | SP1 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:26 |  | SP1 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:27 |  | SP1 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:28 |  | SP1 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:29 |  | SP1 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:30 |  | SP1 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:31 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:32 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:33 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:34 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:35 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:36 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:37 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:38 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:39 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:40 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:41 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:42 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:43 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:44 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:45 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:46 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:47 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:48 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:49 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:50 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:51 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:52 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:53 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:54 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:55 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:56 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:57 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:58 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:59 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:00 |  | SP2 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:01 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:02 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:03 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:04 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:05 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:06 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:07 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:08 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:09 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:10 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:11 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:12 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:13 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:14 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:15 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:16 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:17 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:18 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:19 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:20 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:21 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:22 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:23 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:24 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:25 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:26 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:27 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:28 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:29 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:30 |  | SP3 |  | 0 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:31 |  | SP4 |  | 100 | 0 | 61.4% | 20.3139 | 29.1667 | 20.3139 | 4.1667 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | 0 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:32 |  | SP4 |  | 100 | 0 | 57.89% | 22.1607 | 27.5 | 22.1607 | 4.1667 | -44.3213 | 55 | 96.49% | 1.8467 | 45.8333 | 0 | 17.4167 | 19.2634 | 28.4167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:33 |  | SP4 |  | 100 | 0 | 54.39% | 24.0074 | 25.8333 | 24.0074 | 4.1667 | -48.0148 | 51.6667 | 92.98% | 3.6934 | 44.1667 | 0 | 17.4167 | 21.1101 | 26.75 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:34 |  | SP4 |  | 100 | 0 | 50.88% | 25.8541 | 24.1667 | 25.8541 | 4.1667 | -51.7082 | 48.3333 | 89.47% | 5.5402 | 42.5 | 0 | 17.4167 | 22.9568 | 25.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:35 |  | SP4 |  | 100 | 0 | 47.37% | 27.7008 | 22.5 | 27.7008 | 4.1667 | -55.4017 | 45 | 85.96% | 7.3869 | 40.8333 | 0 | 17.4167 | 24.8036 | 23.4167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:36 |  | SP4 |  | 100 | 0 | 43.86% | 29.5476 | 20.8333 | 29.5476 | 4.1667 | -59.0951 | 41.6667 | 82.46% | 9.2336 | 39.1667 | 0 | 17.4167 | 26.6503 | 21.75 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:37 |  | SP4 |  | 100 | 0 | 40.35% | 31.3943 | 19.1667 | 31.3943 | 4.1667 | -62.7886 | 38.3333 | 78.95% | 11.0803 | 37.5 | 0 | 17.4167 | 28.497 | 20.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:38 |  | SP4 |  | 100 | 0 | 36.84% | 33.241 | 17.5 | 33.241 | 4.1667 | -66.482 | 35 | 75.44% | 12.9271 | 35.8333 | 0 | 17.4167 | 30.3437 | 18.4167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:39 |  | SP4 |  | 100 | 0 | 33.33% | 35.0877 | 15.8333 | 35.0877 | 4.1667 | -70.1754 | 31.6667 | 71.93% | 14.7738 | 34.1667 | 0 | 17.4167 | 32.1904 | 16.75 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:40 |  | SP4 |  | 100 | 0 | 29.82% | 36.9344 | 14.1667 | 36.9344 | 4.1667 | -73.8689 | 28.3333 | 68.42% | 16.6205 | 32.5 | 0 | 17.4167 | 34.0372 | 15.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:41 |  | SP4 |  | 100 | 0 | 26.32% | 38.7812 | 12.5 | 38.7812 | 4.1667 | -77.5623 | 25 | 64.91% | 18.4672 | 30.8333 | 0 | 17.4167 | 35.8839 | 13.4167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:42 |  | SP4 |  | 100 | 0 | 22.81% | 40.6279 | 10.8333 | 40.6279 | 4.1667 | -81.2558 | 21.6667 | 61.4% | 20.3139 | 29.1667 | 0 | 17.4167 | 37.7306 | 11.75 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:43 |  | SP4 |  | 100 | 0 | 19.3% | 42.4746 | 9.1667 | 42.4746 | 4.1667 | -84.9492 | 18.3333 | 57.89% | 22.1607 | 27.5 | 0 | 17.4167 | 39.5773 | 10.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:44 |  | SP4 |  | 100 | 0 | 15.79% | 44.3213 | 7.5 | 44.3213 | 4.1667 | -88.6427 | 15 | 54.39% | 24.0074 | 25.8333 | 0 | 17.4167 | 41.4241 | 8.4167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:45 |  | SP4 |  | 100 | 0 | 12.28% | 46.1681 | 5.8333 | 46.1681 | 4.1667 | -92.3361 | 11.6667 | 50.88% | 25.8541 | 24.1667 | 0 | 17.4167 | 43.2708 | 6.75 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:46 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:47 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:48 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:49 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:50 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:51 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:52 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:53 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:54 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:55 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:56 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:57 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:58 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:59 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:00 |  | SP4 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:01 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:02 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:03 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:04 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:05 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:06 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:07 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:08 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:09 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:10 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:11 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:12 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:13 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:14 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:15 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:16 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:17 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:18 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:19 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:20 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:21 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:22 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:23 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:24 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:25 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:26 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:27 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:28 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:29 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:30 |  | SP5 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:31 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:32 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:33 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:34 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:35 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:36 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:37 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:38 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:39 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:40 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:41 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:42 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:43 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:44 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:45 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:46 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:47 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:48 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:49 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:50 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:51 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:52 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:53 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:54 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:55 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:56 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:57 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:58 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:59 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:00 |  | SP6 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:01 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:02 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:03 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:04 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:05 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:06 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:07 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:08 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:09 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:10 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:11 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:12 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:13 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:14 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:15 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:16 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:17 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:18 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:19 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:20 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:21 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:22 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:23 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:24 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:25 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:26 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:27 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:28 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:29 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:30 |  | SP7 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:31 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:32 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:33 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:34 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:35 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:36 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:37 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:38 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:39 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:40 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:41 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:42 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:43 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:44 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:45 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:46 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:47 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:48 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:49 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:50 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:51 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:52 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:53 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:54 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:55 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:56 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:57 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:58 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:59 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 4:00 |  | SP8 |  | 0 | 0 | 8.772% | 48.0148 | 4.1667 | 48.0148 | 4.1667 | -96.0295 | 8.3333 | 47.37% | 27.7008 | 22.5 | 0 | 17.4167 | 45.1175 | 5.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100

## 4-Second BOA accepted
| BMU |  |  |  |  | Explanation
|  |  | Site: | EXAMPLE BESS | [17 empty] | Input | --> user can configure Battery physical parameters, dispatch profile, BM acceptance, DFR contract commitment
|  |  | MW | MWh |  | Second BOA accepted 00:21 to 00:30 | [15 empty] | Calc | --> calculated fields such as expected SoC, DFR SoE envelope, MW headroom/footroom
|  |  | 100 | 50 |  | MDB/MDO redeclared | [15 empty] | Output | --> MWh MDVO/B profile
|  |  | Min SoC | Max SoC
|  |  | 0% | 100% | [12 empty] | 25 | [5 empty] | Delivery period / Real time
|  |  | Imp_eff | Exp_eff | [18 empty] | Gate Closure
|  |  | 95% | 95%
|  | SoC Limit: | Ok
Energy
| Date | [10 empty] | 30 min rule | 30 min rule | SoC | Day Ahead | Day Ahead | Change |  |  |  | Dynamic Response Contracts
| 2025-02-24 | [6 empty] | Instant | Instant | Declared | Declared | Battery | Battery | before | Declared | Declared | From | Cumulative | ESO Derived | ESO Derived | Low Service |  |  |  |  | Check | High Service
| Time |  |  |  | Battery MW (PN) | ESO MW (BOA) | SoC | MDB (MWh) | MDO (MWh) | MDB (MWh) | MDO (MWh) | MIL (MW) | MEL (MW) | BOAs | MDVB | MDVO | BOA | Change | MDB | MDO | DFR -LF MW | DFR MinSOC | DFR MWh | MW Headroom | Service | Flag | DFR-HF MW | DFR MaxSoC | DFR MWh | MW Footroom | Service
0:00 | 0:01 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 11.6875 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:02 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 11.6875 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:03 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 11.6875 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:04 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 11.6875 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:05 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 11.6875 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:06 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 11.6875 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:07 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 11.6875 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:08 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 11.6875 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:09 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 11.6875 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:10 |  | SP1 |  | 0 | 100 | 100% | 0 | 47.5 | 0 | 11.6875 | 0 | 95 | 100% | 0 | 47.5 | 1.5833 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:11 |  | SP1 |  | 0 | 100 | 96.49% | 1.8467 | 45.8333 | 1.8467 | 11.6875 | -3.6934 | 91.6667 | 100% | 0 | 47.5 | 1.5833 | 1.5833 | 1.5833 | 45.9167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:12 |  | SP1 |  | 0 | 100 | 92.98% | 3.6934 | 44.1667 | 3.6934 | 11.6875 | -7.3869 | 88.3333 | 100% | 0 | 47.5 | 1.5833 | 3.1667 | 3.1667 | 44.3333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:13 |  | SP1 |  | 0 | 100 | 89.47% | 5.5402 | 42.5 | 5.5402 | 11.6875 | -11.0803 | 85 | 100% | 0 | 47.5 | 1.5833 | 4.75 | 4.75 | 42.75 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:14 |  | SP1 |  | 0 | 100 | 85.96% | 7.3869 | 40.8333 | 7.3869 | 11.6875 | -14.7738 | 81.6667 | 100% | 0 | 47.5 | 1.5833 | 6.3333 | 6.3333 | 41.1667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:15 |  | SP1 |  | 0 | 100 | 82.46% | 9.2336 | 39.1667 | 9.2336 | 11.6875 | -18.4672 | 78.3333 | 100% | 0 | 47.5 | 1.5833 | 7.9167 | 7.9167 | 39.5833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:16 |  | SP1 |  | 0 | 100 | 78.95% | 11.0803 | 37.5 | 11.0803 | 11.6875 | -22.1607 | 75 | 100% | 0 | 47.5 | 1.5833 | 9.5 | 9.5 | 38 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:17 |  | SP1 |  | 0 | 100 | 75.44% | 12.9271 | 35.8333 | 11.9806 | 11.6875 | -25.8541 | 71.6667 | 100% | 0 | 47.5 | 1.5833 | 11.0833 | 11.0833 | 36.4167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:18 |  | SP1 |  | 0 | 100 | 71.93% | 14.7738 | 34.1667 | 11.9806 | 11.6875 | -29.5476 | 68.3333 | 100% | 0 | 47.5 | 1.5833 | 12.6667 | 12.6667 | 34.8333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:19 |  | SP1 |  | 0 | 100 | 68.42% | 16.6205 | 32.5 | 11.9806 | 11.6875 | -33.241 | 65 | 100% | 0 | 47.5 | 1.5833 | 14.25 | 14.25 | 33.25 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:20 |  | SP1 |  | 0 | 100 | 64.91% | 18.4672 | 30.8333 | 11.9806 | 11.6875 | -36.9344 | 61.6667 | 100% | 0 | 47.5 | 1.5833 | 15.8333 | 15.8333 | 31.6667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:21 |  | SP1 |  | 0 | -50 | 61.4% | 20.3139 | 29.1667 | 11.9806 | 11.6875 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | -0.87719 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:22 |  | SP1 |  | 0 | -50 | 62.99% | 19.4806 | 29.9188 | 11.9806 | 11.6875 | -38.9612 | 59.8375 | 100% | 0 | 47.5 | -0.87719 | 16.5395 | 16.5395 | 30.9605 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:23 |  | SP1 |  | 0 | -50 | 64.57% | 18.6473 | 30.6708 | 11.9806 | 11.6875 | -37.2946 | 61.3417 | 100% | 0 | 47.5 | -0.87719 | 15.6623 | 15.6623 | 31.8377 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:24 |  | SP1 |  | 0 | -50 | 66.15% | 17.8139 | 31.4229 | 11.9806 | 11.6875 | -35.6279 | 62.8458 | 100% | 0 | 47.5 | -0.87719 | 14.7851 | 14.7851 | 32.7149 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:25 |  | SP1 |  | 0 | -50 | 67.74% | 16.9806 | 32.175 | 11.9806 | 11.6875 | -33.9612 | 64.35 | 100% | 0 | 47.5 | -0.87719 | 13.9079 | 13.9079 | 33.5921 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:26 |  | SP1 |  | 0 | -50 | 69.32% | 16.1473 | 32.9271 | 11.9806 | 11.6875 | -32.2946 | 65.8542 | 100% | 0 | 47.5 | -0.87719 | 13.0307 | 13.0307 | 34.4693 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:27 |  | SP1 |  | 0 | -50 | 70.9% | 15.3139 | 33.6792 | 11.9806 | 11.6875 | -30.6279 | 67.3583 | 100% | 0 | 47.5 | -0.87719 | 12.1535 | 12.1535 | 35.3465 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:28 |  | SP1 |  | 0 | -50 | 72.49% | 14.4806 | 34.4313 | 11.9806 | 11.6875 | -28.9612 | 68.8625 | 100% | 0 | 47.5 | -0.87719 | 11.2763 | 11.2763 | 36.2237 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:29 |  | SP1 |  | 0 | -50 | 74.07% | 13.6473 | 35.1833 | 11.9806 | 11.6875 | -27.2946 | 70.3667 | 100% | 0 | 47.5 | -0.87719 | 10.3991 | 10.3991 | 37.1009 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:30 |  | SP1 |  | 0 | -50 | 75.65% | 12.8139 | 35.9354 | 11.9806 | 11.6875 | -25.6279 | 71.8708 | 100% | 0 | 47.5 | -0.87719 | 9.5219 | 9.5219 | 37.9781 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:31 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:32 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:33 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:34 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:35 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:36 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:37 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:38 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:39 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:40 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:41 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:42 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:43 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:44 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:45 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:46 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:47 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:48 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:49 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:50 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:51 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:52 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:53 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:54 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:55 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:56 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:57 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:58 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:59 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:00 |  | SP2 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:01 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:02 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:03 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:04 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:05 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:06 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:07 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:08 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:09 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:10 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:11 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:12 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:13 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:14 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:15 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:16 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:17 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:18 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:19 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:20 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:21 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:22 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:23 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:24 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:25 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:26 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:27 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:28 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:29 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:30 |  | SP3 |  | 0 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:31 |  | SP4 |  | 100 | 0 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 11.6875 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 0 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:32 |  | SP4 |  | 100 | 0 | 73.73% | 13.8273 | 35.0208 | 13.8273 | 11.6875 | -27.6547 | 70.0417 | 96.49% | 1.8467 | 45.8333 | 0 | 8.6447 | 10.4915 | 37.1886 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:33 |  | SP4 |  | 100 | 0 | 70.22% | 15.6741 | 33.3542 | 15.6741 | 11.6875 | -31.3481 | 66.7083 | 92.98% | 3.6934 | 44.1667 | 0 | 8.6447 | 12.3382 | 35.5219 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:34 |  | SP4 |  | 100 | 0 | 66.71% | 17.5208 | 31.6875 | 17.5208 | 11.6875 | -35.0416 | 63.375 | 89.47% | 5.5402 | 42.5 | 0 | 8.6447 | 14.1849 | 33.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:35 |  | SP4 |  | 100 | 0 | 63.2% | 19.3675 | 30.0208 | 19.3675 | 11.6875 | -38.735 | 60.0417 | 85.96% | 7.3869 | 40.8333 | 0 | 8.6447 | 16.0316 | 32.1886 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:36 |  | SP4 |  | 100 | 0 | 59.69% | 21.2142 | 28.3542 | 21.2142 | 11.6875 | -42.4284 | 56.7083 | 82.46% | 9.2336 | 39.1667 | 0 | 8.6447 | 17.8783 | 30.5219 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:37 |  | SP4 |  | 100 | 0 | 56.18% | 23.0609 | 26.6875 | 23.0609 | 11.6875 | -46.1219 | 53.375 | 78.95% | 11.0803 | 37.5 | 0 | 8.6447 | 19.7251 | 28.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:38 |  | SP4 |  | 100 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 11.6875 | -49.8153 | 50.0417 | 75.44% | 12.9271 | 35.8333 | 0 | 8.6447 | 21.5718 | 27.1886 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:39 |  | SP4 |  | 100 | 0 | 49.17% | 26.7544 | 23.3542 | 26.7544 | 11.6875 | -53.5088 | 46.7083 | 71.93% | 14.7738 | 34.1667 | 0 | 8.6447 | 23.4185 | 25.5219 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:40 |  | SP4 |  | 100 | 0 | 45.66% | 28.6011 | 21.6875 | 28.6011 | 11.6875 | -57.2022 | 43.375 | 68.42% | 16.6205 | 32.5 | 0 | 8.6447 | 25.2652 | 23.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:41 |  | SP4 |  | 100 | 0 | 42.15% | 30.4478 | 20.0208 | 30.4478 | 11.6875 | -60.8957 | 40.0417 | 64.91% | 18.4672 | 30.8333 | 0 | 8.6447 | 27.112 | 22.1886 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:42 |  | SP4 |  | 100 | 0 | 38.64% | 32.2946 | 18.3542 | 32.2946 | 11.6875 | -64.5891 | 36.7083 | 61.4% | 20.3139 | 29.1667 | 0 | 8.6447 | 28.9587 | 20.5219 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:43 |  | SP4 |  | 100 | 0 | 35.13% | 34.1413 | 16.6875 | 34.1413 | 11.6875 | -68.2825 | 33.375 | 57.89% | 22.1607 | 27.5 | 0 | 8.6447 | 30.8054 | 18.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:44 |  | SP4 |  | 100 | 0 | 31.62% | 35.988 | 15.0208 | 35.988 | 11.6875 | -71.976 | 30.0417 | 54.39% | 24.0074 | 25.8333 | 0 | 8.6447 | 32.6521 | 17.1886 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:45 |  | SP4 |  | 100 | 0 | 28.11% | 37.8347 | 13.3542 | 37.8347 | 11.6875 | -75.6694 | 26.7083 | 50.88% | 25.8541 | 24.1667 | 0 | 8.6447 | 34.4988 | 15.5219 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:46 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:47 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:48 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:49 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:50 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:51 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:52 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:53 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:54 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:55 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:56 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:57 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:58 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:59 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:00 |  | SP4 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:01 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:02 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:03 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:04 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:05 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:06 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:07 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:08 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:09 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:10 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:11 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:12 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:13 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:14 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:15 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:16 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:17 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:18 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:19 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:20 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:21 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:22 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:23 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:24 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:25 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:26 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:27 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:28 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:29 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:30 |  | SP5 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:31 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:32 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:33 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:34 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:35 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:36 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:37 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:38 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:39 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:40 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:41 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:42 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:43 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:44 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:45 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:46 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:47 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:48 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:49 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:50 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:51 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:52 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:53 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:54 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:55 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:56 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:57 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:58 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:59 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:00 |  | SP6 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:01 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:02 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:03 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:04 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:05 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:06 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:07 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:08 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:09 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:10 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:11 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:12 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:13 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:14 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:15 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:16 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:17 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:18 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:19 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:20 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:21 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:22 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:23 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:24 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:25 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:26 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:27 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:28 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:29 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:30 |  | SP7 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:31 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:32 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:33 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:34 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:35 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:36 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:37 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:38 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:39 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:40 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:41 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:42 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:43 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:44 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:45 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:46 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:47 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:48 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:49 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:50 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:51 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:52 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:53 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:54 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:55 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:56 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:57 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:58 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:59 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 4:00 |  | SP8 |  | 0 | 0 | 24.61% | 39.6814 | 11.6875 | 39.6814 | 11.6875 | -79.3629 | 23.375 | 47.37% | 27.7008 | 22.5 | 0 | 8.6447 | 36.3456 | 13.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100

## 5-Third BOA accepted
| BMU |  |  |  |  | Explanation
|  |  | Site: | EXAMPLE BESS | [17 empty] | Input | --> user can configure Battery physical parameters, dispatch profile, BM acceptance, DFR contract commitment
|  |  | MW | MWh |  | Third BOA accpeted 00:31 to 00:37. Leaving no Offer Volume available. | [15 empty] | Calc | --> calculated fields such as expected SoC, DFR SoE envelope, MW headroom/footroom
|  |  | 100 | 50 |  | MDB/MDO redeclared | [15 empty] | Output | --> MWh MDVO/B profile
|  |  | Min SoC | Max SoC
|  |  | 0% | 100% | [12 empty] | 25 | [5 empty] | Delivery period / Real time
|  |  | Imp_eff | Exp_eff | [18 empty] | Gate Closure
|  |  | 95% | 95%
|  | SoC Limit: | Ok
Energy
| Date | [10 empty] | 30 min rule | 30 min rule | SoC | Day Ahead | Day Ahead | Change |  |  |  | Dynamic Response Contracts
| 2025-02-24 | [6 empty] | Instant | Instant | Declared | Declared | Battery | Battery | before | Declared | Declared | From | Cumulative | ESO Derived | ESO Derived | Low Service |  |  |  |  | Check | High Service
| Time |  |  |  | Battery MW (PN) | ESO MW (BOA) | SoC | MDB (MWh) | MDO (MWh) | MDB (MWh) | MDO (MWh) | MIL (MW) | MEL (MW) | BOAs | MDVB | MDVO | BOA | Change | MDB | MDO | DFR -LF MW | DFR MinSOC | DFR MWh | MW Headroom | Service | Flag | DFR-HF MW | DFR MaxSoC | DFR MWh | MW Footroom | Service
0:00 | 0:01 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | -50 | 0.020833 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:02 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | -50 | 0.020833 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:03 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | -50 | 0.020833 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:04 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | -50 | 0.020833 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:05 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | -50 | 0.020833 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:06 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | -50 | 0.020833 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:07 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | -50 | 0.020833 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:08 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | -50 | 0.020833 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:09 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | -50 | 0.020833 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:10 |  | SP1 |  | 0 | 100 | 100% | 0 | 47.5 | -50 | 0.020833 | 0 | 95 | 100% | 0 | 47.5 | 1.5833 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:11 |  | SP1 |  | 0 | 100 | 96.49% | 1.8467 | 45.8333 | -50 | 0.020833 | -3.6934 | 91.6667 | 100% | 0 | 47.5 | 1.5833 | 1.5833 | 1.5833 | 45.9167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:12 |  | SP1 |  | 0 | 100 | 92.98% | 3.6934 | 44.1667 | -50 | 0.020833 | -7.3869 | 88.3333 | 100% | 0 | 47.5 | 1.5833 | 3.1667 | 3.1667 | 44.3333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:13 |  | SP1 |  | 0 | 100 | 89.47% | 5.5402 | 42.5 | -50 | 0.020833 | -11.0803 | 85 | 100% | 0 | 47.5 | 1.5833 | 4.75 | 4.75 | 42.75 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:14 |  | SP1 |  | 0 | 100 | 85.96% | 7.3869 | 40.8333 | -50 | 0.020833 | -14.7738 | 81.6667 | 100% | 0 | 47.5 | 1.5833 | 6.3333 | 6.3333 | 41.1667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:15 |  | SP1 |  | 0 | 100 | 82.46% | 9.2336 | 39.1667 | -50 | 0.020833 | -18.4672 | 78.3333 | 100% | 0 | 47.5 | 1.5833 | 7.9167 | 7.9167 | 39.5833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:16 |  | SP1 |  | 0 | 100 | 78.95% | 11.0803 | 37.5 | -50 | 0.020833 | -22.1607 | 75 | 100% | 0 | 47.5 | 1.5833 | 9.5 | 9.5 | 38 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:17 |  | SP1 |  | 0 | 100 | 75.44% | 12.9271 | 35.8333 | -50 | 0.020833 | -25.8541 | 71.6667 | 100% | 0 | 47.5 | 1.5833 | 11.0833 | 11.0833 | 36.4167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:18 |  | SP1 |  | 0 | 100 | 71.93% | 14.7738 | 34.1667 | -50 | 0.020833 | -29.5476 | 68.3333 | 100% | 0 | 47.5 | 1.5833 | 12.6667 | 12.6667 | 34.8333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:19 |  | SP1 |  | 0 | 100 | 68.42% | 16.6205 | 32.5 | -50 | 0.020833 | -33.241 | 65 | 100% | 0 | 47.5 | 1.5833 | 14.25 | 14.25 | 33.25 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:20 |  | SP1 |  | 0 | 100 | 64.91% | 18.4672 | 30.8333 | -50 | 0.020833 | -36.9344 | 61.6667 | 100% | 0 | 47.5 | 1.5833 | 15.8333 | 15.8333 | 31.6667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:21 |  | SP1 |  | 0 | -50 | 61.4% | 20.3139 | 29.1667 | -50 | 0.020833 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | -0.87719 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:22 |  | SP1 |  | 0 | -50 | 62.99% | 19.4806 | 29.9188 | -50 | 0.020833 | -38.9612 | 59.8375 | 100% | 0 | 47.5 | -0.87719 | 16.5395 | 16.5395 | 30.9605 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:23 |  | SP1 |  | 0 | -50 | 64.57% | 18.6473 | 30.6708 | -50 | 0.020833 | -37.2946 | 61.3417 | 100% | 0 | 47.5 | -0.87719 | 15.6623 | 15.6623 | 31.8377 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:24 |  | SP1 |  | 0 | -50 | 66.15% | 17.8139 | 31.4229 | -50 | 0.020833 | -35.6279 | 62.8458 | 100% | 0 | 47.5 | -0.87719 | 14.7851 | 14.7851 | 32.7149 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:25 |  | SP1 |  | 0 | -50 | 67.74% | 16.9806 | 32.175 | -50 | 0.020833 | -33.9612 | 64.35 | 100% | 0 | 47.5 | -0.87719 | 13.9079 | 13.9079 | 33.5921 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:26 |  | SP1 |  | 0 | -50 | 69.32% | 16.1473 | 32.9271 | -50 | 0.020833 | -32.2946 | 65.8542 | 100% | 0 | 47.5 | -0.87719 | 13.0307 | 13.0307 | 34.4693 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:27 |  | SP1 |  | 0 | -50 | 70.9% | 15.3139 | 33.6792 | -50 | 0.020833 | -30.6279 | 67.3583 | 100% | 0 | 47.5 | -0.87719 | 12.1535 | 12.1535 | 35.3465 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:28 |  | SP1 |  | 0 | -50 | 72.49% | 14.4806 | 34.4313 | -50 | 0.020833 | -28.9612 | 68.8625 | 100% | 0 | 47.5 | -0.87719 | 11.2763 | 11.2763 | 36.2237 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:29 |  | SP1 |  | 0 | -50 | 74.07% | 13.6473 | 35.1833 | -50 | 0.020833 | -27.2946 | 70.3667 | 100% | 0 | 47.5 | -0.87719 | 10.3991 | 10.3991 | 37.1009 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:30 |  | SP1 |  | 0 | -50 | 75.65% | 12.8139 | 35.9354 | -50 | 0.020833 | -25.6279 | 71.8708 | 100% | 0 | 47.5 | -0.87719 | 9.5219 | 9.5219 | 37.9781 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:31 |  | SP2 |  | 0 | 100 | 77.24% | 11.9806 | 36.6875 | -50 | 0.020833 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 1.5833 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:32 |  | SP2 |  | 0 | 100 | 73.73% | 13.8273 | 35.0208 | -50 | 0.020833 | -27.6547 | 70.0417 | 100% | 0 | 47.5 | 1.5833 | 10.2281 | 10.2281 | 37.2719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:33 |  | SP2 |  | 0 | 100 | 70.22% | 15.6741 | 33.3542 | -50 | 0.020833 | -31.3481 | 66.7083 | 100% | 0 | 47.5 | 1.5833 | 11.8114 | 11.8114 | 35.6886 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:34 |  | SP2 |  | 0 | 100 | 66.71% | 17.5208 | 31.6875 | -50 | 0.020833 | -35.0416 | 63.375 | 100% | 0 | 47.5 | 1.5833 | 13.3947 | 13.3947 | 34.1053 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:35 |  | SP2 |  | 0 | 100 | 63.2% | 19.3675 | 30.0208 | -50 | 0.020833 | -38.735 | 60.0417 | 100% | 0 | 47.5 | 1.5833 | 14.9781 | 14.9781 | 32.5219 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:36 |  | SP2 |  | 0 | 100 | 59.69% | 21.2142 | 28.3542 | -50 | 0.020833 | -42.4284 | 56.7083 | 100% | 0 | 47.5 | 1.5833 | 16.5614 | 16.5614 | 30.9386 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:37 |  | SP2 |  | 0 | 100 | 56.18% | 23.0609 | 26.6875 | -50 | 0.020833 | -46.1219 | 53.375 | 100% | 0 | 47.5 | 1.5833 | 18.1447 | 18.1447 | 29.3553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:38 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:39 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:40 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:41 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:42 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:43 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:44 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:45 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:46 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:47 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:48 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:49 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:50 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:51 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:52 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:53 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:54 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:55 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:56 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:57 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:58 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:59 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:00 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:01 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:02 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:03 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:04 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:05 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:06 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:07 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:08 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:09 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:10 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:11 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:12 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:13 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:14 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:15 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:16 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:17 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:18 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:19 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:20 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:21 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:22 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:23 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:24 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:25 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:26 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:27 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:28 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:29 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:30 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:31 |  | SP4 |  | 100 | 0 | 52.68% | 24.9077 | 25.0208 | -50 | 0.020833 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:32 |  | SP4 |  | 100 | 0 | 49.17% | 26.7544 | 23.3542 | -50 | 0.020833 | -53.5088 | 46.7083 | 96.49% | 1.8467 | 45.8333 | 0 | 19.7281 | 21.5748 | 26.1053 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:33 |  | SP4 |  | 100 | 0 | 45.66% | 28.6011 | 21.6875 | -50 | 0.020833 | -57.2022 | 43.375 | 92.98% | 3.6934 | 44.1667 | 0 | 19.7281 | 23.4215 | 24.4386 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:34 |  | SP4 |  | 100 | 0 | 42.15% | 30.4478 | 20.0208 | -50 | 0.020833 | -60.8957 | 40.0417 | 89.47% | 5.5402 | 42.5 | 0 | 19.7281 | 25.2682 | 22.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:35 |  | SP4 |  | 100 | 0 | 38.64% | 32.2946 | 18.3542 | -50 | 0.020833 | -64.5891 | 36.7083 | 85.96% | 7.3869 | 40.8333 | 0 | 19.7281 | 27.115 | 21.1053 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:36 |  | SP4 |  | 100 | 0 | 35.13% | 34.1413 | 16.6875 | -50 | 0.020833 | -68.2825 | 33.375 | 82.46% | 9.2336 | 39.1667 | 0 | 19.7281 | 28.9617 | 19.4386 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:37 |  | SP4 |  | 100 | 0 | 31.62% | 35.988 | 15.0208 | -50 | 0.020833 | -71.976 | 30.0417 | 78.95% | 11.0803 | 37.5 | 0 | 19.7281 | 30.8084 | 17.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:38 |  | SP4 |  | 100 | 0 | 28.11% | 37.8347 | 13.3542 | -50 | 0.020833 | -75.6694 | 26.7083 | 75.44% | 12.9271 | 35.8333 | 0 | 19.7281 | 32.6551 | 16.1053 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:39 |  | SP4 |  | 100 | 0 | 24.61% | 39.6814 | 11.6875 | -50 | 0.020833 | -79.3629 | 23.375 | 71.93% | 14.7738 | 34.1667 | 0 | 19.7281 | 34.5018 | 14.4386 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:40 |  | SP4 |  | 100 | 0 | 21.1% | 41.5282 | 10.0208 | -50 | 0.020833 | -83.0563 | 20.0417 | 68.42% | 16.6205 | 32.5 | 0 | 19.7281 | 36.3486 | 12.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:41 |  | SP4 |  | 100 | 0 | 17.59% | 43.3749 | 8.3542 | -50 | 0.020833 | -86.7498 | 16.7083 | 64.91% | 18.4672 | 30.8333 | 0 | 19.7281 | 38.1953 | 11.1053 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:42 |  | SP4 |  | 100 | 0 | 14.08% | 45.2216 | 6.6875 | -50 | 0.020833 | -90.4432 | 13.375 | 61.4% | 20.3139 | 29.1667 | 0 | 19.7281 | 40.042 | 9.4386 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:43 |  | SP4 |  | 100 | 0 | 10.57% | 47.0683 | 5.0208 | -50 | 0.020833 | -94.1367 | 10.0417 | 57.89% | 22.1607 | 27.5 | 0 | 19.7281 | 41.8887 | 7.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:44 |  | SP4 |  | 100 | 0 | 7.061% | 48.9151 | 3.3542 | -50 | 0.020833 | -97.8301 | 6.7083 | 54.39% | 24.0074 | 25.8333 | 0 | 19.7281 | 43.7355 | 6.1053 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:45 |  | SP4 |  | 100 | 0 | 3.553% | -50 | 1.6875 | -50 | 0.020833 | 100 | 3.375 | 50.88% | 25.8541 | 24.1667 | 0 | 19.7281 | 45.5822 | 4.4386 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:46 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:47 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:48 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:49 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:50 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:51 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:52 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:53 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:54 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:55 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:56 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:57 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:58 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:59 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:00 |  | SP4 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:01 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:02 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:03 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:04 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:05 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:06 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:07 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:08 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:09 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:10 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:11 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:12 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:13 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:14 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:15 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:16 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:17 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:18 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:19 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:20 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:21 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:22 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:23 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:24 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:25 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:26 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:27 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:28 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:29 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:30 |  | SP5 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:31 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:32 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:33 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:34 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:35 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:36 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:37 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:38 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:39 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:40 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:41 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:42 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:43 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:44 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:45 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:46 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:47 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:48 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:49 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:50 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:51 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:52 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:53 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:54 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:55 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:56 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:57 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:58 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:59 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:00 |  | SP6 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:01 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:02 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:03 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:04 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:05 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:06 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:07 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:08 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:09 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:10 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:11 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:12 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:13 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:14 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:15 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:16 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:17 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:18 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:19 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:20 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:21 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:22 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:23 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:24 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:25 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:26 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:27 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:28 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:29 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:30 |  | SP7 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:31 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:32 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:33 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:34 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:35 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:36 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:37 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:38 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:39 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:40 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:41 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:42 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:43 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:44 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:45 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:46 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:47 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:48 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:49 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:50 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:51 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:52 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:53 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:54 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:55 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:56 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:57 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:58 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:59 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 4:00 |  | SP8 |  | 0 | 0 | 0.04386% | -50 | 0.020833 | -50 | 0.020833 | 100 | 0.041667 | 47.37% | 27.7008 | 22.5 | 0 | 19.7281 | 47.4289 | 2.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100

## 6-PN Changed in SP4
| BMU |  |  |  |  | Explanation
|  |  | Site: | EXAMPLE BESS | [17 empty] | Input | --> user can configure Battery physical parameters, dispatch profile, BM acceptance, DFR contract commitment
|  |  | MW | MWh |  | PN changed in SP4 to release MDO volume with BM Window. | [15 empty] | Calc | --> calculated fields such as expected SoC, DFR SoE envelope, MW headroom/footroom
|  |  | 100 | 50 |  | MDB/MDO redeclared | [15 empty] | Output | --> MWh MDVO/B profile
|  |  | Min SoC | Max SoC
|  |  | 0% | 100% | [12 empty] | 25 | [5 empty] | Delivery period / Real time
|  |  | Imp_eff | Exp_eff | [18 empty] | Gate Closure
|  |  | 95% | 95%
|  | SoC Limit: | Ok
Energy
| Date | [10 empty] | 30 min rule | 30 min rule | SoC | Day Ahead | Day Ahead | Change |  |  |  | Dynamic Response Contracts
| 2025-02-24 | [6 empty] | Instant | Instant | Declared | Declared | Battery | Battery | before | Declared | Declared | From | Cumulative | ESO Derived | ESO Derived | Low Service |  |  |  |  | Check | High Service
| Time |  |  |  | Battery MW (PN) | ESO MW (BOA) | SoC | MDB (MWh) | MDO (MWh) | MDB (MWh) | MDO (MWh) | MIL (MW) | MEL (MW) | BOAs | MDVB | MDVO | BOA | Change | MDB | MDO | DFR -LF MW | DFR MinSOC | DFR MWh | MW Headroom | Service | Flag | DFR-HF MW | DFR MaxSoC | DFR MWh | MW Footroom | Service
0:00 | 0:01 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 25.0208 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:02 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 25.0208 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:03 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 25.0208 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:04 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 25.0208 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:05 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 25.0208 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:06 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 25.0208 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:07 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 25.0208 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:08 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 25.0208 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:09 |  | SP1 |  | 0 | 0 | 100% | 0 | 47.5 | 0 | 25.0208 | 0 | 95 | 100% | 0 | 47.5 | 0 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:10 |  | SP1 |  | 0 | 100 | 100% | 0 | 47.5 | 0 | 25.0208 | 0 | 95 | 100% | 0 | 47.5 | 1.5833 | 0 | 0 | 47.5 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:11 |  | SP1 |  | 0 | 100 | 96.49% | 1.8467 | 45.8333 | 1.8467 | 25.0208 | -3.6934 | 91.6667 | 100% | 0 | 47.5 | 1.5833 | 1.5833 | 1.5833 | 45.9167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:12 |  | SP1 |  | 0 | 100 | 92.98% | 3.6934 | 44.1667 | 3.6934 | 25.0208 | -7.3869 | 88.3333 | 100% | 0 | 47.5 | 1.5833 | 3.1667 | 3.1667 | 44.3333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:13 |  | SP1 |  | 0 | 100 | 89.47% | 5.5402 | 42.5 | 5.5402 | 25.0208 | -11.0803 | 85 | 100% | 0 | 47.5 | 1.5833 | 4.75 | 4.75 | 42.75 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:14 |  | SP1 |  | 0 | 100 | 85.96% | 7.3869 | 40.8333 | 7.3869 | 25.0208 | -14.7738 | 81.6667 | 100% | 0 | 47.5 | 1.5833 | 6.3333 | 6.3333 | 41.1667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:15 |  | SP1 |  | 0 | 100 | 82.46% | 9.2336 | 39.1667 | 9.2336 | 25.0208 | -18.4672 | 78.3333 | 100% | 0 | 47.5 | 1.5833 | 7.9167 | 7.9167 | 39.5833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:16 |  | SP1 |  | 0 | 100 | 78.95% | 11.0803 | 37.5 | 11.0803 | 25.0208 | -22.1607 | 75 | 100% | 0 | 47.5 | 1.5833 | 9.5 | 9.5 | 38 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:17 |  | SP1 |  | 0 | 100 | 75.44% | 12.9271 | 35.8333 | 11.9806 | 25.0208 | -25.8541 | 71.6667 | 100% | 0 | 47.5 | 1.5833 | 11.0833 | 11.0833 | 36.4167 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:18 |  | SP1 |  | 0 | 100 | 71.93% | 14.7738 | 34.1667 | 11.9806 | 25.0208 | -29.5476 | 68.3333 | 100% | 0 | 47.5 | 1.5833 | 12.6667 | 12.6667 | 34.8333 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:19 |  | SP1 |  | 0 | 100 | 68.42% | 16.6205 | 32.5 | 11.9806 | 25.0208 | -33.241 | 65 | 100% | 0 | 47.5 | 1.5833 | 14.25 | 14.25 | 33.25 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:20 |  | SP1 |  | 0 | 100 | 64.91% | 18.4672 | 30.8333 | 11.9806 | 25.0208 | -36.9344 | 61.6667 | 100% | 0 | 47.5 | 1.5833 | 15.8333 | 15.8333 | 31.6667 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:21 |  | SP1 |  | 0 | -50 | 61.4% | 20.3139 | 29.1667 | 11.9806 | 25.0208 | -40.6279 | 58.3333 | 100% | 0 | 47.5 | -0.87719 | 17.4167 | 17.4167 | 30.0833 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:22 |  | SP1 |  | 0 | -50 | 62.99% | 19.4806 | 29.9188 | 11.9806 | 25.0208 | -38.9612 | 59.8375 | 100% | 0 | 47.5 | -0.87719 | 16.5395 | 16.5395 | 30.9605 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:23 |  | SP1 |  | 0 | -50 | 64.57% | 18.6473 | 30.6708 | 11.9806 | 25.0208 | -37.2946 | 61.3417 | 100% | 0 | 47.5 | -0.87719 | 15.6623 | 15.6623 | 31.8377 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:24 |  | SP1 |  | 0 | -50 | 66.15% | 17.8139 | 31.4229 | 11.9806 | 25.0208 | -35.6279 | 62.8458 | 100% | 0 | 47.5 | -0.87719 | 14.7851 | 14.7851 | 32.7149 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:25 |  | SP1 |  | 0 | -50 | 67.74% | 16.9806 | 32.175 | 11.9806 | 25.0208 | -33.9612 | 64.35 | 100% | 0 | 47.5 | -0.87719 | 13.9079 | 13.9079 | 33.5921 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:26 |  | SP1 |  | 0 | -50 | 69.32% | 16.1473 | 32.9271 | 11.9806 | 25.0208 | -32.2946 | 65.8542 | 100% | 0 | 47.5 | -0.87719 | 13.0307 | 13.0307 | 34.4693 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:27 |  | SP1 |  | 0 | -50 | 70.9% | 15.3139 | 33.6792 | 11.9806 | 25.0208 | -30.6279 | 67.3583 | 100% | 0 | 47.5 | -0.87719 | 12.1535 | 12.1535 | 35.3465 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:28 |  | SP1 |  | 0 | -50 | 72.49% | 14.4806 | 34.4313 | 11.9806 | 25.0208 | -28.9612 | 68.8625 | 100% | 0 | 47.5 | -0.87719 | 11.2763 | 11.2763 | 36.2237 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:29 |  | SP1 |  | 0 | -50 | 74.07% | 13.6473 | 35.1833 | 11.9806 | 25.0208 | -27.2946 | 70.3667 | 100% | 0 | 47.5 | -0.87719 | 10.3991 | 10.3991 | 37.1009 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:30 |  | SP1 |  | 0 | -50 | 75.65% | 12.8139 | 35.9354 | 11.9806 | 25.0208 | -25.6279 | 71.8708 | 100% | 0 | 47.5 | -0.87719 | 9.5219 | 9.5219 | 37.9781 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:31 |  | SP2 |  | 0 | 100 | 77.24% | 11.9806 | 36.6875 | 11.9806 | 25.0208 | -23.9612 | 73.375 | 100% | 0 | 47.5 | 1.5833 | 8.6447 | 8.6447 | 38.8553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:32 |  | SP2 |  | 0 | 100 | 73.73% | 13.8273 | 35.0208 | 13.8273 | 25.0208 | -27.6547 | 70.0417 | 100% | 0 | 47.5 | 1.5833 | 10.2281 | 10.2281 | 37.2719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:33 |  | SP2 |  | 0 | 100 | 70.22% | 15.6741 | 33.3542 | 15.6741 | 25.0208 | -31.3481 | 66.7083 | 100% | 0 | 47.5 | 1.5833 | 11.8114 | 11.8114 | 35.6886 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:34 |  | SP2 |  | 0 | 100 | 66.71% | 17.5208 | 31.6875 | 17.5208 | 25.0208 | -35.0416 | 63.375 | 100% | 0 | 47.5 | 1.5833 | 13.3947 | 13.3947 | 34.1053 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:35 |  | SP2 |  | 0 | 100 | 63.2% | 19.3675 | 30.0208 | 19.3675 | 25.0208 | -38.735 | 60.0417 | 100% | 0 | 47.5 | 1.5833 | 14.9781 | 14.9781 | 32.5219 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:36 |  | SP2 |  | 0 | 100 | 59.69% | 21.2142 | 28.3542 | 21.2142 | 25.0208 | -42.4284 | 56.7083 | 100% | 0 | 47.5 | 1.5833 | 16.5614 | 16.5614 | 30.9386 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:37 |  | SP2 |  | 0 | 100 | 56.18% | 23.0609 | 26.6875 | 23.0609 | 25.0208 | -46.1219 | 53.375 | 100% | 0 | 47.5 | 1.5833 | 18.1447 | 18.1447 | 29.3553 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:38 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:39 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:40 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:41 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:42 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:43 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:44 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:45 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:46 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:47 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
0:00 | 0:48 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:49 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:50 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:51 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:52 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:53 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:54 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:55 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:56 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:57 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:58 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 0:59 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:00 |  | SP2 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:01 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:02 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:03 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:04 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:05 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:06 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:07 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:08 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:09 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:10 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:11 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:12 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:13 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:14 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:15 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:16 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:17 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:18 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:19 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:20 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:21 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:22 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:23 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:24 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:25 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:26 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:27 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:28 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:29 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:30 |  | SP3 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:31 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:32 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:33 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:34 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:35 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:36 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:37 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:38 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:39 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:40 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:41 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:42 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:43 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:44 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:45 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:46 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:47 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:48 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:49 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:50 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:51 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:52 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:53 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:54 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:55 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:56 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:57 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:58 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 1:59 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:00 |  | SP4 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:01 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:02 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:03 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:04 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:05 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:06 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:07 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:08 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:09 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:10 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:11 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:12 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:13 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:14 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:15 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:16 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:17 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:18 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:19 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:20 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:21 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:22 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:23 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:24 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:25 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:26 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:27 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:28 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:29 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:30 |  | SP5 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:31 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:32 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:33 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:34 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:35 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:36 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:37 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:38 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:39 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:40 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:41 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:42 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:43 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:44 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:45 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:46 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:47 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:48 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:49 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:50 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:51 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:52 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:53 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:54 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:55 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:56 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:57 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:58 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 2:59 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:00 |  | SP6 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:01 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:02 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:03 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:04 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:05 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:06 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:07 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:08 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:09 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:10 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:11 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:12 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:13 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:14 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:15 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:16 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:17 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:18 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:19 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:20 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:21 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:22 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:23 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:24 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:25 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:26 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:27 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:28 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:29 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:30 |  | SP7 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:31 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:32 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:33 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:34 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:35 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:36 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:37 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:38 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:39 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:40 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:41 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:42 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:43 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:44 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:45 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:46 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:47 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:48 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:49 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:50 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:51 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:52 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:53 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:54 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:55 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:56 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:57 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:58 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 3:59 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100
| 4:00 |  | SP8 |  | 0 | 0 | 52.68% | 24.9077 | 25.0208 | 24.9077 | 25.0208 | -49.8153 | 50.0417 | 100% | 0 | 47.5 | 0 | 19.7281 | 19.7281 | 27.7719 | 0 | 0% | 0 | 100 |  | 0 | 0 | 100% | 0 | -100