## Version
Date | Version | Details
2025-03-14 | 1 | This file only contains the indicative reporting associated with draft data for GC0151 for March 2025. This file will be updated in April 2025 to reflect the full data set.
2025-04-15 | 2 | This file only contains the indicative reporting associated with data for GC0151 for March 2025. This file is updated in April 2025 to reflect the full data set.
2025-05-01 | 3 | This file contains the reporting associated with data for GC0105 & GC0151 for March 2025.

## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.
MW trip/loss of all generation/ interconnection related to the incident | Positive sign: indicates a loss of infeed, generator or importing interconnector. Negative sign: indicates a loss of outfeed, exporting interconnector.

## Transmission Faults (GC0151)
Location | Network Operator | Date Time | Voltage Trace (Refer to sheet) | Notes
Walney Extension Export Cable 4 | OFTO | 2025-03-08 16:50
Aberthaw 275kV Reserve Busbar | NGET | 2025-03-09 23:48
Blyth - Eccles - Stew 2 400kV circuit | NGET/SPT | 2025-03-14 20:59
Smeaton - Portobello - Shrubhill 2 275kV circuit, Poob 275/33kV SGT2A, Shru 275/33kV SGT2A | SPT | 2025-03-16 01:33
Fleet 400/132kV SGT1A | NGET | 2025-03-17 03:37
North Hyde 66kV substation, 275/66kV SGT3 | NGET | 2025-03-20 23:22
North Hyde 66kV Substation, 275/66kV SGT1 | NGET | 2025-03-20 23:49
Blackhillock - Moray West 1 circuit | SHETL | 2025-03-28 11:57

## System Incidents (GC0105)
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; |  | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) |  | Transmission fault | Voltage Dip | Additional data
20250302-1 | Trip of IFA2 | Importing from FR to GB | 2025-03-02 03:52 | 20250302-1 | 50.059 | 49.815 | -0.16658 | 143 | IFA2 | 991.71
20250310-1 | Trip of PEMB-41 |  | 2025-03-10 07:00 | 20250310-1 | 50.09 | 50.012 | -0.026232 | 210 | PEMB-41 | 420
20250310-2 | Loss of Demand | Loss of demand at Dunbar followed by TO switching | 2025-03-10 23:27 | 20250310-2 | [7 empty] | SPEN | 8
20250313-1 | Trip of MEDP-1 | Instantaneous loss 137.2MW | 2025-03-13 19:28 | 20250313-1 | 49.957 | 49.927 | -0.014876 | 298 | MEDP-1 | 263.95
20250314-1 | Trip of DRAX units | DRAX-1 (654.94MW) - Instantaneous DRAX-2 (612.51MW) & DRAX-3 (609.52) - 5sec later | 2025-03-14 08:52 | 20250314-1 | 50.121 | 49.673 | -0.094812 | 267 | DRAX-1 DRAX-2, DRAX-3 | 1876.97
20250314-2 | Trip of PEMB-11 |  | 2025-03-14 22:09 | 20250314-2 | 50.022 | 49.898 | -0.050838 | 241 | PEMB-11 | 444.68
20250319-1 | Trip of SPLN-1 | Instantaneous loss 249MW | 2025-03-19 12:16 | 20250319-1 | 50.044 | 49.958 | -0.019857 | 225 | SPLN-1 | 848.98
20250319-2 | Trip of MEDP-1 | Instantaneous loss 145.44MW | 2025-03-19 19:54 | 20250319-2 | 50.16 | 50.124 | -0.015125 | 302 | MEDP-1 | 395.75
20250320-1 | Trip of COSO-1 | Instantaneous loss 232.19MW | 2025-03-20 17:30 | 20250320-1 | 49.982 | 49.907 | -0.027723 | 239 | COSO-1 | 600.11
20250320-2 | Loss of Demand | Loss of demand at North Hyde substation due to SGT3 fire | 2025-03-20 23:49 | 20250320-2 | [7 empty] | SSEN | 96 | North Hyde SGT3 on fire
20250323-1 | Trip of CDCL-1 | Instantaneous loss 248.88MW | 2025-03-23 08:47 | 20250323-1 | 49.94 | 49.873 | -0.048343 | 149 | CDCL-1 | 299.39
20250324-1 | Loss of Demand | Loss of demand at Lydney and Port Ham for switching time | 2025-03-24 10:31 | 20250324-1 | [7 empty] | NGED | 4

## 20250302-1
In GMT
Date | Time | Freq
2025-03-02 | 3:51 | 50.062 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-02 | 3:51 | 50.061 | 222 | BRITNED | 676.211
2025-03-02 | 3:51 | 50.059 | 268 | WBURB-2 | 428.156
2025-03-02 | 3:51 | 50.067 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-02 | 3:51 | 50.069 |  | Viking Link | -648.9
2025-03-02 | 3:51 | 50.068 |  | Viking Link | 1398.96
2025-03-02 | 3:51 | 50.065 | 209 | DRAXX-3 | 626.95
2025-03-02 | 3:51 | 50.073 | 154 | CDCL-1 | 391.57
2025-03-02 | 3:51 | 50.072 | 268 | ROCK-1 | 468.495
2025-03-02 | 3:51 | 50.063 | 148 | IFA Bipole1 | 945.473
2025-03-02 | 3:51 | 50.062 | 132 | IFA Bipole1 | 999.1
2025-03-02 | 3:51 | 50.068 | 141 | IFA Bipole2 | 1000
2025-03-02 | 3:52 | 50.065 | 135 | IFA Bipole1 | 996.75
2025-03-02 | 3:52 | 50.06 |  | Viking Link | -780.3
2025-03-02 | 3:52 | 50.061
2025-03-02 | 3:52 | 50.063
2025-03-02 | 3:52 | 50.059
2025-03-02 | 3:52 | 50.056
2025-03-02 | 3:52 | 50.069
2025-03-02 | 3:52 | 50.072 | 130 | HEYM12 | 271.908
2025-03-02 | 3:52 | 50.067 | 228 | HUMR-1 | 303.75
2025-03-02 | 3:52 | 50.067
2025-03-02 | 3:52 | 50.074
2025-03-02 | 3:52 | 50.071
2025-03-02 | 3:52 | 50.067
2025-03-02 | 3:52 | 50.066
2025-03-02 | 3:52 | 50.073
2025-03-02 | 3:52 | 50.067
2025-03-02 | 3:52 | 50.061
2025-03-02 | 3:52 | 50.06
2025-03-02 | 3:52 | 50.066 | 211 | CDCL-1 | 291.5
2025-03-02 | 3:52 | 50.063 | 199 | STAY-2 | 413.125
2025-03-02 | 3:52 | 50.059 | 173 | CDCL-1 | 397.375
2025-03-02 | 3:52 | 50.065 | 248 | SEAB-2 | 361.25
2025-03-02 | 3:52 | 50.064 | 255 | FRANCE | 995.65
2025-03-02 | 3:52 | 50.059 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-02 | 3:52 | 50.065
2025-03-02 | 3:52 | 50.075
2025-03-02 | 3:52 | 50.072
2025-03-02 | 3:52 | 50.061
2025-03-02 | 3:52 | 50.062
2025-03-02 | 3:52 | 50.068
2025-03-02 | 3:52 | 50.066
2025-03-02 | 3:52 | 50.061
2025-03-02 | 3:52 | 50.062
2025-03-02 | 3:52 | 50.062
2025-03-02 | 3:52 | 50.053
2025-03-02 | 3:52 | 50.051
2025-03-02 | 3:52 | 50.049
2025-03-02 | 3:52 | 50.055
2025-03-02 | 3:52 | 50.059
2025-03-02 | 3:52 | 50.06
2025-03-02 | 3:52 | 50.059
2025-03-02 | 3:52 | 49.987
2025-03-02 | 3:52 | 49.868
2025-03-02 | 3:52 | 49.818
2025-03-02 | 3:52 | 49.815
2025-03-02 | 3:52 | 49.822
2025-03-02 | 3:52 | 49.835
2025-03-02 | 3:52 | 49.831
2025-03-02 | 3:52 | 49.83
2025-03-02 | 3:52 | 49.834
2025-03-02 | 3:52 | 49.838
2025-03-02 | 3:52 | 49.835
2025-03-02 | 3:52 | 49.828
2025-03-02 | 3:52 | 49.836
2025-03-02 | 3:52 | 49.837
2025-03-02 | 3:52 | 49.828
2025-03-02 | 3:52 | 49.828
2025-03-02 | 3:52 | 49.836
2025-03-02 | 3:52 | 49.828
2025-03-02 | 3:52 | 49.822
2025-03-02 | 3:52 | 49.826
2025-03-02 | 3:53 | 49.832
2025-03-02 | 3:53 | 49.827
2025-03-02 | 3:53 | 49.818
2025-03-02 | 3:53 | 49.826
2025-03-02 | 3:53 | 49.827
2025-03-02 | 3:53 | 49.82
2025-03-02 | 3:53 | 49.819
2025-03-02 | 3:53 | 49.824
2025-03-02 | 3:53 | 49.819
2025-03-02 | 3:53 | 49.818
2025-03-02 | 3:53 | 49.819
2025-03-02 | 3:53 | 49.822
2025-03-02 | 3:53 | 49.821
2025-03-02 | 3:53 | 49.816
2025-03-02 | 3:53 | 49.823
2025-03-02 | 3:53 | 49.819
2025-03-02 | 3:53 | 49.813
2025-03-02 | 3:53 | 49.812
2025-03-02 | 3:53 | 49.822
2025-03-02 | 3:53 | 49.816
2025-03-02 | 3:53 | 49.812
2025-03-02 | 3:53 | 49.814
2025-03-02 | 3:53 | 49.818
2025-03-02 | 3:53 | 49.817
2025-03-02 | 3:53 | 49.81
2025-03-02 | 3:53 | 49.819
2025-03-02 | 3:53 | 49.811
2025-03-02 | 3:53 | 49.814
2025-03-02 | 3:53 | 49.819
2025-03-02 | 3:53 | 49.813
2025-03-02 | 3:53 | 49.815
2025-03-02 | 3:53 | 49.815
2025-03-02 | 3:53 | 49.81
2025-03-02 | 3:53 | 49.808
2025-03-02 | 3:53 | 49.815
2025-03-02 | 3:53 | 49.815
2025-03-02 | 3:53 | 49.81
2025-03-02 | 3:53 | 49.806
2025-03-02 | 3:53 | 49.817
2025-03-02 | 3:53 | 49.812
2025-03-02 | 3:53 | 49.806
2025-03-02 | 3:53 | 49.813
2025-03-02 | 3:53 | 49.818
2025-03-02 | 3:53 | 49.811
2025-03-02 | 3:53 | 49.808
2025-03-02 | 3:53 | 49.816
2025-03-02 | 3:53 | 49.817
2025-03-02 | 3:53 | 49.815
2025-03-02 | 3:53 | 49.813
2025-03-02 | 3:53 | 49.825
2025-03-02 | 3:53 | 49.822
2025-03-02 | 3:53 | 49.821
2025-03-02 | 3:53 | 49.829
2025-03-02 | 3:53 | 49.833
2025-03-02 | 3:53 | 49.833
2025-03-02 | 3:53 | 49.834
2025-03-02 | 3:53 | 49.844
2025-03-02 | 3:53 | 49.846
2025-03-02 | 3:53 | 49.84
2025-03-02 | 3:54 | 49.841
2025-03-02 | 3:54 | 49.849
2025-03-02 | 3:54 | 49.847
2025-03-02 | 3:54 | 49.843
2025-03-02 | 3:54 | 49.847
2025-03-02 | 3:54 | 49.851
2025-03-02 | 3:54 | 49.847
2025-03-02 | 3:54 | 49.845
2025-03-02 | 3:54 | 49.853
2025-03-02 | 3:54 | 49.853
2025-03-02 | 3:54 | 49.848
2025-03-02 | 3:54 | 49.847
2025-03-02 | 3:54 | 49.854
2025-03-02 | 3:54 | 49.854
2025-03-02 | 3:54 | 49.847
2025-03-02 | 3:54 | 49.854
2025-03-02 | 3:54 | 49.856
2025-03-02 | 3:54 | 49.849
2025-03-02 | 3:54 | 49.848
2025-03-02 | 3:54 | 49.854
2025-03-02 | 3:54 | 49.855
2025-03-02 | 3:54 | 49.848
2025-03-02 | 3:54 | 49.848
2025-03-02 | 3:54 | 49.855
2025-03-02 | 3:54 | 49.851
2025-03-02 | 3:54 | 49.846
2025-03-02 | 3:54 | 49.851
2025-03-02 | 3:54 | 49.856
2025-03-02 | 3:54 | 49.851
2025-03-02 | 3:54 | 49.847
2025-03-02 | 3:54 | 49.856
2025-03-02 | 3:54 | 49.855
2025-03-02 | 3:54 | 49.85
2025-03-02 | 3:54 | 49.854
2025-03-02 | 3:54 | 49.864
2025-03-02 | 3:54 | 49.856
2025-03-02 | 3:54 | 49.851
2025-03-02 | 3:54 | 49.856
2025-03-02 | 3:54 | 49.859
2025-03-02 | 3:54 | 49.855
2025-03-02 | 3:54 | 49.858
2025-03-02 | 3:54 | 49.86
2025-03-02 | 3:54 | 49.853
2025-03-02 | 3:54 | 49.861
2025-03-02 | 3:54 | 49.856
2025-03-02 | 3:54 | 49.853
2025-03-02 | 3:54 | 49.858
2025-03-02 | 3:54 | 49.863
2025-03-02 | 3:54 | 49.86
2025-03-02 | 3:54 | 49.855
2025-03-02 | 3:54 | 49.863
2025-03-02 | 3:54 | 49.862
2025-03-02 | 3:54 | 49.857
2025-03-02 | 3:54 | 49.855
2025-03-02 | 3:54 | 49.863
2025-03-02 | 3:54 | 49.859
2025-03-02 | 3:54 | 49.855
2025-03-02 | 3:54 | 49.858
2025-03-02 | 3:54 | 49.862
2025-03-02 | 3:54 | 49.859
2025-03-02 | 3:54 | 49.857
2025-03-02 | 3:55 | 49.862
2025-03-02 | 3:55 | 49.862
2025-03-02 | 3:55 | 49.855
2025-03-02 | 3:55 | 49.855
2025-03-02 | 3:55 | 49.864
2025-03-02 | 3:55 | 49.859
2025-03-02 | 3:55 | 49.857
2025-03-02 | 3:55 | 49.861
2025-03-02 | 3:55 | 49.866
2025-03-02 | 3:55 | 49.862
2025-03-02 | 3:55 | 49.858
2025-03-02 | 3:55 | 49.865
2025-03-02 | 3:55 | 49.866
2025-03-02 | 3:55 | 49.858
2025-03-02 | 3:55 | 49.859
2025-03-02 | 3:55 | 49.868
2025-03-02 | 3:55 | 49.865
2025-03-02 | 3:55 | 49.863
2025-03-02 | 3:55 | 49.866
2025-03-02 | 3:55 | 49.87
2025-03-02 | 3:55 | 49.863
2025-03-02 | 3:55 | 49.858
2025-03-02 | 3:55 | 49.865
2025-03-02 | 3:55 | 49.868
2025-03-02 | 3:55 | 49.86
2025-03-02 | 3:55 | 49.859
2025-03-02 | 3:55 | 49.868
2025-03-02 | 3:55 | 49.864
2025-03-02 | 3:55 | 49.862
2025-03-02 | 3:55 | 49.863
2025-03-02 | 3:55 | 49.865
2025-03-02 | 3:55 | 49.866
2025-03-02 | 3:55 | 49.864
2025-03-02 | 3:55 | 49.865
2025-03-02 | 3:55 | 49.867
2025-03-02 | 3:55 | 49.861
2025-03-02 | 3:55 | 49.859
2025-03-02 | 3:55 | 49.869
2025-03-02 | 3:55 | 49.868
2025-03-02 | 3:55 | 49.861
2025-03-02 | 3:55 | 49.862
2025-03-02 | 3:55 | 49.87
2025-03-02 | 3:55 | 49.868
2025-03-02 | 3:55 | 49.864
2025-03-02 | 3:55 | 49.868
2025-03-02 | 3:55 | 49.865
2025-03-02 | 3:55 | 49.871
2025-03-02 | 3:55 | 49.873
2025-03-02 | 3:55 | 49.865
2025-03-02 | 3:55 | 49.867
2025-03-02 | 3:55 | 49.873
2025-03-02 | 3:55 | 49.87
2025-03-02 | 3:55 | 49.866
2025-03-02 | 3:55 | 49.867
2025-03-02 | 3:55 | 49.873
2025-03-02 | 3:55 | 49.866
2025-03-02 | 3:55 | 49.864
2025-03-02 | 3:55 | 49.868
2025-03-02 | 3:55 | 49.873
2025-03-02 | 3:56 | 49.868
2025-03-02 | 3:56 | 49.864
2025-03-02 | 3:56 | 49.872
2025-03-02 | 3:56 | 49.871
2025-03-02 | 3:56 | 49.864
2025-03-02 | 3:56 | 49.863
2025-03-02 | 3:56 | 49.871
2025-03-02 | 3:56 | 49.867
2025-03-02 | 3:56 | 49.866
2025-03-02 | 3:56 | 49.872
2025-03-02 | 3:56 | 49.871
2025-03-02 | 3:56 | 49.866
2025-03-02 | 3:56 | 49.863
2025-03-02 | 3:56 | 49.867
2025-03-02 | 3:56 | 49.867
2025-03-02 | 3:56 | 49.858
2025-03-02 | 3:56 | 49.859
2025-03-02 | 3:56 | 49.864
2025-03-02 | 3:56 | 49.861
2025-03-02 | 3:56 | 49.859
2025-03-02 | 3:56 | 49.863
2025-03-02 | 3:56 | 49.869
2025-03-02 | 3:56 | 49.867
2025-03-02 | 3:56 | 49.865
2025-03-02 | 3:56 | 49.87
2025-03-02 | 3:56 | 49.872
2025-03-02 | 3:56 | 49.869
2025-03-02 | 3:56 | 49.864
2025-03-02 | 3:56 | 49.873
2025-03-02 | 3:56 | 49.872
2025-03-02 | 3:56 | 49.865
2025-03-02 | 3:56 | 49.87
2025-03-02 | 3:56 | 49.881
2025-03-02 | 3:56 | 49.878
2025-03-02 | 3:56 | 49.872
2025-03-02 | 3:56 | 49.874
2025-03-02 | 3:56 | 49.876
2025-03-02 | 3:56 | 49.873
2025-03-02 | 3:56 | 49.874
2025-03-02 | 3:56 | 49.882
2025-03-02 | 3:56 | 49.883
2025-03-02 | 3:56 | 49.88
2025-03-02 | 3:56 | 49.884
2025-03-02 | 3:56 | 49.891
2025-03-02 | 3:56 | 49.884
2025-03-02 | 3:56 | 49.88
2025-03-02 | 3:56 | 49.884
2025-03-02 | 3:56 | 49.891
2025-03-02 | 3:56 | 49.888
2025-03-02 | 3:56 | 49.884
2025-03-02 | 3:56 | 49.889
2025-03-02 | 3:56 | 49.884
2025-03-02 | 3:56 | 49.88
2025-03-02 | 3:56 | 49.883
2025-03-02 | 3:56 | 49.894
2025-03-02 | 3:56 | 49.892
2025-03-02 | 3:56 | 49.886
2025-03-02 | 3:56 | 49.892
2025-03-02 | 3:56 | 49.897
2025-03-02 | 3:56 | 49.893
2025-03-02 | 3:56 | 49.888
2025-03-02 | 3:57 | 49.897
2025-03-02 | 3:57 | 49.897
2025-03-02 | 3:57 | 49.886
2025-03-02 | 3:57 | 49.886
2025-03-02 | 3:57 | 49.894
2025-03-02 | 3:57 | 49.891
2025-03-02 | 3:57 | 49.882
2025-03-02 | 3:57 | 49.886
2025-03-02 | 3:57 | 49.888
2025-03-02 | 3:57 | 49.885
2025-03-02 | 3:57 | 49.886
2025-03-02 | 3:57 | 49.893
2025-03-02 | 3:57 | 49.893
2025-03-02 | 3:57 | 49.886
2025-03-02 | 3:57 | 49.887
2025-03-02 | 3:57 | 49.894
2025-03-02 | 3:57 | 49.892
2025-03-02 | 3:57 | 49.89
2025-03-02 | 3:57 | 49.892
2025-03-02 | 3:57 | 49.887
2025-03-02 | 3:57 | 49.894
2025-03-02 | 3:57 | 49.896
2025-03-02 | 3:57 | 49.887
2025-03-02 | 3:57 | 49.888
2025-03-02 | 3:57 | 49.895
2025-03-02 | 3:57 | 49.894
2025-03-02 | 3:57 | 49.885
2025-03-02 | 3:57 | 49.884
2025-03-02 | 3:57 | 49.891
2025-03-02 | 3:57 | 49.884
2025-03-02 | 3:57 | 49.878
2025-03-02 | 3:57 | 49.886
2025-03-02 | 3:57 | 49.888
2025-03-02 | 3:57 | 49.88
2025-03-02 | 3:57 | 49.882
2025-03-02 | 3:57 | 49.893
2025-03-02 | 3:57 | 49.892
2025-03-02 | 3:57 | 49.887
2025-03-02 | 3:57 | 49.889
2025-03-02 | 3:57 | 49.896
2025-03-02 | 3:57 | 49.891
2025-03-02 | 3:57 | 49.886
2025-03-02 | 3:57 | 49.893
2025-03-02 | 3:57 | 49.895
2025-03-02 | 3:57 | 49.888
2025-03-02 | 3:57 | 49.885
2025-03-02 | 3:57 | 49.892
2025-03-02 | 3:57 | 49.897
2025-03-02 | 3:57 | 49.888
2025-03-02 | 3:57 | 49.886
2025-03-02 | 3:57 | 49.897
2025-03-02 | 3:57 | 49.894
2025-03-02 | 3:57 | 49.887
2025-03-02 | 3:57 | 49.888
2025-03-02 | 3:57 | 49.89
2025-03-02 | 3:57 | 49.889
2025-03-02 | 3:57 | 49.89
2025-03-02 | 3:57 | 49.896
2025-03-02 | 3:57 | 49.895
2025-03-02 | 3:58 | 49.887
2025-03-02 | 3:58 | 49.887
2025-03-02 | 3:58 | 49.895
2025-03-02 | 3:58 | 49.891
2025-03-02 | 3:58 | 49.885
2025-03-02 | 3:58 | 49.892
2025-03-02 | 3:58 | 49.894
2025-03-02 | 3:58 | 49.891
2025-03-02 | 3:58 | 49.891
2025-03-02 | 3:58 | 49.899
2025-03-02 | 3:58 | 49.897
2025-03-02 | 3:58 | 49.889
2025-03-02 | 3:58 | 49.891
2025-03-02 | 3:58 | 49.898
2025-03-02 | 3:58 | 49.894
2025-03-02 | 3:58 | 49.889
2025-03-02 | 3:58 | 49.892
2025-03-02 | 3:58 | 49.894
2025-03-02 | 3:58 | 49.889
2025-03-02 | 3:58 | 49.887
2025-03-02 | 3:58 | 49.895
2025-03-02 | 3:58 | 49.894
2025-03-02 | 3:58 | 49.887
2025-03-02 | 3:58 | 49.888
2025-03-02 | 3:58 | 49.894
2025-03-02 | 3:58 | 49.89
2025-03-02 | 3:58 | 49.886
2025-03-02 | 3:58 | 49.892
2025-03-02 | 3:58 | 49.893
2025-03-02 | 3:58 | 49.889
2025-03-02 | 3:58 | 49.885
2025-03-02 | 3:58 | 49.892
2025-03-02 | 3:58 | 49.891
2025-03-02 | 3:58 | 49.885
2025-03-02 | 3:58 | 49.888
2025-03-02 | 3:58 | 49.893
2025-03-02 | 3:58 | 49.891
2025-03-02 | 3:58 | 49.886
2025-03-02 | 3:58 | 49.888
2025-03-02 | 3:58 | 49.886
2025-03-02 | 3:58 | 49.893
2025-03-02 | 3:58 | 49.892
2025-03-02 | 3:58 | 49.886
2025-03-02 | 3:58 | 49.886
2025-03-02 | 3:58 | 49.893
2025-03-02 | 3:58 | 49.89
2025-03-02 | 3:58 | 49.885
2025-03-02 | 3:58 | 49.891
2025-03-02 | 3:58 | 49.892
2025-03-02 | 3:58 | 49.886
2025-03-02 | 3:58 | 49.884
2025-03-02 | 3:58 | 49.893
2025-03-02 | 3:58 | 49.891
2025-03-02 | 3:58 | 49.885
2025-03-02 | 3:58 | 49.884
2025-03-02 | 3:58 | 49.892
2025-03-02 | 3:58 | 49.889
2025-03-02 | 3:58 | 49.887
2025-03-02 | 3:58 | 49.893
2025-03-02 | 3:58 | 49.894
2025-03-02 | 3:58 | 49.888
2025-03-02 | 3:59 | 49.886
2025-03-02 | 3:59 | 49.892
2025-03-02 | 3:59 | 49.892
2025-03-02 | 3:59 | 49.887
2025-03-02 | 3:59 | 49.887
2025-03-02 | 3:59 | 49.894
2025-03-02 | 3:59 | 49.89
2025-03-02 | 3:59 | 49.885
2025-03-02 | 3:59 | 49.89
2025-03-02 | 3:59 | 49.894
2025-03-02 | 3:59 | 49.89
2025-03-02 | 3:59 | 49.887
2025-03-02 | 3:59 | 49.893
2025-03-02 | 3:59 | 49.893
2025-03-02 | 3:59 | 49.886
2025-03-02 | 3:59 | 49.886
2025-03-02 | 3:59 | 49.892
2025-03-02 | 3:59 | 49.89
2025-03-02 | 3:59 | 49.885
2025-03-02 | 3:59 | 49.889
2025-03-02 | 3:59 | 49.893
2025-03-02 | 3:59 | 49.888
2025-03-02 | 3:59 | 49.886
2025-03-02 | 3:59 | 49.893
2025-03-02 | 3:59 | 49.893
2025-03-02 | 3:59 | 49.887
2025-03-02 | 3:59 | 49.887
2025-03-02 | 3:59 | 49.893
2025-03-02 | 3:59 | 49.889
2025-03-02 | 3:59 | 49.885
2025-03-02 | 3:59 | 49.884
2025-03-02 | 3:59 | 49.886
2025-03-02 | 3:59 | 49.882
2025-03-02 | 3:59 | 49.88
2025-03-02 | 3:59 | 49.888
2025-03-02 | 3:59 | 49.886
2025-03-02 | 3:59 | 49.88
2025-03-02 | 3:59 | 49.881
2025-03-02 | 3:59 | 49.888
2025-03-02 | 3:59 | 49.881
2025-03-02 | 3:59 | 49.874
2025-03-02 | 3:59 | 49.877
2025-03-02 | 3:59 | 49.881
2025-03-02 | 3:59 | 49.877
2025-03-02 | 3:59 | 49.873
2025-03-02 | 3:59 | 49.88
2025-03-02 | 3:59 | 49.88
2025-03-02 | 3:59 | 49.875
2025-03-02 | 3:59 | 49.873
2025-03-02 | 3:59 | 49.882
2025-03-02 | 3:59 | 49.879
2025-03-02 | 3:59 | 49.877
2025-03-02 | 3:59 | 49.881
2025-03-02 | 3:59 | 49.884
2025-03-02 | 3:59 | 49.88
2025-03-02 | 3:59 | 49.878
2025-03-02 | 3:59 | 49.883
2025-03-02 | 3:59 | 49.884
2025-03-02 | 3:59 | 49.879
2025-03-02 | 4:00 | 49.878
2025-03-02 | 4:00 | 49.884
2025-03-02 | 4:00 | 49.881
2025-03-02 | 4:00 | 49.877
2025-03-02 | 4:00 | 49.878
2025-03-02 | 4:00 | 49.877
2025-03-02 | 4:00 | 49.883
2025-03-02 | 4:00 | 49.885
2025-03-02 | 4:00 | 49.882
2025-03-02 | 4:00 | 49.879
2025-03-02 | 4:00 | 49.882
2025-03-02 | 4:00 | 49.885
2025-03-02 | 4:00 | 49.881
2025-03-02 | 4:00 | 49.88
2025-03-02 | 4:00 | 49.886
2025-03-02 | 4:00 | 49.887
2025-03-02 | 4:00 | 49.882
2025-03-02 | 4:00 | 49.882
2025-03-02 | 4:00 | 49.888
2025-03-02 | 4:00 | 49.886
2025-03-02 | 4:00 | 49.88
2025-03-02 | 4:00 | 49.887
2025-03-02 | 4:00 | 49.891
2025-03-02 | 4:00 | 49.887
2025-03-02 | 4:00 | 49.884
2025-03-02 | 4:00 | 49.889
2025-03-02 | 4:00 | 49.891
2025-03-02 | 4:00 | 49.886
2025-03-02 | 4:00 | 49.888
2025-03-02 | 4:00 | 49.897
2025-03-02 | 4:00 | 49.894
2025-03-02 | 4:00 | 49.894
2025-03-02 | 4:00 | 49.898
2025-03-02 | 4:00 | 49.898
2025-03-02 | 4:00 | 49.894
2025-03-02 | 4:00 | 49.886
2025-03-02 | 4:00 | 49.891
2025-03-02 | 4:00 | 49.89
2025-03-02 | 4:00 | 49.884
2025-03-02 | 4:00 | 49.884
2025-03-02 | 4:00 | 49.892
2025-03-02 | 4:00 | 49.887
2025-03-02 | 4:00 | 49.884
2025-03-02 | 4:00 | 49.888
2025-03-02 | 4:00 | 49.893
2025-03-02 | 4:00 | 49.888
2025-03-02 | 4:00 | 49.885
2025-03-02 | 4:00 | 49.893
2025-03-02 | 4:00 | 49.893
2025-03-02 | 4:00 | 49.887
2025-03-02 | 4:00 | 49.886
2025-03-02 | 4:00 | 49.892
2025-03-02 | 4:00 | 49.887
2025-03-02 | 4:00 | 49.883
2025-03-02 | 4:00 | 49.885
2025-03-02 | 4:00 | 49.889
2025-03-02 | 4:00 | 49.887
2025-03-02 | 4:00 | 49.886
2025-03-02 | 4:00 | 49.893
2025-03-02 | 4:00 | 49.891
2025-03-02 | 4:00 | 49.888
2025-03-02 | 4:01 | 49.886
2025-03-02 | 4:01 | 49.894
2025-03-02 | 4:01 | 49.89
2025-03-02 | 4:01 | 49.884
2025-03-02 | 4:01 | 49.885
2025-03-02 | 4:01 | 49.891
2025-03-02 | 4:01 | 49.886
2025-03-02 | 4:01 | 49.881
2025-03-02 | 4:01 | 49.886
2025-03-02 | 4:01 | 49.887
2025-03-02 | 4:01 | 49.879
2025-03-02 | 4:01 | 49.882
2025-03-02 | 4:01 | 49.892
2025-03-02 | 4:01 | 49.892
2025-03-02 | 4:01 | 49.885
2025-03-02 | 4:01 | 49.885
2025-03-02 | 4:01 | 49.891
2025-03-02 | 4:01 | 49.887
2025-03-02 | 4:01 | 49.89
2025-03-02 | 4:01 | 49.904
2025-03-02 | 4:01 | 49.906
2025-03-02 | 4:01 | 49.9
2025-03-02 | 4:01 | 49.896
2025-03-02 | 4:01 | 49.901
2025-03-02 | 4:01 | 49.899
2025-03-02 | 4:01 | 49.891
2025-03-02 | 4:01 | 49.892
2025-03-02 | 4:01 | 49.901
2025-03-02 | 4:01 | 49.898
2025-03-02 | 4:01 | 49.894
2025-03-02 | 4:01 | 49.899
2025-03-02 | 4:01 | 49.901
2025-03-02 | 4:01 | 49.893
2025-03-02 | 4:01 | 49.893
2025-03-02 | 4:01 | 49.899
2025-03-02 | 4:01 | 49.9
2025-03-02 | 4:01 | 49.901
2025-03-02 | 4:01 | 49.896
2025-03-02 | 4:01 | 49.892
2025-03-02 | 4:01 | 49.896
2025-03-02 | 4:01 | 49.899
2025-03-02 | 4:01 | 49.893
2025-03-02 | 4:01 | 49.889
2025-03-02 | 4:01 | 49.896
2025-03-02 | 4:01 | 49.895
2025-03-02 | 4:01 | 49.89
2025-03-02 | 4:01 | 49.895
2025-03-02 | 4:01 | 49.895
2025-03-02 | 4:01 | 49.893
2025-03-02 | 4:01 | 49.891
2025-03-02 | 4:01 | 49.894
2025-03-02 | 4:01 | 49.899
2025-03-02 | 4:01 | 49.898
2025-03-02 | 4:01 | 49.892
2025-03-02 | 4:01 | 49.897
2025-03-02 | 4:01 | 49.901
2025-03-02 | 4:01 | 49.898
2025-03-02 | 4:01 | 49.895
2025-03-02 | 4:01 | 49.904
2025-03-02 | 4:01 | 49.904
2025-03-02 | 4:02 | 49.899
2025-03-02 | 4:02 | 49.899
2025-03-02 | 4:02 | 49.907
2025-03-02 | 4:02 | 49.904
2025-03-02 | 4:02 | 49.903
2025-03-02 | 4:02 | 49.907
2025-03-02 | 4:02 | 49.912
2025-03-02 | 4:02 | 49.909
2025-03-02 | 4:02 | 49.907
2025-03-02 | 4:02 | 49.913
2025-03-02 | 4:02 | 49.913
2025-03-02 | 4:02 | 49.908
2025-03-02 | 4:02 | 49.91
2025-03-02 | 4:02 | 49.917
2025-03-02 | 4:02 | 49.912
2025-03-02 | 4:02 | 49.909
2025-03-02 | 4:02 | 49.914
2025-03-02 | 4:02 | 49.917
2025-03-02 | 4:02 | 49.914
2025-03-02 | 4:02 | 49.911
2025-03-02 | 4:02 | 49.918
2025-03-02 | 4:02 | 49.918
2025-03-02 | 4:02 | 49.913
2025-03-02 | 4:02 | 49.914
2025-03-02 | 4:02 | 49.921
2025-03-02 | 4:02 | 49.921
2025-03-02 | 4:02 | 49.914
2025-03-02 | 4:02 | 49.914
2025-03-02 | 4:02 | 49.922
2025-03-02 | 4:02 | 49.918
2025-03-02 | 4:02 | 49.908
2025-03-02 | 4:02 | 49.908
2025-03-02 | 4:02 | 49.909
2025-03-02 | 4:02 | 49.906
2025-03-02 | 4:02 | 49.903
2025-03-02 | 4:02 | 49.911
2025-03-02 | 4:02 | 49.913
2025-03-02 | 4:02 | 49.908
2025-03-02 | 4:02 | 49.909
2025-03-02 | 4:02 | 49.916
2025-03-02 | 4:02 | 49.912
2025-03-02 | 4:02 | 49.908
2025-03-02 | 4:02 | 49.911
2025-03-02 | 4:02 | 49.915
2025-03-02 | 4:02 | 49.911
2025-03-02 | 4:02 | 49.909
2025-03-02 | 4:02 | 49.916
2025-03-02 | 4:02 | 49.917
2025-03-02 | 4:02 | 49.911
2025-03-02 | 4:02 | 49.912
2025-03-02 | 4:02 | 49.918
2025-03-02 | 4:02 | 49.914
2025-03-02 | 4:02 | 49.912
2025-03-02 | 4:02 | 49.915
2025-03-02 | 4:02 | 49.918
2025-03-02 | 4:02 | 49.913
2025-03-02 | 4:02 | 49.91
2025-03-02 | 4:02 | 49.916
2025-03-02 | 4:02 | 49.915
2025-03-02 | 4:03 | 49.91
2025-03-02 | 4:03 | 49.909
2025-03-02 | 4:03 | 49.916
2025-03-02 | 4:03 | 49.912
2025-03-02 | 4:03 | 49.909
2025-03-02 | 4:03 | 49.909
2025-03-02 | 4:03 | 49.909
2025-03-02 | 4:03 | 49.912
2025-03-02 | 4:03 | 49.916
2025-03-02 | 4:03 | 49.909
2025-03-02 | 4:03 | 49.902
2025-03-02 | 4:03 | 49.905
2025-03-02 | 4:03 | 49.903
2025-03-02 | 4:03 | 49.896
2025-03-02 | 4:03 | 49.896
2025-03-02 | 4:03 | 49.901
2025-03-02 | 4:03 | 49.898
2025-03-02 | 4:03 | 49.893
2025-03-02 | 4:03 | 49.897
2025-03-02 | 4:03 | 49.899
2025-03-02 | 4:03 | 49.896
2025-03-02 | 4:03 | 49.892
2025-03-02 | 4:03 | 49.899
2025-03-02 | 4:03 | 49.9
2025-03-02 | 4:03 | 49.9
2025-03-02 | 4:03 | 49.898
2025-03-02 | 4:03 | 49.897
2025-03-02 | 4:03 | 49.893
2025-03-02 | 4:03 | 49.9
2025-03-02 | 4:03 | 49.9
2025-03-02 | 4:03 | 49.892
2025-03-02 | 4:03 | 49.89
2025-03-02 | 4:03 | 49.897
2025-03-02 | 4:03 | 49.896
2025-03-02 | 4:03 | 49.897
2025-03-02 | 4:03 | 49.895
2025-03-02 | 4:03 | 49.898
2025-03-02 | 4:03 | 49.899
2025-03-02 | 4:03 | 49.899
2025-03-02 | 4:03 | 49.891
2025-03-02 | 4:03 | 49.892
2025-03-02 | 4:03 | 49.899
2025-03-02 | 4:03 | 49.894
2025-03-02 | 4:03 | 49.891
2025-03-02 | 4:03 | 49.895
2025-03-02 | 4:03 | 49.898
2025-03-02 | 4:03 | 49.895
2025-03-02 | 4:03 | 49.89
2025-03-02 | 4:03 | 49.897
2025-03-02 | 4:03 | 49.897
2025-03-02 | 4:03 | 49.889
2025-03-02 | 4:03 | 49.887
2025-03-02 | 4:03 | 49.896
2025-03-02 | 4:03 | 49.892
2025-03-02 | 4:03 | 49.888
2025-03-02 | 4:03 | 49.889
2025-03-02 | 4:03 | 49.896
2025-03-02 | 4:03 | 49.894
2025-03-02 | 4:03 | 49.89
2025-03-02 | 4:03 | 49.894
2025-03-02 | 4:04 | 49.897
2025-03-02 | 4:04 | 49.894
2025-03-02 | 4:04 | 49.893
2025-03-02 | 4:04 | 49.898
2025-03-02 | 4:04 | 49.897
2025-03-02 | 4:04 | 49.892
2025-03-02 | 4:04 | 49.892
2025-03-02 | 4:04 | 49.9
2025-03-02 | 4:04 | 49.896
2025-03-02 | 4:04 | 49.893
2025-03-02 | 4:04 | 49.896
2025-03-02 | 4:04 | 49.899
2025-03-02 | 4:04 | 49.896
2025-03-02 | 4:04 | 49.891
2025-03-02 | 4:04 | 49.898
2025-03-02 | 4:04 | 49.898
2025-03-02 | 4:04 | 49.893
2025-03-02 | 4:04 | 49.892
2025-03-02 | 4:04 | 49.899
2025-03-02 | 4:04 | 49.895
2025-03-02 | 4:04 | 49.891
2025-03-02 | 4:04 | 49.894
2025-03-02 | 4:04 | 49.898
2025-03-02 | 4:04 | 49.893
2025-03-02 | 4:04 | 49.893
2025-03-02 | 4:04 | 49.898
2025-03-02 | 4:04 | 49.898
2025-03-02 | 4:04 | 49.892
2025-03-02 | 4:04 | 49.896
2025-03-02 | 4:04 | 49.902
2025-03-02 | 4:04 | 49.898
2025-03-02 | 4:04 | 49.898
2025-03-02 | 4:04 | 49.912
2025-03-02 | 4:04 | 49.918
2025-03-02 | 4:04 | 49.916
2025-03-02 | 4:04 | 49.915
2025-03-02 | 4:04 | 49.927
2025-03-02 | 4:04 | 49.927
2025-03-02 | 4:04 | 49.925
2025-03-02 | 4:04 | 49.926
2025-03-02 | 4:04 | 49.932
2025-03-02 | 4:04 | 49.93
2025-03-02 | 4:04 | 49.926
2025-03-02 | 4:04 | 49.931
2025-03-02 | 4:04 | 49.935
2025-03-02 | 4:04 | 49.934
2025-03-02 | 4:04 | 49.931
2025-03-02 | 4:04 | 49.936
2025-03-02 | 4:04 | 49.936
2025-03-02 | 4:04 | 49.93
2025-03-02 | 4:04 | 49.932
2025-03-02 | 4:04 | 49.94
2025-03-02 | 4:04 | 49.935
2025-03-02 | 4:04 | 49.934
2025-03-02 | 4:04 | 49.937
2025-03-02 | 4:04 | 49.943
2025-03-02 | 4:04 | 49.942
2025-03-02 | 4:04 | 49.937
2025-03-02 | 4:04 | 49.938
2025-03-02 | 4:04 | 49.947
2025-03-02 | 4:04 | 49.948
2025-03-02 | 4:05 | 49.939
2025-03-02 | 4:05 | 49.938
2025-03-02 | 4:05 | 49.939
2025-03-02 | 4:05 | 49.943
2025-03-02 | 4:05 | 49.937
2025-03-02 | 4:05 | 49.935
2025-03-02 | 4:05 | 49.944
2025-03-02 | 4:05 | 49.948
2025-03-02 | 4:05 | 49.946
2025-03-02 | 4:05 | 49.942
2025-03-02 | 4:05 | 49.95
2025-03-02 | 4:05 | 49.949
2025-03-02 | 4:05 | 49.942
2025-03-02 | 4:05 | 49.941
2025-03-02 | 4:05 | 49.947
2025-03-02 | 4:05 | 49.947
2025-03-02 | 4:05 | 49.941
2025-03-02 | 4:05 | 49.946
2025-03-02 | 4:05 | 49.938
2025-03-02 | 4:05 | 49.941
2025-03-02 | 4:05 | 49.94
2025-03-02 | 4:05 | 49.94
2025-03-02 | 4:05 | 49.937
2025-03-02 | 4:05 | 49.949
2025-03-02 | 4:05 | 49.951
2025-03-02 | 4:05 | 49.947
2025-03-02 | 4:05 | 49.946
2025-03-02 | 4:05 | 49.955
2025-03-02 | 4:05 | 49.952
2025-03-02 | 4:05 | 49.947
2025-03-02 | 4:05 | 49.947
2025-03-02 | 4:05 | 49.953
2025-03-02 | 4:05 | 49.951
2025-03-02 | 4:05 | 49.945
2025-03-02 | 4:05 | 49.943
2025-03-02 | 4:05 | 49.95
2025-03-02 | 4:05 | 49.948
2025-03-02 | 4:05 | 49.944
2025-03-02 | 4:05 | 49.944
2025-03-02 | 4:05 | 49.951
2025-03-02 | 4:05 | 49.954
2025-03-02 | 4:05 | 49.952
2025-03-02 | 4:05 | 49.951
2025-03-02 | 4:05 | 49.957
2025-03-02 | 4:05 | 49.957
2025-03-02 | 4:05 | 49.95
2025-03-02 | 4:05 | 49.949
2025-03-02 | 4:05 | 49.959
2025-03-02 | 4:05 | 49.955
2025-03-02 | 4:05 | 49.952
2025-03-02 | 4:05 | 49.949
2025-03-02 | 4:05 | 49.95
2025-03-02 | 4:05 | 49.944
2025-03-02 | 4:05 | 49.944
2025-03-02 | 4:05 | 49.95
2025-03-02 | 4:05 | 49.954
2025-03-02 | 4:05 | 49.949
2025-03-02 | 4:05 | 49.948
2025-03-02 | 4:05 | 49.956
2025-03-02 | 4:06 | 49.95
2025-03-02 | 4:06 | 49.945
2025-03-02 | 4:06 | 49.948
2025-03-02 | 4:06 | 49.948
2025-03-02 | 4:06 | 49.943
2025-03-02 | 4:06 | 49.94
2025-03-02 | 4:06 | 49.944
2025-03-02 | 4:06 | 49.944
2025-03-02 | 4:06 | 49.936
2025-03-02 | 4:06 | 49.938
2025-03-02 | 4:06 | 49.948
2025-03-02 | 4:06 | 49.947
2025-03-02 | 4:06 | 49.945
2025-03-02 | 4:06 | 49.947
2025-03-02 | 4:06 | 49.95
2025-03-02 | 4:06 | 49.944
2025-03-02 | 4:06 | 49.946
2025-03-02 | 4:06 | 49.953
2025-03-02 | 4:06 | 49.954
2025-03-02 | 4:06 | 49.948
2025-03-02 | 4:06 | 49.944
2025-03-02 | 4:06 | 49.953
2025-03-02 | 4:06 | 49.947
2025-03-02 | 4:06 | 49.945
2025-03-02 | 4:06 | 49.947
2025-03-02 | 4:06 | 49.951
2025-03-02 | 4:06 | 49.947
2025-03-02 | 4:06 | 49.94
2025-03-02 | 4:06 | 49.948
2025-03-02 | 4:06 | 49.947
2025-03-02 | 4:06 | 49.937
2025-03-02 | 4:06 | 49.937
2025-03-02 | 4:06 | 49.94
2025-03-02 | 4:06 | 49.937
2025-03-02 | 4:06 | 49.933
2025-03-02 | 4:06 | 49.939
2025-03-02 | 4:06 | 49.943
2025-03-02 | 4:06 | 49.94
2025-03-02 | 4:06 | 49.936
2025-03-02 | 4:06 | 49.943
2025-03-02 | 4:06 | 49.941
2025-03-02 | 4:06 | 49.935
2025-03-02 | 4:06 | 49.934
2025-03-02 | 4:06 | 49.941
2025-03-02 | 4:06 | 49.942
2025-03-02 | 4:06 | 49.94
2025-03-02 | 4:06 | 49.944
2025-03-02 | 4:06 | 49.948
2025-03-02 | 4:06 | 49.943
2025-03-02 | 4:06 | 49.942
2025-03-02 | 4:06 | 49.948
2025-03-02 | 4:06 | 49.944
2025-03-02 | 4:06 | 49.939
2025-03-02 | 4:06 | 49.941
2025-03-02 | 4:06 | 49.949
2025-03-02 | 4:06 | 49.946
2025-03-02 | 4:06 | 49.941
2025-03-02 | 4:06 | 49.947
2025-03-02 | 4:06 | 49.948
2025-03-02 | 4:06 | 49.949
2025-03-02 | 4:06 | 49.945
2025-03-02 | 4:07 | 49.948
2025-03-02 | 4:07 | 49.948
2025-03-02 | 4:07 | 49.943
2025-03-02 | 4:07 | 49.944
2025-03-02 | 4:07 | 49.949
2025-03-02 | 4:07 | 49.949
2025-03-02 | 4:07 | 49.943
2025-03-02 | 4:07 | 49.947
2025-03-02 | 4:07 | 49.951
2025-03-02 | 4:07 | 49.947
2025-03-02 | 4:07 | 49.945
2025-03-02 | 4:07 | 49.953
2025-03-02 | 4:07 | 49.951
2025-03-02 | 4:07 | 49.943
2025-03-02 | 4:07 | 49.943
2025-03-02 | 4:07 | 49.949
2025-03-02 | 4:07 | 49.943
2025-03-02 | 4:07 | 49.941
2025-03-02 | 4:07 | 49.948
2025-03-02 | 4:07 | 49.949
2025-03-02 | 4:07 | 49.944
2025-03-02 | 4:07 | 49.942
2025-03-02 | 4:07 | 49.949
2025-03-02 | 4:07 | 49.95
2025-03-02 | 4:07 | 49.941
2025-03-02 | 4:07 | 49.937
2025-03-02 | 4:07 | 49.944
2025-03-02 | 4:07 | 49.938
2025-03-02 | 4:07 | 49.934
2025-03-02 | 4:07 | 49.936
2025-03-02 | 4:07 | 49.936
2025-03-02 | 4:07 | 49.933
2025-03-02 | 4:07 | 49.93
2025-03-02 | 4:07 | 49.939
2025-03-02 | 4:07 | 49.937
2025-03-02 | 4:07 | 49.93
2025-03-02 | 4:07 | 49.93
2025-03-02 | 4:07 | 49.936
2025-03-02 | 4:07 | 49.933
2025-03-02 | 4:07 | 49.928
2025-03-02 | 4:07 | 49.931
2025-03-02 | 4:07 | 49.932
2025-03-02 | 4:07 | 49.928
2025-03-02 | 4:07 | 49.926
2025-03-02 | 4:07 | 49.933
2025-03-02 | 4:07 | 49.931
2025-03-02 | 4:07 | 49.928
2025-03-02 | 4:07 | 49.933
2025-03-02 | 4:07 | 49.941
2025-03-02 | 4:07 | 49.939
2025-03-02 | 4:07 | 49.936
2025-03-02 | 4:07 | 49.939
2025-03-02 | 4:07 | 49.94
2025-03-02 | 4:07 | 49.932
2025-03-02 | 4:07 | 49.927
2025-03-02 | 4:07 | 49.935
2025-03-02 | 4:07 | 49.937
2025-03-02 | 4:07 | 49.93
2025-03-02 | 4:07 | 49.928
2025-03-02 | 4:08 | 49.935
2025-03-02 | 4:08 | 49.93
2025-03-02 | 4:08 | 49.933
2025-03-02 | 4:08 | 49.933
2025-03-02 | 4:08 | 49.938
2025-03-02 | 4:08 | 49.934
2025-03-02 | 4:08 | 49.937
2025-03-02 | 4:08 | 49.931
2025-03-02 | 4:08 | 49.933
2025-03-02 | 4:08 | 49.939
2025-03-02 | 4:08 | 49.935
2025-03-02 | 4:08 | 49.93
2025-03-02 | 4:08 | 49.935
2025-03-02 | 4:08 | 49.936
2025-03-02 | 4:08 | 49.932
2025-03-02 | 4:08 | 49.926
2025-03-02 | 4:08 | 49.934
2025-03-02 | 4:08 | 49.936
2025-03-02 | 4:08 | 49.933
2025-03-02 | 4:08 | 49.933
2025-03-02 | 4:08 | 49.941
2025-03-02 | 4:08 | 49.942
2025-03-02 | 4:08 | 49.939
2025-03-02 | 4:08 | 49.94
2025-03-02 | 4:08 | 49.944
2025-03-02 | 4:08 | 49.939
2025-03-02 | 4:08 | 49.935
2025-03-02 | 4:08 | 49.941
2025-03-02 | 4:08 | 49.945
2025-03-02 | 4:08 | 49.94
2025-03-02 | 4:08 | 49.94
2025-03-02 | 4:08 | 49.946
2025-03-02 | 4:08 | 49.94
2025-03-02 | 4:08 | 49.936
2025-03-02 | 4:08 | 49.94
2025-03-02 | 4:08 | 49.943
2025-03-02 | 4:08 | 49.937
2025-03-02 | 4:08 | 49.935
2025-03-02 | 4:08 | 49.944
2025-03-02 | 4:08 | 49.946
2025-03-02 | 4:08 | 49.939
2025-03-02 | 4:08 | 49.939
2025-03-02 | 4:08 | 49.944
2025-03-02 | 4:08 | 49.942
2025-03-02 | 4:08 | 49.942
2025-03-02 | 4:08 | 49.946
2025-03-02 | 4:08 | 49.948
2025-03-02 | 4:08 | 49.942
2025-03-02 | 4:08 | 49.939
2025-03-02 | 4:08 | 49.946
2025-03-02 | 4:08 | 49.947
2025-03-02 | 4:08 | 49.941
2025-03-02 | 4:08 | 49.942
2025-03-02 | 4:08 | 49.947
2025-03-02 | 4:08 | 49.943
2025-03-02 | 4:08 | 49.94
2025-03-02 | 4:08 | 49.943
2025-03-02 | 4:08 | 49.943
2025-03-02 | 4:08 | 49.936
2025-03-02 | 4:08 | 49.935
2025-03-02 | 4:08 | 49.944
2025-03-02 | 4:09 | 49.943
2025-03-02 | 4:09 | 49.939
2025-03-02 | 4:09 | 49.939
2025-03-02 | 4:09 | 49.946
2025-03-02 | 4:09 | 49.942
2025-03-02 | 4:09 | 49.942
2025-03-02 | 4:09 | 49.948
2025-03-02 | 4:09 | 49.95
2025-03-02 | 4:09 | 49.95
2025-03-02 | 4:09 | 49.95
2025-03-02 | 4:09 | 49.958
2025-03-02 | 4:09 | 49.955
2025-03-02 | 4:09 | 49.946
2025-03-02 | 4:09 | 49.944
2025-03-02 | 4:09 | 49.949
2025-03-02 | 4:09 | 49.951
2025-03-02 | 4:09 | 49.95
2025-03-02 | 4:09 | 49.954
2025-03-02 | 4:09 | 49.952
2025-03-02 | 4:09 | 49.936
2025-03-02 | 4:09 | 49.922
2025-03-02 | 4:09 | 49.921
2025-03-02 | 4:09 | 49.916
2025-03-02 | 4:09 | 49.907
2025-03-02 | 4:09 | 49.9
2025-03-02 | 4:09 | 49.903
2025-03-02 | 4:09 | 49.895
2025-03-02 | 4:09 | 49.889
2025-03-02 | 4:09 | 49.892
2025-03-02 | 4:09 | 49.895
2025-03-02 | 4:09 | 49.892
2025-03-02 | 4:09 | 49.891
2025-03-02 | 4:09 | 49.897
2025-03-02 | 4:09 | 49.897
2025-03-02 | 4:09 | 49.892
2025-03-02 | 4:09 | 49.891
2025-03-02 | 4:09 | 49.897
2025-03-02 | 4:09 | 49.896
2025-03-02 | 4:09 | 49.892
2025-03-02 | 4:09 | 49.893
2025-03-02 | 4:09 | 49.896
2025-03-02 | 4:09 | 49.89
2025-03-02 | 4:09 | 49.89
2025-03-02 | 4:09 | 49.897
2025-03-02 | 4:09 | 49.897
2025-03-02 | 4:09 | 49.894
2025-03-02 | 4:09 | 49.897
2025-03-02 | 4:09 | 49.906
2025-03-02 | 4:09 | 49.901
2025-03-02 | 4:09 | 49.897
2025-03-02 | 4:09 | 49.902
2025-03-02 | 4:09 | 49.905
2025-03-02 | 4:09 | 49.901
2025-03-02 | 4:09 | 49.895
2025-03-02 | 4:09 | 49.902
2025-03-02 | 4:09 | 49.904
2025-03-02 | 4:09 | 49.895
2025-03-02 | 4:09 | 49.892
2025-03-02 | 4:09 | 49.9
2025-03-02 | 4:10 | 49.897
2025-03-02 | 4:10 | 49.891
2025-03-02 | 4:10 | 49.896
2025-03-02 | 4:10 | 49.902
2025-03-02 | 4:10 | 49.897
2025-03-02 | 4:10 | 49.892
2025-03-02 | 4:10 | 49.9
2025-03-02 | 4:10 | 49.899
2025-03-02 | 4:10 | 49.894
2025-03-02 | 4:10 | 49.894
2025-03-02 | 4:10 | 49.902
2025-03-02 | 4:10 | 49.897
2025-03-02 | 4:10 | 49.895
2025-03-02 | 4:10 | 49.898
2025-03-02 | 4:10 | 49.902
2025-03-02 | 4:10 | 49.897
2025-03-02 | 4:10 | 49.894
2025-03-02 | 4:10 | 49.904
2025-03-02 | 4:10 | 49.903
2025-03-02 | 4:10 | 49.897
2025-03-02 | 4:10 | 49.899
2025-03-02 | 4:10 | 49.902
2025-03-02 | 4:10 | 49.898
2025-03-02 | 4:10 | 49.9
2025-03-02 | 4:10 | 49.896
2025-03-02 | 4:10 | 49.892
2025-03-02 | 4:10 | 49.898
2025-03-02 | 4:10 | 49.897
2025-03-02 | 4:10 | 49.893
2025-03-02 | 4:10 | 49.891
2025-03-02 | 4:10 | 49.898
2025-03-02 | 4:10 | 49.892
2025-03-02 | 4:10 | 49.89
2025-03-02 | 4:10 | 49.893
2025-03-02 | 4:10 | 49.897
2025-03-02 | 4:10 | 49.894
2025-03-02 | 4:10 | 49.89
2025-03-02 | 4:10 | 49.897
2025-03-02 | 4:10 | 49.896
2025-03-02 | 4:10 | 49.891
2025-03-02 | 4:10 | 49.891
2025-03-02 | 4:10 | 49.898
2025-03-02 | 4:10 | 49.895
2025-03-02 | 4:10 | 49.891
2025-03-02 | 4:10 | 49.893
2025-03-02 | 4:10 | 49.896
2025-03-02 | 4:10 | 49.893
2025-03-02 | 4:10 | 49.892
2025-03-02 | 4:10 | 49.901
2025-03-02 | 4:10 | 49.899
2025-03-02 | 4:10 | 49.892
2025-03-02 | 4:10 | 49.892
2025-03-02 | 4:10 | 49.898
2025-03-02 | 4:10 | 49.894
2025-03-02 | 4:10 | 49.889
2025-03-02 | 4:10 | 49.893
2025-03-02 | 4:10 | 49.898
2025-03-02 | 4:10 | 49.892
2025-03-02 | 4:10 | 49.888
2025-03-02 | 4:10 | 49.895
2025-03-02 | 4:10 | 49.895
2025-03-02 | 4:11 | 49.89
2025-03-02 | 4:11 | 49.89
2025-03-02 | 4:11 | 49.896
2025-03-02 | 4:11 | 49.892
2025-03-02 | 4:11 | 49.888
2025-03-02 | 4:11 | 49.89
2025-03-02 | 4:11 | 49.894
2025-03-02 | 4:11 | 49.889
2025-03-02 | 4:11 | 49.888
2025-03-02 | 4:11 | 49.893
2025-03-02 | 4:11 | 49.893
2025-03-02 | 4:11 | 49.887
2025-03-02 | 4:11 | 49.888
2025-03-02 | 4:11 | 49.893
2025-03-02 | 4:11 | 49.889
2025-03-02 | 4:11 | 49.876
2025-03-02 | 4:11 | 49.897
2025-03-02 | 4:11 | 49.904
2025-03-02 | 4:11 | 49.902
2025-03-02 | 4:11 | 49.898
2025-03-02 | 4:11 | 49.904
2025-03-02 | 4:11 | 49.904
2025-03-02 | 4:11 | 49.897
2025-03-02 | 4:11 | 49.897
2025-03-02 | 4:11 | 49.905
2025-03-02 | 4:11 | 49.901
2025-03-02 | 4:11 | 49.898
2025-03-02 | 4:11 | 49.901
2025-03-02 | 4:11 | 49.905
2025-03-02 | 4:11 | 49.902
2025-03-02 | 4:11 | 49.896
2025-03-02 | 4:11 | 49.904
2025-03-02 | 4:11 | 49.905
2025-03-02 | 4:11 | 49.898
2025-03-02 | 4:11 | 49.898
2025-03-02 | 4:11 | 49.906
2025-03-02 | 4:11 | 49.902
2025-03-02 | 4:11 | 49.906
2025-03-02 | 4:11 | 49.906
2025-03-02 | 4:11 | 49.9
2025-03-02 | 4:11 | 49.905
2025-03-02 | 4:11 | 49.907
2025-03-02 | 4:11 | 49.904
2025-03-02 | 4:11 | 49.902
2025-03-02 | 4:11 | 49.903
2025-03-02 | 4:11 | 49.904
2025-03-02 | 4:11 | 49.911
2025-03-02 | 4:11 | 49.907
2025-03-02 | 4:11 | 49.903
2025-03-02 | 4:11 | 49.907
2025-03-02 | 4:11 | 49.911
2025-03-02 | 4:11 | 49.908
2025-03-02 | 4:11 | 49.911
2025-03-02 | 4:11 | 49.913
2025-03-02 | 4:11 | 49.904
2025-03-02 | 4:11 | 49.909
2025-03-02 | 4:11 | 49.906
2025-03-02 | 4:11 | 49.903
2025-03-02 | 4:11 | 49.906
2025-03-02 | 4:12 | 49.913
2025-03-02 | 4:12 | 49.908
2025-03-02 | 4:12 | 49.904
2025-03-02 | 4:12 | 49.912
2025-03-02 | 4:12 | 49.91
2025-03-02 | 4:12 | 49.908
2025-03-02 | 4:12 | 49.906
2025-03-02 | 4:12 | 49.912
2025-03-02 | 4:12 | 49.911
2025-03-02 | 4:12 | 49.905
2025-03-02 | 4:12 | 49.907
2025-03-02 | 4:12 | 49.914
2025-03-02 | 4:12 | 49.911
2025-03-02 | 4:12 | 49.906
2025-03-02 | 4:12 | 49.912
2025-03-02 | 4:12 | 49.913
2025-03-02 | 4:12 | 49.908
2025-03-02 | 4:12 | 49.906
2025-03-02 | 4:12 | 49.913
2025-03-02 | 4:12 | 49.913
2025-03-02 | 4:12 | 49.912
2025-03-02 | 4:12 | 49.906
2025-03-02 | 4:12 | 49.913
2025-03-02 | 4:12 | 49.907
2025-03-02 | 4:12 | 49.906
2025-03-02 | 4:12 | 49.909
2025-03-02 | 4:12 | 49.906
2025-03-02 | 4:12 | 49.909
2025-03-02 | 4:12 | 49.907
2025-03-02 | 4:12 | 49.915
2025-03-02 | 4:12 | 49.915
2025-03-02 | 4:12 | 49.907
2025-03-02 | 4:12 | 49.906
2025-03-02 | 4:12 | 49.913
2025-03-02 | 4:12 | 49.909
2025-03-02 | 4:12 | 49.903
2025-03-02 | 4:12 | 49.908
2025-03-02 | 4:12 | 49.911
2025-03-02 | 4:12 | 49.906
2025-03-02 | 4:12 | 49.901
2025-03-02 | 4:12 | 49.909
2025-03-02 | 4:12 | 49.908
2025-03-02 | 4:12 | 49.901
2025-03-02 | 4:12 | 49.9
2025-03-02 | 4:12 | 49.905
2025-03-02 | 4:12 | 49.904
2025-03-02 | 4:12 | 49.896
2025-03-02 | 4:12 | 49.895
2025-03-02 | 4:12 | 49.901
2025-03-02 | 4:12 | 49.897
2025-03-02 | 4:12 | 49.893
2025-03-02 | 4:12 | 49.899
2025-03-02 | 4:12 | 49.899
2025-03-02 | 4:12 | 49.895
2025-03-02 | 4:12 | 49.892
2025-03-02 | 4:12 | 49.9
2025-03-02 | 4:12 | 49.901
2025-03-02 | 4:12 | 49.893
2025-03-02 | 4:12 | 49.892
2025-03-02 | 4:12 | 49.9
2025-03-02 | 4:12 | 49.897
2025-03-02 | 4:13 | 49.893
2025-03-02 | 4:13 | 49.896
2025-03-02 | 4:13 | 49.9
2025-03-02 | 4:13 | 49.894
2025-03-02 | 4:13 | 49.894
2025-03-02 | 4:13 | 49.898
2025-03-02 | 4:13 | 49.896
2025-03-02 | 4:13 | 49.884
2025-03-02 | 4:13 | 49.882
2025-03-02 | 4:13 | 49.893
2025-03-02 | 4:13 | 49.89
2025-03-02 | 4:13 | 49.881
2025-03-02 | 4:13 | 49.888
2025-03-02 | 4:13 | 49.889
2025-03-02 | 4:13 | 49.887
2025-03-02 | 4:13 | 49.883
2025-03-02 | 4:13 | 49.892
2025-03-02 | 4:13 | 49.889
2025-03-02 | 4:13 | 49.882
2025-03-02 | 4:13 | 49.884
2025-03-02 | 4:13 | 49.889
2025-03-02 | 4:13 | 49.887
2025-03-02 | 4:13 | 49.882
2025-03-02 | 4:13 | 49.889
2025-03-02 | 4:13 | 49.889
2025-03-02 | 4:13 | 49.884
2025-03-02 | 4:13 | 49.881
2025-03-02 | 4:13 | 49.89
2025-03-02 | 4:13 | 49.891
2025-03-02 | 4:13 | 49.883
2025-03-02 | 4:13 | 49.88
2025-03-02 | 4:13 | 49.887
2025-03-02 | 4:13 | 49.882
2025-03-02 | 4:13 | 49.88
2025-03-02 | 4:13 | 49.881
2025-03-02 | 4:13 | 49.889
2025-03-02 | 4:13 | 49.886
2025-03-02 | 4:13 | 49.88
2025-03-02 | 4:13 | 49.881
2025-03-02 | 4:13 | 49.879
2025-03-02 | 4:13 | 49.885
2025-03-02 | 4:13 | 49.885
2025-03-02 | 4:13 | 49.88
2025-03-02 | 4:13 | 49.878
2025-03-02 | 4:13 | 49.887
2025-03-02 | 4:13 | 49.88
2025-03-02 | 4:13 | 49.876
2025-03-02 | 4:13 | 49.881
2025-03-02 | 4:13 | 49.889
2025-03-02 | 4:13 | 49.884
2025-03-02 | 4:13 | 49.885
2025-03-02 | 4:13 | 49.892
2025-03-02 | 4:13 | 49.891
2025-03-02 | 4:13 | 49.885
2025-03-02 | 4:13 | 49.884
2025-03-02 | 4:13 | 49.893
2025-03-02 | 4:13 | 49.888
2025-03-02 | 4:13 | 49.882
2025-03-02 | 4:13 | 49.888
2025-03-02 | 4:14 | 49.889
2025-03-02 | 4:14 | 49.881
2025-03-02 | 4:14 | 49.881
2025-03-02 | 4:14 | 49.89
2025-03-02 | 4:14 | 49.89
2025-03-02 | 4:14 | 49.887
2025-03-02 | 4:14 | 49.888
2025-03-02 | 4:14 | 49.895
2025-03-02 | 4:14 | 49.893
2025-03-02 | 4:14 | 49.887
2025-03-02 | 4:14 | 49.895
2025-03-02 | 4:14 | 49.897
2025-03-02 | 4:14 | 49.889
2025-03-02 | 4:14 | 49.891
2025-03-02 | 4:14 | 49.897
2025-03-02 | 4:14 | 49.889
2025-03-02 | 4:14 | 49.884
2025-03-02 | 4:14 | 49.886
2025-03-02 | 4:14 | 49.891
2025-03-02 | 4:14 | 49.886
2025-03-02 | 4:14 | 49.882
2025-03-02 | 4:14 | 49.891
2025-03-02 | 4:14 | 49.891
2025-03-02 | 4:14 | 49.884
2025-03-02 | 4:14 | 49.885
2025-03-02 | 4:14 | 49.892
2025-03-02 | 4:14 | 49.888
2025-03-02 | 4:14 | 49.885
2025-03-02 | 4:14 | 49.89
2025-03-02 | 4:14 | 49.896
2025-03-02 | 4:14 | 49.892
2025-03-02 | 4:14 | 49.888
2025-03-02 | 4:14 | 49.894
2025-03-02 | 4:14 | 49.894
2025-03-02 | 4:14 | 49.888
2025-03-02 | 4:14 | 49.889
2025-03-02 | 4:14 | 49.898
2025-03-02 | 4:14 | 49.897
2025-03-02 | 4:14 | 49.889
2025-03-02 | 4:14 | 49.89
2025-03-02 | 4:14 | 49.896
2025-03-02 | 4:14 | 49.891
2025-03-02 | 4:14 | 49.888
2025-03-02 | 4:14 | 49.894
2025-03-02 | 4:14 | 49.896
2025-03-02 | 4:14 | 49.891
2025-03-02 | 4:14 | 49.892
2025-03-02 | 4:14 | 49.898
2025-03-02 | 4:14 | 49.893
2025-03-02 | 4:14 | 49.888
2025-03-02 | 4:14 | 49.89
2025-03-02 | 4:14 | 49.896
2025-03-02 | 4:14 | 49.89
2025-03-02 | 4:14 | 49.893
2025-03-02 | 4:14 | 49.888
2025-03-02 | 4:14 | 49.889
2025-03-02 | 4:14 | 49.896
2025-03-02 | 4:14 | 49.893
2025-03-02 | 4:14 | 49.888
2025-03-02 | 4:14 | 49.893
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.893
2025-03-02 | 4:15 | 49.891
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.9
2025-03-02 | 4:15 | 49.89
2025-03-02 | 4:15 | 49.899
2025-03-02 | 4:15 | 49.892
2025-03-02 | 4:15 | 49.893
2025-03-02 | 4:15 | 49.897
2025-03-02 | 4:15 | 49.891
2025-03-02 | 4:15 | 49.891
2025-03-02 | 4:15 | 49.897
2025-03-02 | 4:15 | 49.894
2025-03-02 | 4:15 | 49.892
2025-03-02 | 4:15 | 49.897
2025-03-02 | 4:15 | 49.89
2025-03-02 | 4:15 | 49.889
2025-03-02 | 4:15 | 49.893
2025-03-02 | 4:15 | 49.898
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.893
2025-03-02 | 4:15 | 49.887
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.9
2025-03-02 | 4:15 | 49.892
2025-03-02 | 4:15 | 49.894
2025-03-02 | 4:15 | 49.898
2025-03-02 | 4:15 | 49.894
2025-03-02 | 4:15 | 49.893
2025-03-02 | 4:15 | 49.899
2025-03-02 | 4:15 | 49.895
2025-03-02 | 4:15 | 49.888
2025-03-02 | 4:15 | 49.893
2025-03-02 | 4:15 | 49.9
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.893
2025-03-02 | 4:15 | 49.9
2025-03-02 | 4:15 | 49.898
2025-03-02 | 4:15 | 49.894
2025-03-02 | 4:15 | 49.894
2025-03-02 | 4:15 | 49.899
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.89
2025-03-02 | 4:15 | 49.891
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.889
2025-03-02 | 4:15 | 49.888
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.895
2025-03-02 | 4:15 | 49.89
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.889
2025-03-02 | 4:15 | 49.894
2025-03-02 | 4:15 | 49.896
2025-03-02 | 4:15 | 49.895
2025-03-02 | 4:15 | 49.893
2025-03-02 | 4:15 | 49.901
2025-03-02 | 4:15 | 49.899
2025-03-02 | 4:16 | 49.893
2025-03-02 | 4:16 | 49.895
2025-03-02 | 4:16 | 49.9
2025-03-02 | 4:16 | 49.895
2025-03-02 | 4:16 | 49.892
2025-03-02 | 4:16 | 49.901
2025-03-02 | 4:16 | 49.899
2025-03-02 | 4:16 | 49.898
2025-03-02 | 4:16 | 49.902
2025-03-02 | 4:16 | 49.908
2025-03-02 | 4:16 | 49.905
2025-03-02 | 4:16 | 49.898
2025-03-02 | 4:16 | 49.907
2025-03-02 | 4:16 | 49.908
2025-03-02 | 4:16 | 49.903
2025-03-02 | 4:16 | 49.903
2025-03-02 | 4:16 | 49.909
2025-03-02 | 4:16 | 49.903
2025-03-02 | 4:16 | 49.899
2025-03-02 | 4:16 | 49.901
2025-03-02 | 4:16 | 49.909
2025-03-02 | 4:16 | 49.902
2025-03-02 | 4:16 | 49.901
2025-03-02 | 4:16 | 49.909
2025-03-02 | 4:16 | 49.914
2025-03-02 | 4:16 | 49.914
2025-03-02 | 4:16 | 49.918
2025-03-02 | 4:16 | 49.927
2025-03-02 | 4:16 | 49.921
2025-03-02 | 4:16 | 49.917
2025-03-02 | 4:16 | 49.919
2025-03-02 | 4:16 | 49.922
2025-03-02 | 4:16 | 49.919
2025-03-02 | 4:16 | 49.91
2025-03-02 | 4:16 | 49.909
2025-03-02 | 4:16 | 49.908
2025-03-02 | 4:16 | 49.917
2025-03-02 | 4:16 | 49.915
2025-03-02 | 4:16 | 49.912
2025-03-02 | 4:16 | 49.916
2025-03-02 | 4:16 | 49.918
2025-03-02 | 4:16 | 49.912
2025-03-02 | 4:16 | 49.905
2025-03-02 | 4:16 | 49.911
2025-03-02 | 4:16 | 49.908
2025-03-02 | 4:16 | 49.905
2025-03-02 | 4:16 | 49.908
2025-03-02 | 4:16 | 49.91
2025-03-02 | 4:16 | 49.906
2025-03-02 | 4:16 | 49.908
2025-03-02 | 4:16 | 49.905
2025-03-02 | 4:16 | 49.901
2025-03-02 | 4:16 | 49.908
2025-03-02 | 4:16 | 49.904
2025-03-02 | 4:16 | 49.91
2025-03-02 | 4:16 | 49.908
2025-03-02 | 4:16 | 49.901
2025-03-02 | 4:16 | 49.899
2025-03-02 | 4:16 | 49.906
2025-03-02 | 4:16 | 49.903
2025-03-02 | 4:16 | 49.901
2025-03-02 | 4:17 | 49.902
2025-03-02 | 4:17 | 49.906
2025-03-02 | 4:17 | 49.903
2025-03-02 | 4:17 | 49.9
2025-03-02 | 4:17 | 49.906
2025-03-02 | 4:17 | 49.907
2025-03-02 | 4:17 | 49.902
2025-03-02 | 4:17 | 49.901
2025-03-02 | 4:17 | 49.91
2025-03-02 | 4:17 | 49.905
2025-03-02 | 4:17 | 49.9
2025-03-02 | 4:17 | 49.904
2025-03-02 | 4:17 | 49.907
2025-03-02 | 4:17 | 49.903
2025-03-02 | 4:17 | 49.896
2025-03-02 | 4:17 | 49.905
2025-03-02 | 4:17 | 49.904
2025-03-02 | 4:17 | 49.9
2025-03-02 | 4:17 | 49.902
2025-03-02 | 4:17 | 49.91
2025-03-02 | 4:17 | 49.907
2025-03-02 | 4:17 | 49.9
2025-03-02 | 4:17 | 49.903
2025-03-02 | 4:17 | 49.908
2025-03-02 | 4:17 | 49.905
2025-03-02 | 4:17 | 49.901
2025-03-02 | 4:17 | 49.909
2025-03-02 | 4:17 | 49.913
2025-03-02 | 4:17 | 49.907
2025-03-02 | 4:17 | 49.903
2025-03-02 | 4:17 | 49.913
2025-03-02 | 4:17 | 49.916
2025-03-02 | 4:17 | 49.916
2025-03-02 | 4:17 | 49.925
2025-03-02 | 4:17 | 49.93
2025-03-02 | 4:17 | 49.926
2025-03-02 | 4:17 | 49.922
2025-03-02 | 4:17 | 49.928
2025-03-02 | 4:17 | 49.928
2025-03-02 | 4:17 | 49.927
2025-03-02 | 4:17 | 49.924
2025-03-02 | 4:17 | 49.929
2025-03-02 | 4:17 | 49.935
2025-03-02 | 4:17 | 49.933
2025-03-02 | 4:17 | 49.929
2025-03-02 | 4:17 | 49.929
2025-03-02 | 4:17 | 49.939
2025-03-02 | 4:17 | 49.937
2025-03-02 | 4:17 | 49.928
2025-03-02 | 4:17 | 49.927
2025-03-02 | 4:17 | 49.93
2025-03-02 | 4:17 | 49.929
2025-03-02 | 4:17 | 49.931
2025-03-02 | 4:17 | 49.938
2025-03-02 | 4:17 | 49.946
2025-03-02 | 4:17 | 49.94
2025-03-02 | 4:17 | 49.935
2025-03-02 | 4:17 | 49.944
2025-03-02 | 4:17 | 49.944
2025-03-02 | 4:18 | 49.94
2025-03-02 | 4:18 | 49.935
2025-03-02 | 4:18 | 49.943
2025-03-02 | 4:18 | 49.941
2025-03-02 | 4:18 | 49.931
2025-03-02 | 4:18 | 49.931
2025-03-02 | 4:18 | 49.934
2025-03-02 | 4:18 | 49.929
2025-03-02 | 4:18 | 49.926
2025-03-02 | 4:18 | 49.933
2025-03-02 | 4:18 | 49.94
2025-03-02 | 4:18 | 49.935
2025-03-02 | 4:18 | 49.933
2025-03-02 | 4:18 | 49.939
2025-03-02 | 4:18 | 49.936
2025-03-02 | 4:18 | 49.931
2025-03-02 | 4:18 | 49.932
2025-03-02 | 4:18 | 49.939
2025-03-02 | 4:18 | 49.938
2025-03-02 | 4:18 | 49.936
2025-03-02 | 4:18 | 49.941
2025-03-02 | 4:18 | 49.943
2025-03-02 | 4:18 | 49.938
2025-03-02 | 4:18 | 49.934
2025-03-02 | 4:18 | 49.941
2025-03-02 | 4:18 | 49.941
2025-03-02 | 4:18 | 49.936
2025-03-02 | 4:18 | 49.939
2025-03-02 | 4:18 | 49.952
2025-03-02 | 4:18 | 49.949
2025-03-02 | 4:18 | 49.945
2025-03-02 | 4:18 | 49.941
2025-03-02 | 4:18 | 49.948
2025-03-02 | 4:18 | 49.943
2025-03-02 | 4:18 | 49.94
2025-03-02 | 4:18 | 49.945
2025-03-02 | 4:18 | 49.95
2025-03-02 | 4:18 | 49.943
2025-03-02 | 4:18 | 49.938
2025-03-02 | 4:18 | 49.943
2025-03-02 | 4:18 | 49.94
2025-03-02 | 4:18 | 49.934
2025-03-02 | 4:18 | 49.935
2025-03-02 | 4:18 | 49.944
2025-03-02 | 4:18 | 49.939
2025-03-02 | 4:18 | 49.94
2025-03-02 | 4:18 | 49.933
2025-03-02 | 4:18 | 49.932
2025-03-02 | 4:18 | 49.938
2025-03-02 | 4:18 | 49.932
2025-03-02 | 4:18 | 49.937
2025-03-02 | 4:18 | 49.937
2025-03-02 | 4:18 | 49.933
2025-03-02 | 4:18 | 49.93
2025-03-02 | 4:18 | 49.94
2025-03-02 | 4:18 | 49.938
2025-03-02 | 4:18 | 49.933
2025-03-02 | 4:18 | 49.933
2025-03-02 | 4:18 | 49.94
2025-03-02 | 4:18 | 49.934
2025-03-02 | 4:18 | 49.933
2025-03-02 | 4:19 | 49.94
2025-03-02 | 4:19 | 49.941
2025-03-02 | 4:19 | 49.938
2025-03-02 | 4:19 | 49.932
2025-03-02 | 4:19 | 49.941
2025-03-02 | 4:19 | 49.942
2025-03-02 | 4:19 | 49.936
2025-03-02 | 4:19 | 49.937
2025-03-02 | 4:19 | 49.946
2025-03-02 | 4:19 | 49.942
2025-03-02 | 4:19 | 49.937
2025-03-02 | 4:19 | 49.943
2025-03-02 | 4:19 | 49.947
2025-03-02 | 4:19 | 49.947
2025-03-02 | 4:19 | 49.937
2025-03-02 | 4:19 | 49.936
2025-03-02 | 4:19 | 49.942
2025-03-02 | 4:19 | 49.948
2025-03-02 | 4:19 | 49.941
2025-03-02 | 4:19 | 49.943
2025-03-02 | 4:19 | 49.947
2025-03-02 | 4:19 | 49.949
2025-03-02 | 4:19 | 49.945
2025-03-02 | 4:19 | 49.944
2025-03-02 | 4:19 | 49.95
2025-03-02 | 4:19 | 49.953
2025-03-02 | 4:19 | 49.948
2025-03-02 | 4:19 | 49.947
2025-03-02 | 4:19 | 49.959
2025-03-02 | 4:19 | 49.96
2025-03-02 | 4:19 | 49.955
2025-03-02 | 4:19 | 49.959
2025-03-02 | 4:19 | 49.974
2025-03-02 | 4:19 | 49.974
2025-03-02 | 4:19 | 49.974
2025-03-02 | 4:19 | 49.988
2025-03-02 | 4:19 | 50.001
2025-03-02 | 4:19 | 50.005
2025-03-02 | 4:19 | 50.017
2025-03-02 | 4:19 | 50.033
2025-03-02 | 4:19 | 50.039
2025-03-02 | 4:19 | 50.039
2025-03-02 | 4:19 | 50.045
2025-03-02 | 4:19 | 50.054
2025-03-02 | 4:19 | 50.054
2025-03-02 | 4:19 | 50.049
2025-03-02 | 4:19 | 50.052
2025-03-02 | 4:19 | 50.053
2025-03-02 | 4:19 | 50.048
2025-03-02 | 4:19 | 50.049
2025-03-02 | 4:19 | 50.056
2025-03-02 | 4:19 | 50.052
2025-03-02 | 4:19 | 50.046
2025-03-02 | 4:19 | 50.05
2025-03-02 | 4:19 | 50.057
2025-03-02 | 4:19 | 50.047
2025-03-02 | 4:19 | 50.044
2025-03-02 | 4:19 | 50.049
2025-03-02 | 4:19 | 50.047
2025-03-02 | 4:20 | 50.042
2025-03-02 | 4:20 | 50.037
2025-03-02 | 4:20 | 50.042
2025-03-02 | 4:20 | 50.042
2025-03-02 | 4:20 | 50.053
2025-03-02 | 4:20 | 50.054
2025-03-02 | 4:20 | 50.05
2025-03-02 | 4:20 | 50.048
2025-03-02 | 4:20 | 50.056
2025-03-02 | 4:20 | 50.051
2025-03-02 | 4:20 | 50.047
2025-03-02 | 4:20 | 50.052
2025-03-02 | 4:20 | 50.052
2025-03-02 | 4:20 | 50.051
2025-03-02 | 4:20 | 50.046
2025-03-02 | 4:20 | 50.052
2025-03-02 | 4:20 | 50.048
2025-03-02 | 4:20 | 50.04
2025-03-02 | 4:20 | 50.043
2025-03-02 | 4:20 | 50.053
2025-03-02 | 4:20 | 50.051
2025-03-02 | 4:20 | 50.041
2025-03-02 | 4:20 | 50.044
2025-03-02 | 4:20 | 50.046
2025-03-02 | 4:20 | 50.045
2025-03-02 | 4:20 | 50.047
2025-03-02 | 4:20 | 50.054
2025-03-02 | 4:20 | 50.058
2025-03-02 | 4:20 | 50.052
2025-03-02 | 4:20 | 50.043
2025-03-02 | 4:20 | 50.048
2025-03-02 | 4:20 | 50.045
2025-03-02 | 4:20 | 50.042
2025-03-02 | 4:20 | 50.037
2025-03-02 | 4:20 | 50.041
2025-03-02 | 4:20 | 50.044
2025-03-02 | 4:20 | 50.039
2025-03-02 | 4:20 | 50.041

## 20250310-1
In GMT
Date | Time | Freq
2025-03-10 | 6:59 | 50.148 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-10 | 6:59 | 50.148 | 222 | BRITNED | 676.211
2025-03-10 | 6:59 | 50.15 | 268 | WBURB-2 | 428.156
2025-03-10 | 6:59 | 50.151 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-10 | 6:59 | 50.151 |  | Viking Link | -648.9
2025-03-10 | 6:59 | 50.15 |  | Viking Link | 1398.96
2025-03-10 | 6:59 | 50.148 | 209 | DRAXX-3 | 626.95
2025-03-10 | 6:59 | 50.147 | 154 | CDCL-1 | 391.57
2025-03-10 | 6:59 | 50.144 | 268 | ROCK-1 | 468.495
2025-03-10 | 6:59 | 50.141 | 148 | IFA Bipole1 | 945.473
2025-03-10 | 6:59 | 50.136 | 132 | IFA Bipole1 | 999.1
2025-03-10 | 6:59 | 50.132 | 141 | IFA Bipole2 | 1000
2025-03-10 | 6:59 | 50.129 | 135 | IFA Bipole1 | 996.75
2025-03-10 | 6:59 | 50.127 |  | Viking Link | -780.3
2025-03-10 | 6:59 | 50.126
2025-03-10 | 6:59 | 50.126
2025-03-10 | 6:59 | 50.128
2025-03-10 | 6:59 | 50.128
2025-03-10 | 6:59 | 50.132
2025-03-10 | 6:59 | 50.137 | 130 | HEYM12 | 271.908
2025-03-10 | 6:59 | 50.142 | 228 | HUMR-1 | 303.75
2025-03-10 | 6:59 | 50.142
2025-03-10 | 6:59 | 50.141
2025-03-10 | 6:59 | 50.14
2025-03-10 | 6:59 | 50.139
2025-03-10 | 6:59 | 50.139
2025-03-10 | 6:59 | 50.138
2025-03-10 | 6:59 | 50.134
2025-03-10 | 6:59 | 50.132
2025-03-10 | 6:59 | 50.129
2025-03-10 | 7:00 | 50.126 | 211 | CDCL-1 | 291.5
2025-03-10 | 7:00 | 50.124 | 199 | STAY-2 | 413.125
2025-03-10 | 7:00 | 50.123 | 173 | CDCL-1 | 397.375
2025-03-10 | 7:00 | 50.124 | 248 | SEAB-2 | 361.25
2025-03-10 | 7:00 | 50.123 | 255 | FRANCE | 995.65
2025-03-10 | 7:00 | 50.122 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-10 | 7:00 | 50.123
2025-03-10 | 7:00 | 50.123
2025-03-10 | 7:00 | 50.125
2025-03-10 | 7:00 | 50.125
2025-03-10 | 7:00 | 50.123
2025-03-10 | 7:00 | 50.12
2025-03-10 | 7:00 | 50.116
2025-03-10 | 7:00 | 50.114
2025-03-10 | 7:00 | 50.114
2025-03-10 | 7:00 | 50.113
2025-03-10 | 7:00 | 50.11
2025-03-10 | 7:00 | 50.107
2025-03-10 | 7:00 | 50.105
2025-03-10 | 7:00 | 50.106
2025-03-10 | 7:00 | 50.105
2025-03-10 | 7:00 | 50.105
2025-03-10 | 7:00 | 50.104
2025-03-10 | 7:00 | 50.101
2025-03-10 | 7:00 | 50.098
2025-03-10 | 7:00 | 50.097
2025-03-10 | 7:00 | 50.096
2025-03-10 | 7:00 | 50.096
2025-03-10 | 7:00 | 50.097
2025-03-10 | 7:00 | 50.094
2025-03-10 | 7:00 | 50.09
2025-03-10 | 7:00 | 50.076
2025-03-10 | 7:00 | 50.052
2025-03-10 | 7:00 | 50.035
2025-03-10 | 7:00 | 50.025
2025-03-10 | 7:00 | 50.017
2025-03-10 | 7:00 | 50.014
2025-03-10 | 7:00 | 50.012
2025-03-10 | 7:00 | 50.013
2025-03-10 | 7:00 | 50.016
2025-03-10 | 7:00 | 50.016
2025-03-10 | 7:00 | 50.016
2025-03-10 | 7:00 | 50.015
2025-03-10 | 7:00 | 50.016
2025-03-10 | 7:00 | 50.017
2025-03-10 | 7:00 | 50.017
2025-03-10 | 7:00 | 50.018
2025-03-10 | 7:00 | 50.016
2025-03-10 | 7:00 | 50.016
2025-03-10 | 7:00 | 50.014
2025-03-10 | 7:00 | 50.013
2025-03-10 | 7:00 | 50.01
2025-03-10 | 7:00 | 50.015
2025-03-10 | 7:00 | 50.021
2025-03-10 | 7:00 | 50.026
2025-03-10 | 7:00 | 50.033
2025-03-10 | 7:00 | 50.036
2025-03-10 | 7:00 | 50.039
2025-03-10 | 7:00 | 50.041
2025-03-10 | 7:00 | 50.04
2025-03-10 | 7:00 | 50.04
2025-03-10 | 7:01 | 50.039
2025-03-10 | 7:01 | 50.036
2025-03-10 | 7:01 | 50.033
2025-03-10 | 7:01 | 50.032
2025-03-10 | 7:01 | 50.03
2025-03-10 | 7:01 | 50.03
2025-03-10 | 7:01 | 50.032
2025-03-10 | 7:01 | 50.032
2025-03-10 | 7:01 | 50.035
2025-03-10 | 7:01 | 50.036
2025-03-10 | 7:01 | 50.04
2025-03-10 | 7:01 | 50.041
2025-03-10 | 7:01 | 50.045
2025-03-10 | 7:01 | 50.047
2025-03-10 | 7:01 | 50.046
2025-03-10 | 7:01 | 50.045
2025-03-10 | 7:01 | 50.043
2025-03-10 | 7:01 | 50.04
2025-03-10 | 7:01 | 50.038
2025-03-10 | 7:01 | 50.038
2025-03-10 | 7:01 | 50.039
2025-03-10 | 7:01 | 50.042
2025-03-10 | 7:01 | 50.043
2025-03-10 | 7:01 | 50.043
2025-03-10 | 7:01 | 50.042
2025-03-10 | 7:01 | 50.041
2025-03-10 | 7:01 | 50.039
2025-03-10 | 7:01 | 50.037
2025-03-10 | 7:01 | 50.038
2025-03-10 | 7:01 | 50.037
2025-03-10 | 7:01 | 50.037
2025-03-10 | 7:01 | 50.035
2025-03-10 | 7:01 | 50.035
2025-03-10 | 7:01 | 50.035
2025-03-10 | 7:01 | 50.035
2025-03-10 | 7:01 | 50.035
2025-03-10 | 7:01 | 50.034
2025-03-10 | 7:01 | 50.033
2025-03-10 | 7:01 | 50.033
2025-03-10 | 7:01 | 50.031
2025-03-10 | 7:01 | 50.028
2025-03-10 | 7:01 | 50.026
2025-03-10 | 7:01 | 50.024
2025-03-10 | 7:01 | 50.025
2025-03-10 | 7:01 | 50.028
2025-03-10 | 7:01 | 50.033
2025-03-10 | 7:01 | 50.035
2025-03-10 | 7:01 | 50.036
2025-03-10 | 7:01 | 50.039
2025-03-10 | 7:01 | 50.041
2025-03-10 | 7:01 | 50.042
2025-03-10 | 7:01 | 50.043
2025-03-10 | 7:01 | 50.044
2025-03-10 | 7:01 | 50.042
2025-03-10 | 7:01 | 50.042
2025-03-10 | 7:01 | 50.042
2025-03-10 | 7:01 | 50.041
2025-03-10 | 7:01 | 50.043
2025-03-10 | 7:01 | 50.045
2025-03-10 | 7:02 | 50.049
2025-03-10 | 7:02 | 50.049
2025-03-10 | 7:02 | 50.048
2025-03-10 | 7:02 | 50.049
2025-03-10 | 7:02 | 50.05
2025-03-10 | 7:02 | 50.048
2025-03-10 | 7:02 | 50.046
2025-03-10 | 7:02 | 50.046
2025-03-10 | 7:02 | 50.047
2025-03-10 | 7:02 | 50.044
2025-03-10 | 7:02 | 50.044
2025-03-10 | 7:02 | 50.045
2025-03-10 | 7:02 | 50.048
2025-03-10 | 7:02 | 50.05
2025-03-10 | 7:02 | 50.053
2025-03-10 | 7:02 | 50.058
2025-03-10 | 7:02 | 50.062
2025-03-10 | 7:02 | 50.067
2025-03-10 | 7:02 | 50.067
2025-03-10 | 7:02 | 50.067
2025-03-10 | 7:02 | 50.068
2025-03-10 | 7:02 | 50.068
2025-03-10 | 7:02 | 50.068
2025-03-10 | 7:02 | 50.067
2025-03-10 | 7:02 | 50.066
2025-03-10 | 7:02 | 50.065
2025-03-10 | 7:02 | 50.064
2025-03-10 | 7:02 | 50.065
2025-03-10 | 7:02 | 50.066
2025-03-10 | 7:02 | 50.068
2025-03-10 | 7:02 | 50.07
2025-03-10 | 7:02 | 50.072
2025-03-10 | 7:02 | 50.074
2025-03-10 | 7:02 | 50.075
2025-03-10 | 7:02 | 50.076
2025-03-10 | 7:02 | 50.074
2025-03-10 | 7:02 | 50.068
2025-03-10 | 7:02 | 50.059
2025-03-10 | 7:02 | 50.054
2025-03-10 | 7:02 | 50.05
2025-03-10 | 7:02 | 50.046
2025-03-10 | 7:02 | 50.044
2025-03-10 | 7:02 | 50.04
2025-03-10 | 7:02 | 50.039
2025-03-10 | 7:02 | 50.038
2025-03-10 | 7:02 | 50.036
2025-03-10 | 7:02 | 50.033
2025-03-10 | 7:02 | 50.029
2025-03-10 | 7:02 | 50.027
2025-03-10 | 7:02 | 50.026
2025-03-10 | 7:02 | 50.027
2025-03-10 | 7:02 | 50.029
2025-03-10 | 7:02 | 50.03
2025-03-10 | 7:02 | 50.03
2025-03-10 | 7:02 | 50.031
2025-03-10 | 7:02 | 50.032
2025-03-10 | 7:02 | 50.033
2025-03-10 | 7:02 | 50.033
2025-03-10 | 7:02 | 50.033
2025-03-10 | 7:02 | 50.033
2025-03-10 | 7:02 | 50.031
2025-03-10 | 7:03 | 50.031
2025-03-10 | 7:03 | 50.029
2025-03-10 | 7:03 | 50.029
2025-03-10 | 7:03 | 50.027
2025-03-10 | 7:03 | 50.022
2025-03-10 | 7:03 | 50.02
2025-03-10 | 7:03 | 50.016
2025-03-10 | 7:03 | 50.018
2025-03-10 | 7:03 | 50.019
2025-03-10 | 7:03 | 50.021
2025-03-10 | 7:03 | 50.023
2025-03-10 | 7:03 | 50.024
2025-03-10 | 7:03 | 50.024
2025-03-10 | 7:03 | 50.024
2025-03-10 | 7:03 | 50.028
2025-03-10 | 7:03 | 50.03
2025-03-10 | 7:03 | 50.033
2025-03-10 | 7:03 | 50.036
2025-03-10 | 7:03 | 50.036
2025-03-10 | 7:03 | 50.037
2025-03-10 | 7:03 | 50.039
2025-03-10 | 7:03 | 50.037
2025-03-10 | 7:03 | 50.036
2025-03-10 | 7:03 | 50.035
2025-03-10 | 7:03 | 50.035
2025-03-10 | 7:03 | 50.034
2025-03-10 | 7:03 | 50.034
2025-03-10 | 7:03 | 50.034
2025-03-10 | 7:03 | 50.034
2025-03-10 | 7:03 | 50.034
2025-03-10 | 7:03 | 50.034
2025-03-10 | 7:03 | 50.028
2025-03-10 | 7:03 | 50.022
2025-03-10 | 7:03 | 50.016
2025-03-10 | 7:03 | 50.011
2025-03-10 | 7:03 | 50.007
2025-03-10 | 7:03 | 50.002
2025-03-10 | 7:03 | 49.999
2025-03-10 | 7:03 | 49.995
2025-03-10 | 7:03 | 49.991
2025-03-10 | 7:03 | 49.987
2025-03-10 | 7:03 | 49.98
2025-03-10 | 7:03 | 49.973
2025-03-10 | 7:03 | 49.97
2025-03-10 | 7:03 | 49.968
2025-03-10 | 7:03 | 49.963
2025-03-10 | 7:03 | 49.961
2025-03-10 | 7:03 | 49.959
2025-03-10 | 7:03 | 49.958
2025-03-10 | 7:03 | 49.958
2025-03-10 | 7:03 | 49.957
2025-03-10 | 7:03 | 49.957
2025-03-10 | 7:03 | 49.955
2025-03-10 | 7:03 | 49.952
2025-03-10 | 7:03 | 49.95
2025-03-10 | 7:03 | 49.949
2025-03-10 | 7:03 | 49.95
2025-03-10 | 7:03 | 49.951
2025-03-10 | 7:03 | 49.953
2025-03-10 | 7:04 | 49.956
2025-03-10 | 7:04 | 49.958
2025-03-10 | 7:04 | 49.958
2025-03-10 | 7:04 | 49.961
2025-03-10 | 7:04 | 49.959
2025-03-10 | 7:04 | 49.959
2025-03-10 | 7:04 | 49.96
2025-03-10 | 7:04 | 49.959
2025-03-10 | 7:04 | 49.96
2025-03-10 | 7:04 | 49.96
2025-03-10 | 7:04 | 49.96
2025-03-10 | 7:04 | 49.957
2025-03-10 | 7:04 | 49.955
2025-03-10 | 7:04 | 49.951
2025-03-10 | 7:04 | 49.948
2025-03-10 | 7:04 | 49.944
2025-03-10 | 7:04 | 49.943
2025-03-10 | 7:04 | 49.941
2025-03-10 | 7:04 | 49.94
2025-03-10 | 7:04 | 49.941
2025-03-10 | 7:04 | 49.944
2025-03-10 | 7:04 | 49.946
2025-03-10 | 7:04 | 49.949
2025-03-10 | 7:04 | 49.951
2025-03-10 | 7:04 | 49.953
2025-03-10 | 7:04 | 49.955
2025-03-10 | 7:04 | 49.958
2025-03-10 | 7:04 | 49.96
2025-03-10 | 7:04 | 49.961
2025-03-10 | 7:04 | 49.962
2025-03-10 | 7:04 | 49.961
2025-03-10 | 7:04 | 49.959
2025-03-10 | 7:04 | 49.956
2025-03-10 | 7:04 | 49.954
2025-03-10 | 7:04 | 49.954
2025-03-10 | 7:04 | 49.953
2025-03-10 | 7:04 | 49.95
2025-03-10 | 7:04 | 49.949
2025-03-10 | 7:04 | 49.946

## 20250310-2
In GMT
Date | Time | Freq
2025-03-10 | 23:26 | 50.097 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-10 | 23:26 | 50.098 | 222 | BRITNED | 676.211
2025-03-10 | 23:26 | 50.098 | 268 | WBURB-2 | 428.156
2025-03-10 | 23:26 | 50.096 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-10 | 23:26 | 50.091 |  | Viking Link | -648.9
2025-03-10 | 23:26 | 50.09 |  | Viking Link | 1398.96
2025-03-10 | 23:26 | 50.089 | 209 | DRAXX-3 | 626.95
2025-03-10 | 23:26 | 50.09 | 154 | CDCL-1 | 391.57
2025-03-10 | 23:26 | 50.095 | 268 | ROCK-1 | 468.495
2025-03-10 | 23:26 | 50.096 | 148 | IFA Bipole1 | 945.473
2025-03-10 | 23:26 | 50.097 | 132 | IFA Bipole1 | 999.1
2025-03-10 | 23:26 | 50.097 | 141 | IFA Bipole2 | 1000
2025-03-10 | 23:26 | 50.097 | 135 | IFA Bipole1 | 996.75
2025-03-10 | 23:26 | 50.099 |  | Viking Link | -780.3
2025-03-10 | 23:26 | 50.099
2025-03-10 | 23:26 | 50.099
2025-03-10 | 23:26 | 50.098
2025-03-10 | 23:26 | 50.101
2025-03-10 | 23:26 | 50.1
2025-03-10 | 23:26 | 50.101 | 130 | HEYM12 | 271.908
2025-03-10 | 23:26 | 50.1 | 228 | HUMR-1 | 303.75
2025-03-10 | 23:26 | 50.097
2025-03-10 | 23:26 | 50.095
2025-03-10 | 23:26 | 50.093
2025-03-10 | 23:26 | 50.093
2025-03-10 | 23:26 | 50.093
2025-03-10 | 23:26 | 50.093
2025-03-10 | 23:26 | 50.094
2025-03-10 | 23:26 | 50.095
2025-03-10 | 23:26 | 50.097
2025-03-10 | 23:26 | 50.095 | 211 | CDCL-1 | 291.5
2025-03-10 | 23:26 | 50.093 | 199 | STAY-2 | 413.125
2025-03-10 | 23:26 | 50.088 | 173 | CDCL-1 | 397.375
2025-03-10 | 23:26 | 50.085 | 248 | SEAB-2 | 361.25
2025-03-10 | 23:26 | 50.08 | 255 | FRANCE | 995.65
2025-03-10 | 23:26 | 50.078 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-10 | 23:26 | 50.078
2025-03-10 | 23:26 | 50.081
2025-03-10 | 23:26 | 50.083
2025-03-10 | 23:26 | 50.086
2025-03-10 | 23:26 | 50.09
2025-03-10 | 23:26 | 50.092
2025-03-10 | 23:26 | 50.093
2025-03-10 | 23:26 | 50.094
2025-03-10 | 23:26 | 50.095
2025-03-10 | 23:26 | 50.096
2025-03-10 | 23:26 | 50.097
2025-03-10 | 23:26 | 50.098
2025-03-10 | 23:26 | 50.098
2025-03-10 | 23:26 | 50.099
2025-03-10 | 23:26 | 50.098
2025-03-10 | 23:26 | 50.099
2025-03-10 | 23:26 | 50.098
2025-03-10 | 23:26 | 50.1
2025-03-10 | 23:26 | 50.1
2025-03-10 | 23:26 | 50.102
2025-03-10 | 23:27 | 50.102
2025-03-10 | 23:27 | 50.101
2025-03-10 | 23:27 | 50.102
2025-03-10 | 23:27 | 50.105
2025-03-10 | 23:27 | 50.106
2025-03-10 | 23:27 | 50.108
2025-03-10 | 23:27 | 50.107
2025-03-10 | 23:27 | 50.108
2025-03-10 | 23:27 | 50.109
2025-03-10 | 23:27 | 50.108
2025-03-10 | 23:27 | 50.105
2025-03-10 | 23:27 | 50.102
2025-03-10 | 23:27 | 50.104
2025-03-10 | 23:27 | 50.103
2025-03-10 | 23:27 | 50.101
2025-03-10 | 23:27 | 50.104
2025-03-10 | 23:27 | 50.103
2025-03-10 | 23:27 | 50.104
2025-03-10 | 23:27 | 50.104
2025-03-10 | 23:27 | 50.105
2025-03-10 | 23:27 | 50.104
2025-03-10 | 23:27 | 50.105
2025-03-10 | 23:27 | 50.105
2025-03-10 | 23:27 | 50.105
2025-03-10 | 23:27 | 50.104
2025-03-10 | 23:27 | 50.103
2025-03-10 | 23:27 | 50.103
2025-03-10 | 23:27 | 50.105
2025-03-10 | 23:27 | 50.105
2025-03-10 | 23:27 | 50.105
2025-03-10 | 23:27 | 50.102
2025-03-10 | 23:27 | 50.103
2025-03-10 | 23:27 | 50.101
2025-03-10 | 23:27 | 50.102
2025-03-10 | 23:27 | 50.102
2025-03-10 | 23:27 | 50.103
2025-03-10 | 23:27 | 50.104
2025-03-10 | 23:27 | 50.104
2025-03-10 | 23:27 | 50.106
2025-03-10 | 23:27 | 50.109
2025-03-10 | 23:27 | 50.11
2025-03-10 | 23:27 | 50.111
2025-03-10 | 23:27 | 50.112
2025-03-10 | 23:27 | 50.114
2025-03-10 | 23:27 | 50.115
2025-03-10 | 23:27 | 50.115
2025-03-10 | 23:27 | 50.116
2025-03-10 | 23:27 | 50.117
2025-03-10 | 23:27 | 50.118
2025-03-10 | 23:27 | 50.119
2025-03-10 | 23:27 | 50.12
2025-03-10 | 23:27 | 50.12
2025-03-10 | 23:27 | 50.121
2025-03-10 | 23:27 | 50.12
2025-03-10 | 23:27 | 50.119
2025-03-10 | 23:27 | 50.117
2025-03-10 | 23:27 | 50.118
2025-03-10 | 23:27 | 50.117
2025-03-10 | 23:27 | 50.117
2025-03-10 | 23:28 | 50.116
2025-03-10 | 23:28 | 50.117
2025-03-10 | 23:28 | 50.114
2025-03-10 | 23:28 | 50.117
2025-03-10 | 23:28 | 50.119
2025-03-10 | 23:28 | 50.12
2025-03-10 | 23:28 | 50.118
2025-03-10 | 23:28 | 50.116
2025-03-10 | 23:28 | 50.116
2025-03-10 | 23:28 | 50.116
2025-03-10 | 23:28 | 50.116
2025-03-10 | 23:28 | 50.116
2025-03-10 | 23:28 | 50.117
2025-03-10 | 23:28 | 50.118
2025-03-10 | 23:28 | 50.116
2025-03-10 | 23:28 | 50.115
2025-03-10 | 23:28 | 50.115
2025-03-10 | 23:28 | 50.117
2025-03-10 | 23:28 | 50.118
2025-03-10 | 23:28 | 50.118
2025-03-10 | 23:28 | 50.114
2025-03-10 | 23:28 | 50.111
2025-03-10 | 23:28 | 50.108
2025-03-10 | 23:28 | 50.11
2025-03-10 | 23:28 | 50.11
2025-03-10 | 23:28 | 50.109
2025-03-10 | 23:28 | 50.111
2025-03-10 | 23:28 | 50.112
2025-03-10 | 23:28 | 50.112
2025-03-10 | 23:28 | 50.112
2025-03-10 | 23:28 | 50.112
2025-03-10 | 23:28 | 50.11
2025-03-10 | 23:28 | 50.108
2025-03-10 | 23:28 | 50.109
2025-03-10 | 23:28 | 50.109
2025-03-10 | 23:28 | 50.111
2025-03-10 | 23:28 | 50.112
2025-03-10 | 23:28 | 50.114
2025-03-10 | 23:28 | 50.117
2025-03-10 | 23:28 | 50.118
2025-03-10 | 23:28 | 50.117
2025-03-10 | 23:28 | 50.118
2025-03-10 | 23:28 | 50.118
2025-03-10 | 23:28 | 50.118
2025-03-10 | 23:28 | 50.116
2025-03-10 | 23:28 | 50.118
2025-03-10 | 23:28 | 50.116
2025-03-10 | 23:28 | 50.115
2025-03-10 | 23:28 | 50.113
2025-03-10 | 23:28 | 50.116
2025-03-10 | 23:28 | 50.118
2025-03-10 | 23:28 | 50.119
2025-03-10 | 23:28 | 50.12
2025-03-10 | 23:28 | 50.122
2025-03-10 | 23:28 | 50.123
2025-03-10 | 23:28 | 50.123
2025-03-10 | 23:28 | 50.124
2025-03-10 | 23:28 | 50.126
2025-03-10 | 23:28 | 50.126
2025-03-10 | 23:28 | 50.127
2025-03-10 | 23:28 | 50.128
2025-03-10 | 23:29 | 50.126
2025-03-10 | 23:29 | 50.125
2025-03-10 | 23:29 | 50.127
2025-03-10 | 23:29 | 50.127
2025-03-10 | 23:29 | 50.127
2025-03-10 | 23:29 | 50.128
2025-03-10 | 23:29 | 50.128
2025-03-10 | 23:29 | 50.128
2025-03-10 | 23:29 | 50.128
2025-03-10 | 23:29 | 50.128
2025-03-10 | 23:29 | 50.128
2025-03-10 | 23:29 | 50.123
2025-03-10 | 23:29 | 50.124
2025-03-10 | 23:29 | 50.125
2025-03-10 | 23:29 | 50.129
2025-03-10 | 23:29 | 50.129
2025-03-10 | 23:29 | 50.129
2025-03-10 | 23:29 | 50.127
2025-03-10 | 23:29 | 50.126
2025-03-10 | 23:29 | 50.124
2025-03-10 | 23:29 | 50.123
2025-03-10 | 23:29 | 50.124
2025-03-10 | 23:29 | 50.125
2025-03-10 | 23:29 | 50.126
2025-03-10 | 23:29 | 50.125
2025-03-10 | 23:29 | 50.124
2025-03-10 | 23:29 | 50.125
2025-03-10 | 23:29 | 50.126
2025-03-10 | 23:29 | 50.124
2025-03-10 | 23:29 | 50.123
2025-03-10 | 23:29 | 50.122
2025-03-10 | 23:29 | 50.122
2025-03-10 | 23:29 | 50.123
2025-03-10 | 23:29 | 50.125
2025-03-10 | 23:29 | 50.127
2025-03-10 | 23:29 | 50.127
2025-03-10 | 23:29 | 50.125
2025-03-10 | 23:29 | 50.125
2025-03-10 | 23:29 | 50.126
2025-03-10 | 23:29 | 50.127
2025-03-10 | 23:29 | 50.129
2025-03-10 | 23:29 | 50.131
2025-03-10 | 23:29 | 50.13
2025-03-10 | 23:29 | 50.13
2025-03-10 | 23:29 | 50.13
2025-03-10 | 23:29 | 50.129
2025-03-10 | 23:29 | 50.131
2025-03-10 | 23:29 | 50.13
2025-03-10 | 23:29 | 50.131
2025-03-10 | 23:29 | 50.13
2025-03-10 | 23:29 | 50.129
2025-03-10 | 23:29 | 50.129
2025-03-10 | 23:29 | 50.129
2025-03-10 | 23:29 | 50.129
2025-03-10 | 23:29 | 50.13
2025-03-10 | 23:29 | 50.131
2025-03-10 | 23:29 | 50.133
2025-03-10 | 23:29 | 50.133
2025-03-10 | 23:29 | 50.135
2025-03-10 | 23:30 | 50.134
2025-03-10 | 23:30 | 50.132
2025-03-10 | 23:30 | 50.13
2025-03-10 | 23:30 | 50.13
2025-03-10 | 23:30 | 50.132
2025-03-10 | 23:30 | 50.136
2025-03-10 | 23:30 | 50.138
2025-03-10 | 23:30 | 50.137
2025-03-10 | 23:30 | 50.134
2025-03-10 | 23:30 | 50.133
2025-03-10 | 23:30 | 50.131
2025-03-10 | 23:30 | 50.13
2025-03-10 | 23:30 | 50.129
2025-03-10 | 23:30 | 50.13
2025-03-10 | 23:30 | 50.13
2025-03-10 | 23:30 | 50.131
2025-03-10 | 23:30 | 50.133
2025-03-10 | 23:30 | 50.134
2025-03-10 | 23:30 | 50.13
2025-03-10 | 23:30 | 50.131
2025-03-10 | 23:30 | 50.129
2025-03-10 | 23:30 | 50.129
2025-03-10 | 23:30 | 50.131
2025-03-10 | 23:30 | 50.133
2025-03-10 | 23:30 | 50.132
2025-03-10 | 23:30 | 50.132
2025-03-10 | 23:30 | 50.134
2025-03-10 | 23:30 | 50.134
2025-03-10 | 23:30 | 50.133
2025-03-10 | 23:30 | 50.133
2025-03-10 | 23:30 | 50.131
2025-03-10 | 23:30 | 50.125
2025-03-10 | 23:30 | 50.121
2025-03-10 | 23:30 | 50.119
2025-03-10 | 23:30 | 50.121
2025-03-10 | 23:30 | 50.122
2025-03-10 | 23:30 | 50.121
2025-03-10 | 23:30 | 50.121
2025-03-10 | 23:30 | 50.118
2025-03-10 | 23:30 | 50.116
2025-03-10 | 23:30 | 50.116
2025-03-10 | 23:30 | 50.114
2025-03-10 | 23:30 | 50.113
2025-03-10 | 23:30 | 50.115
2025-03-10 | 23:30 | 50.112
2025-03-10 | 23:30 | 50.112
2025-03-10 | 23:30 | 50.112
2025-03-10 | 23:30 | 50.111
2025-03-10 | 23:30 | 50.109
2025-03-10 | 23:30 | 50.106
2025-03-10 | 23:30 | 50.103
2025-03-10 | 23:30 | 50.101
2025-03-10 | 23:30 | 50.1
2025-03-10 | 23:30 | 50.099
2025-03-10 | 23:30 | 50.096
2025-03-10 | 23:30 | 50.094
2025-03-10 | 23:30 | 50.092
2025-03-10 | 23:30 | 50.089
2025-03-10 | 23:30 | 50.087
2025-03-10 | 23:30 | 50.084
2025-03-10 | 23:30 | 50.08
2025-03-10 | 23:31 | 50.079
2025-03-10 | 23:31 | 50.077
2025-03-10 | 23:31 | 50.078
2025-03-10 | 23:31 | 50.077
2025-03-10 | 23:31 | 50.077
2025-03-10 | 23:31 | 50.077
2025-03-10 | 23:31 | 50.077
2025-03-10 | 23:31 | 50.076
2025-03-10 | 23:31 | 50.075
2025-03-10 | 23:31 | 50.074
2025-03-10 | 23:31 | 50.072
2025-03-10 | 23:31 | 50.071
2025-03-10 | 23:31 | 50.068
2025-03-10 | 23:31 | 50.065
2025-03-10 | 23:31 | 50.065
2025-03-10 | 23:31 | 50.063
2025-03-10 | 23:31 | 50.063
2025-03-10 | 23:31 | 50.062
2025-03-10 | 23:31 | 50.062
2025-03-10 | 23:31 | 50.064
2025-03-10 | 23:31 | 50.072
2025-03-10 | 23:31 | 50.076
2025-03-10 | 23:31 | 50.079
2025-03-10 | 23:31 | 50.079
2025-03-10 | 23:31 | 50.078
2025-03-10 | 23:31 | 50.075
2025-03-10 | 23:31 | 50.071
2025-03-10 | 23:31 | 50.07
2025-03-10 | 23:31 | 50.069
2025-03-10 | 23:31 | 50.07
2025-03-10 | 23:31 | 50.065
2025-03-10 | 23:31 | 50.062
2025-03-10 | 23:31 | 50.061
2025-03-10 | 23:31 | 50.061
2025-03-10 | 23:31 | 50.064
2025-03-10 | 23:31 | 50.066
2025-03-10 | 23:31 | 50.066
2025-03-10 | 23:31 | 50.066
2025-03-10 | 23:31 | 50.065
2025-03-10 | 23:31 | 50.064
2025-03-10 | 23:31 | 50.06
2025-03-10 | 23:31 | 50.057
2025-03-10 | 23:31 | 50.057
2025-03-10 | 23:31 | 50.059
2025-03-10 | 23:31 | 50.063
2025-03-10 | 23:31 | 50.068
2025-03-10 | 23:31 | 50.07
2025-03-10 | 23:31 | 50.069
2025-03-10 | 23:31 | 50.067
2025-03-10 | 23:31 | 50.065
2025-03-10 | 23:31 | 50.065
2025-03-10 | 23:31 | 50.068
2025-03-10 | 23:31 | 50.067
2025-03-10 | 23:31 | 50.064
2025-03-10 | 23:31 | 50.064
2025-03-10 | 23:31 | 50.065
2025-03-10 | 23:31 | 50.066
2025-03-10 | 23:31 | 50.068
2025-03-10 | 23:31 | 50.067
2025-03-10 | 23:32 | 50.067
2025-03-10 | 23:32 | 50.065
2025-03-10 | 23:32 | 50.066
2025-03-10 | 23:32 | 50.064
2025-03-10 | 23:32 | 50.061
2025-03-10 | 23:32 | 50.057
2025-03-10 | 23:32 | 50.057
2025-03-10 | 23:32 | 50.059
2025-03-10 | 23:32 | 50.059
2025-03-10 | 23:32 | 50.062
2025-03-10 | 23:32 | 50.064
2025-03-10 | 23:32 | 50.069
2025-03-10 | 23:32 | 50.069
2025-03-10 | 23:32 | 50.068
2025-03-10 | 23:32 | 50.068
2025-03-10 | 23:32 | 50.066
2025-03-10 | 23:32 | 50.067
2025-03-10 | 23:32 | 50.065
2025-03-10 | 23:32 | 50.062
2025-03-10 | 23:32 | 50.06
2025-03-10 | 23:32 | 50.06
2025-03-10 | 23:32 | 50.059
2025-03-10 | 23:32 | 50.06
2025-03-10 | 23:32 | 50.061
2025-03-10 | 23:32 | 50.064
2025-03-10 | 23:32 | 50.065
2025-03-10 | 23:32 | 50.067
2025-03-10 | 23:32 | 50.07
2025-03-10 | 23:32 | 50.069
2025-03-10 | 23:32 | 50.069
2025-03-10 | 23:32 | 50.069
2025-03-10 | 23:32 | 50.065
2025-03-10 | 23:32 | 50.063
2025-03-10 | 23:32 | 50.06
2025-03-10 | 23:32 | 50.06
2025-03-10 | 23:32 | 50.06
2025-03-10 | 23:32 | 50.062
2025-03-10 | 23:32 | 50.063
2025-03-10 | 23:32 | 50.064
2025-03-10 | 23:32 | 50.063
2025-03-10 | 23:32 | 50.063
2025-03-10 | 23:32 | 50.066
2025-03-10 | 23:32 | 50.069
2025-03-10 | 23:32 | 50.068
2025-03-10 | 23:32 | 50.064
2025-03-10 | 23:32 | 50.061
2025-03-10 | 23:32 | 50.061
2025-03-10 | 23:32 | 50.062
2025-03-10 | 23:32 | 50.064
2025-03-10 | 23:32 | 50.063
2025-03-10 | 23:32 | 50.063
2025-03-10 | 23:32 | 50.066
2025-03-10 | 23:32 | 50.068
2025-03-10 | 23:32 | 50.068
2025-03-10 | 23:32 | 50.066
2025-03-10 | 23:32 | 50.066
2025-03-10 | 23:32 | 50.065
2025-03-10 | 23:32 | 50.066
2025-03-10 | 23:32 | 50.067
2025-03-10 | 23:32 | 50.069
2025-03-10 | 23:32 | 50.069
2025-03-10 | 23:33 | 50.069
2025-03-10 | 23:33 | 50.068
2025-03-10 | 23:33 | 50.067
2025-03-10 | 23:33 | 50.066
2025-03-10 | 23:33 | 50.066
2025-03-10 | 23:33 | 50.066
2025-03-10 | 23:33 | 50.067
2025-03-10 | 23:33 | 50.066
2025-03-10 | 23:33 | 50.065
2025-03-10 | 23:33 | 50.067
2025-03-10 | 23:33 | 50.067
2025-03-10 | 23:33 | 50.068
2025-03-10 | 23:33 | 50.068
2025-03-10 | 23:33 | 50.069
2025-03-10 | 23:33 | 50.068
2025-03-10 | 23:33 | 50.066
2025-03-10 | 23:33 | 50.066
2025-03-10 | 23:33 | 50.064
2025-03-10 | 23:33 | 50.062
2025-03-10 | 23:33 | 50.063
2025-03-10 | 23:33 | 50.063
2025-03-10 | 23:33 | 50.063
2025-03-10 | 23:33 | 50.061
2025-03-10 | 23:33 | 50.061
2025-03-10 | 23:33 | 50.061
2025-03-10 | 23:33 | 50.063
2025-03-10 | 23:33 | 50.065
2025-03-10 | 23:33 | 50.066
2025-03-10 | 23:33 | 50.065
2025-03-10 | 23:33 | 50.066
2025-03-10 | 23:33 | 50.063
2025-03-10 | 23:33 | 50.061
2025-03-10 | 23:33 | 50.058
2025-03-10 | 23:33 | 50.057
2025-03-10 | 23:33 | 50.055
2025-03-10 | 23:33 | 50.053
2025-03-10 | 23:33 | 50.055
2025-03-10 | 23:33 | 50.059
2025-03-10 | 23:33 | 50.062
2025-03-10 | 23:33 | 50.063
2025-03-10 | 23:33 | 50.06
2025-03-10 | 23:33 | 50.057
2025-03-10 | 23:33 | 50.054
2025-03-10 | 23:33 | 50.053
2025-03-10 | 23:33 | 50.054
2025-03-10 | 23:33 | 50.056
2025-03-10 | 23:33 | 50.057
2025-03-10 | 23:33 | 50.06
2025-03-10 | 23:33 | 50.061
2025-03-10 | 23:33 | 50.061
2025-03-10 | 23:33 | 50.061
2025-03-10 | 23:33 | 50.06
2025-03-10 | 23:33 | 50.055
2025-03-10 | 23:33 | 50.056
2025-03-10 | 23:33 | 50.057
2025-03-10 | 23:33 | 50.061
2025-03-10 | 23:33 | 50.062
2025-03-10 | 23:33 | 50.061
2025-03-10 | 23:33 | 50.06
2025-03-10 | 23:34 | 50.062
2025-03-10 | 23:34 | 50.062
2025-03-10 | 23:34 | 50.063
2025-03-10 | 23:34 | 50.064
2025-03-10 | 23:34 | 50.064
2025-03-10 | 23:34 | 50.068
2025-03-10 | 23:34 | 50.069
2025-03-10 | 23:34 | 50.067
2025-03-10 | 23:34 | 50.068
2025-03-10 | 23:34 | 50.068
2025-03-10 | 23:34 | 50.071
2025-03-10 | 23:34 | 50.072
2025-03-10 | 23:34 | 50.071
2025-03-10 | 23:34 | 50.069
2025-03-10 | 23:34 | 50.066
2025-03-10 | 23:34 | 50.066
2025-03-10 | 23:34 | 50.069
2025-03-10 | 23:34 | 50.071
2025-03-10 | 23:34 | 50.073
2025-03-10 | 23:34 | 50.074
2025-03-10 | 23:34 | 50.078
2025-03-10 | 23:34 | 50.077
2025-03-10 | 23:34 | 50.075
2025-03-10 | 23:34 | 50.076
2025-03-10 | 23:34 | 50.075
2025-03-10 | 23:34 | 50.077
2025-03-10 | 23:34 | 50.079
2025-03-10 | 23:34 | 50.076
2025-03-10 | 23:34 | 50.076
2025-03-10 | 23:34 | 50.077
2025-03-10 | 23:34 | 50.081
2025-03-10 | 23:34 | 50.08
2025-03-10 | 23:34 | 50.078
2025-03-10 | 23:34 | 50.077
2025-03-10 | 23:34 | 50.076
2025-03-10 | 23:34 | 50.079
2025-03-10 | 23:34 | 50.079
2025-03-10 | 23:34 | 50.079
2025-03-10 | 23:34 | 50.081
2025-03-10 | 23:34 | 50.083
2025-03-10 | 23:34 | 50.082
2025-03-10 | 23:34 | 50.08
2025-03-10 | 23:34 | 50.08
2025-03-10 | 23:34 | 50.081
2025-03-10 | 23:34 | 50.084
2025-03-10 | 23:34 | 50.085
2025-03-10 | 23:34 | 50.085
2025-03-10 | 23:34 | 50.083
2025-03-10 | 23:34 | 50.08
2025-03-10 | 23:34 | 50.08
2025-03-10 | 23:34 | 50.081
2025-03-10 | 23:34 | 50.081
2025-03-10 | 23:34 | 50.081
2025-03-10 | 23:34 | 50.079
2025-03-10 | 23:34 | 50.079
2025-03-10 | 23:34 | 50.078
2025-03-10 | 23:34 | 50.081
2025-03-10 | 23:34 | 50.08
2025-03-10 | 23:34 | 50.079
2025-03-10 | 23:34 | 50.076
2025-03-10 | 23:34 | 50.074
2025-03-10 | 23:35 | 50.076
2025-03-10 | 23:35 | 50.076
2025-03-10 | 23:35 | 50.077
2025-03-10 | 23:35 | 50.084
2025-03-10 | 23:35 | 50.091
2025-03-10 | 23:35 | 50.094
2025-03-10 | 23:35 | 50.093
2025-03-10 | 23:35 | 50.09
2025-03-10 | 23:35 | 50.087
2025-03-10 | 23:35 | 50.084
2025-03-10 | 23:35 | 50.083
2025-03-10 | 23:35 | 50.086
2025-03-10 | 23:35 | 50.086
2025-03-10 | 23:35 | 50.087
2025-03-10 | 23:35 | 50.088
2025-03-10 | 23:35 | 50.089
2025-03-10 | 23:35 | 50.089
2025-03-10 | 23:35 | 50.09
2025-03-10 | 23:35 | 50.089
2025-03-10 | 23:35 | 50.089
2025-03-10 | 23:35 | 50.086
2025-03-10 | 23:35 | 50.085
2025-03-10 | 23:35 | 50.087
2025-03-10 | 23:35 | 50.089
2025-03-10 | 23:35 | 50.089
2025-03-10 | 23:35 | 50.088
2025-03-10 | 23:35 | 50.084
2025-03-10 | 23:35 | 50.082
2025-03-10 | 23:35 | 50.081
2025-03-10 | 23:35 | 50.083
2025-03-10 | 23:35 | 50.081
2025-03-10 | 23:35 | 50.082
2025-03-10 | 23:35 | 50.084
2025-03-10 | 23:35 | 50.086
2025-03-10 | 23:35 | 50.088
2025-03-10 | 23:35 | 50.088
2025-03-10 | 23:35 | 50.085
2025-03-10 | 23:35 | 50.087
2025-03-10 | 23:35 | 50.086
2025-03-10 | 23:35 | 50.085
2025-03-10 | 23:35 | 50.084
2025-03-10 | 23:35 | 50.083
2025-03-10 | 23:35 | 50.083
2025-03-10 | 23:35 | 50.083
2025-03-10 | 23:35 | 50.084
2025-03-10 | 23:35 | 50.085
2025-03-10 | 23:35 | 50.087
2025-03-10 | 23:35 | 50.086
2025-03-10 | 23:35 | 50.088
2025-03-10 | 23:35 | 50.089
2025-03-10 | 23:35 | 50.088
2025-03-10 | 23:35 | 50.087
2025-03-10 | 23:35 | 50.088
2025-03-10 | 23:35 | 50.086
2025-03-10 | 23:35 | 50.085
2025-03-10 | 23:35 | 50.084
2025-03-10 | 23:35 | 50.084
2025-03-10 | 23:35 | 50.086
2025-03-10 | 23:35 | 50.088
2025-03-10 | 23:36 | 50.089
2025-03-10 | 23:36 | 50.086
2025-03-10 | 23:36 | 50.085
2025-03-10 | 23:36 | 50.086
2025-03-10 | 23:36 | 50.088
2025-03-10 | 23:36 | 50.088
2025-03-10 | 23:36 | 50.089
2025-03-10 | 23:36 | 50.089
2025-03-10 | 23:36 | 50.087
2025-03-10 | 23:36 | 50.088
2025-03-10 | 23:36 | 50.087
2025-03-10 | 23:36 | 50.088
2025-03-10 | 23:36 | 50.087
2025-03-10 | 23:36 | 50.088
2025-03-10 | 23:36 | 50.091
2025-03-10 | 23:36 | 50.094
2025-03-10 | 23:36 | 50.096
2025-03-10 | 23:36 | 50.097
2025-03-10 | 23:36 | 50.097
2025-03-10 | 23:36 | 50.098
2025-03-10 | 23:36 | 50.098
2025-03-10 | 23:36 | 50.097
2025-03-10 | 23:36 | 50.096
2025-03-10 | 23:36 | 50.095
2025-03-10 | 23:36 | 50.095
2025-03-10 | 23:36 | 50.096
2025-03-10 | 23:36 | 50.096
2025-03-10 | 23:36 | 50.098
2025-03-10 | 23:36 | 50.099
2025-03-10 | 23:36 | 50.098
2025-03-10 | 23:36 | 50.097
2025-03-10 | 23:36 | 50.096
2025-03-10 | 23:36 | 50.096
2025-03-10 | 23:36 | 50.097
2025-03-10 | 23:36 | 50.099
2025-03-10 | 23:36 | 50.101
2025-03-10 | 23:36 | 50.102
2025-03-10 | 23:36 | 50.1
2025-03-10 | 23:36 | 50.099
2025-03-10 | 23:36 | 50.099
2025-03-10 | 23:36 | 50.103
2025-03-10 | 23:36 | 50.104
2025-03-10 | 23:36 | 50.103
2025-03-10 | 23:36 | 50.101
2025-03-10 | 23:36 | 50.101
2025-03-10 | 23:36 | 50.1
2025-03-10 | 23:36 | 50.103
2025-03-10 | 23:36 | 50.101
2025-03-10 | 23:36 | 50.1
2025-03-10 | 23:36 | 50.098
2025-03-10 | 23:36 | 50.096
2025-03-10 | 23:36 | 50.096
2025-03-10 | 23:36 | 50.096
2025-03-10 | 23:36 | 50.096
2025-03-10 | 23:36 | 50.097
2025-03-10 | 23:36 | 50.098
2025-03-10 | 23:36 | 50.1
2025-03-10 | 23:36 | 50.101
2025-03-10 | 23:36 | 50.101
2025-03-10 | 23:36 | 50.1
2025-03-10 | 23:36 | 50.097
2025-03-10 | 23:37 | 50.096
2025-03-10 | 23:37 | 50.095
2025-03-10 | 23:37 | 50.099
2025-03-10 | 23:37 | 50.102
2025-03-10 | 23:37 | 50.103
2025-03-10 | 23:37 | 50.102
2025-03-10 | 23:37 | 50.1
2025-03-10 | 23:37 | 50.099
2025-03-10 | 23:37 | 50.099
2025-03-10 | 23:37 | 50.099
2025-03-10 | 23:37 | 50.099
2025-03-10 | 23:37 | 50.099
2025-03-10 | 23:37 | 50.1
2025-03-10 | 23:37 | 50.101
2025-03-10 | 23:37 | 50.1
2025-03-10 | 23:37 | 50.1
2025-03-10 | 23:37 | 50.099
2025-03-10 | 23:37 | 50.099
2025-03-10 | 23:37 | 50.098
2025-03-10 | 23:37 | 50.1
2025-03-10 | 23:37 | 50.1
2025-03-10 | 23:37 | 50.099
2025-03-10 | 23:37 | 50.098
2025-03-10 | 23:37 | 50.096
2025-03-10 | 23:37 | 50.092
2025-03-10 | 23:37 | 50.091
2025-03-10 | 23:37 | 50.089
2025-03-10 | 23:37 | 50.087
2025-03-10 | 23:37 | 50.084
2025-03-10 | 23:37 | 50.084
2025-03-10 | 23:37 | 50.085
2025-03-10 | 23:37 | 50.086
2025-03-10 | 23:37 | 50.086
2025-03-10 | 23:37 | 50.084
2025-03-10 | 23:37 | 50.085
2025-03-10 | 23:37 | 50.084
2025-03-10 | 23:37 | 50.082
2025-03-10 | 23:37 | 50.083
2025-03-10 | 23:37 | 50.085
2025-03-10 | 23:37 | 50.085
2025-03-10 | 23:37 | 50.087
2025-03-10 | 23:37 | 50.09
2025-03-10 | 23:37 | 50.091
2025-03-10 | 23:37 | 50.092
2025-03-10 | 23:37 | 50.092
2025-03-10 | 23:37 | 50.093
2025-03-10 | 23:37 | 50.093
2025-03-10 | 23:37 | 50.091
2025-03-10 | 23:37 | 50.089
2025-03-10 | 23:37 | 50.089
2025-03-10 | 23:37 | 50.091
2025-03-10 | 23:37 | 50.093
2025-03-10 | 23:37 | 50.096
2025-03-10 | 23:37 | 50.096
2025-03-10 | 23:37 | 50.096
2025-03-10 | 23:37 | 50.095
2025-03-10 | 23:37 | 50.095
2025-03-10 | 23:37 | 50.097
2025-03-10 | 23:37 | 50.097
2025-03-10 | 23:38 | 50.101
2025-03-10 | 23:38 | 50.101
2025-03-10 | 23:38 | 50.102
2025-03-10 | 23:38 | 50.102
2025-03-10 | 23:38 | 50.102
2025-03-10 | 23:38 | 50.101
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.108
2025-03-10 | 23:38 | 50.112
2025-03-10 | 23:38 | 50.112
2025-03-10 | 23:38 | 50.112
2025-03-10 | 23:38 | 50.11
2025-03-10 | 23:38 | 50.108
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.105
2025-03-10 | 23:38 | 50.107
2025-03-10 | 23:38 | 50.107
2025-03-10 | 23:38 | 50.107
2025-03-10 | 23:38 | 50.106
2025-03-10 | 23:38 | 50.105
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.102
2025-03-10 | 23:38 | 50.102
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.102
2025-03-10 | 23:38 | 50.101
2025-03-10 | 23:38 | 50.1
2025-03-10 | 23:38 | 50.102
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.105
2025-03-10 | 23:38 | 50.106
2025-03-10 | 23:38 | 50.106
2025-03-10 | 23:38 | 50.106
2025-03-10 | 23:38 | 50.105
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.104
2025-03-10 | 23:38 | 50.105
2025-03-10 | 23:38 | 50.105
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.1
2025-03-10 | 23:38 | 50.101
2025-03-10 | 23:38 | 50.102
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.103
2025-03-10 | 23:38 | 50.105
2025-03-10 | 23:38 | 50.105
2025-03-10 | 23:38 | 50.107
2025-03-10 | 23:38 | 50.109
2025-03-10 | 23:39 | 50.109
2025-03-10 | 23:39 | 50.109
2025-03-10 | 23:39 | 50.11
2025-03-10 | 23:39 | 50.11
2025-03-10 | 23:39 | 50.111
2025-03-10 | 23:39 | 50.11
2025-03-10 | 23:39 | 50.109
2025-03-10 | 23:39 | 50.108
2025-03-10 | 23:39 | 50.107
2025-03-10 | 23:39 | 50.107
2025-03-10 | 23:39 | 50.107
2025-03-10 | 23:39 | 50.108
2025-03-10 | 23:39 | 50.109
2025-03-10 | 23:39 | 50.109
2025-03-10 | 23:39 | 50.11
2025-03-10 | 23:39 | 50.11
2025-03-10 | 23:39 | 50.11
2025-03-10 | 23:39 | 50.109
2025-03-10 | 23:39 | 50.11
2025-03-10 | 23:39 | 50.112
2025-03-10 | 23:39 | 50.113
2025-03-10 | 23:39 | 50.114
2025-03-10 | 23:39 | 50.114
2025-03-10 | 23:39 | 50.114
2025-03-10 | 23:39 | 50.115
2025-03-10 | 23:39 | 50.117
2025-03-10 | 23:39 | 50.116
2025-03-10 | 23:39 | 50.116
2025-03-10 | 23:39 | 50.116
2025-03-10 | 23:39 | 50.112
2025-03-10 | 23:39 | 50.111
2025-03-10 | 23:39 | 50.112
2025-03-10 | 23:39 | 50.114
2025-03-10 | 23:39 | 50.111
2025-03-10 | 23:39 | 50.112
2025-03-10 | 23:39 | 50.111
2025-03-10 | 23:39 | 50.109
2025-03-10 | 23:39 | 50.107
2025-03-10 | 23:39 | 50.102
2025-03-10 | 23:39 | 50.097
2025-03-10 | 23:39 | 50.095
2025-03-10 | 23:39 | 50.095
2025-03-10 | 23:39 | 50.096
2025-03-10 | 23:39 | 50.098
2025-03-10 | 23:39 | 50.1
2025-03-10 | 23:39 | 50.103
2025-03-10 | 23:39 | 50.104
2025-03-10 | 23:39 | 50.105
2025-03-10 | 23:39 | 50.105
2025-03-10 | 23:39 | 50.105
2025-03-10 | 23:39 | 50.107
2025-03-10 | 23:39 | 50.107
2025-03-10 | 23:39 | 50.106
2025-03-10 | 23:39 | 50.105
2025-03-10 | 23:39 | 50.104
2025-03-10 | 23:39 | 50.105
2025-03-10 | 23:39 | 50.103
2025-03-10 | 23:39 | 50.104
2025-03-10 | 23:39 | 50.107
2025-03-10 | 23:40 | 50.107
2025-03-10 | 23:40 | 50.104
2025-03-10 | 23:40 | 50.103
2025-03-10 | 23:40 | 50.103
2025-03-10 | 23:40 | 50.106
2025-03-10 | 23:40 | 50.108
2025-03-10 | 23:40 | 50.109
2025-03-10 | 23:40 | 50.109
2025-03-10 | 23:40 | 50.111
2025-03-10 | 23:40 | 50.112
2025-03-10 | 23:40 | 50.111
2025-03-10 | 23:40 | 50.111
2025-03-10 | 23:40 | 50.114
2025-03-10 | 23:40 | 50.113
2025-03-10 | 23:40 | 50.113
2025-03-10 | 23:40 | 50.114
2025-03-10 | 23:40 | 50.115
2025-03-10 | 23:40 | 50.116
2025-03-10 | 23:40 | 50.116
2025-03-10 | 23:40 | 50.115
2025-03-10 | 23:40 | 50.114
2025-03-10 | 23:40 | 50.113
2025-03-10 | 23:40 | 50.113
2025-03-10 | 23:40 | 50.113
2025-03-10 | 23:40 | 50.112
2025-03-10 | 23:40 | 50.113
2025-03-10 | 23:40 | 50.113
2025-03-10 | 23:40 | 50.111
2025-03-10 | 23:40 | 50.11
2025-03-10 | 23:40 | 50.109
2025-03-10 | 23:40 | 50.107
2025-03-10 | 23:40 | 50.104
2025-03-10 | 23:40 | 50.104
2025-03-10 | 23:40 | 50.107
2025-03-10 | 23:40 | 50.11
2025-03-10 | 23:40 | 50.112
2025-03-10 | 23:40 | 50.111
2025-03-10 | 23:40 | 50.109
2025-03-10 | 23:40 | 50.109
2025-03-10 | 23:40 | 50.11
2025-03-10 | 23:40 | 50.112
2025-03-10 | 23:40 | 50.111
2025-03-10 | 23:40 | 50.112
2025-03-10 | 23:40 | 50.112
2025-03-10 | 23:40 | 50.113
2025-03-10 | 23:40 | 50.114
2025-03-10 | 23:40 | 50.117
2025-03-10 | 23:40 | 50.117
2025-03-10 | 23:40 | 50.118
2025-03-10 | 23:40 | 50.119
2025-03-10 | 23:40 | 50.12
2025-03-10 | 23:40 | 50.121
2025-03-10 | 23:40 | 50.118
2025-03-10 | 23:40 | 50.116
2025-03-10 | 23:40 | 50.116
2025-03-10 | 23:40 | 50.115
2025-03-10 | 23:40 | 50.117
2025-03-10 | 23:40 | 50.117
2025-03-10 | 23:40 | 50.117
2025-03-10 | 23:40 | 50.118
2025-03-10 | 23:40 | 50.12
2025-03-10 | 23:41 | 50.119
2025-03-10 | 23:41 | 50.117
2025-03-10 | 23:41 | 50.114
2025-03-10 | 23:41 | 50.114
2025-03-10 | 23:41 | 50.111
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.109
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.109
2025-03-10 | 23:41 | 50.111
2025-03-10 | 23:41 | 50.112
2025-03-10 | 23:41 | 50.114
2025-03-10 | 23:41 | 50.115
2025-03-10 | 23:41 | 50.116
2025-03-10 | 23:41 | 50.114
2025-03-10 | 23:41 | 50.113
2025-03-10 | 23:41 | 50.112
2025-03-10 | 23:41 | 50.111
2025-03-10 | 23:41 | 50.111
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.109
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.109
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.112
2025-03-10 | 23:41 | 50.113
2025-03-10 | 23:41 | 50.112
2025-03-10 | 23:41 | 50.112
2025-03-10 | 23:41 | 50.111
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.109
2025-03-10 | 23:41 | 50.107
2025-03-10 | 23:41 | 50.107
2025-03-10 | 23:41 | 50.107
2025-03-10 | 23:41 | 50.105
2025-03-10 | 23:41 | 50.105
2025-03-10 | 23:41 | 50.107
2025-03-10 | 23:41 | 50.108
2025-03-10 | 23:41 | 50.109
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.113
2025-03-10 | 23:41 | 50.114
2025-03-10 | 23:41 | 50.112
2025-03-10 | 23:41 | 50.112
2025-03-10 | 23:41 | 50.11
2025-03-10 | 23:41 | 50.112
2025-03-10 | 23:41 | 50.114
2025-03-10 | 23:41 | 50.115
2025-03-10 | 23:41 | 50.115
2025-03-10 | 23:41 | 50.116
2025-03-10 | 23:41 | 50.117
2025-03-10 | 23:41 | 50.117
2025-03-10 | 23:41 | 50.119
2025-03-10 | 23:41 | 50.118
2025-03-10 | 23:41 | 50.119
2025-03-10 | 23:41 | 50.119
2025-03-10 | 23:42 | 50.118
2025-03-10 | 23:42 | 50.117
2025-03-10 | 23:42 | 50.117
2025-03-10 | 23:42 | 50.117
2025-03-10 | 23:42 | 50.117
2025-03-10 | 23:42 | 50.118
2025-03-10 | 23:42 | 50.118
2025-03-10 | 23:42 | 50.118
2025-03-10 | 23:42 | 50.118
2025-03-10 | 23:42 | 50.117
2025-03-10 | 23:42 | 50.117
2025-03-10 | 23:42 | 50.118
2025-03-10 | 23:42 | 50.117
2025-03-10 | 23:42 | 50.116
2025-03-10 | 23:42 | 50.117
2025-03-10 | 23:42 | 50.118
2025-03-10 | 23:42 | 50.117
2025-03-10 | 23:42 | 50.117
2025-03-10 | 23:42 | 50.116
2025-03-10 | 23:42 | 50.116
2025-03-10 | 23:42 | 50.114
2025-03-10 | 23:42 | 50.115
2025-03-10 | 23:42 | 50.113
2025-03-10 | 23:42 | 50.112
2025-03-10 | 23:42 | 50.113
2025-03-10 | 23:42 | 50.114
2025-03-10 | 23:42 | 50.115
2025-03-10 | 23:42 | 50.115
2025-03-10 | 23:42 | 50.114
2025-03-10 | 23:42 | 50.114
2025-03-10 | 23:42 | 50.114
2025-03-10 | 23:42 | 50.112
2025-03-10 | 23:42 | 50.111
2025-03-10 | 23:42 | 50.112
2025-03-10 | 23:42 | 50.112
2025-03-10 | 23:42 | 50.111
2025-03-10 | 23:42 | 50.112
2025-03-10 | 23:42 | 50.111
2025-03-10 | 23:42 | 50.111
2025-03-10 | 23:42 | 50.112
2025-03-10 | 23:42 | 50.109
2025-03-10 | 23:42 | 50.108
2025-03-10 | 23:42 | 50.107
2025-03-10 | 23:42 | 50.108
2025-03-10 | 23:42 | 50.108
2025-03-10 | 23:42 | 50.107
2025-03-10 | 23:42 | 50.108
2025-03-10 | 23:42 | 50.108
2025-03-10 | 23:42 | 50.109
2025-03-10 | 23:42 | 50.107
2025-03-10 | 23:42 | 50.107
2025-03-10 | 23:42 | 50.108
2025-03-10 | 23:42 | 50.108
2025-03-10 | 23:42 | 50.107
2025-03-10 | 23:42 | 50.106
2025-03-10 | 23:42 | 50.106
2025-03-10 | 23:42 | 50.107
2025-03-10 | 23:42 | 50.108
2025-03-10 | 23:42 | 50.108
2025-03-10 | 23:42 | 50.107
2025-03-10 | 23:42 | 50.108
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:43 | 50.108
2025-03-10 | 23:43 | 50.109
2025-03-10 | 23:43 | 50.11
2025-03-10 | 23:43 | 50.109
2025-03-10 | 23:43 | 50.108
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:43 | 50.109
2025-03-10 | 23:43 | 50.11
2025-03-10 | 23:43 | 50.11
2025-03-10 | 23:43 | 50.11
2025-03-10 | 23:43 | 50.109
2025-03-10 | 23:43 | 50.109
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:43 | 50.106
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:43 | 50.108
2025-03-10 | 23:43 | 50.106
2025-03-10 | 23:43 | 50.104
2025-03-10 | 23:43 | 50.104
2025-03-10 | 23:43 | 50.105
2025-03-10 | 23:43 | 50.103
2025-03-10 | 23:43 | 50.101
2025-03-10 | 23:43 | 50.102
2025-03-10 | 23:43 | 50.102
2025-03-10 | 23:43 | 50.105
2025-03-10 | 23:43 | 50.106
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:43 | 50.106
2025-03-10 | 23:43 | 50.105
2025-03-10 | 23:43 | 50.103
2025-03-10 | 23:43 | 50.102
2025-03-10 | 23:43 | 50.101
2025-03-10 | 23:43 | 50.102
2025-03-10 | 23:43 | 50.102
2025-03-10 | 23:43 | 50.101
2025-03-10 | 23:43 | 50.101
2025-03-10 | 23:43 | 50.1
2025-03-10 | 23:43 | 50.098
2025-03-10 | 23:43 | 50.1
2025-03-10 | 23:43 | 50.1
2025-03-10 | 23:43 | 50.1
2025-03-10 | 23:43 | 50.098
2025-03-10 | 23:43 | 50.1
2025-03-10 | 23:43 | 50.1
2025-03-10 | 23:43 | 50.103
2025-03-10 | 23:43 | 50.105
2025-03-10 | 23:43 | 50.106
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:43 | 50.105
2025-03-10 | 23:43 | 50.106
2025-03-10 | 23:43 | 50.105
2025-03-10 | 23:43 | 50.105
2025-03-10 | 23:43 | 50.105
2025-03-10 | 23:43 | 50.107
2025-03-10 | 23:44 | 50.107
2025-03-10 | 23:44 | 50.107
2025-03-10 | 23:44 | 50.107
2025-03-10 | 23:44 | 50.105
2025-03-10 | 23:44 | 50.103
2025-03-10 | 23:44 | 50.1
2025-03-10 | 23:44 | 50.101
2025-03-10 | 23:44 | 50.103
2025-03-10 | 23:44 | 50.098
2025-03-10 | 23:44 | 50.099
2025-03-10 | 23:44 | 50.101
2025-03-10 | 23:44 | 50.101
2025-03-10 | 23:44 | 50.102
2025-03-10 | 23:44 | 50.101
2025-03-10 | 23:44 | 50.099
2025-03-10 | 23:44 | 50.096
2025-03-10 | 23:44 | 50.094
2025-03-10 | 23:44 | 50.09
2025-03-10 | 23:44 | 50.089
2025-03-10 | 23:44 | 50.091
2025-03-10 | 23:44 | 50.09
2025-03-10 | 23:44 | 50.087
2025-03-10 | 23:44 | 50.088
2025-03-10 | 23:44 | 50.087
2025-03-10 | 23:44 | 50.084
2025-03-10 | 23:44 | 50.084
2025-03-10 | 23:44 | 50.088
2025-03-10 | 23:44 | 50.088
2025-03-10 | 23:44 | 50.087
2025-03-10 | 23:44 | 50.087
2025-03-10 | 23:44 | 50.087
2025-03-10 | 23:44 | 50.088
2025-03-10 | 23:44 | 50.091
2025-03-10 | 23:44 | 50.092
2025-03-10 | 23:44 | 50.095
2025-03-10 | 23:44 | 50.096
2025-03-10 | 23:44 | 50.096
2025-03-10 | 23:44 | 50.099
2025-03-10 | 23:44 | 50.1
2025-03-10 | 23:44 | 50.102
2025-03-10 | 23:44 | 50.102
2025-03-10 | 23:44 | 50.1
2025-03-10 | 23:44 | 50.099
2025-03-10 | 23:44 | 50.099
2025-03-10 | 23:44 | 50.098
2025-03-10 | 23:44 | 50.099
2025-03-10 | 23:44 | 50.1
2025-03-10 | 23:44 | 50.101
2025-03-10 | 23:44 | 50.103
2025-03-10 | 23:44 | 50.105
2025-03-10 | 23:44 | 50.106
2025-03-10 | 23:44 | 50.105
2025-03-10 | 23:44 | 50.103
2025-03-10 | 23:44 | 50.104
2025-03-10 | 23:44 | 50.104
2025-03-10 | 23:44 | 50.102
2025-03-10 | 23:44 | 50.104
2025-03-10 | 23:44 | 50.107
2025-03-10 | 23:44 | 50.105
2025-03-10 | 23:44 | 50.104
2025-03-10 | 23:44 | 50.106
2025-03-10 | 23:45 | 50.107
2025-03-10 | 23:45 | 50.107
2025-03-10 | 23:45 | 50.104
2025-03-10 | 23:45 | 50.105
2025-03-10 | 23:45 | 50.106
2025-03-10 | 23:45 | 50.103
2025-03-10 | 23:45 | 50.101
2025-03-10 | 23:45 | 50.103
2025-03-10 | 23:45 | 50.103
2025-03-10 | 23:45 | 50.1
2025-03-10 | 23:45 | 50.099
2025-03-10 | 23:45 | 50.095
2025-03-10 | 23:45 | 50.092
2025-03-10 | 23:45 | 50.088
2025-03-10 | 23:45 | 50.091
2025-03-10 | 23:45 | 50.091
2025-03-10 | 23:45 | 50.09
2025-03-10 | 23:45 | 50.09
2025-03-10 | 23:45 | 50.091
2025-03-10 | 23:45 | 50.09
2025-03-10 | 23:45 | 50.087
2025-03-10 | 23:45 | 50.084
2025-03-10 | 23:45 | 50.087
2025-03-10 | 23:45 | 50.089
2025-03-10 | 23:45 | 50.091
2025-03-10 | 23:45 | 50.088
2025-03-10 | 23:45 | 50.087
2025-03-10 | 23:45 | 50.085
2025-03-10 | 23:45 | 50.086
2025-03-10 | 23:45 | 50.087
2025-03-10 | 23:45 | 50.084
2025-03-10 | 23:45 | 50.08
2025-03-10 | 23:45 | 50.078
2025-03-10 | 23:45 | 50.08
2025-03-10 | 23:45 | 50.085
2025-03-10 | 23:45 | 50.087
2025-03-10 | 23:45 | 50.088
2025-03-10 | 23:45 | 50.086
2025-03-10 | 23:45 | 50.082
2025-03-10 | 23:45 | 50.08
2025-03-10 | 23:45 | 50.082
2025-03-10 | 23:45 | 50.086
2025-03-10 | 23:45 | 50.086
2025-03-10 | 23:45 | 50.086
2025-03-10 | 23:45 | 50.085
2025-03-10 | 23:45 | 50.086
2025-03-10 | 23:45 | 50.085
2025-03-10 | 23:45 | 50.085
2025-03-10 | 23:45 | 50.087
2025-03-10 | 23:45 | 50.088
2025-03-10 | 23:45 | 50.09
2025-03-10 | 23:45 | 50.095
2025-03-10 | 23:45 | 50.099
2025-03-10 | 23:45 | 50.095
2025-03-10 | 23:45 | 50.088
2025-03-10 | 23:45 | 50.086
2025-03-10 | 23:45 | 50.087
2025-03-10 | 23:45 | 50.088
2025-03-10 | 23:45 | 50.09
2025-03-10 | 23:46 | 50.091
2025-03-10 | 23:46 | 50.091
2025-03-10 | 23:46 | 50.088
2025-03-10 | 23:46 | 50.088
2025-03-10 | 23:46 | 50.088
2025-03-10 | 23:46 | 50.088
2025-03-10 | 23:46 | 50.089
2025-03-10 | 23:46 | 50.089
2025-03-10 | 23:46 | 50.087
2025-03-10 | 23:46 | 50.088
2025-03-10 | 23:46 | 50.088
2025-03-10 | 23:46 | 50.09
2025-03-10 | 23:46 | 50.089
2025-03-10 | 23:46 | 50.087
2025-03-10 | 23:46 | 50.084
2025-03-10 | 23:46 | 50.083
2025-03-10 | 23:46 | 50.081
2025-03-10 | 23:46 | 50.081
2025-03-10 | 23:46 | 50.08
2025-03-10 | 23:46 | 50.076
2025-03-10 | 23:46 | 50.073
2025-03-10 | 23:46 | 50.073
2025-03-10 | 23:46 | 50.073
2025-03-10 | 23:46 | 50.072
2025-03-10 | 23:46 | 50.069
2025-03-10 | 23:46 | 50.068
2025-03-10 | 23:46 | 50.066
2025-03-10 | 23:46 | 50.07
2025-03-10 | 23:46 | 50.072
2025-03-10 | 23:46 | 50.071
2025-03-10 | 23:46 | 50.069
2025-03-10 | 23:46 | 50.067
2025-03-10 | 23:46 | 50.066
2025-03-10 | 23:46 | 50.068
2025-03-10 | 23:46 | 50.071
2025-03-10 | 23:46 | 50.071
2025-03-10 | 23:46 | 50.071
2025-03-10 | 23:46 | 50.071
2025-03-10 | 23:46 | 50.067
2025-03-10 | 23:46 | 50.069
2025-03-10 | 23:46 | 50.07
2025-03-10 | 23:46 | 50.074
2025-03-10 | 23:46 | 50.078
2025-03-10 | 23:46 | 50.082
2025-03-10 | 23:46 | 50.083
2025-03-10 | 23:46 | 50.083
2025-03-10 | 23:46 | 50.082
2025-03-10 | 23:46 | 50.077
2025-03-10 | 23:46 | 50.072
2025-03-10 | 23:46 | 50.068
2025-03-10 | 23:46 | 50.07
2025-03-10 | 23:46 | 50.073
2025-03-10 | 23:46 | 50.073
2025-03-10 | 23:46 | 50.074
2025-03-10 | 23:46 | 50.072
2025-03-10 | 23:46 | 50.072
2025-03-10 | 23:46 | 50.069
2025-03-10 | 23:46 | 50.066
2025-03-10 | 23:46 | 50.066
2025-03-10 | 23:46 | 50.067
2025-03-10 | 23:46 | 50.068
2025-03-10 | 23:47 | 50.071
2025-03-10 | 23:47 | 50.077
2025-03-10 | 23:47 | 50.079
2025-03-10 | 23:47 | 50.078
2025-03-10 | 23:47 | 50.076
2025-03-10 | 23:47 | 50.078
2025-03-10 | 23:47 | 50.079
2025-03-10 | 23:47 | 50.078
2025-03-10 | 23:47 | 50.076
2025-03-10 | 23:47 | 50.076
2025-03-10 | 23:47 | 50.075
2025-03-10 | 23:47 | 50.073
2025-03-10 | 23:47 | 50.073
2025-03-10 | 23:47 | 50.073
2025-03-10 | 23:47 | 50.073
2025-03-10 | 23:47 | 50.075
2025-03-10 | 23:47 | 50.073
2025-03-10 | 23:47 | 50.07
2025-03-10 | 23:47 | 50.067
2025-03-10 | 23:47 | 50.066
2025-03-10 | 23:47 | 50.064
2025-03-10 | 23:47 | 50.064
2025-03-10 | 23:47 | 50.064
2025-03-10 | 23:47 | 50.067
2025-03-10 | 23:47 | 50.069
2025-03-10 | 23:47 | 50.07
2025-03-10 | 23:47 | 50.073
2025-03-10 | 23:47 | 50.074
2025-03-10 | 23:47 | 50.077
2025-03-10 | 23:47 | 50.081
2025-03-10 | 23:47 | 50.083
2025-03-10 | 23:47 | 50.085
2025-03-10 | 23:47 | 50.084
2025-03-10 | 23:47 | 50.08
2025-03-10 | 23:47 | 50.077
2025-03-10 | 23:47 | 50.072
2025-03-10 | 23:47 | 50.07
2025-03-10 | 23:47 | 50.068
2025-03-10 | 23:47 | 50.069
2025-03-10 | 23:47 | 50.067
2025-03-10 | 23:47 | 50.066
2025-03-10 | 23:47 | 50.066
2025-03-10 | 23:47 | 50.066
2025-03-10 | 23:47 | 50.067
2025-03-10 | 23:47 | 50.065
2025-03-10 | 23:47 | 50.067
2025-03-10 | 23:47 | 50.068
2025-03-10 | 23:47 | 50.068
2025-03-10 | 23:47 | 50.069
2025-03-10 | 23:47 | 50.071
2025-03-10 | 23:47 | 50.071
2025-03-10 | 23:47 | 50.073
2025-03-10 | 23:47 | 50.071
2025-03-10 | 23:47 | 50.07
2025-03-10 | 23:47 | 50.069
2025-03-10 | 23:47 | 50.068
2025-03-10 | 23:47 | 50.067
2025-03-10 | 23:47 | 50.068
2025-03-10 | 23:47 | 50.072
2025-03-10 | 23:48 | 50.073
2025-03-10 | 23:48 | 50.071
2025-03-10 | 23:48 | 50.067
2025-03-10 | 23:48 | 50.065
2025-03-10 | 23:48 | 50.059
2025-03-10 | 23:48 | 50.054
2025-03-10 | 23:48 | 50.054
2025-03-10 | 23:48 | 50.054
2025-03-10 | 23:48 | 50.054
2025-03-10 | 23:48 | 50.054
2025-03-10 | 23:48 | 50.055
2025-03-10 | 23:48 | 50.057
2025-03-10 | 23:48 | 50.057
2025-03-10 | 23:48 | 50.056
2025-03-10 | 23:48 | 50.055
2025-03-10 | 23:48 | 50.056
2025-03-10 | 23:48 | 50.052
2025-03-10 | 23:48 | 50.047
2025-03-10 | 23:48 | 50.047
2025-03-10 | 23:48 | 50.049
2025-03-10 | 23:48 | 50.046
2025-03-10 | 23:48 | 50.045
2025-03-10 | 23:48 | 50.045
2025-03-10 | 23:48 | 50.048
2025-03-10 | 23:48 | 50.049
2025-03-10 | 23:48 | 50.05
2025-03-10 | 23:48 | 50.048
2025-03-10 | 23:48 | 50.046
2025-03-10 | 23:48 | 50.046
2025-03-10 | 23:48 | 50.046
2025-03-10 | 23:48 | 50.045
2025-03-10 | 23:48 | 50.044
2025-03-10 | 23:48 | 50.044
2025-03-10 | 23:48 | 50.042
2025-03-10 | 23:48 | 50.042
2025-03-10 | 23:48 | 50.043
2025-03-10 | 23:48 | 50.043
2025-03-10 | 23:48 | 50.041
2025-03-10 | 23:48 | 50.042
2025-03-10 | 23:48 | 50.042
2025-03-10 | 23:48 | 50.042
2025-03-10 | 23:48 | 50.042
2025-03-10 | 23:48 | 50.044
2025-03-10 | 23:48 | 50.044
2025-03-10 | 23:48 | 50.046
2025-03-10 | 23:48 | 50.046
2025-03-10 | 23:48 | 50.045
2025-03-10 | 23:48 | 50.045
2025-03-10 | 23:48 | 50.044
2025-03-10 | 23:48 | 50.042
2025-03-10 | 23:48 | 50.04
2025-03-10 | 23:48 | 50.041
2025-03-10 | 23:48 | 50.041
2025-03-10 | 23:48 | 50.039
2025-03-10 | 23:48 | 50.04
2025-03-10 | 23:48 | 50.045
2025-03-10 | 23:48 | 50.049
2025-03-10 | 23:48 | 50.052
2025-03-10 | 23:48 | 50.051
2025-03-10 | 23:48 | 50.053
2025-03-10 | 23:48 | 50.049
2025-03-10 | 23:49 | 50.049
2025-03-10 | 23:49 | 50.048
2025-03-10 | 23:49 | 50.048
2025-03-10 | 23:49 | 50.047
2025-03-10 | 23:49 | 50.048
2025-03-10 | 23:49 | 50.048
2025-03-10 | 23:49 | 50.049
2025-03-10 | 23:49 | 50.049
2025-03-10 | 23:49 | 50.047
2025-03-10 | 23:49 | 50.046
2025-03-10 | 23:49 | 50.049
2025-03-10 | 23:49 | 50.051
2025-03-10 | 23:49 | 50.053
2025-03-10 | 23:49 | 50.056
2025-03-10 | 23:49 | 50.059
2025-03-10 | 23:49 | 50.057
2025-03-10 | 23:49 | 50.055
2025-03-10 | 23:49 | 50.053
2025-03-10 | 23:49 | 50.053
2025-03-10 | 23:49 | 50.054
2025-03-10 | 23:49 | 50.051
2025-03-10 | 23:49 | 50.05
2025-03-10 | 23:49 | 50.049
2025-03-10 | 23:49 | 50.048
2025-03-10 | 23:49 | 50.049
2025-03-10 | 23:49 | 50.051
2025-03-10 | 23:49 | 50.052
2025-03-10 | 23:49 | 50.055
2025-03-10 | 23:49 | 50.053
2025-03-10 | 23:49 | 50.056
2025-03-10 | 23:49 | 50.056
2025-03-10 | 23:49 | 50.055
2025-03-10 | 23:49 | 50.056
2025-03-10 | 23:49 | 50.056
2025-03-10 | 23:49 | 50.058
2025-03-10 | 23:49 | 50.059
2025-03-10 | 23:49 | 50.059
2025-03-10 | 23:49 | 50.058
2025-03-10 | 23:49 | 50.056
2025-03-10 | 23:49 | 50.055
2025-03-10 | 23:49 | 50.056
2025-03-10 | 23:49 | 50.056
2025-03-10 | 23:49 | 50.057
2025-03-10 | 23:49 | 50.055
2025-03-10 | 23:49 | 50.054
2025-03-10 | 23:49 | 50.054
2025-03-10 | 23:49 | 50.058
2025-03-10 | 23:49 | 50.059
2025-03-10 | 23:49 | 50.059
2025-03-10 | 23:49 | 50.059
2025-03-10 | 23:49 | 50.059
2025-03-10 | 23:49 | 50.058
2025-03-10 | 23:49 | 50.057
2025-03-10 | 23:49 | 50.061
2025-03-10 | 23:49 | 50.065
2025-03-10 | 23:49 | 50.064
2025-03-10 | 23:49 | 50.059
2025-03-10 | 23:49 | 50.053
2025-03-10 | 23:49 | 50.052
2025-03-10 | 23:50 | 50.052
2025-03-10 | 23:50 | 50.052
2025-03-10 | 23:50 | 50.052
2025-03-10 | 23:50 | 50.054
2025-03-10 | 23:50 | 50.057
2025-03-10 | 23:50 | 50.061
2025-03-10 | 23:50 | 50.06
2025-03-10 | 23:50 | 50.061
2025-03-10 | 23:50 | 50.061
2025-03-10 | 23:50 | 50.062
2025-03-10 | 23:50 | 50.06
2025-03-10 | 23:50 | 50.058
2025-03-10 | 23:50 | 50.056
2025-03-10 | 23:50 | 50.056
2025-03-10 | 23:50 | 50.057
2025-03-10 | 23:50 | 50.059
2025-03-10 | 23:50 | 50.061
2025-03-10 | 23:50 | 50.059
2025-03-10 | 23:50 | 50.058
2025-03-10 | 23:50 | 50.057
2025-03-10 | 23:50 | 50.054
2025-03-10 | 23:50 | 50.053
2025-03-10 | 23:50 | 50.05
2025-03-10 | 23:50 | 50.05
2025-03-10 | 23:50 | 50.048
2025-03-10 | 23:50 | 50.047
2025-03-10 | 23:50 | 50.048
2025-03-10 | 23:50 | 50.048
2025-03-10 | 23:50 | 50.049
2025-03-10 | 23:50 | 50.049
2025-03-10 | 23:50 | 50.045
2025-03-10 | 23:50 | 50.04
2025-03-10 | 23:50 | 50.038
2025-03-10 | 23:50 | 50.038
2025-03-10 | 23:50 | 50.042
2025-03-10 | 23:50 | 50.047
2025-03-10 | 23:50 | 50.052
2025-03-10 | 23:50 | 50.054
2025-03-10 | 23:50 | 50.053
2025-03-10 | 23:50 | 50.054
2025-03-10 | 23:50 | 50.054
2025-03-10 | 23:50 | 50.053
2025-03-10 | 23:50 | 50.052
2025-03-10 | 23:50 | 50.051
2025-03-10 | 23:50 | 50.05
2025-03-10 | 23:50 | 50.051
2025-03-10 | 23:50 | 50.053
2025-03-10 | 23:50 | 50.054
2025-03-10 | 23:50 | 50.056
2025-03-10 | 23:50 | 50.056
2025-03-10 | 23:50 | 50.054
2025-03-10 | 23:50 | 50.049
2025-03-10 | 23:50 | 50.047
2025-03-10 | 23:50 | 50.046
2025-03-10 | 23:50 | 50.048
2025-03-10 | 23:50 | 50.047
2025-03-10 | 23:50 | 50.049
2025-03-10 | 23:50 | 50.05
2025-03-10 | 23:50 | 50.051
2025-03-10 | 23:50 | 50.052
2025-03-10 | 23:50 | 50.051
2025-03-10 | 23:51 | 50.051
2025-03-10 | 23:51 | 50.051
2025-03-10 | 23:51 | 50.052
2025-03-10 | 23:51 | 50.053
2025-03-10 | 23:51 | 50.053
2025-03-10 | 23:51 | 50.055
2025-03-10 | 23:51 | 50.057
2025-03-10 | 23:51 | 50.055
2025-03-10 | 23:51 | 50.056
2025-03-10 | 23:51 | 50.058
2025-03-10 | 23:51 | 50.059
2025-03-10 | 23:51 | 50.057
2025-03-10 | 23:51 | 50.056
2025-03-10 | 23:51 | 50.055
2025-03-10 | 23:51 | 50.056
2025-03-10 | 23:51 | 50.055
2025-03-10 | 23:51 | 50.051
2025-03-10 | 23:51 | 50.051
2025-03-10 | 23:51 | 50.054
2025-03-10 | 23:51 | 50.054
2025-03-10 | 23:51 | 50.054
2025-03-10 | 23:51 | 50.053
2025-03-10 | 23:51 | 50.057
2025-03-10 | 23:51 | 50.061
2025-03-10 | 23:51 | 50.062
2025-03-10 | 23:51 | 50.061
2025-03-10 | 23:51 | 50.058
2025-03-10 | 23:51 | 50.058
2025-03-10 | 23:51 | 50.06
2025-03-10 | 23:51 | 50.062
2025-03-10 | 23:51 | 50.061
2025-03-10 | 23:51 | 50.062
2025-03-10 | 23:51 | 50.059
2025-03-10 | 23:51 | 50.057
2025-03-10 | 23:51 | 50.058
2025-03-10 | 23:51 | 50.06
2025-03-10 | 23:51 | 50.063
2025-03-10 | 23:51 | 50.063
2025-03-10 | 23:51 | 50.063
2025-03-10 | 23:51 | 50.064
2025-03-10 | 23:51 | 50.064
2025-03-10 | 23:51 | 50.062
2025-03-10 | 23:51 | 50.063
2025-03-10 | 23:51 | 50.063
2025-03-10 | 23:51 | 50.063
2025-03-10 | 23:51 | 50.064
2025-03-10 | 23:51 | 50.065
2025-03-10 | 23:51 | 50.064
2025-03-10 | 23:51 | 50.063
2025-03-10 | 23:51 | 50.063
2025-03-10 | 23:51 | 50.066
2025-03-10 | 23:51 | 50.067
2025-03-10 | 23:51 | 50.069
2025-03-10 | 23:51 | 50.067
2025-03-10 | 23:51 | 50.067
2025-03-10 | 23:51 | 50.069
2025-03-10 | 23:51 | 50.077
2025-03-10 | 23:51 | 50.079
2025-03-10 | 23:51 | 50.081
2025-03-10 | 23:52 | 50.077
2025-03-10 | 23:52 | 50.073
2025-03-10 | 23:52 | 50.072
2025-03-10 | 23:52 | 50.071
2025-03-10 | 23:52 | 50.071
2025-03-10 | 23:52 | 50.075
2025-03-10 | 23:52 | 50.077
2025-03-10 | 23:52 | 50.078
2025-03-10 | 23:52 | 50.077
2025-03-10 | 23:52 | 50.075
2025-03-10 | 23:52 | 50.073
2025-03-10 | 23:52 | 50.069
2025-03-10 | 23:52 | 50.07
2025-03-10 | 23:52 | 50.071
2025-03-10 | 23:52 | 50.072
2025-03-10 | 23:52 | 50.075
2025-03-10 | 23:52 | 50.073
2025-03-10 | 23:52 | 50.081
2025-03-10 | 23:52 | 50.093
2025-03-10 | 23:52 | 50.096
2025-03-10 | 23:52 | 50.095
2025-03-10 | 23:52 | 50.091
2025-03-10 | 23:52 | 50.083
2025-03-10 | 23:52 | 50.078
2025-03-10 | 23:52 | 50.073
2025-03-10 | 23:52 | 50.069
2025-03-10 | 23:52 | 50.065
2025-03-10 | 23:52 | 50.066
2025-03-10 | 23:52 | 50.067
2025-03-10 | 23:52 | 50.07
2025-03-10 | 23:52 | 50.07
2025-03-10 | 23:52 | 50.068
2025-03-10 | 23:52 | 50.067
2025-03-10 | 23:52 | 50.07
2025-03-10 | 23:52 | 50.073
2025-03-10 | 23:52 | 50.073
2025-03-10 | 23:52 | 50.073
2025-03-10 | 23:52 | 50.074
2025-03-10 | 23:52 | 50.074
2025-03-10 | 23:52 | 50.074
2025-03-10 | 23:52 | 50.075
2025-03-10 | 23:52 | 50.074
2025-03-10 | 23:52 | 50.071
2025-03-10 | 23:52 | 50.071
2025-03-10 | 23:52 | 50.073
2025-03-10 | 23:52 | 50.076
2025-03-10 | 23:52 | 50.076
2025-03-10 | 23:52 | 50.078
2025-03-10 | 23:52 | 50.079
2025-03-10 | 23:52 | 50.08
2025-03-10 | 23:52 | 50.081
2025-03-10 | 23:52 | 50.078
2025-03-10 | 23:52 | 50.075
2025-03-10 | 23:52 | 50.072
2025-03-10 | 23:52 | 50.072
2025-03-10 | 23:52 | 50.071
2025-03-10 | 23:52 | 50.069
2025-03-10 | 23:52 | 50.067
2025-03-10 | 23:52 | 50.067
2025-03-10 | 23:52 | 50.069
2025-03-10 | 23:52 | 50.07
2025-03-10 | 23:53 | 50.07
2025-03-10 | 23:53 | 50.069
2025-03-10 | 23:53 | 50.072
2025-03-10 | 23:53 | 50.075
2025-03-10 | 23:53 | 50.077
2025-03-10 | 23:53 | 50.077
2025-03-10 | 23:53 | 50.075
2025-03-10 | 23:53 | 50.073
2025-03-10 | 23:53 | 50.07
2025-03-10 | 23:53 | 50.07
2025-03-10 | 23:53 | 50.069
2025-03-10 | 23:53 | 50.069
2025-03-10 | 23:53 | 50.068
2025-03-10 | 23:53 | 50.068
2025-03-10 | 23:53 | 50.068
2025-03-10 | 23:53 | 50.065
2025-03-10 | 23:53 | 50.065
2025-03-10 | 23:53 | 50.066
2025-03-10 | 23:53 | 50.068
2025-03-10 | 23:53 | 50.069
2025-03-10 | 23:53 | 50.069
2025-03-10 | 23:53 | 50.068
2025-03-10 | 23:53 | 50.069
2025-03-10 | 23:53 | 50.07
2025-03-10 | 23:53 | 50.07
2025-03-10 | 23:53 | 50.07
2025-03-10 | 23:53 | 50.069
2025-03-10 | 23:53 | 50.068
2025-03-10 | 23:53 | 50.069
2025-03-10 | 23:53 | 50.068
2025-03-10 | 23:53 | 50.066
2025-03-10 | 23:53 | 50.066
2025-03-10 | 23:53 | 50.069
2025-03-10 | 23:53 | 50.072
2025-03-10 | 23:53 | 50.075
2025-03-10 | 23:53 | 50.075
2025-03-10 | 23:53 | 50.074
2025-03-10 | 23:53 | 50.076
2025-03-10 | 23:53 | 50.074
2025-03-10 | 23:53 | 50.073
2025-03-10 | 23:53 | 50.073
2025-03-10 | 23:53 | 50.074
2025-03-10 | 23:53 | 50.073
2025-03-10 | 23:53 | 50.074
2025-03-10 | 23:53 | 50.075
2025-03-10 | 23:53 | 50.076
2025-03-10 | 23:53 | 50.075
2025-03-10 | 23:53 | 50.073
2025-03-10 | 23:53 | 50.072
2025-03-10 | 23:53 | 50.068
2025-03-10 | 23:53 | 50.064
2025-03-10 | 23:53 | 50.064
2025-03-10 | 23:53 | 50.064
2025-03-10 | 23:53 | 50.067
2025-03-10 | 23:53 | 50.067
2025-03-10 | 23:53 | 50.066
2025-03-10 | 23:53 | 50.066
2025-03-10 | 23:53 | 50.066
2025-03-10 | 23:53 | 50.066
2025-03-10 | 23:54 | 50.066
2025-03-10 | 23:54 | 50.067
2025-03-10 | 23:54 | 50.067
2025-03-10 | 23:54 | 50.068
2025-03-10 | 23:54 | 50.072
2025-03-10 | 23:54 | 50.075
2025-03-10 | 23:54 | 50.076
2025-03-10 | 23:54 | 50.076
2025-03-10 | 23:54 | 50.075
2025-03-10 | 23:54 | 50.074
2025-03-10 | 23:54 | 50.074
2025-03-10 | 23:54 | 50.073
2025-03-10 | 23:54 | 50.073
2025-03-10 | 23:54 | 50.072
2025-03-10 | 23:54 | 50.071
2025-03-10 | 23:54 | 50.072
2025-03-10 | 23:54 | 50.072
2025-03-10 | 23:54 | 50.072
2025-03-10 | 23:54 | 50.072
2025-03-10 | 23:54 | 50.069
2025-03-10 | 23:54 | 50.065
2025-03-10 | 23:54 | 50.062
2025-03-10 | 23:54 | 50.062
2025-03-10 | 23:54 | 50.062
2025-03-10 | 23:54 | 50.06
2025-03-10 | 23:54 | 50.06
2025-03-10 | 23:54 | 50.059
2025-03-10 | 23:54 | 50.06
2025-03-10 | 23:54 | 50.06
2025-03-10 | 23:54 | 50.062
2025-03-10 | 23:54 | 50.061
2025-03-10 | 23:54 | 50.061
2025-03-10 | 23:54 | 50.06
2025-03-10 | 23:54 | 50.06
2025-03-10 | 23:54 | 50.06
2025-03-10 | 23:54 | 50.06
2025-03-10 | 23:54 | 50.062
2025-03-10 | 23:54 | 50.061
2025-03-10 | 23:54 | 50.059
2025-03-10 | 23:54 | 50.059
2025-03-10 | 23:54 | 50.058
2025-03-10 | 23:54 | 50.057
2025-03-10 | 23:54 | 50.056
2025-03-10 | 23:54 | 50.057
2025-03-10 | 23:54 | 50.057
2025-03-10 | 23:54 | 50.058
2025-03-10 | 23:54 | 50.058
2025-03-10 | 23:54 | 50.056
2025-03-10 | 23:54 | 50.057
2025-03-10 | 23:54 | 50.059
2025-03-10 | 23:54 | 50.061
2025-03-10 | 23:54 | 50.061
2025-03-10 | 23:54 | 50.06
2025-03-10 | 23:54 | 50.059
2025-03-10 | 23:54 | 50.057
2025-03-10 | 23:54 | 50.059
2025-03-10 | 23:54 | 50.06
2025-03-10 | 23:54 | 50.061
2025-03-10 | 23:54 | 50.059
2025-03-10 | 23:54 | 50.058
2025-03-10 | 23:54 | 50.057
2025-03-10 | 23:55 | 50.06
2025-03-10 | 23:55 | 50.063
2025-03-10 | 23:55 | 50.069
2025-03-10 | 23:55 | 50.071
2025-03-10 | 23:55 | 50.072
2025-03-10 | 23:55 | 50.073
2025-03-10 | 23:55 | 50.075
2025-03-10 | 23:55 | 50.074
2025-03-10 | 23:55 | 50.074
2025-03-10 | 23:55 | 50.072
2025-03-10 | 23:55 | 50.07
2025-03-10 | 23:55 | 50.069
2025-03-10 | 23:55 | 50.068
2025-03-10 | 23:55 | 50.067
2025-03-10 | 23:55 | 50.067
2025-03-10 | 23:55 | 50.064
2025-03-10 | 23:55 | 50.061
2025-03-10 | 23:55 | 50.058
2025-03-10 | 23:55 | 50.058
2025-03-10 | 23:55 | 50.057
2025-03-10 | 23:55 | 50.057
2025-03-10 | 23:55 | 50.055
2025-03-10 | 23:55 | 50.055
2025-03-10 | 23:55 | 50.056
2025-03-10 | 23:55 | 50.058
2025-03-10 | 23:55 | 50.058
2025-03-10 | 23:55 | 50.058
2025-03-10 | 23:55 | 50.059
2025-03-10 | 23:55 | 50.058
2025-03-10 | 23:55 | 50.06
2025-03-10 | 23:55 | 50.059
2025-03-10 | 23:55 | 50.061
2025-03-10 | 23:55 | 50.062
2025-03-10 | 23:55 | 50.061
2025-03-10 | 23:55 | 50.06
2025-03-10 | 23:55 | 50.058
2025-03-10 | 23:55 | 50.056
2025-03-10 | 23:55 | 50.055
2025-03-10 | 23:55 | 50.058
2025-03-10 | 23:55 | 50.063
2025-03-10 | 23:55 | 50.064
2025-03-10 | 23:55 | 50.063
2025-03-10 | 23:55 | 50.063
2025-03-10 | 23:55 | 50.062
2025-03-10 | 23:55 | 50.059
2025-03-10 | 23:55 | 50.057
2025-03-10 | 23:55 | 50.063
2025-03-10 | 23:55 | 50.07
2025-03-10 | 23:55 | 50.073
2025-03-10 | 23:55 | 50.074
2025-03-10 | 23:55 | 50.074
2025-03-10 | 23:55 | 50.075
2025-03-10 | 23:55 | 50.076
2025-03-10 | 23:55 | 50.079
2025-03-10 | 23:55 | 50.081
2025-03-10 | 23:55 | 50.081
2025-03-10 | 23:55 | 50.08
2025-03-10 | 23:55 | 50.08
2025-03-10 | 23:55 | 50.081
2025-03-10 | 23:56 | 50.081
2025-03-10 | 23:56 | 50.081
2025-03-10 | 23:56 | 50.081
2025-03-10 | 23:56 | 50.081
2025-03-10 | 23:56 | 50.082
2025-03-10 | 23:56 | 50.085
2025-03-10 | 23:56 | 50.087
2025-03-10 | 23:56 | 50.089
2025-03-10 | 23:56 | 50.091
2025-03-10 | 23:56 | 50.092
2025-03-10 | 23:56 | 50.09
2025-03-10 | 23:56 | 50.088
2025-03-10 | 23:56 | 50.088
2025-03-10 | 23:56 | 50.091
2025-03-10 | 23:56 | 50.092
2025-03-10 | 23:56 | 50.094
2025-03-10 | 23:56 | 50.096
2025-03-10 | 23:56 | 50.094
2025-03-10 | 23:56 | 50.095
2025-03-10 | 23:56 | 50.096
2025-03-10 | 23:56 | 50.096
2025-03-10 | 23:56 | 50.095
2025-03-10 | 23:56 | 50.095
2025-03-10 | 23:56 | 50.095
2025-03-10 | 23:56 | 50.095
2025-03-10 | 23:56 | 50.094
2025-03-10 | 23:56 | 50.094
2025-03-10 | 23:56 | 50.093
2025-03-10 | 23:56 | 50.093
2025-03-10 | 23:56 | 50.093
2025-03-10 | 23:56 | 50.096
2025-03-10 | 23:56 | 50.1
2025-03-10 | 23:56 | 50.102
2025-03-10 | 23:56 | 50.103
2025-03-10 | 23:56 | 50.104
2025-03-10 | 23:56 | 50.105
2025-03-10 | 23:56 | 50.103
2025-03-10 | 23:56 | 50.102
2025-03-10 | 23:56 | 50.1
2025-03-10 | 23:56 | 50.1
2025-03-10 | 23:56 | 50.101
2025-03-10 | 23:56 | 50.102
2025-03-10 | 23:56 | 50.1
2025-03-10 | 23:56 | 50.099
2025-03-10 | 23:56 | 50.098
2025-03-10 | 23:56 | 50.098
2025-03-10 | 23:56 | 50.098
2025-03-10 | 23:56 | 50.096
2025-03-10 | 23:56 | 50.096
2025-03-10 | 23:56 | 50.098
2025-03-10 | 23:56 | 50.098
2025-03-10 | 23:56 | 50.1
2025-03-10 | 23:56 | 50.1
2025-03-10 | 23:56 | 50.1
2025-03-10 | 23:56 | 50.102
2025-03-10 | 23:56 | 50.103
2025-03-10 | 23:56 | 50.104
2025-03-10 | 23:56 | 50.105
2025-03-10 | 23:56 | 50.106
2025-03-10 | 23:56 | 50.106
2025-03-10 | 23:56 | 50.107
2025-03-10 | 23:57 | 50.106
2025-03-10 | 23:57 | 50.106
2025-03-10 | 23:57 | 50.106
2025-03-10 | 23:57 | 50.103
2025-03-10 | 23:57 | 50.104
2025-03-10 | 23:57 | 50.105
2025-03-10 | 23:57 | 50.106
2025-03-10 | 23:57 | 50.108
2025-03-10 | 23:57 | 50.108
2025-03-10 | 23:57 | 50.108
2025-03-10 | 23:57 | 50.107
2025-03-10 | 23:57 | 50.107
2025-03-10 | 23:57 | 50.109
2025-03-10 | 23:57 | 50.111
2025-03-10 | 23:57 | 50.11
2025-03-10 | 23:57 | 50.108
2025-03-10 | 23:57 | 50.108
2025-03-10 | 23:57 | 50.11
2025-03-10 | 23:57 | 50.109
2025-03-10 | 23:57 | 50.108
2025-03-10 | 23:57 | 50.106
2025-03-10 | 23:57 | 50.107
2025-03-10 | 23:57 | 50.109
2025-03-10 | 23:57 | 50.111
2025-03-10 | 23:57 | 50.108
2025-03-10 | 23:57 | 50.102
2025-03-10 | 23:57 | 50.092
2025-03-10 | 23:57 | 50.086
2025-03-10 | 23:57 | 50.078
2025-03-10 | 23:57 | 50.074
2025-03-10 | 23:57 | 50.065
2025-03-10 | 23:57 | 50.061
2025-03-10 | 23:57 | 50.059
2025-03-10 | 23:57 | 50.06
2025-03-10 | 23:57 | 50.06
2025-03-10 | 23:57 | 50.061
2025-03-10 | 23:57 | 50.062
2025-03-10 | 23:57 | 50.062
2025-03-10 | 23:57 | 50.062
2025-03-10 | 23:57 | 50.064
2025-03-10 | 23:57 | 50.065
2025-03-10 | 23:57 | 50.065
2025-03-10 | 23:57 | 50.063
2025-03-10 | 23:57 | 50.063
2025-03-10 | 23:57 | 50.061
2025-03-10 | 23:57 | 50.061
2025-03-10 | 23:57 | 50.06
2025-03-10 | 23:57 | 50.061
2025-03-10 | 23:57 | 50.06
2025-03-10 | 23:57 | 50.06
2025-03-10 | 23:57 | 50.057
2025-03-10 | 23:57 | 50.056
2025-03-10 | 23:57 | 50.052
2025-03-10 | 23:57 | 50.051
2025-03-10 | 23:57 | 50.053
2025-03-10 | 23:57 | 50.055
2025-03-10 | 23:57 | 50.055
2025-03-10 | 23:57 | 50.055
2025-03-10 | 23:57 | 50.056
2025-03-10 | 23:58 | 50.057
2025-03-10 | 23:58 | 50.055
2025-03-10 | 23:58 | 50.054
2025-03-10 | 23:58 | 50.054
2025-03-10 | 23:58 | 50.056
2025-03-10 | 23:58 | 50.058
2025-03-10 | 23:58 | 50.063
2025-03-10 | 23:58 | 50.066
2025-03-10 | 23:58 | 50.07
2025-03-10 | 23:58 | 50.071
2025-03-10 | 23:58 | 50.07
2025-03-10 | 23:58 | 50.067
2025-03-10 | 23:58 | 50.066
2025-03-10 | 23:58 | 50.065
2025-03-10 | 23:58 | 50.064
2025-03-10 | 23:58 | 50.061
2025-03-10 | 23:58 | 50.061
2025-03-10 | 23:58 | 50.057
2025-03-10 | 23:58 | 50.051
2025-03-10 | 23:58 | 50.043
2025-03-10 | 23:58 | 50.041
2025-03-10 | 23:58 | 50.043
2025-03-10 | 23:58 | 50.045
2025-03-10 | 23:58 | 50.045
2025-03-10 | 23:58 | 50.045
2025-03-10 | 23:58 | 50.045
2025-03-10 | 23:58 | 50.043
2025-03-10 | 23:58 | 50.04
2025-03-10 | 23:58 | 50.037
2025-03-10 | 23:58 | 50.037
2025-03-10 | 23:58 | 50.036
2025-03-10 | 23:58 | 50.031
2025-03-10 | 23:58 | 50.032
2025-03-10 | 23:58 | 50.033
2025-03-10 | 23:58 | 50.034
2025-03-10 | 23:58 | 50.035
2025-03-10 | 23:58 | 50.036
2025-03-10 | 23:58 | 50.035
2025-03-10 | 23:58 | 50.036
2025-03-10 | 23:58 | 50.035
2025-03-10 | 23:58 | 50.039
2025-03-10 | 23:58 | 50.04
2025-03-10 | 23:58 | 50.042
2025-03-10 | 23:58 | 50.044
2025-03-10 | 23:58 | 50.042
2025-03-10 | 23:58 | 50.041
2025-03-10 | 23:58 | 50.037
2025-03-10 | 23:58 | 50.036
2025-03-10 | 23:58 | 50.036
2025-03-10 | 23:58 | 50.037
2025-03-10 | 23:58 | 50.038
2025-03-10 | 23:58 | 50.038
2025-03-10 | 23:58 | 50.037
2025-03-10 | 23:58 | 50.039
2025-03-10 | 23:58 | 50.041
2025-03-10 | 23:58 | 50.042
2025-03-10 | 23:58 | 50.04
2025-03-10 | 23:58 | 50.037
2025-03-10 | 23:58 | 50.036
2025-03-10 | 23:58 | 50.036
2025-03-10 | 23:58 | 50.037
2025-03-10 | 23:59 | 50.039
2025-03-10 | 23:59 | 50.04
2025-03-10 | 23:59 | 50.04
2025-03-10 | 23:59 | 50.037
2025-03-10 | 23:59 | 50.034
2025-03-10 | 23:59 | 50.035
2025-03-10 | 23:59 | 50.035
2025-03-10 | 23:59 | 50.036
2025-03-10 | 23:59 | 50.036
2025-03-10 | 23:59 | 50.041
2025-03-10 | 23:59 | 50.041
2025-03-10 | 23:59 | 50.041
2025-03-10 | 23:59 | 50.04
2025-03-10 | 23:59 | 50.043
2025-03-10 | 23:59 | 50.044
2025-03-10 | 23:59 | 50.048
2025-03-10 | 23:59 | 50.047
2025-03-10 | 23:59 | 50.049
2025-03-10 | 23:59 | 50.05
2025-03-10 | 23:59 | 50.05
2025-03-10 | 23:59 | 50.053
2025-03-10 | 23:59 | 50.056
2025-03-10 | 23:59 | 50.058
2025-03-10 | 23:59 | 50.058
2025-03-10 | 23:59 | 50.057
2025-03-10 | 23:59 | 50.056
2025-03-10 | 23:59 | 50.055
2025-03-10 | 23:59 | 50.054
2025-03-10 | 23:59 | 50.052
2025-03-10 | 23:59 | 50.055
2025-03-10 | 23:59 | 50.053
2025-03-10 | 23:59 | 50.053
2025-03-10 | 23:59 | 50.053
2025-03-10 | 23:59 | 50.055
2025-03-10 | 23:59 | 50.054
2025-03-10 | 23:59 | 50.057
2025-03-10 | 23:59 | 50.059
2025-03-10 | 23:59 | 50.058
2025-03-10 | 23:59 | 50.057
2025-03-10 | 23:59 | 50.057
2025-03-10 | 23:59 | 50.056
2025-03-10 | 23:59 | 50.057
2025-03-10 | 23:59 | 50.058
2025-03-10 | 23:59 | 50.063
2025-03-10 | 23:59 | 50.063
2025-03-10 | 23:59 | 50.066
2025-03-10 | 23:59 | 50.062
2025-03-10 | 23:59 | 50.065
2025-03-10 | 23:59 | 50.065
2025-03-10 | 23:59 | 50.065
2025-03-10 | 23:59 | 50.064
2025-03-10 | 23:59 | 50.063
2025-03-10 | 23:59 | 50.063
2025-03-10 | 23:59 | 50.063
2025-03-10 | 23:59 | 50.067
2025-03-10 | 23:59 | 50.066
2025-03-10 | 23:59 | 50.069
2025-03-10 | 23:59 | 50.068
2025-03-10 | 23:59 | 50.071
2025-03-10 | 24:00 | 50.064
2025-03-10 | 24:00 | 50.063
2025-03-10 | 24:00 | 50.065
2025-03-10 | 24:00 | 50.067
2025-03-10 | 24:00 | 50.071
2025-03-10 | 24:00 | 50.072
2025-03-10 | 24:00 | 50.077
2025-03-10 | 24:00 | 50.078
2025-03-10 | 24:00 | 50.08
2025-03-10 | 24:00 | 50.08
2025-03-10 | 24:00 | 50.081
2025-03-10 | 24:00 | 50.084
2025-03-10 | 24:00 | 50.083
2025-03-10 | 24:00 | 50.083
2025-03-10 | 24:00 | 50.081
2025-03-10 | 24:00 | 50.08
2025-03-10 | 24:00 | 50.079
2025-03-10 | 24:00 | 50.083
2025-03-10 | 24:00 | 50.084
2025-03-10 | 24:00 | 50.083
2025-03-10 | 24:00 | 50.085
2025-03-10 | 24:00 | 50.086
2025-03-10 | 24:00 | 50.088
2025-03-10 | 24:00 | 50.087
2025-03-10 | 24:00 | 50.089
2025-03-10 | 24:00 | 50.091
2025-03-10 | 24:00 | 50.089
2025-03-10 | 24:00 | 50.087
2025-03-10 | 24:00 | 50.087
2025-03-10 | 24:00 | 50.086
2025-03-11 | 0:00 | 50.085
2025-03-11 | 0:00 | 50.065
2025-03-11 | 0:00 | 50.039
2025-03-11 | 0:00 | 50.024
2025-03-11 | 0:00 | 50.027
2025-03-11 | 0:00 | 50.03
2025-03-11 | 0:00 | 50.032
2025-03-11 | 0:00 | 50.034
2025-03-11 | 0:00 | 50.035
2025-03-11 | 0:00 | 50.034
2025-03-11 | 0:00 | 50.036
2025-03-11 | 0:00 | 50.036
2025-03-11 | 0:00 | 50.037
2025-03-11 | 0:00 | 50.035
2025-03-11 | 0:00 | 50.035
2025-03-11 | 0:00 | 50.037
2025-03-11 | 0:00 | 50.037
2025-03-11 | 0:00 | 50.037
2025-03-11 | 0:00 | 50.038
2025-03-11 | 0:00 | 50.041
2025-03-11 | 0:00 | 50.043
2025-03-11 | 0:00 | 50.04
2025-03-11 | 0:00 | 50.035
2025-03-11 | 0:00 | 50.031
2025-03-11 | 0:00 | 50.029
2025-03-11 | 0:00 | 50.027
2025-03-11 | 0:00 | 50.029
2025-03-11 | 0:00 | 50.026
2025-03-11 | 0:00 | 50.025
2025-03-11 | 0:00 | 50.026
2025-03-11 | 0:00 | 50.032
2025-03-11 | 0:01 | 50.042
2025-03-11 | 0:01 | 50.046
2025-03-11 | 0:01 | 50.047
2025-03-11 | 0:01 | 50.045
2025-03-11 | 0:01 | 50.037
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.029
2025-03-11 | 0:01 | 50.028
2025-03-11 | 0:01 | 50.028
2025-03-11 | 0:01 | 50.031
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.03
2025-03-11 | 0:01 | 50.027
2025-03-11 | 0:01 | 50.023
2025-03-11 | 0:01 | 50.02
2025-03-11 | 0:01 | 50.021
2025-03-11 | 0:01 | 50.019
2025-03-11 | 0:01 | 50.022
2025-03-11 | 0:01 | 50.022
2025-03-11 | 0:01 | 50.021
2025-03-11 | 0:01 | 50.023
2025-03-11 | 0:01 | 50.029
2025-03-11 | 0:01 | 50.032
2025-03-11 | 0:01 | 50.03
2025-03-11 | 0:01 | 50.033
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.033
2025-03-11 | 0:01 | 50.031
2025-03-11 | 0:01 | 50.033
2025-03-11 | 0:01 | 50.032
2025-03-11 | 0:01 | 50.031
2025-03-11 | 0:01 | 50.033
2025-03-11 | 0:01 | 50.033
2025-03-11 | 0:01 | 50.035
2025-03-11 | 0:01 | 50.036
2025-03-11 | 0:01 | 50.033
2025-03-11 | 0:01 | 50.033
2025-03-11 | 0:01 | 50.031
2025-03-11 | 0:01 | 50.032
2025-03-11 | 0:01 | 50.032
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.035
2025-03-11 | 0:01 | 50.033
2025-03-11 | 0:01 | 50.034
2025-03-11 | 0:01 | 50.031
2025-03-11 | 0:01 | 50.029
2025-03-11 | 0:01 | 50.026
2025-03-11 | 0:01 | 50.028
2025-03-11 | 0:01 | 50.028
2025-03-11 | 0:01 | 50.029
2025-03-11 | 0:01 | 50.031
2025-03-11 | 0:01 | 50.032
2025-03-11 | 0:01 | 50.033
2025-03-11 | 0:02 | 50.033
2025-03-11 | 0:02 | 50.037
2025-03-11 | 0:02 | 50.04
2025-03-11 | 0:02 | 50.041
2025-03-11 | 0:02 | 50.041
2025-03-11 | 0:02 | 50.038
2025-03-11 | 0:02 | 50.037
2025-03-11 | 0:02 | 50.035
2025-03-11 | 0:02 | 50.033
2025-03-11 | 0:02 | 50.031
2025-03-11 | 0:02 | 50.034
2025-03-11 | 0:02 | 50.035
2025-03-11 | 0:02 | 50.036
2025-03-11 | 0:02 | 50.036
2025-03-11 | 0:02 | 50.037
2025-03-11 | 0:02 | 50.035
2025-03-11 | 0:02 | 50.036
2025-03-11 | 0:02 | 50.037
2025-03-11 | 0:02 | 50.039
2025-03-11 | 0:02 | 50.038
2025-03-11 | 0:02 | 50.04
2025-03-11 | 0:02 | 50.037
2025-03-11 | 0:02 | 50.037
2025-03-11 | 0:02 | 50.034
2025-03-11 | 0:02 | 50.031
2025-03-11 | 0:02 | 50.032
2025-03-11 | 0:02 | 50.035
2025-03-11 | 0:02 | 50.037
2025-03-11 | 0:02 | 50.041
2025-03-11 | 0:02 | 50.042
2025-03-11 | 0:02 | 50.046
2025-03-11 | 0:02 | 50.04
2025-03-11 | 0:02 | 50.035
2025-03-11 | 0:02 | 50.033
2025-03-11 | 0:02 | 50.032
2025-03-11 | 0:02 | 50.032
2025-03-11 | 0:02 | 50.031
2025-03-11 | 0:02 | 50.033
2025-03-11 | 0:02 | 50.032
2025-03-11 | 0:02 | 50.03
2025-03-11 | 0:02 | 50.03
2025-03-11 | 0:02 | 50.03
2025-03-11 | 0:02 | 50.028
2025-03-11 | 0:02 | 50.025
2025-03-11 | 0:02 | 50.022
2025-03-11 | 0:02 | 50.019
2025-03-11 | 0:02 | 50.018
2025-03-11 | 0:02 | 50.021
2025-03-11 | 0:02 | 50.024
2025-03-11 | 0:02 | 50.023
2025-03-11 | 0:02 | 50.023
2025-03-11 | 0:02 | 50.025
2025-03-11 | 0:02 | 50.026
2025-03-11 | 0:02 | 50.026
2025-03-11 | 0:02 | 50.025
2025-03-11 | 0:02 | 50.024
2025-03-11 | 0:02 | 50.023
2025-03-11 | 0:02 | 50.019
2025-03-11 | 0:02 | 50.017
2025-03-11 | 0:02 | 50.014
2025-03-11 | 0:02 | 50.015
2025-03-11 | 0:03 | 50.015
2025-03-11 | 0:03 | 50.015
2025-03-11 | 0:03 | 50.015
2025-03-11 | 0:03 | 50.016
2025-03-11 | 0:03 | 50.02
2025-03-11 | 0:03 | 50.023
2025-03-11 | 0:03 | 50.024
2025-03-11 | 0:03 | 50.024
2025-03-11 | 0:03 | 50.023
2025-03-11 | 0:03 | 50.024
2025-03-11 | 0:03 | 50.026
2025-03-11 | 0:03 | 50.029
2025-03-11 | 0:03 | 50.031
2025-03-11 | 0:03 | 50.033
2025-03-11 | 0:03 | 50.038
2025-03-11 | 0:03 | 50.04
2025-03-11 | 0:03 | 50.041
2025-03-11 | 0:03 | 50.042
2025-03-11 | 0:03 | 50.043
2025-03-11 | 0:03 | 50.044
2025-03-11 | 0:03 | 50.045
2025-03-11 | 0:03 | 50.043
2025-03-11 | 0:03 | 50.039
2025-03-11 | 0:03 | 50.036
2025-03-11 | 0:03 | 50.033
2025-03-11 | 0:03 | 50.032
2025-03-11 | 0:03 | 50.032
2025-03-11 | 0:03 | 50.032
2025-03-11 | 0:03 | 50.031
2025-03-11 | 0:03 | 50.031
2025-03-11 | 0:03 | 50.028
2025-03-11 | 0:03 | 50.028
2025-03-11 | 0:03 | 50.028
2025-03-11 | 0:03 | 50.027
2025-03-11 | 0:03 | 50.024
2025-03-11 | 0:03 | 50.023
2025-03-11 | 0:03 | 50.023
2025-03-11 | 0:03 | 50.024
2025-03-11 | 0:03 | 50.027
2025-03-11 | 0:03 | 50.031
2025-03-11 | 0:03 | 50.032
2025-03-11 | 0:03 | 50.031
2025-03-11 | 0:03 | 50.028
2025-03-11 | 0:03 | 50.03
2025-03-11 | 0:03 | 50.029
2025-03-11 | 0:03 | 50.026
2025-03-11 | 0:03 | 50.03
2025-03-11 | 0:03 | 50.032
2025-03-11 | 0:03 | 50.033
2025-03-11 | 0:03 | 50.034
2025-03-11 | 0:03 | 50.034
2025-03-11 | 0:03 | 50.035
2025-03-11 | 0:03 | 50.033
2025-03-11 | 0:03 | 50.033
2025-03-11 | 0:03 | 50.036
2025-03-11 | 0:03 | 50.039
2025-03-11 | 0:03 | 50.037
2025-03-11 | 0:03 | 50.038
2025-03-11 | 0:03 | 50.037
2025-03-11 | 0:04 | 50.036
2025-03-11 | 0:04 | 50.036
2025-03-11 | 0:04 | 50.039
2025-03-11 | 0:04 | 50.037
2025-03-11 | 0:04 | 50.036
2025-03-11 | 0:04 | 50.035
2025-03-11 | 0:04 | 50.034
2025-03-11 | 0:04 | 50.031
2025-03-11 | 0:04 | 50.029
2025-03-11 | 0:04 | 50.033
2025-03-11 | 0:04 | 50.035
2025-03-11 | 0:04 | 50.035
2025-03-11 | 0:04 | 50.037
2025-03-11 | 0:04 | 50.036
2025-03-11 | 0:04 | 50.038
2025-03-11 | 0:04 | 50.036
2025-03-11 | 0:04 | 50.034
2025-03-11 | 0:04 | 50.035
2025-03-11 | 0:04 | 50.034
2025-03-11 | 0:04 | 50.038
2025-03-11 | 0:04 | 50.043
2025-03-11 | 0:04 | 50.046
2025-03-11 | 0:04 | 50.048
2025-03-11 | 0:04 | 50.047
2025-03-11 | 0:04 | 50.046
2025-03-11 | 0:04 | 50.047
2025-03-11 | 0:04 | 50.048
2025-03-11 | 0:04 | 50.05
2025-03-11 | 0:04 | 50.05
2025-03-11 | 0:04 | 50.051
2025-03-11 | 0:04 | 50.049
2025-03-11 | 0:04 | 50.045
2025-03-11 | 0:04 | 50.043
2025-03-11 | 0:04 | 50.044
2025-03-11 | 0:04 | 50.05
2025-03-11 | 0:04 | 50.051
2025-03-11 | 0:04 | 50.048
2025-03-11 | 0:04 | 50.046
2025-03-11 | 0:04 | 50.045
2025-03-11 | 0:04 | 50.045
2025-03-11 | 0:04 | 50.042
2025-03-11 | 0:04 | 50.036
2025-03-11 | 0:04 | 50.033
2025-03-11 | 0:04 | 50.034
2025-03-11 | 0:04 | 50.038
2025-03-11 | 0:04 | 50.049
2025-03-11 | 0:04 | 50.056
2025-03-11 | 0:04 | 50.057
2025-03-11 | 0:04 | 50.052
2025-03-11 | 0:04 | 50.045
2025-03-11 | 0:04 | 50.042
2025-03-11 | 0:04 | 50.04
2025-03-11 | 0:04 | 50.04
2025-03-11 | 0:04 | 50.039
2025-03-11 | 0:04 | 50.04
2025-03-11 | 0:04 | 50.039
2025-03-11 | 0:04 | 50.037
2025-03-11 | 0:04 | 50.037
2025-03-11 | 0:04 | 50.04
2025-03-11 | 0:04 | 50.042
2025-03-11 | 0:04 | 50.044
2025-03-11 | 0:05 | 50.041
2025-03-11 | 0:05 | 50.039
2025-03-11 | 0:05 | 50.037
2025-03-11 | 0:05 | 50.037
2025-03-11 | 0:05 | 50.035
2025-03-11 | 0:05 | 50.033
2025-03-11 | 0:05 | 50.031
2025-03-11 | 0:05 | 50.032
2025-03-11 | 0:05 | 50.032
2025-03-11 | 0:05 | 50.032
2025-03-11 | 0:05 | 50.035
2025-03-11 | 0:05 | 50.04
2025-03-11 | 0:05 | 50.045
2025-03-11 | 0:05 | 50.046
2025-03-11 | 0:05 | 50.047
2025-03-11 | 0:05 | 50.045
2025-03-11 | 0:05 | 50.044
2025-03-11 | 0:05 | 50.043
2025-03-11 | 0:05 | 50.044
2025-03-11 | 0:05 | 50.042
2025-03-11 | 0:05 | 50.041
2025-03-11 | 0:05 | 50.042
2025-03-11 | 0:05 | 50.043
2025-03-11 | 0:05 | 50.045
2025-03-11 | 0:05 | 50.043
2025-03-11 | 0:05 | 50.041
2025-03-11 | 0:05 | 50.04
2025-03-11 | 0:05 | 50.041
2025-03-11 | 0:05 | 50.043
2025-03-11 | 0:05 | 50.042
2025-03-11 | 0:05 | 50.038
2025-03-11 | 0:05 | 50.036
2025-03-11 | 0:05 | 50.037
2025-03-11 | 0:05 | 50.037
2025-03-11 | 0:05 | 50.038
2025-03-11 | 0:05 | 50.038
2025-03-11 | 0:05 | 50.039
2025-03-11 | 0:05 | 50.041
2025-03-11 | 0:05 | 50.042
2025-03-11 | 0:05 | 50.042
2025-03-11 | 0:05 | 50.039
2025-03-11 | 0:05 | 50.038
2025-03-11 | 0:05 | 50.036
2025-03-11 | 0:05 | 50.033
2025-03-11 | 0:05 | 50.031
2025-03-11 | 0:05 | 50.028
2025-03-11 | 0:05 | 50.025
2025-03-11 | 0:05 | 50.025
2025-03-11 | 0:05 | 50.027
2025-03-11 | 0:05 | 50.028
2025-03-11 | 0:05 | 50.029
2025-03-11 | 0:05 | 50.025
2025-03-11 | 0:05 | 50.024
2025-03-11 | 0:05 | 50.023
2025-03-11 | 0:05 | 50.026
2025-03-11 | 0:05 | 50.028
2025-03-11 | 0:05 | 50.03
2025-03-11 | 0:05 | 50.03
2025-03-11 | 0:05 | 50.026
2025-03-11 | 0:06 | 50.022
2025-03-11 | 0:06 | 50.017
2025-03-11 | 0:06 | 50.018
2025-03-11 | 0:06 | 50.02
2025-03-11 | 0:06 | 50.025
2025-03-11 | 0:06 | 50.029
2025-03-11 | 0:06 | 50.029
2025-03-11 | 0:06 | 50.027
2025-03-11 | 0:06 | 50.027
2025-03-11 | 0:06 | 50.026
2025-03-11 | 0:06 | 50.025
2025-03-11 | 0:06 | 50.024
2025-03-11 | 0:06 | 50.025
2025-03-11 | 0:06 | 50.024
2025-03-11 | 0:06 | 50.02
2025-03-11 | 0:06 | 50.019
2025-03-11 | 0:06 | 50.017
2025-03-11 | 0:06 | 50.016
2025-03-11 | 0:06 | 50.017
2025-03-11 | 0:06 | 50.017
2025-03-11 | 0:06 | 50.019
2025-03-11 | 0:06 | 50.029
2025-03-11 | 0:06 | 50.039
2025-03-11 | 0:06 | 50.044
2025-03-11 | 0:06 | 50.044
2025-03-11 | 0:06 | 50.043
2025-03-11 | 0:06 | 50.042
2025-03-11 | 0:06 | 50.042
2025-03-11 | 0:06 | 50.042
2025-03-11 | 0:06 | 50.043
2025-03-11 | 0:06 | 50.042
2025-03-11 | 0:06 | 50.037
2025-03-11 | 0:06 | 50.034
2025-03-11 | 0:06 | 50.031
2025-03-11 | 0:06 | 50.029
2025-03-11 | 0:06 | 50.029
2025-03-11 | 0:06 | 50.026
2025-03-11 | 0:06 | 50.026
2025-03-11 | 0:06 | 50.023
2025-03-11 | 0:06 | 50.022
2025-03-11 | 0:06 | 50.022
2025-03-11 | 0:06 | 50.024
2025-03-11 | 0:06 | 50.025
2025-03-11 | 0:06 | 50.025
2025-03-11 | 0:06 | 50.027
2025-03-11 | 0:06 | 50.029
2025-03-11 | 0:06 | 50.031
2025-03-11 | 0:06 | 50.03
2025-03-11 | 0:06 | 50.026
2025-03-11 | 0:06 | 50.023
2025-03-11 | 0:06 | 50.02
2025-03-11 | 0:06 | 50.021
2025-03-11 | 0:06 | 50.02
2025-03-11 | 0:06 | 50.019
2025-03-11 | 0:06 | 50.02
2025-03-11 | 0:06 | 50.018
2025-03-11 | 0:06 | 50.015
2025-03-11 | 0:06 | 50.014
2025-03-11 | 0:06 | 50.012
2025-03-11 | 0:06 | 50.013
2025-03-11 | 0:06 | 50.012
2025-03-11 | 0:07 | 50.013
2025-03-11 | 0:07 | 50.014
2025-03-11 | 0:07 | 50.013
2025-03-11 | 0:07 | 50.013
2025-03-11 | 0:07 | 50.011
2025-03-11 | 0:07 | 50.011
2025-03-11 | 0:07 | 50.009
2025-03-11 | 0:07 | 50.008
2025-03-11 | 0:07 | 50.007
2025-03-11 | 0:07 | 50.006
2025-03-11 | 0:07 | 50.008
2025-03-11 | 0:07 | 50.009
2025-03-11 | 0:07 | 50.011
2025-03-11 | 0:07 | 50.012
2025-03-11 | 0:07 | 50.015
2025-03-11 | 0:07 | 50.017
2025-03-11 | 0:07 | 50.018
2025-03-11 | 0:07 | 50.019
2025-03-11 | 0:07 | 50.018
2025-03-11 | 0:07 | 50.018
2025-03-11 | 0:07 | 50.021
2025-03-11 | 0:07 | 50.025
2025-03-11 | 0:07 | 50.027
2025-03-11 | 0:07 | 50.029
2025-03-11 | 0:07 | 50.028
2025-03-11 | 0:07 | 50.028
2025-03-11 | 0:07 | 50.028
2025-03-11 | 0:07 | 50.028
2025-03-11 | 0:07 | 50.028
2025-03-11 | 0:07 | 50.026
2025-03-11 | 0:07 | 50.023
2025-03-11 | 0:07 | 50.023
2025-03-11 | 0:07 | 50.021
2025-03-11 | 0:07 | 50.021
2025-03-11 | 0:07 | 50.02
2025-03-11 | 0:07 | 50.02
2025-03-11 | 0:07 | 50.019
2025-03-11 | 0:07 | 50.02
2025-03-11 | 0:07 | 50.018
2025-03-11 | 0:07 | 50.015
2025-03-11 | 0:07 | 50.014
2025-03-11 | 0:07 | 50.016
2025-03-11 | 0:07 | 50.018
2025-03-11 | 0:07 | 50.018
2025-03-11 | 0:07 | 50.018
2025-03-11 | 0:07 | 50.015
2025-03-11 | 0:07 | 50.014
2025-03-11 | 0:07 | 50.014
2025-03-11 | 0:07 | 50.015
2025-03-11 | 0:07 | 50.016
2025-03-11 | 0:07 | 50.017
2025-03-11 | 0:07 | 50.02
2025-03-11 | 0:07 | 50.019
2025-03-11 | 0:07 | 50.019
2025-03-11 | 0:07 | 50.017
2025-03-11 | 0:07 | 50.014
2025-03-11 | 0:07 | 50.012
2025-03-11 | 0:07 | 50.01
2025-03-11 | 0:07 | 50.012
2025-03-11 | 0:08 | 50.012
2025-03-11 | 0:08 | 50.011
2025-03-11 | 0:08 | 50.008
2025-03-11 | 0:08 | 50.005
2025-03-11 | 0:08 | 50.003
2025-03-11 | 0:08 | 49.999
2025-03-11 | 0:08 | 49.993
2025-03-11 | 0:08 | 49.988
2025-03-11 | 0:08 | 49.985
2025-03-11 | 0:08 | 49.982
2025-03-11 | 0:08 | 49.98
2025-03-11 | 0:08 | 49.98
2025-03-11 | 0:08 | 49.98
2025-03-11 | 0:08 | 49.982
2025-03-11 | 0:08 | 49.983
2025-03-11 | 0:08 | 49.985
2025-03-11 | 0:08 | 49.987
2025-03-11 | 0:08 | 49.988
2025-03-11 | 0:08 | 49.995
2025-03-11 | 0:08 | 50.003
2025-03-11 | 0:08 | 50.011
2025-03-11 | 0:08 | 50.018
2025-03-11 | 0:08 | 50.025
2025-03-11 | 0:08 | 50.028
2025-03-11 | 0:08 | 50.025
2025-03-11 | 0:08 | 50.023
2025-03-11 | 0:08 | 50.022
2025-03-11 | 0:08 | 50.022
2025-03-11 | 0:08 | 50.022
2025-03-11 | 0:08 | 50.025
2025-03-11 | 0:08 | 50.023
2025-03-11 | 0:08 | 50.019
2025-03-11 | 0:08 | 50.014
2025-03-11 | 0:08 | 50.013
2025-03-11 | 0:08 | 50.013
2025-03-11 | 0:08 | 50.013
2025-03-11 | 0:08 | 50.014
2025-03-11 | 0:08 | 50.014
2025-03-11 | 0:08 | 50.012
2025-03-11 | 0:08 | 50.009
2025-03-11 | 0:08 | 50.009
2025-03-11 | 0:08 | 50.009
2025-03-11 | 0:08 | 50.01
2025-03-11 | 0:08 | 50.01
2025-03-11 | 0:08 | 50.011
2025-03-11 | 0:08 | 50.01
2025-03-11 | 0:08 | 50.008
2025-03-11 | 0:08 | 50.004
2025-03-11 | 0:08 | 49.999
2025-03-11 | 0:08 | 49.995
2025-03-11 | 0:08 | 49.992
2025-03-11 | 0:08 | 49.99
2025-03-11 | 0:08 | 49.986
2025-03-11 | 0:08 | 49.984
2025-03-11 | 0:08 | 49.983
2025-03-11 | 0:08 | 49.986
2025-03-11 | 0:08 | 49.988
2025-03-11 | 0:08 | 49.988
2025-03-11 | 0:08 | 49.989
2025-03-11 | 0:08 | 49.991
2025-03-11 | 0:08 | 49.993
2025-03-11 | 0:09 | 49.998
2025-03-11 | 0:09 | 50.002
2025-03-11 | 0:09 | 50.004
2025-03-11 | 0:09 | 50.005
2025-03-11 | 0:09 | 50.006

## 20250313-1
In GMT
Date | Time | Freq
2025-03-13 | 19:27 | 49.962 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-13 | 19:27 | 49.962 | 222 | BRITNED | 676.211
2025-03-13 | 19:27 | 49.963 | 268 | WBURB-2 | 428.156
2025-03-13 | 19:27 | 49.963 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-13 | 19:27 | 49.961 |  | Viking Link | -648.9
2025-03-13 | 19:27 | 49.961 |  | Viking Link | 1398.96
2025-03-13 | 19:27 | 49.96 | 209 | DRAXX-3 | 626.95
2025-03-13 | 19:27 | 49.959 | 154 | CDCL-1 | 391.57
2025-03-13 | 19:27 | 49.96 | 268 | ROCK-1 | 468.495
2025-03-13 | 19:27 | 49.961 | 148 | IFA Bipole1 | 945.473
2025-03-13 | 19:27 | 49.961 | 132 | IFA Bipole1 | 999.1
2025-03-13 | 19:27 | 49.964 | 141 | IFA Bipole2 | 1000
2025-03-13 | 19:27 | 49.965 | 135 | IFA Bipole1 | 996.75
2025-03-13 | 19:27 | 49.967 |  | Viking Link | -780.3
2025-03-13 | 19:27 | 49.967
2025-03-13 | 19:27 | 49.968
2025-03-13 | 19:27 | 49.967
2025-03-13 | 19:27 | 49.969
2025-03-13 | 19:27 | 49.969
2025-03-13 | 19:27 | 49.969 | 130 | HEYM12 | 271.908
2025-03-13 | 19:27 | 49.97 | 228 | HUMR-1 | 303.75
2025-03-13 | 19:27 | 49.972
2025-03-13 | 19:27 | 49.975
2025-03-13 | 19:27 | 49.977
2025-03-13 | 19:27 | 49.979
2025-03-13 | 19:27 | 49.978
2025-03-13 | 19:27 | 49.98
2025-03-13 | 19:27 | 49.981
2025-03-13 | 19:27 | 49.981
2025-03-13 | 19:27 | 49.98
2025-03-13 | 19:27 | 49.978 | 211 | CDCL-1 | 291.5
2025-03-13 | 19:27 | 49.978 | 199 | STAY-2 | 413.125
2025-03-13 | 19:27 | 49.977 | 173 | CDCL-1 | 397.375
2025-03-13 | 19:27 | 49.978 | 248 | SEAB-2 | 361.25
2025-03-13 | 19:27 | 49.977 | 255 | FRANCE | 995.65
2025-03-13 | 19:27 | 49.977 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-13 | 19:27 | 49.976
2025-03-13 | 19:27 | 49.976
2025-03-13 | 19:27 | 49.975
2025-03-13 | 19:28 | 49.975
2025-03-13 | 19:28 | 49.972
2025-03-13 | 19:28 | 49.972
2025-03-13 | 19:28 | 49.973
2025-03-13 | 19:28 | 49.972
2025-03-13 | 19:28 | 49.971
2025-03-13 | 19:28 | 49.971
2025-03-13 | 19:28 | 49.968
2025-03-13 | 19:28 | 49.966
2025-03-13 | 19:28 | 49.961
2025-03-13 | 19:28 | 49.96
2025-03-13 | 19:28 | 49.958
2025-03-13 | 19:28 | 49.957
2025-03-13 | 19:28 | 49.957
2025-03-13 | 19:28 | 49.957
2025-03-13 | 19:28 | 49.949
2025-03-13 | 19:28 | 49.939
2025-03-13 | 19:28 | 49.931
2025-03-13 | 19:28 | 49.928
2025-03-13 | 19:28 | 49.927
2025-03-13 | 19:28 | 49.929
2025-03-13 | 19:28 | 49.93
2025-03-13 | 19:28 | 49.932
2025-03-13 | 19:28 | 49.931
2025-03-13 | 19:28 | 49.932
2025-03-13 | 19:28 | 49.93
2025-03-13 | 19:28 | 49.929
2025-03-13 | 19:28 | 49.927
2025-03-13 | 19:28 | 49.923
2025-03-13 | 19:28 | 49.92
2025-03-13 | 19:28 | 49.919
2025-03-13 | 19:28 | 49.919
2025-03-13 | 19:28 | 49.921
2025-03-13 | 19:28 | 49.919
2025-03-13 | 19:28 | 49.918
2025-03-13 | 19:28 | 49.919
2025-03-13 | 19:28 | 49.919
2025-03-13 | 19:28 | 49.92
2025-03-13 | 19:28 | 49.92
2025-03-13 | 19:28 | 49.918
2025-03-13 | 19:28 | 49.918
2025-03-13 | 19:28 | 49.919
2025-03-13 | 19:28 | 49.919
2025-03-13 | 19:28 | 49.92
2025-03-13 | 19:28 | 49.92
2025-03-13 | 19:28 | 49.92
2025-03-13 | 19:28 | 49.92
2025-03-13 | 19:28 | 49.92
2025-03-13 | 19:28 | 49.922
2025-03-13 | 19:28 | 49.921
2025-03-13 | 19:28 | 49.919
2025-03-13 | 19:28 | 49.919
2025-03-13 | 19:28 | 49.918
2025-03-13 | 19:28 | 49.917
2025-03-13 | 19:28 | 49.916
2025-03-13 | 19:28 | 49.914
2025-03-13 | 19:28 | 49.916
2025-03-13 | 19:28 | 49.916
2025-03-13 | 19:28 | 49.917
2025-03-13 | 19:28 | 49.92
2025-03-13 | 19:28 | 49.921
2025-03-13 | 19:29 | 49.919
2025-03-13 | 19:29 | 49.918
2025-03-13 | 19:29 | 49.917
2025-03-13 | 19:29 | 49.915
2025-03-13 | 19:29 | 49.914
2025-03-13 | 19:29 | 49.915
2025-03-13 | 19:29 | 49.914
2025-03-13 | 19:29 | 49.915
2025-03-13 | 19:29 | 49.915
2025-03-13 | 19:29 | 49.914
2025-03-13 | 19:29 | 49.914
2025-03-13 | 19:29 | 49.916
2025-03-13 | 19:29 | 49.916
2025-03-13 | 19:29 | 49.917
2025-03-13 | 19:29 | 49.917
2025-03-13 | 19:29 | 49.917
2025-03-13 | 19:29 | 49.914
2025-03-13 | 19:29 | 49.913
2025-03-13 | 19:29 | 49.911
2025-03-13 | 19:29 | 49.912
2025-03-13 | 19:29 | 49.911
2025-03-13 | 19:29 | 49.913
2025-03-13 | 19:29 | 49.917
2025-03-13 | 19:29 | 49.918
2025-03-13 | 19:29 | 49.919
2025-03-13 | 19:29 | 49.921
2025-03-13 | 19:29 | 49.922
2025-03-13 | 19:29 | 49.922
2025-03-13 | 19:29 | 49.924
2025-03-13 | 19:29 | 49.926
2025-03-13 | 19:29 | 49.927
2025-03-13 | 19:29 | 49.932
2025-03-13 | 19:29 | 49.936
2025-03-13 | 19:29 | 49.938
2025-03-13 | 19:29 | 49.941
2025-03-13 | 19:29 | 49.942
2025-03-13 | 19:29 | 49.942
2025-03-13 | 19:29 | 49.942
2025-03-13 | 19:29 | 49.944
2025-03-13 | 19:29 | 49.946
2025-03-13 | 19:29 | 49.948
2025-03-13 | 19:29 | 49.947
2025-03-13 | 19:29 | 49.947
2025-03-13 | 19:29 | 49.947
2025-03-13 | 19:29 | 49.948
2025-03-13 | 19:29 | 49.948
2025-03-13 | 19:29 | 49.946
2025-03-13 | 19:29 | 49.945
2025-03-13 | 19:29 | 49.944
2025-03-13 | 19:29 | 49.945
2025-03-13 | 19:29 | 49.948
2025-03-13 | 19:29 | 49.95
2025-03-13 | 19:29 | 49.953
2025-03-13 | 19:29 | 49.956
2025-03-13 | 19:29 | 49.96
2025-03-13 | 19:29 | 49.964
2025-03-13 | 19:29 | 49.967
2025-03-13 | 19:29 | 49.97
2025-03-13 | 19:29 | 49.972
2025-03-13 | 19:30 | 49.971
2025-03-13 | 19:30 | 49.97
2025-03-13 | 19:30 | 49.97
2025-03-13 | 19:30 | 49.973
2025-03-13 | 19:30 | 49.975
2025-03-13 | 19:30 | 49.979
2025-03-13 | 19:30 | 49.979
2025-03-13 | 19:30 | 49.981
2025-03-13 | 19:30 | 49.981
2025-03-13 | 19:30 | 49.983
2025-03-13 | 19:30 | 49.984
2025-03-13 | 19:30 | 49.986
2025-03-13 | 19:30 | 49.988
2025-03-13 | 19:30 | 49.992
2025-03-13 | 19:30 | 49.996
2025-03-13 | 19:30 | 50
2025-03-13 | 19:30 | 50.001
2025-03-13 | 19:30 | 50.003
2025-03-13 | 19:30 | 50.004
2025-03-13 | 19:30 | 50.004
2025-03-13 | 19:30 | 50.005
2025-03-13 | 19:30 | 50.005
2025-03-13 | 19:30 | 50.001
2025-03-13 | 19:30 | 49.998
2025-03-13 | 19:30 | 49.996
2025-03-13 | 19:30 | 49.994
2025-03-13 | 19:30 | 49.994
2025-03-13 | 19:30 | 49.993
2025-03-13 | 19:30 | 49.989
2025-03-13 | 19:30 | 49.986
2025-03-13 | 19:30 | 49.983
2025-03-13 | 19:30 | 49.973
2025-03-13 | 19:30 | 49.962
2025-03-13 | 19:30 | 49.954
2025-03-13 | 19:30 | 49.949
2025-03-13 | 19:30 | 49.942
2025-03-13 | 19:30 | 49.939
2025-03-13 | 19:30 | 49.935
2025-03-13 | 19:30 | 49.934
2025-03-13 | 19:30 | 49.932
2025-03-13 | 19:30 | 49.932
2025-03-13 | 19:30 | 49.933
2025-03-13 | 19:30 | 49.933
2025-03-13 | 19:30 | 49.936
2025-03-13 | 19:30 | 49.936
2025-03-13 | 19:30 | 49.936
2025-03-13 | 19:30 | 49.939
2025-03-13 | 19:30 | 49.94
2025-03-13 | 19:30 | 49.939
2025-03-13 | 19:30 | 49.939
2025-03-13 | 19:30 | 49.938
2025-03-13 | 19:30 | 49.936
2025-03-13 | 19:30 | 49.937
2025-03-13 | 19:30 | 49.937
2025-03-13 | 19:30 | 49.938
2025-03-13 | 19:30 | 49.942
2025-03-13 | 19:30 | 49.945
2025-03-13 | 19:30 | 49.945
2025-03-13 | 19:30 | 49.947
2025-03-13 | 19:30 | 49.948
2025-03-13 | 19:30 | 49.948
2025-03-13 | 19:31 | 49.947
2025-03-13 | 19:31 | 49.947
2025-03-13 | 19:31 | 49.946
2025-03-13 | 19:31 | 49.946
2025-03-13 | 19:31 | 49.946
2025-03-13 | 19:31 | 49.945
2025-03-13 | 19:31 | 49.944
2025-03-13 | 19:31 | 49.945
2025-03-13 | 19:31 | 49.944
2025-03-13 | 19:31 | 49.942
2025-03-13 | 19:31 | 49.942
2025-03-13 | 19:31 | 49.942
2025-03-13 | 19:31 | 49.943
2025-03-13 | 19:31 | 49.943
2025-03-13 | 19:31 | 49.944

## 20250314-1
In GMT
Date | Time | Freq
2025-03-14 | 8:51 | 50.115 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-14 | 8:51 | 50.117 | 222 | BRITNED | 676.211
2025-03-14 | 8:51 | 50.119 | 268 | WBURB-2 | 428.156
2025-03-14 | 8:51 | 50.122 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-14 | 8:51 | 50.122 |  | Viking Link | -648.9
2025-03-14 | 8:51 | 50.123 |  | Viking Link | 1398.96
2025-03-14 | 8:51 | 50.124 | 209 | DRAXX-3 | 626.95
2025-03-14 | 8:51 | 50.123 | 154 | CDCL-1 | 391.57
2025-03-14 | 8:51 | 50.123 | 268 | ROCK-1 | 468.495
2025-03-14 | 8:51 | 50.121 | 148 | IFA Bipole1 | 945.473
2025-03-14 | 8:51 | 50.118 | 132 | IFA Bipole1 | 999.1
2025-03-14 | 8:51 | 50.117 | 141 | IFA Bipole2 | 1000
2025-03-14 | 8:51 | 50.117 | 135 | IFA Bipole1 | 996.75
2025-03-14 | 8:51 | 50.117 |  | Viking Link | -780.3
2025-03-14 | 8:51 | 50.115
2025-03-14 | 8:51 | 50.116
2025-03-14 | 8:51 | 50.116
2025-03-14 | 8:51 | 50.115
2025-03-14 | 8:51 | 50.117
2025-03-14 | 8:51 | 50.116 | 130 | HEYM12 | 271.908
2025-03-14 | 8:51 | 50.117 | 228 | HUMR-1 | 303.75
2025-03-14 | 8:51 | 50.118
2025-03-14 | 8:51 | 50.118
2025-03-14 | 8:51 | 50.117
2025-03-14 | 8:51 | 50.118
2025-03-14 | 8:51 | 50.119
2025-03-14 | 8:51 | 50.118
2025-03-14 | 8:51 | 50.116
2025-03-14 | 8:51 | 50.117
2025-03-14 | 8:51 | 50.117
2025-03-14 | 8:51 | 50.12 | 211 | CDCL-1 | 291.5
2025-03-14 | 8:51 | 50.119 | 199 | STAY-2 | 413.125
2025-03-14 | 8:51 | 50.118 | 173 | CDCL-1 | 397.375
2025-03-14 | 8:51 | 50.118 | 248 | SEAB-2 | 361.25
2025-03-14 | 8:51 | 50.119 | 255 | FRANCE | 995.65
2025-03-14 | 8:51 | 50.123 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-14 | 8:51 | 50.127
2025-03-14 | 8:51 | 50.125
2025-03-14 | 8:51 | 50.125
2025-03-14 | 8:51 | 50.126
2025-03-14 | 8:51 | 50.129
2025-03-14 | 8:51 | 50.13
2025-03-14 | 8:51 | 50.131
2025-03-14 | 8:51 | 50.128
2025-03-14 | 8:51 | 50.127
2025-03-14 | 8:51 | 50.124
2025-03-14 | 8:51 | 50.124
2025-03-14 | 8:51 | 50.121
2025-03-14 | 8:51 | 50.121
2025-03-14 | 8:51 | 50.119
2025-03-14 | 8:51 | 50.119
2025-03-14 | 8:51 | 50.119
2025-03-14 | 8:51 | 50.12
2025-03-14 | 8:52 | 50.123
2025-03-14 | 8:52 | 50.126
2025-03-14 | 8:52 | 50.126
2025-03-14 | 8:52 | 50.127
2025-03-14 | 8:52 | 50.127
2025-03-14 | 8:52 | 50.126
2025-03-14 | 8:52 | 50.123
2025-03-14 | 8:52 | 50.121
2025-03-14 | 8:52 | 50.078
2025-03-14 | 8:52 | 50.043
2025-03-14 | 8:52 | 50.01
2025-03-14 | 8:52 | 49.987
2025-03-14 | 8:52 | 49.966
2025-03-14 | 8:52 | 49.939
2025-03-14 | 8:52 | 49.871
2025-03-14 | 8:52 | 49.788
2025-03-14 | 8:52 | 49.733
2025-03-14 | 8:52 | 49.699
2025-03-14 | 8:52 | 49.681
2025-03-14 | 8:52 | 49.675
2025-03-14 | 8:52 | 49.673
2025-03-14 | 8:52 | 49.674
2025-03-14 | 8:52 | 49.676
2025-03-14 | 8:52 | 49.678
2025-03-14 | 8:52 | 49.677
2025-03-14 | 8:52 | 49.676
2025-03-14 | 8:52 | 49.677
2025-03-14 | 8:52 | 49.676
2025-03-14 | 8:52 | 49.675
2025-03-14 | 8:52 | 49.675
2025-03-14 | 8:52 | 49.675
2025-03-14 | 8:52 | 49.675
2025-03-14 | 8:52 | 49.674
2025-03-14 | 8:52 | 49.674
2025-03-14 | 8:52 | 49.675
2025-03-14 | 8:52 | 49.672
2025-03-14 | 8:52 | 49.67
2025-03-14 | 8:52 | 49.67
2025-03-14 | 8:52 | 49.669
2025-03-14 | 8:52 | 49.668
2025-03-14 | 8:52 | 49.669
2025-03-14 | 8:52 | 49.674
2025-03-14 | 8:52 | 49.679
2025-03-14 | 8:52 | 49.683
2025-03-14 | 8:52 | 49.687
2025-03-14 | 8:52 | 49.689
2025-03-14 | 8:52 | 49.691
2025-03-14 | 8:52 | 49.694
2025-03-14 | 8:52 | 49.695
2025-03-14 | 8:52 | 49.695
2025-03-14 | 8:52 | 49.694
2025-03-14 | 8:52 | 49.692
2025-03-14 | 8:52 | 49.695
2025-03-14 | 8:52 | 49.696
2025-03-14 | 8:52 | 49.697
2025-03-14 | 8:52 | 49.698
2025-03-14 | 8:52 | 49.699
2025-03-14 | 8:52 | 49.704
2025-03-14 | 8:52 | 49.708
2025-03-14 | 8:52 | 49.709
2025-03-14 | 8:52 | 49.71
2025-03-14 | 8:53 | 49.708
2025-03-14 | 8:53 | 49.706
2025-03-14 | 8:53 | 49.707
2025-03-14 | 8:53 | 49.709
2025-03-14 | 8:53 | 49.713
2025-03-14 | 8:53 | 49.714
2025-03-14 | 8:53 | 49.715
2025-03-14 | 8:53 | 49.713
2025-03-14 | 8:53 | 49.714
2025-03-14 | 8:53 | 49.715
2025-03-14 | 8:53 | 49.718
2025-03-14 | 8:53 | 49.717
2025-03-14 | 8:53 | 49.717
2025-03-14 | 8:53 | 49.72
2025-03-14 | 8:53 | 49.72
2025-03-14 | 8:53 | 49.721
2025-03-14 | 8:53 | 49.72
2025-03-14 | 8:53 | 49.722
2025-03-14 | 8:53 | 49.724
2025-03-14 | 8:53 | 49.722
2025-03-14 | 8:53 | 49.72
2025-03-14 | 8:53 | 49.718
2025-03-14 | 8:53 | 49.716
2025-03-14 | 8:53 | 49.717
2025-03-14 | 8:53 | 49.72
2025-03-14 | 8:53 | 49.722
2025-03-14 | 8:53 | 49.723
2025-03-14 | 8:53 | 49.723
2025-03-14 | 8:53 | 49.723
2025-03-14 | 8:53 | 49.72
2025-03-14 | 8:53 | 49.72
2025-03-14 | 8:53 | 49.718
2025-03-14 | 8:53 | 49.717
2025-03-14 | 8:53 | 49.716
2025-03-14 | 8:53 | 49.714
2025-03-14 | 8:53 | 49.712
2025-03-14 | 8:53 | 49.711
2025-03-14 | 8:53 | 49.707
2025-03-14 | 8:53 | 49.705
2025-03-14 | 8:53 | 49.704
2025-03-14 | 8:53 | 49.703
2025-03-14 | 8:53 | 49.703
2025-03-14 | 8:53 | 49.702
2025-03-14 | 8:53 | 49.704
2025-03-14 | 8:53 | 49.705
2025-03-14 | 8:53 | 49.707
2025-03-14 | 8:53 | 49.708
2025-03-14 | 8:53 | 49.711
2025-03-14 | 8:53 | 49.713
2025-03-14 | 8:53 | 49.717
2025-03-14 | 8:53 | 49.721
2025-03-14 | 8:53 | 49.727
2025-03-14 | 8:53 | 49.733
2025-03-14 | 8:53 | 49.741
2025-03-14 | 8:53 | 49.749
2025-03-14 | 8:53 | 49.758
2025-03-14 | 8:53 | 49.763
2025-03-14 | 8:53 | 49.773
2025-03-14 | 8:53 | 49.778
2025-03-14 | 8:54 | 49.784
2025-03-14 | 8:54 | 49.79
2025-03-14 | 8:54 | 49.797
2025-03-14 | 8:54 | 49.802
2025-03-14 | 8:54 | 49.808
2025-03-14 | 8:54 | 49.813
2025-03-14 | 8:54 | 49.814
2025-03-14 | 8:54 | 49.815
2025-03-14 | 8:54 | 49.817
2025-03-14 | 8:54 | 49.819
2025-03-14 | 8:54 | 49.82
2025-03-14 | 8:54 | 49.82
2025-03-14 | 8:54 | 49.823
2025-03-14 | 8:54 | 49.827
2025-03-14 | 8:54 | 49.83
2025-03-14 | 8:54 | 49.831
2025-03-14 | 8:54 | 49.834
2025-03-14 | 8:54 | 49.834
2025-03-14 | 8:54 | 49.836
2025-03-14 | 8:54 | 49.836
2025-03-14 | 8:54 | 49.838
2025-03-14 | 8:54 | 49.842
2025-03-14 | 8:54 | 49.844
2025-03-14 | 8:54 | 49.846
2025-03-14 | 8:54 | 49.847
2025-03-14 | 8:54 | 49.845
2025-03-14 | 8:54 | 49.845
2025-03-14 | 8:54 | 49.845
2025-03-14 | 8:54 | 49.846
2025-03-14 | 8:54 | 49.847
2025-03-14 | 8:54 | 49.85
2025-03-14 | 8:54 | 49.851
2025-03-14 | 8:54 | 49.852
2025-03-14 | 8:54 | 49.853
2025-03-14 | 8:54 | 49.854
2025-03-14 | 8:54 | 49.854
2025-03-14 | 8:54 | 49.855
2025-03-14 | 8:54 | 49.856
2025-03-14 | 8:54 | 49.857
2025-03-14 | 8:54 | 49.856
2025-03-14 | 8:54 | 49.857
2025-03-14 | 8:54 | 49.858
2025-03-14 | 8:54 | 49.86
2025-03-14 | 8:54 | 49.862
2025-03-14 | 8:54 | 49.863
2025-03-14 | 8:54 | 49.864
2025-03-14 | 8:54 | 49.865
2025-03-14 | 8:54 | 49.865
2025-03-14 | 8:54 | 49.865
2025-03-14 | 8:54 | 49.866
2025-03-14 | 8:54 | 49.866
2025-03-14 | 8:54 | 49.867
2025-03-14 | 8:54 | 49.868
2025-03-14 | 8:54 | 49.867
2025-03-14 | 8:54 | 49.866
2025-03-14 | 8:54 | 49.864
2025-03-14 | 8:54 | 49.862
2025-03-14 | 8:54 | 49.862
2025-03-14 | 8:54 | 49.861
2025-03-14 | 8:54 | 49.862
2025-03-14 | 8:54 | 49.863
2025-03-14 | 8:55 | 49.864
2025-03-14 | 8:55 | 49.868
2025-03-14 | 8:55 | 49.869
2025-03-14 | 8:55 | 49.871
2025-03-14 | 8:55 | 49.87
2025-03-14 | 8:55 | 49.873
2025-03-14 | 8:55 | 49.873
2025-03-14 | 8:55 | 49.875
2025-03-14 | 8:55 | 49.875
2025-03-14 | 8:55 | 49.876
2025-03-14 | 8:55 | 49.874
2025-03-14 | 8:55 | 49.873
2025-03-14 | 8:55 | 49.873
2025-03-14 | 8:55 | 49.872
2025-03-14 | 8:55 | 49.872
2025-03-14 | 8:55 | 49.873
2025-03-14 | 8:55 | 49.874
2025-03-14 | 8:55 | 49.875
2025-03-14 | 8:55 | 49.876
2025-03-14 | 8:55 | 49.877
2025-03-14 | 8:55 | 49.878
2025-03-14 | 8:55 | 49.879
2025-03-14 | 8:55 | 49.879
2025-03-14 | 8:55 | 49.877
2025-03-14 | 8:55 | 49.878
2025-03-14 | 8:55 | 49.876
2025-03-14 | 8:55 | 49.877
2025-03-14 | 8:55 | 49.876
2025-03-14 | 8:55 | 49.876
2025-03-14 | 8:55 | 49.875
2025-03-14 | 8:55 | 49.873
2025-03-14 | 8:55 | 49.876
2025-03-14 | 8:55 | 49.876
2025-03-14 | 8:55 | 49.877
2025-03-14 | 8:55 | 49.878
2025-03-14 | 8:55 | 49.879
2025-03-14 | 8:55 | 49.882
2025-03-14 | 8:55 | 49.882
2025-03-14 | 8:55 | 49.883
2025-03-14 | 8:55 | 49.886
2025-03-14 | 8:55 | 49.89
2025-03-14 | 8:55 | 49.891
2025-03-14 | 8:55 | 49.892
2025-03-14 | 8:55 | 49.892
2025-03-14 | 8:55 | 49.892
2025-03-14 | 8:55 | 49.891
2025-03-14 | 8:55 | 49.889
2025-03-14 | 8:55 | 49.888
2025-03-14 | 8:55 | 49.887
2025-03-14 | 8:55 | 49.89
2025-03-14 | 8:55 | 49.892
2025-03-14 | 8:55 | 49.892
2025-03-14 | 8:55 | 49.893
2025-03-14 | 8:55 | 49.892
2025-03-14 | 8:55 | 49.893
2025-03-14 | 8:55 | 49.893
2025-03-14 | 8:55 | 49.893
2025-03-14 | 8:55 | 49.895
2025-03-14 | 8:55 | 49.894
2025-03-14 | 8:56 | 49.894
2025-03-14 | 8:56 | 49.894
2025-03-14 | 8:56 | 49.894
2025-03-14 | 8:56 | 49.891
2025-03-14 | 8:56 | 49.89
2025-03-14 | 8:56 | 49.888
2025-03-14 | 8:56 | 49.89
2025-03-14 | 8:56 | 49.888
2025-03-14 | 8:56 | 49.886
2025-03-14 | 8:56 | 49.888
2025-03-14 | 8:56 | 49.887
2025-03-14 | 8:56 | 49.887
2025-03-14 | 8:56 | 49.887
2025-03-14 | 8:56 | 49.887
2025-03-14 | 8:56 | 49.888
2025-03-14 | 8:56 | 49.887
2025-03-14 | 8:56 | 49.888
2025-03-14 | 8:56 | 49.889
2025-03-14 | 8:56 | 49.89
2025-03-14 | 8:56 | 49.889
2025-03-14 | 8:56 | 49.888
2025-03-14 | 8:56 | 49.886
2025-03-14 | 8:56 | 49.887
2025-03-14 | 8:56 | 49.888
2025-03-14 | 8:56 | 49.889
2025-03-14 | 8:56 | 49.89
2025-03-14 | 8:56 | 49.891
2025-03-14 | 8:56 | 49.892
2025-03-14 | 8:56 | 49.894
2025-03-14 | 8:56 | 49.896
2025-03-14 | 8:56 | 49.899
2025-03-14 | 8:56 | 49.9
2025-03-14 | 8:56 | 49.903
2025-03-14 | 8:56 | 49.904
2025-03-14 | 8:56 | 49.905
2025-03-14 | 8:56 | 49.907
2025-03-14 | 8:56 | 49.907
2025-03-14 | 8:56 | 49.905
2025-03-14 | 8:56 | 49.905
2025-03-14 | 8:56 | 49.904
2025-03-14 | 8:56 | 49.905
2025-03-14 | 8:56 | 49.905
2025-03-14 | 8:56 | 49.906
2025-03-14 | 8:56 | 49.908
2025-03-14 | 8:56 | 49.91
2025-03-14 | 8:56 | 49.91
2025-03-14 | 8:56 | 49.913
2025-03-14 | 8:56 | 49.913
2025-03-14 | 8:56 | 49.917
2025-03-14 | 8:56 | 49.917
2025-03-14 | 8:56 | 49.919
2025-03-14 | 8:56 | 49.921
2025-03-14 | 8:56 | 49.922
2025-03-14 | 8:56 | 49.921
2025-03-14 | 8:56 | 49.921
2025-03-14 | 8:56 | 49.921
2025-03-14 | 8:56 | 49.921
2025-03-14 | 8:56 | 49.92
2025-03-14 | 8:56 | 49.922
2025-03-14 | 8:56 | 49.923
2025-03-14 | 8:56 | 49.922
2025-03-14 | 8:57 | 49.921
2025-03-14 | 8:57 | 49.921
2025-03-14 | 8:57 | 49.922
2025-03-14 | 8:57 | 49.924
2025-03-14 | 8:57 | 49.924
2025-03-14 | 8:57 | 49.924
2025-03-14 | 8:57 | 49.923
2025-03-14 | 8:57 | 49.923
2025-03-14 | 8:57 | 49.923
2025-03-14 | 8:57 | 49.924
2025-03-14 | 8:57 | 49.923
2025-03-14 | 8:57 | 49.924
2025-03-14 | 8:57 | 49.924
2025-03-14 | 8:57 | 49.922
2025-03-14 | 8:57 | 49.92
2025-03-14 | 8:57 | 49.919
2025-03-14 | 8:57 | 49.92
2025-03-14 | 8:57 | 49.919
2025-03-14 | 8:57 | 49.917
2025-03-14 | 8:57 | 49.915
2025-03-14 | 8:57 | 49.915
2025-03-14 | 8:57 | 49.915
2025-03-14 | 8:57 | 49.914
2025-03-14 | 8:57 | 49.911
2025-03-14 | 8:57 | 49.909
2025-03-14 | 8:57 | 49.909
2025-03-14 | 8:57 | 49.908
2025-03-14 | 8:57 | 49.909
2025-03-14 | 8:57 | 49.908
2025-03-14 | 8:57 | 49.907
2025-03-14 | 8:57 | 49.905
2025-03-14 | 8:57 | 49.903
2025-03-14 | 8:57 | 49.901
2025-03-14 | 8:57 | 49.9
2025-03-14 | 8:57 | 49.9
2025-03-14 | 8:57 | 49.902
2025-03-14 | 8:57 | 49.902
2025-03-14 | 8:57 | 49.904
2025-03-14 | 8:57 | 49.906
2025-03-14 | 8:57 | 49.909
2025-03-14 | 8:57 | 49.91
2025-03-14 | 8:57 | 49.91
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.911
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.914
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.913
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.911
2025-03-14 | 8:57 | 49.91
2025-03-14 | 8:57 | 49.912
2025-03-14 | 8:57 | 49.913
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.913
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.915
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.913
2025-03-14 | 8:58 | 49.911
2025-03-14 | 8:58 | 49.912
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.916
2025-03-14 | 8:58 | 49.915
2025-03-14 | 8:58 | 49.916
2025-03-14 | 8:58 | 49.916
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.918
2025-03-14 | 8:58 | 49.918
2025-03-14 | 8:58 | 49.92
2025-03-14 | 8:58 | 49.919
2025-03-14 | 8:58 | 49.918
2025-03-14 | 8:58 | 49.918
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.916
2025-03-14 | 8:58 | 49.92
2025-03-14 | 8:58 | 49.92
2025-03-14 | 8:58 | 49.919
2025-03-14 | 8:58 | 49.919
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.916
2025-03-14 | 8:58 | 49.915
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.915
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.912
2025-03-14 | 8:58 | 49.91
2025-03-14 | 8:58 | 49.909
2025-03-14 | 8:58 | 49.909
2025-03-14 | 8:58 | 49.91
2025-03-14 | 8:58 | 49.91
2025-03-14 | 8:58 | 49.912
2025-03-14 | 8:58 | 49.913
2025-03-14 | 8:58 | 49.914
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.917
2025-03-14 | 8:58 | 49.919
2025-03-14 | 8:58 | 49.922
2025-03-14 | 8:58 | 49.923
2025-03-14 | 8:58 | 49.927
2025-03-14 | 8:58 | 49.929
2025-03-14 | 8:58 | 49.929
2025-03-14 | 8:58 | 49.931
2025-03-14 | 8:59 | 49.932
2025-03-14 | 8:59 | 49.932
2025-03-14 | 8:59 | 49.934
2025-03-14 | 8:59 | 49.936
2025-03-14 | 8:59 | 49.939
2025-03-14 | 8:59 | 49.941
2025-03-14 | 8:59 | 49.945
2025-03-14 | 8:59 | 49.949
2025-03-14 | 8:59 | 49.951
2025-03-14 | 8:59 | 49.954
2025-03-14 | 8:59 | 49.957
2025-03-14 | 8:59 | 49.96
2025-03-14 | 8:59 | 49.962
2025-03-14 | 8:59 | 49.962
2025-03-14 | 8:59 | 49.962
2025-03-14 | 8:59 | 49.962
2025-03-14 | 8:59 | 49.962
2025-03-14 | 8:59 | 49.96
2025-03-14 | 8:59 | 49.958
2025-03-14 | 8:59 | 49.956
2025-03-14 | 8:59 | 49.955
2025-03-14 | 8:59 | 49.954
2025-03-14 | 8:59 | 49.954
2025-03-14 | 8:59 | 49.954
2025-03-14 | 8:59 | 49.952
2025-03-14 | 8:59 | 49.953
2025-03-14 | 8:59 | 49.952
2025-03-14 | 8:59 | 49.951
2025-03-14 | 8:59 | 49.95
2025-03-14 | 8:59 | 49.948
2025-03-14 | 8:59 | 49.941
2025-03-14 | 8:59 | 49.935
2025-03-14 | 8:59 | 49.93
2025-03-14 | 8:59 | 49.928
2025-03-14 | 8:59 | 49.927
2025-03-14 | 8:59 | 49.926
2025-03-14 | 8:59 | 49.925
2025-03-14 | 8:59 | 49.925
2025-03-14 | 8:59 | 49.925
2025-03-14 | 8:59 | 49.924
2025-03-14 | 8:59 | 49.926
2025-03-14 | 8:59 | 49.928
2025-03-14 | 8:59 | 49.93
2025-03-14 | 8:59 | 49.93
2025-03-14 | 8:59 | 49.929
2025-03-14 | 8:59 | 49.928
2025-03-14 | 8:59 | 49.928
2025-03-14 | 8:59 | 49.929
2025-03-14 | 8:59 | 49.929
2025-03-14 | 8:59 | 49.928
2025-03-14 | 8:59 | 49.928
2025-03-14 | 8:59 | 49.925
2025-03-14 | 8:59 | 49.922
2025-03-14 | 8:59 | 49.919
2025-03-14 | 8:59 | 49.918
2025-03-14 | 8:59 | 49.917
2025-03-14 | 8:59 | 49.917
2025-03-14 | 8:59 | 49.919
2025-03-14 | 8:59 | 49.921
2025-03-14 | 9:00 | 49.926
2025-03-14 | 9:00 | 49.928
2025-03-14 | 9:00 | 49.929
2025-03-14 | 9:00 | 49.931
2025-03-14 | 9:00 | 49.932
2025-03-14 | 9:00 | 49.933
2025-03-14 | 9:00 | 49.932
2025-03-14 | 9:00 | 49.935
2025-03-14 | 9:00 | 49.934
2025-03-14 | 9:00 | 49.934
2025-03-14 | 9:00 | 49.934
2025-03-14 | 9:00 | 49.932
2025-03-14 | 9:00 | 49.93
2025-03-14 | 9:00 | 49.929
2025-03-14 | 9:00 | 49.927
2025-03-14 | 9:00 | 49.925
2025-03-14 | 9:00 | 49.924
2025-03-14 | 9:00 | 49.923
2025-03-14 | 9:00 | 49.923
2025-03-14 | 9:00 | 49.924
2025-03-14 | 9:00 | 49.923
2025-03-14 | 9:00 | 49.924
2025-03-14 | 9:00 | 49.923
2025-03-14 | 9:00 | 49.924
2025-03-14 | 9:00 | 49.922
2025-03-14 | 9:00 | 49.925
2025-03-14 | 9:00 | 49.925
2025-03-14 | 9:00 | 49.925
2025-03-14 | 9:00 | 49.923
2025-03-14 | 9:00 | 49.922
2025-03-14 | 9:00 | 49.918
2025-03-14 | 9:00 | 49.911
2025-03-14 | 9:00 | 49.9
2025-03-14 | 9:00 | 49.891
2025-03-14 | 9:00 | 49.887
2025-03-14 | 9:00 | 49.885
2025-03-14 | 9:00 | 49.885
2025-03-14 | 9:00 | 49.885
2025-03-14 | 9:00 | 49.885
2025-03-14 | 9:00 | 49.886
2025-03-14 | 9:00 | 49.888
2025-03-14 | 9:00 | 49.888
2025-03-14 | 9:00 | 49.887
2025-03-14 | 9:00 | 49.887
2025-03-14 | 9:00 | 49.887
2025-03-14 | 9:00 | 49.889
2025-03-14 | 9:00 | 49.887
2025-03-14 | 9:00 | 49.886
2025-03-14 | 9:00 | 49.884
2025-03-14 | 9:00 | 49.877
2025-03-14 | 9:00 | 49.871
2025-03-14 | 9:00 | 49.865
2025-03-14 | 9:00 | 49.862
2025-03-14 | 9:00 | 49.859
2025-03-14 | 9:00 | 49.857
2025-03-14 | 9:00 | 49.856
2025-03-14 | 9:00 | 49.855
2025-03-14 | 9:00 | 49.855
2025-03-14 | 9:00 | 49.855
2025-03-14 | 9:00 | 49.856
2025-03-14 | 9:00 | 49.856
2025-03-14 | 9:01 | 49.857
2025-03-14 | 9:01 | 49.857
2025-03-14 | 9:01 | 49.857
2025-03-14 | 9:01 | 49.857
2025-03-14 | 9:01 | 49.856
2025-03-14 | 9:01 | 49.857
2025-03-14 | 9:01 | 49.858
2025-03-14 | 9:01 | 49.859
2025-03-14 | 9:01 | 49.86
2025-03-14 | 9:01 | 49.859
2025-03-14 | 9:01 | 49.858
2025-03-14 | 9:01 | 49.858
2025-03-14 | 9:01 | 49.86
2025-03-14 | 9:01 | 49.861
2025-03-14 | 9:01 | 49.865
2025-03-14 | 9:01 | 49.867
2025-03-14 | 9:01 | 49.871
2025-03-14 | 9:01 | 49.873
2025-03-14 | 9:01 | 49.874
2025-03-14 | 9:01 | 49.873
2025-03-14 | 9:01 | 49.874
2025-03-14 | 9:01 | 49.875
2025-03-14 | 9:01 | 49.876
2025-03-14 | 9:01 | 49.874
2025-03-14 | 9:01 | 49.874
2025-03-14 | 9:01 | 49.875
2025-03-14 | 9:01 | 49.874
2025-03-14 | 9:01 | 49.876
2025-03-14 | 9:01 | 49.878
2025-03-14 | 9:01 | 49.878
2025-03-14 | 9:01 | 49.877
2025-03-14 | 9:01 | 49.877
2025-03-14 | 9:01 | 49.879
2025-03-14 | 9:01 | 49.877
2025-03-14 | 9:01 | 49.877
2025-03-14 | 9:01 | 49.876
2025-03-14 | 9:01 | 49.872
2025-03-14 | 9:01 | 49.872
2025-03-14 | 9:01 | 49.871
2025-03-14 | 9:01 | 49.87
2025-03-14 | 9:01 | 49.872
2025-03-14 | 9:01 | 49.873
2025-03-14 | 9:01 | 49.873
2025-03-14 | 9:01 | 49.875
2025-03-14 | 9:01 | 49.875
2025-03-14 | 9:01 | 49.876
2025-03-14 | 9:01 | 49.878
2025-03-14 | 9:01 | 49.875
2025-03-14 | 9:01 | 49.876
2025-03-14 | 9:01 | 49.877
2025-03-14 | 9:01 | 49.878
2025-03-14 | 9:01 | 49.879
2025-03-14 | 9:01 | 49.88
2025-03-14 | 9:01 | 49.878
2025-03-14 | 9:01 | 49.878
2025-03-14 | 9:01 | 49.882
2025-03-14 | 9:01 | 49.883
2025-03-14 | 9:01 | 49.885
2025-03-14 | 9:01 | 49.889
2025-03-14 | 9:02 | 49.89
2025-03-14 | 9:02 | 49.889
2025-03-14 | 9:02 | 49.889
2025-03-14 | 9:02 | 49.889
2025-03-14 | 9:02 | 49.89
2025-03-14 | 9:02 | 49.892
2025-03-14 | 9:02 | 49.893
2025-03-14 | 9:02 | 49.893
2025-03-14 | 9:02 | 49.892
2025-03-14 | 9:02 | 49.892
2025-03-14 | 9:02 | 49.892
2025-03-14 | 9:02 | 49.893
2025-03-14 | 9:02 | 49.895
2025-03-14 | 9:02 | 49.898
2025-03-14 | 9:02 | 49.898
2025-03-14 | 9:02 | 49.902
2025-03-14 | 9:02 | 49.903
2025-03-14 | 9:02 | 49.906
2025-03-14 | 9:02 | 49.909
2025-03-14 | 9:02 | 49.913
2025-03-14 | 9:02 | 49.914
2025-03-14 | 9:02 | 49.914
2025-03-14 | 9:02 | 49.913
2025-03-14 | 9:02 | 49.913
2025-03-14 | 9:02 | 49.914
2025-03-14 | 9:02 | 49.915
2025-03-14 | 9:02 | 49.916
2025-03-14 | 9:02 | 49.917
2025-03-14 | 9:02 | 49.918
2025-03-14 | 9:02 | 49.917
2025-03-14 | 9:02 | 49.917
2025-03-14 | 9:02 | 49.918
2025-03-14 | 9:02 | 49.921
2025-03-14 | 9:02 | 49.924
2025-03-14 | 9:02 | 49.927
2025-03-14 | 9:02 | 49.929
2025-03-14 | 9:02 | 49.931
2025-03-14 | 9:02 | 49.93
2025-03-14 | 9:02 | 49.93
2025-03-14 | 9:02 | 49.931
2025-03-14 | 9:02 | 49.928
2025-03-14 | 9:02 | 49.927
2025-03-14 | 9:02 | 49.927
2025-03-14 | 9:02 | 49.926
2025-03-14 | 9:02 | 49.924
2025-03-14 | 9:02 | 49.922
2025-03-14 | 9:02 | 49.921
2025-03-14 | 9:02 | 49.92
2025-03-14 | 9:02 | 49.923
2025-03-14 | 9:02 | 49.924
2025-03-14 | 9:02 | 49.925
2025-03-14 | 9:02 | 49.924
2025-03-14 | 9:02 | 49.926
2025-03-14 | 9:02 | 49.926
2025-03-14 | 9:02 | 49.924
2025-03-14 | 9:02 | 49.924
2025-03-14 | 9:02 | 49.923
2025-03-14 | 9:02 | 49.922
2025-03-14 | 9:02 | 49.923
2025-03-14 | 9:02 | 49.924
2025-03-14 | 9:02 | 49.93
2025-03-14 | 9:03 | 49.932
2025-03-14 | 9:03 | 49.934
2025-03-14 | 9:03 | 49.938
2025-03-14 | 9:03 | 49.939
2025-03-14 | 9:03 | 49.94
2025-03-14 | 9:03 | 49.941
2025-03-14 | 9:03 | 49.939
2025-03-14 | 9:03 | 49.939
2025-03-14 | 9:03 | 49.937
2025-03-14 | 9:03 | 49.938
2025-03-14 | 9:03 | 49.938
2025-03-14 | 9:03 | 49.939
2025-03-14 | 9:03 | 49.941
2025-03-14 | 9:03 | 49.941
2025-03-14 | 9:03 | 49.942
2025-03-14 | 9:03 | 49.941
2025-03-14 | 9:03 | 49.941
2025-03-14 | 9:03 | 49.942
2025-03-14 | 9:03 | 49.941
2025-03-14 | 9:03 | 49.94
2025-03-14 | 9:03 | 49.937
2025-03-14 | 9:03 | 49.936
2025-03-14 | 9:03 | 49.934
2025-03-14 | 9:03 | 49.932
2025-03-14 | 9:03 | 49.932
2025-03-14 | 9:03 | 49.933
2025-03-14 | 9:03 | 49.935
2025-03-14 | 9:03 | 49.936
2025-03-14 | 9:03 | 49.935
2025-03-14 | 9:03 | 49.934
2025-03-14 | 9:03 | 49.932
2025-03-14 | 9:03 | 49.931
2025-03-14 | 9:03 | 49.931
2025-03-14 | 9:03 | 49.932
2025-03-14 | 9:03 | 49.933
2025-03-14 | 9:03 | 49.932
2025-03-14 | 9:03 | 49.935
2025-03-14 | 9:03 | 49.933
2025-03-14 | 9:03 | 49.933
2025-03-14 | 9:03 | 49.935
2025-03-14 | 9:03 | 49.937
2025-03-14 | 9:03 | 49.936
2025-03-14 | 9:03 | 49.941
2025-03-14 | 9:03 | 49.94
2025-03-14 | 9:03 | 49.941
2025-03-14 | 9:03 | 49.943
2025-03-14 | 9:03 | 49.948
2025-03-14 | 9:03 | 49.952
2025-03-14 | 9:03 | 49.955
2025-03-14 | 9:03 | 49.956
2025-03-14 | 9:03 | 49.957
2025-03-14 | 9:03 | 49.955
2025-03-14 | 9:03 | 49.953
2025-03-14 | 9:03 | 49.952
2025-03-14 | 9:03 | 49.95
2025-03-14 | 9:03 | 49.951
2025-03-14 | 9:03 | 49.95
2025-03-14 | 9:03 | 49.953
2025-03-14 | 9:03 | 49.959
2025-03-14 | 9:04 | 49.965
2025-03-14 | 9:04 | 49.969
2025-03-14 | 9:04 | 49.974
2025-03-14 | 9:04 | 49.982
2025-03-14 | 9:04 | 49.985
2025-03-14 | 9:04 | 49.989
2025-03-14 | 9:04 | 49.997
2025-03-14 | 9:04 | 50
2025-03-14 | 9:04 | 50.006
2025-03-14 | 9:04 | 50.009
2025-03-14 | 9:04 | 50.014
2025-03-14 | 9:04 | 50.013
2025-03-14 | 9:04 | 50.013
2025-03-14 | 9:04 | 50.015
2025-03-14 | 9:04 | 50.015
2025-03-14 | 9:04 | 50.015
2025-03-14 | 9:04 | 50.015
2025-03-14 | 9:04 | 50.017
2025-03-14 | 9:04 | 50.018
2025-03-14 | 9:04 | 50.018
2025-03-14 | 9:04 | 50.019
2025-03-14 | 9:04 | 50.024
2025-03-14 | 9:04 | 50.026
2025-03-14 | 9:04 | 50.03
2025-03-14 | 9:04 | 50.031
2025-03-14 | 9:04 | 50.033
2025-03-14 | 9:04 | 50.035
2025-03-14 | 9:04 | 50.035
2025-03-14 | 9:04 | 50.038
2025-03-14 | 9:04 | 50.037
2025-03-14 | 9:04 | 50.038
2025-03-14 | 9:04 | 50.038
2025-03-14 | 9:04 | 50.04
2025-03-14 | 9:04 | 50.04
2025-03-14 | 9:04 | 50.042
2025-03-14 | 9:04 | 50.044
2025-03-14 | 9:04 | 50.047
2025-03-14 | 9:04 | 50.047
2025-03-14 | 9:04 | 50.049
2025-03-14 | 9:04 | 50.046
2025-03-14 | 9:04 | 50.044
2025-03-14 | 9:04 | 50.043
2025-03-14 | 9:04 | 50.039
2025-03-14 | 9:04 | 50.039
2025-03-14 | 9:04 | 50.039
2025-03-14 | 9:04 | 50.038
2025-03-14 | 9:04 | 50.036
2025-03-14 | 9:04 | 50.034
2025-03-14 | 9:04 | 50.033
2025-03-14 | 9:04 | 50.031
2025-03-14 | 9:04 | 50.03
2025-03-14 | 9:04 | 50.027
2025-03-14 | 9:04 | 50.027
2025-03-14 | 9:04 | 50.028
2025-03-14 | 9:04 | 50.029
2025-03-14 | 9:04 | 50.031
2025-03-14 | 9:04 | 50.034
2025-03-14 | 9:04 | 50.034
2025-03-14 | 9:04 | 50.038
2025-03-14 | 9:04 | 50.04
2025-03-14 | 9:04 | 50.043
2025-03-14 | 9:05 | 50.044
2025-03-14 | 9:05 | 50.044
2025-03-14 | 9:05 | 50.046
2025-03-14 | 9:05 | 50.045
2025-03-14 | 9:05 | 50.046
2025-03-14 | 9:05 | 50.046
2025-03-14 | 9:05 | 50.045

## 20250314-2
In GMT
Date | Time | Freq
2025-03-14 | 22:08 | 50.027 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-14 | 22:08 | 50.028 | 222 | BRITNED | 676.211
2025-03-14 | 22:08 | 50.03 | 268 | WBURB-2 | 428.156
2025-03-14 | 22:08 | 50.031 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-14 | 22:08 | 50.032 |  | Viking Link | -648.9
2025-03-14 | 22:08 | 50.032 |  | Viking Link | 1398.96
2025-03-14 | 22:08 | 50.029 | 209 | DRAXX-3 | 626.95
2025-03-14 | 22:08 | 50.024 | 154 | CDCL-1 | 391.57
2025-03-14 | 22:08 | 50.021 | 268 | ROCK-1 | 468.495
2025-03-14 | 22:08 | 50.018 | 148 | IFA Bipole1 | 945.473
2025-03-14 | 22:08 | 50.02 | 132 | IFA Bipole1 | 999.1
2025-03-14 | 22:08 | 50.019 | 141 | IFA Bipole2 | 1000
2025-03-14 | 22:08 | 50.019 | 135 | IFA Bipole1 | 996.75
2025-03-14 | 22:08 | 50.018 |  | Viking Link | -780.3
2025-03-14 | 22:08 | 50.019
2025-03-14 | 22:08 | 50.019
2025-03-14 | 22:08 | 50.022
2025-03-14 | 22:08 | 50.023
2025-03-14 | 22:08 | 50.023
2025-03-14 | 22:08 | 50.024 | 130 | HEYM12 | 271.908
2025-03-14 | 22:08 | 50.025 | 228 | HUMR-1 | 303.75
2025-03-14 | 22:08 | 50.027
2025-03-14 | 22:08 | 50.026
2025-03-14 | 22:08 | 50.026
2025-03-14 | 22:08 | 50.027
2025-03-14 | 22:08 | 50.027
2025-03-14 | 22:08 | 50.027
2025-03-14 | 22:08 | 50.028
2025-03-14 | 22:08 | 50.029
2025-03-14 | 22:08 | 50.03
2025-03-14 | 22:08 | 50.029 | 211 | CDCL-1 | 291.5
2025-03-14 | 22:08 | 50.027 | 199 | STAY-2 | 413.125
2025-03-14 | 22:08 | 50.025 | 173 | CDCL-1 | 397.375
2025-03-14 | 22:08 | 50.022 | 248 | SEAB-2 | 361.25
2025-03-14 | 22:08 | 50.02 | 255 | FRANCE | 995.65
2025-03-14 | 22:08 | 50.018 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-14 | 22:09 | 50.018
2025-03-14 | 22:09 | 50.02
2025-03-14 | 22:09 | 50.021
2025-03-14 | 22:09 | 50.024
2025-03-14 | 22:09 | 50.027
2025-03-14 | 22:09 | 50.026
2025-03-14 | 22:09 | 50.025
2025-03-14 | 22:09 | 50.024
2025-03-14 | 22:09 | 50.022
2025-03-14 | 22:09 | 50.02
2025-03-14 | 22:09 | 50.017
2025-03-14 | 22:09 | 50.016
2025-03-14 | 22:09 | 50.012
2025-03-14 | 22:09 | 50.009
2025-03-14 | 22:09 | 50.006
2025-03-14 | 22:09 | 50.004
2025-03-14 | 22:09 | 50.005
2025-03-14 | 22:09 | 50.004
2025-03-14 | 22:09 | 50.006
2025-03-14 | 22:09 | 50.008
2025-03-14 | 22:09 | 50.01
2025-03-14 | 22:09 | 50.013
2025-03-14 | 22:09 | 50.016
2025-03-14 | 22:09 | 50.02
2025-03-14 | 22:09 | 50.022
2025-03-14 | 22:09 | 50
2025-03-14 | 22:09 | 49.964
2025-03-14 | 22:09 | 49.938
2025-03-14 | 22:09 | 49.921
2025-03-14 | 22:09 | 49.912
2025-03-14 | 22:09 | 49.907
2025-03-14 | 22:09 | 49.905
2025-03-14 | 22:09 | 49.904
2025-03-14 | 22:09 | 49.904
2025-03-14 | 22:09 | 49.903
2025-03-14 | 22:09 | 49.902
2025-03-14 | 22:09 | 49.901
2025-03-14 | 22:09 | 49.901
2025-03-14 | 22:09 | 49.9
2025-03-14 | 22:09 | 49.898
2025-03-14 | 22:09 | 49.898
2025-03-14 | 22:09 | 49.899
2025-03-14 | 22:09 | 49.899
2025-03-14 | 22:09 | 49.9
2025-03-14 | 22:09 | 49.9
2025-03-14 | 22:09 | 49.899
2025-03-14 | 22:09 | 49.898
2025-03-14 | 22:09 | 49.896
2025-03-14 | 22:09 | 49.894
2025-03-14 | 22:09 | 49.892
2025-03-14 | 22:09 | 49.889
2025-03-14 | 22:09 | 49.885
2025-03-14 | 22:09 | 49.883
2025-03-14 | 22:09 | 49.882
2025-03-14 | 22:09 | 49.883
2025-03-14 | 22:09 | 49.884
2025-03-14 | 22:09 | 49.884
2025-03-14 | 22:09 | 49.883
2025-03-14 | 22:09 | 49.882
2025-03-14 | 22:10 | 49.882
2025-03-14 | 22:10 | 49.88
2025-03-14 | 22:10 | 49.88
2025-03-14 | 22:10 | 49.881
2025-03-14 | 22:10 | 49.881
2025-03-14 | 22:10 | 49.882
2025-03-14 | 22:10 | 49.882
2025-03-14 | 22:10 | 49.885
2025-03-14 | 22:10 | 49.886
2025-03-14 | 22:10 | 49.888
2025-03-14 | 22:10 | 49.889
2025-03-14 | 22:10 | 49.89
2025-03-14 | 22:10 | 49.89
2025-03-14 | 22:10 | 49.891
2025-03-14 | 22:10 | 49.891
2025-03-14 | 22:10 | 49.892
2025-03-14 | 22:10 | 49.89
2025-03-14 | 22:10 | 49.892
2025-03-14 | 22:10 | 49.894
2025-03-14 | 22:10 | 49.895
2025-03-14 | 22:10 | 49.895
2025-03-14 | 22:10 | 49.895
2025-03-14 | 22:10 | 49.895
2025-03-14 | 22:10 | 49.894
2025-03-14 | 22:10 | 49.894
2025-03-14 | 22:10 | 49.893
2025-03-14 | 22:10 | 49.891
2025-03-14 | 22:10 | 49.89
2025-03-14 | 22:10 | 49.889
2025-03-14 | 22:10 | 49.888
2025-03-14 | 22:10 | 49.886
2025-03-14 | 22:10 | 49.885
2025-03-14 | 22:10 | 49.885
2025-03-14 | 22:10 | 49.886
2025-03-14 | 22:10 | 49.886
2025-03-14 | 22:10 | 49.887
2025-03-14 | 22:10 | 49.889
2025-03-14 | 22:10 | 49.89
2025-03-14 | 22:10 | 49.888
2025-03-14 | 22:10 | 49.887
2025-03-14 | 22:10 | 49.887
2025-03-14 | 22:10 | 49.887
2025-03-14 | 22:10 | 49.888
2025-03-14 | 22:10 | 49.888
2025-03-14 | 22:10 | 49.888
2025-03-14 | 22:10 | 49.887
2025-03-14 | 22:10 | 49.887
2025-03-14 | 22:10 | 49.888
2025-03-14 | 22:10 | 49.888
2025-03-14 | 22:10 | 49.887
2025-03-14 | 22:10 | 49.888
2025-03-14 | 22:10 | 49.886
2025-03-14 | 22:10 | 49.886
2025-03-14 | 22:10 | 49.885
2025-03-14 | 22:10 | 49.885
2025-03-14 | 22:10 | 49.886
2025-03-14 | 22:10 | 49.885
2025-03-14 | 22:10 | 49.885
2025-03-14 | 22:10 | 49.887
2025-03-14 | 22:10 | 49.889
2025-03-14 | 22:10 | 49.888
2025-03-14 | 22:11 | 49.888
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.89
2025-03-14 | 22:11 | 49.89
2025-03-14 | 22:11 | 49.89
2025-03-14 | 22:11 | 49.891
2025-03-14 | 22:11 | 49.893
2025-03-14 | 22:11 | 49.894
2025-03-14 | 22:11 | 49.896
2025-03-14 | 22:11 | 49.896
2025-03-14 | 22:11 | 49.896
2025-03-14 | 22:11 | 49.897
2025-03-14 | 22:11 | 49.897
2025-03-14 | 22:11 | 49.899
2025-03-14 | 22:11 | 49.899
2025-03-14 | 22:11 | 49.897
2025-03-14 | 22:11 | 49.895
2025-03-14 | 22:11 | 49.894
2025-03-14 | 22:11 | 49.893
2025-03-14 | 22:11 | 49.891
2025-03-14 | 22:11 | 49.891
2025-03-14 | 22:11 | 49.891
2025-03-14 | 22:11 | 49.893
2025-03-14 | 22:11 | 49.892
2025-03-14 | 22:11 | 49.892
2025-03-14 | 22:11 | 49.891
2025-03-14 | 22:11 | 49.891
2025-03-14 | 22:11 | 49.891
2025-03-14 | 22:11 | 49.89
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.89
2025-03-14 | 22:11 | 49.892
2025-03-14 | 22:11 | 49.892
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.891
2025-03-14 | 22:11 | 49.89
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.887
2025-03-14 | 22:11 | 49.886
2025-03-14 | 22:11 | 49.886
2025-03-14 | 22:11 | 49.884
2025-03-14 | 22:11 | 49.883
2025-03-14 | 22:11 | 49.882
2025-03-14 | 22:11 | 49.884
2025-03-14 | 22:11 | 49.885
2025-03-14 | 22:11 | 49.887
2025-03-14 | 22:11 | 49.889
2025-03-14 | 22:11 | 49.891
2025-03-14 | 22:11 | 49.895
2025-03-14 | 22:11 | 49.898
2025-03-14 | 22:11 | 49.899
2025-03-14 | 22:11 | 49.898
2025-03-14 | 22:11 | 49.898
2025-03-14 | 22:12 | 49.898
2025-03-14 | 22:12 | 49.897
2025-03-14 | 22:12 | 49.896
2025-03-14 | 22:12 | 49.897
2025-03-14 | 22:12 | 49.898
2025-03-14 | 22:12 | 49.895
2025-03-14 | 22:12 | 49.895
2025-03-14 | 22:12 | 49.895
2025-03-14 | 22:12 | 49.897
2025-03-14 | 22:12 | 49.897
2025-03-14 | 22:12 | 49.898
2025-03-14 | 22:12 | 49.898
2025-03-14 | 22:12 | 49.899
2025-03-14 | 22:12 | 49.904
2025-03-14 | 22:12 | 49.91
2025-03-14 | 22:12 | 49.912
2025-03-14 | 22:12 | 49.914
2025-03-14 | 22:12 | 49.914
2025-03-14 | 22:12 | 49.916
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.916
2025-03-14 | 22:12 | 49.918
2025-03-14 | 22:12 | 49.918
2025-03-14 | 22:12 | 49.918
2025-03-14 | 22:12 | 49.919
2025-03-14 | 22:12 | 49.919
2025-03-14 | 22:12 | 49.916
2025-03-14 | 22:12 | 49.916
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.913
2025-03-14 | 22:12 | 49.912
2025-03-14 | 22:12 | 49.912
2025-03-14 | 22:12 | 49.914
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.916
2025-03-14 | 22:12 | 49.916
2025-03-14 | 22:12 | 49.917
2025-03-14 | 22:12 | 49.916
2025-03-14 | 22:12 | 49.918
2025-03-14 | 22:12 | 49.919
2025-03-14 | 22:12 | 49.92
2025-03-14 | 22:12 | 49.919
2025-03-14 | 22:12 | 49.92
2025-03-14 | 22:12 | 49.918
2025-03-14 | 22:12 | 49.918
2025-03-14 | 22:12 | 49.917
2025-03-14 | 22:12 | 49.917
2025-03-14 | 22:12 | 49.916
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.915
2025-03-14 | 22:12 | 49.914
2025-03-14 | 22:12 | 49.913
2025-03-14 | 22:12 | 49.916
2025-03-14 | 22:13 | 49.919
2025-03-14 | 22:13 | 49.921
2025-03-14 | 22:13 | 49.923
2025-03-14 | 22:13 | 49.925
2025-03-14 | 22:13 | 49.924
2025-03-14 | 22:13 | 49.924
2025-03-14 | 22:13 | 49.923
2025-03-14 | 22:13 | 49.924
2025-03-14 | 22:13 | 49.926
2025-03-14 | 22:13 | 49.927
2025-03-14 | 22:13 | 49.928
2025-03-14 | 22:13 | 49.928
2025-03-14 | 22:13 | 49.928
2025-03-14 | 22:13 | 49.927
2025-03-14 | 22:13 | 49.927
2025-03-14 | 22:13 | 49.924
2025-03-14 | 22:13 | 49.923
2025-03-14 | 22:13 | 49.921
2025-03-14 | 22:13 | 49.919
2025-03-14 | 22:13 | 49.916
2025-03-14 | 22:13 | 49.916
2025-03-14 | 22:13 | 49.914
2025-03-14 | 22:13 | 49.916
2025-03-14 | 22:13 | 49.918
2025-03-14 | 22:13 | 49.92
2025-03-14 | 22:13 | 49.921
2025-03-14 | 22:13 | 49.919
2025-03-14 | 22:13 | 49.919
2025-03-14 | 22:13 | 49.919
2025-03-14 | 22:13 | 49.92
2025-03-14 | 22:13 | 49.921
2025-03-14 | 22:13 | 49.923
2025-03-14 | 22:13 | 49.923
2025-03-14 | 22:13 | 49.927
2025-03-14 | 22:13 | 49.928
2025-03-14 | 22:13 | 49.928
2025-03-14 | 22:13 | 49.928
2025-03-14 | 22:13 | 49.927
2025-03-14 | 22:13 | 49.927
2025-03-14 | 22:13 | 49.926
2025-03-14 | 22:13 | 49.924
2025-03-14 | 22:13 | 49.923
2025-03-14 | 22:13 | 49.925
2025-03-14 | 22:13 | 49.926
2025-03-14 | 22:13 | 49.927
2025-03-14 | 22:13 | 49.926
2025-03-14 | 22:13 | 49.928
2025-03-14 | 22:13 | 49.93
2025-03-14 | 22:13 | 49.931
2025-03-14 | 22:13 | 49.932
2025-03-14 | 22:13 | 49.932
2025-03-14 | 22:13 | 49.931
2025-03-14 | 22:13 | 49.933
2025-03-14 | 22:13 | 49.934
2025-03-14 | 22:13 | 49.935
2025-03-14 | 22:13 | 49.936
2025-03-14 | 22:13 | 49.937
2025-03-14 | 22:13 | 49.939
2025-03-14 | 22:13 | 49.94
2025-03-14 | 22:14 | 49.941
2025-03-14 | 22:14 | 49.94
2025-03-14 | 22:14 | 49.94
2025-03-14 | 22:14 | 49.941
2025-03-14 | 22:14 | 49.939
2025-03-14 | 22:14 | 49.939
2025-03-14 | 22:14 | 49.939
2025-03-14 | 22:14 | 49.938
2025-03-14 | 22:14 | 49.939
2025-03-14 | 22:14 | 49.94
2025-03-14 | 22:14 | 49.942
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.943
2025-03-14 | 22:14 | 49.941
2025-03-14 | 22:14 | 49.939
2025-03-14 | 22:14 | 49.938
2025-03-14 | 22:14 | 49.937
2025-03-14 | 22:14 | 49.934
2025-03-14 | 22:14 | 49.933
2025-03-14 | 22:14 | 49.935
2025-03-14 | 22:14 | 49.937
2025-03-14 | 22:14 | 49.937
2025-03-14 | 22:14 | 49.938
2025-03-14 | 22:14 | 49.942
2025-03-14 | 22:14 | 49.943
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.943
2025-03-14 | 22:14 | 49.943
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.944
2025-03-14 | 22:14 | 49.945
2025-03-14 | 22:14 | 49.947
2025-03-14 | 22:14 | 49.948
2025-03-14 | 22:14 | 49.951
2025-03-14 | 22:14 | 49.954
2025-03-14 | 22:14 | 49.957
2025-03-14 | 22:14 | 49.959
2025-03-14 | 22:14 | 49.962
2025-03-14 | 22:14 | 49.964
2025-03-14 | 22:14 | 49.965
2025-03-14 | 22:14 | 49.966
2025-03-14 | 22:14 | 49.965
2025-03-14 | 22:14 | 49.965
2025-03-14 | 22:14 | 49.963
2025-03-14 | 22:15 | 49.963
2025-03-14 | 22:15 | 49.961
2025-03-14 | 22:15 | 49.962
2025-03-14 | 22:15 | 49.962
2025-03-14 | 22:15 | 49.962
2025-03-14 | 22:15 | 49.962
2025-03-14 | 22:15 | 49.963
2025-03-14 | 22:15 | 49.964
2025-03-14 | 22:15 | 49.965
2025-03-14 | 22:15 | 49.964
2025-03-14 | 22:15 | 49.964
2025-03-14 | 22:15 | 49.966
2025-03-14 | 22:15 | 49.967
2025-03-14 | 22:15 | 49.969
2025-03-14 | 22:15 | 49.97
2025-03-14 | 22:15 | 49.969
2025-03-14 | 22:15 | 49.969
2025-03-14 | 22:15 | 49.967
2025-03-14 | 22:15 | 49.967
2025-03-14 | 22:15 | 49.965
2025-03-14 | 22:15 | 49.964
2025-03-14 | 22:15 | 49.964
2025-03-14 | 22:15 | 49.966
2025-03-14 | 22:15 | 49.968
2025-03-14 | 22:15 | 49.971
2025-03-14 | 22:15 | 49.973
2025-03-14 | 22:15 | 49.974
2025-03-14 | 22:15 | 49.975
2025-03-14 | 22:15 | 49.975
2025-03-14 | 22:15 | 49.977
2025-03-14 | 22:15 | 49.977
2025-03-14 | 22:15 | 49.978
2025-03-14 | 22:15 | 49.977
2025-03-14 | 22:15 | 49.978
2025-03-14 | 22:15 | 49.979
2025-03-14 | 22:15 | 49.978
2025-03-14 | 22:15 | 49.977
2025-03-14 | 22:15 | 49.978
2025-03-14 | 22:15 | 49.976
2025-03-14 | 22:15 | 49.974
2025-03-14 | 22:15 | 49.973
2025-03-14 | 22:15 | 49.971
2025-03-14 | 22:15 | 49.97
2025-03-14 | 22:15 | 49.97
2025-03-14 | 22:15 | 49.971
2025-03-14 | 22:15 | 49.969
2025-03-14 | 22:15 | 49.969
2025-03-14 | 22:15 | 49.969
2025-03-14 | 22:15 | 49.97
2025-03-14 | 22:15 | 49.97
2025-03-14 | 22:15 | 49.97
2025-03-14 | 22:15 | 49.971
2025-03-14 | 22:15 | 49.972
2025-03-14 | 22:15 | 49.974
2025-03-14 | 22:15 | 49.974
2025-03-14 | 22:15 | 49.974
2025-03-14 | 22:15 | 49.977
2025-03-14 | 22:15 | 49.978
2025-03-14 | 22:15 | 49.978
2025-03-14 | 22:16 | 49.979
2025-03-14 | 22:16 | 49.982
2025-03-14 | 22:16 | 49.983
2025-03-14 | 22:16 | 49.985
2025-03-14 | 22:16 | 49.985
2025-03-14 | 22:16 | 49.987
2025-03-14 | 22:16 | 49.988
2025-03-14 | 22:16 | 49.99
2025-03-14 | 22:16 | 49.988
2025-03-14 | 22:16 | 49.987
2025-03-14 | 22:16 | 49.987
2025-03-14 | 22:16 | 49.985
2025-03-14 | 22:16 | 49.984
2025-03-14 | 22:16 | 49.983
2025-03-14 | 22:16 | 49.982
2025-03-14 | 22:16 | 49.981
2025-03-14 | 22:16 | 49.981
2025-03-14 | 22:16 | 49.98
2025-03-14 | 22:16 | 49.98
2025-03-14 | 22:16 | 49.98
2025-03-14 | 22:16 | 49.981
2025-03-14 | 22:16 | 49.98
2025-03-14 | 22:16 | 49.978
2025-03-14 | 22:16 | 49.978
2025-03-14 | 22:16 | 49.979
2025-03-14 | 22:16 | 49.982
2025-03-14 | 22:16 | 49.983
2025-03-14 | 22:16 | 49.983
2025-03-14 | 22:16 | 49.983
2025-03-14 | 22:16 | 49.984
2025-03-14 | 22:16 | 49.985
2025-03-14 | 22:16 | 49.985
2025-03-14 | 22:16 | 49.983
2025-03-14 | 22:16 | 49.984
2025-03-14 | 22:16 | 49.982
2025-03-14 | 22:16 | 49.983
2025-03-14 | 22:16 | 49.981
2025-03-14 | 22:16 | 49.979
2025-03-14 | 22:16 | 49.978
2025-03-14 | 22:16 | 49.979
2025-03-14 | 22:16 | 49.981
2025-03-14 | 22:16 | 49.984
2025-03-14 | 22:16 | 49.986
2025-03-14 | 22:16 | 49.989
2025-03-14 | 22:16 | 49.989
2025-03-14 | 22:16 | 49.994
2025-03-14 | 22:16 | 49.997
2025-03-14 | 22:16 | 50
2025-03-14 | 22:16 | 50.004
2025-03-14 | 22:16 | 50.007
2025-03-14 | 22:16 | 50.009
2025-03-14 | 22:16 | 50.011
2025-03-14 | 22:16 | 50.013
2025-03-14 | 22:16 | 50.014
2025-03-14 | 22:16 | 50.016
2025-03-14 | 22:16 | 50.017
2025-03-14 | 22:16 | 50.02
2025-03-14 | 22:16 | 50.02
2025-03-14 | 22:16 | 50.02
2025-03-14 | 22:16 | 50.019
2025-03-14 | 22:16 | 50.019
2025-03-14 | 22:17 | 50.02
2025-03-14 | 22:17 | 50.02
2025-03-14 | 22:17 | 50.021
2025-03-14 | 22:17 | 50.025
2025-03-14 | 22:17 | 50.026
2025-03-14 | 22:17 | 50.028
2025-03-14 | 22:17 | 50.029
2025-03-14 | 22:17 | 50.029
2025-03-14 | 22:17 | 50.031
2025-03-14 | 22:17 | 50.033
2025-03-14 | 22:17 | 50.032
2025-03-14 | 22:17 | 50.032
2025-03-14 | 22:17 | 50.031
2025-03-14 | 22:17 | 50.03
2025-03-14 | 22:17 | 50.029
2025-03-14 | 22:17 | 50.031
2025-03-14 | 22:17 | 50.032
2025-03-14 | 22:17 | 50.034
2025-03-14 | 22:17 | 50.036
2025-03-14 | 22:17 | 50.036
2025-03-14 | 22:17 | 50.037
2025-03-14 | 22:17 | 50.037
2025-03-14 | 22:17 | 50.036
2025-03-14 | 22:17 | 50.037
2025-03-14 | 22:17 | 50.037
2025-03-14 | 22:17 | 50.037
2025-03-14 | 22:17 | 50.037
2025-03-14 | 22:17 | 50.035
2025-03-14 | 22:17 | 50.036
2025-03-14 | 22:17 | 50.036
2025-03-14 | 22:17 | 50.036
2025-03-14 | 22:17 | 50.035
2025-03-14 | 22:17 | 50.033
2025-03-14 | 22:17 | 50.031
2025-03-14 | 22:17 | 50.03
2025-03-14 | 22:17 | 50.029
2025-03-14 | 22:17 | 50.028
2025-03-14 | 22:17 | 50.028
2025-03-14 | 22:17 | 50.031
2025-03-14 | 22:17 | 50.032
2025-03-14 | 22:17 | 50.031
2025-03-14 | 22:17 | 50.031
2025-03-14 | 22:17 | 50.032
2025-03-14 | 22:17 | 50.031
2025-03-14 | 22:17 | 50.032
2025-03-14 | 22:17 | 50.032
2025-03-14 | 22:17 | 50.031

## 20250319-1
In GMT
Date | Time | Freq
2025-03-19 | 12:15 | 50.03 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-19 | 12:15 | 50.03 | 222 | BRITNED | 676.211
2025-03-19 | 12:15 | 50.033 | 268 | WBURB-2 | 428.156
2025-03-19 | 12:15 | 50.035 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-19 | 12:15 | 50.036 |  | Viking Link | -648.9
2025-03-19 | 12:15 | 50.035 |  | Viking Link | 1398.96
2025-03-19 | 12:15 | 50.035 | 209 | DRAXX-3 | 626.95
2025-03-19 | 12:15 | 50.035 | 154 | CDCL-1 | 391.57
2025-03-19 | 12:15 | 50.037 | 268 | ROCK-1 | 468.495
2025-03-19 | 12:15 | 50.037 | 148 | IFA Bipole1 | 945.473
2025-03-19 | 12:15 | 50.037 | 132 | IFA Bipole1 | 999.1
2025-03-19 | 12:15 | 50.037 | 141 | IFA Bipole2 | 1000
2025-03-19 | 12:15 | 50.037 | 135 | IFA Bipole1 | 996.75
2025-03-19 | 12:15 | 50.039 |  | Viking Link | -780.3
2025-03-19 | 12:15 | 50.039
2025-03-19 | 12:15 | 50.041
2025-03-19 | 12:15 | 50.042
2025-03-19 | 12:15 | 50.041
2025-03-19 | 12:15 | 50.043
2025-03-19 | 12:15 | 50.042 | 130 | HEYM12 | 271.908
2025-03-19 | 12:15 | 50.042 | 228 | HUMR-1 | 303.75
2025-03-19 | 12:15 | 50.042
2025-03-19 | 12:15 | 50.043
2025-03-19 | 12:15 | 50.041
2025-03-19 | 12:15 | 50.041
2025-03-19 | 12:15 | 50.044
2025-03-19 | 12:15 | 50.044
2025-03-19 | 12:15 | 50.045
2025-03-19 | 12:15 | 50.041
2025-03-19 | 12:15 | 50.038
2025-03-19 | 12:15 | 50.041 | 211 | CDCL-1 | 291.5
2025-03-19 | 12:15 | 50.038 | 199 | STAY-2 | 413.125
2025-03-19 | 12:15 | 50.038 | 173 | CDCL-1 | 397.375
2025-03-19 | 12:15 | 50.041 | 248 | SEAB-2 | 361.25
2025-03-19 | 12:15 | 50.045 | 255 | FRANCE | 995.65
2025-03-19 | 12:15 | 50.047 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-19 | 12:15 | 50.048
2025-03-19 | 12:15 | 50.05
2025-03-19 | 12:15 | 50.054
2025-03-19 | 12:15 | 50.055
2025-03-19 | 12:15 | 50.057
2025-03-19 | 12:15 | 50.059
2025-03-19 | 12:15 | 50.06
2025-03-19 | 12:15 | 50.06
2025-03-19 | 12:15 | 50.059
2025-03-19 | 12:15 | 50.055
2025-03-19 | 12:15 | 50.057
2025-03-19 | 12:15 | 50.055
2025-03-19 | 12:15 | 50.053
2025-03-19 | 12:15 | 50.052
2025-03-19 | 12:15 | 50.052
2025-03-19 | 12:15 | 50.051
2025-03-19 | 12:15 | 50.053
2025-03-19 | 12:15 | 50.051
2025-03-19 | 12:15 | 50.052
2025-03-19 | 12:15 | 50.048
2025-03-19 | 12:15 | 50.047
2025-03-19 | 12:16 | 50.043
2025-03-19 | 12:16 | 50.042
2025-03-19 | 12:16 | 50.043
2025-03-19 | 12:16 | 50.045
2025-03-19 | 12:16 | 50.044
2025-03-19 | 12:16 | 50.032
2025-03-19 | 12:16 | 50.01
2025-03-19 | 12:16 | 49.997
2025-03-19 | 12:16 | 49.988
2025-03-19 | 12:16 | 49.978
2025-03-19 | 12:16 | 49.969
2025-03-19 | 12:16 | 49.964
2025-03-19 | 12:16 | 49.961
2025-03-19 | 12:16 | 49.96
2025-03-19 | 12:16 | 49.958
2025-03-19 | 12:16 | 49.96
2025-03-19 | 12:16 | 49.96
2025-03-19 | 12:16 | 49.962
2025-03-19 | 12:16 | 49.961
2025-03-19 | 12:16 | 49.96
2025-03-19 | 12:16 | 49.961
2025-03-19 | 12:16 | 49.961
2025-03-19 | 12:16 | 49.961
2025-03-19 | 12:16 | 49.962
2025-03-19 | 12:16 | 49.96
2025-03-19 | 12:16 | 49.958
2025-03-19 | 12:16 | 49.955
2025-03-19 | 12:16 | 49.953
2025-03-19 | 12:16 | 49.953
2025-03-19 | 12:16 | 49.953
2025-03-19 | 12:16 | 49.951
2025-03-19 | 12:16 | 49.95
2025-03-19 | 12:16 | 49.95
2025-03-19 | 12:16 | 49.953
2025-03-19 | 12:16 | 49.951
2025-03-19 | 12:16 | 49.944
2025-03-19 | 12:16 | 49.94
2025-03-19 | 12:16 | 49.939
2025-03-19 | 12:16 | 49.94
2025-03-19 | 12:16 | 49.938
2025-03-19 | 12:16 | 49.935
2025-03-19 | 12:16 | 49.931
2025-03-19 | 12:16 | 49.928
2025-03-19 | 12:16 | 49.926
2025-03-19 | 12:16 | 49.926
2025-03-19 | 12:16 | 49.925
2025-03-19 | 12:16 | 49.922
2025-03-19 | 12:16 | 49.921
2025-03-19 | 12:16 | 49.921
2025-03-19 | 12:16 | 49.923
2025-03-19 | 12:16 | 49.923
2025-03-19 | 12:16 | 49.924
2025-03-19 | 12:16 | 49.925
2025-03-19 | 12:16 | 49.927
2025-03-19 | 12:16 | 49.93
2025-03-19 | 12:16 | 49.932
2025-03-19 | 12:16 | 49.934
2025-03-19 | 12:16 | 49.935
2025-03-19 | 12:16 | 49.935
2025-03-19 | 12:16 | 49.933
2025-03-19 | 12:16 | 49.93
2025-03-19 | 12:17 | 49.929
2025-03-19 | 12:17 | 49.921
2025-03-19 | 12:17 | 49.914
2025-03-19 | 12:17 | 49.907
2025-03-19 | 12:17 | 49.903
2025-03-19 | 12:17 | 49.901
2025-03-19 | 12:17 | 49.898
2025-03-19 | 12:17 | 49.895
2025-03-19 | 12:17 | 49.896
2025-03-19 | 12:17 | 49.893
2025-03-19 | 12:17 | 49.893
2025-03-19 | 12:17 | 49.891
2025-03-19 | 12:17 | 49.888
2025-03-19 | 12:17 | 49.889
2025-03-19 | 12:17 | 49.888
2025-03-19 | 12:17 | 49.887
2025-03-19 | 12:17 | 49.888
2025-03-19 | 12:17 | 49.887
2025-03-19 | 12:17 | 49.889
2025-03-19 | 12:17 | 49.886
2025-03-19 | 12:17 | 49.885
2025-03-19 | 12:17 | 49.883
2025-03-19 | 12:17 | 49.881
2025-03-19 | 12:17 | 49.88
2025-03-19 | 12:17 | 49.882
2025-03-19 | 12:17 | 49.882
2025-03-19 | 12:17 | 49.878
2025-03-19 | 12:17 | 49.879
2025-03-19 | 12:17 | 49.876
2025-03-19 | 12:17 | 49.86
2025-03-19 | 12:17 | 49.843
2025-03-19 | 12:17 | 49.834
2025-03-19 | 12:17 | 49.832
2025-03-19 | 12:17 | 49.833
2025-03-19 | 12:17 | 49.835
2025-03-19 | 12:17 | 49.837
2025-03-19 | 12:17 | 49.839
2025-03-19 | 12:17 | 49.84
2025-03-19 | 12:17 | 49.84
2025-03-19 | 12:17 | 49.84
2025-03-19 | 12:17 | 49.842
2025-03-19 | 12:17 | 49.844
2025-03-19 | 12:17 | 49.844
2025-03-19 | 12:17 | 49.843
2025-03-19 | 12:17 | 49.844
2025-03-19 | 12:17 | 49.84
2025-03-19 | 12:17 | 49.84
2025-03-19 | 12:17 | 49.842
2025-03-19 | 12:17 | 49.843
2025-03-19 | 12:17 | 49.844
2025-03-19 | 12:17 | 49.844
2025-03-19 | 12:17 | 49.846
2025-03-19 | 12:17 | 49.848
2025-03-19 | 12:17 | 49.854
2025-03-19 | 12:17 | 49.86
2025-03-19 | 12:17 | 49.862
2025-03-19 | 12:17 | 49.864
2025-03-19 | 12:17 | 49.863
2025-03-19 | 12:17 | 49.861
2025-03-19 | 12:18 | 49.861
2025-03-19 | 12:18 | 49.856
2025-03-19 | 12:18 | 49.85
2025-03-19 | 12:18 | 49.848
2025-03-19 | 12:18 | 49.849
2025-03-19 | 12:18 | 49.849
2025-03-19 | 12:18 | 49.847
2025-03-19 | 12:18 | 49.85
2025-03-19 | 12:18 | 49.85
2025-03-19 | 12:18 | 49.848
2025-03-19 | 12:18 | 49.846
2025-03-19 | 12:18 | 49.847
2025-03-19 | 12:18 | 49.85
2025-03-19 | 12:18 | 49.849
2025-03-19 | 12:18 | 49.847
2025-03-19 | 12:18 | 49.847
2025-03-19 | 12:18 | 49.849
2025-03-19 | 12:18 | 49.851
2025-03-19 | 12:18 | 49.851
2025-03-19 | 12:18 | 49.852
2025-03-19 | 12:18 | 49.854
2025-03-19 | 12:18 | 49.859
2025-03-19 | 12:18 | 49.861
2025-03-19 | 12:18 | 49.861
2025-03-19 | 12:18 | 49.86
2025-03-19 | 12:18 | 49.863
2025-03-19 | 12:18 | 49.866
2025-03-19 | 12:18 | 49.866
2025-03-19 | 12:18 | 49.863
2025-03-19 | 12:18 | 49.863
2025-03-19 | 12:18 | 49.864
2025-03-19 | 12:18 | 49.858
2025-03-19 | 12:18 | 49.857
2025-03-19 | 12:18 | 49.856
2025-03-19 | 12:18 | 49.855
2025-03-19 | 12:18 | 49.853
2025-03-19 | 12:18 | 49.857
2025-03-19 | 12:18 | 49.857
2025-03-19 | 12:18 | 49.86
2025-03-19 | 12:18 | 49.857
2025-03-19 | 12:18 | 49.854
2025-03-19 | 12:18 | 49.854
2025-03-19 | 12:18 | 49.858
2025-03-19 | 12:18 | 49.86
2025-03-19 | 12:18 | 49.86
2025-03-19 | 12:18 | 49.861
2025-03-19 | 12:18 | 49.869
2025-03-19 | 12:18 | 49.873
2025-03-19 | 12:18 | 49.871
2025-03-19 | 12:18 | 49.869
2025-03-19 | 12:18 | 49.868
2025-03-19 | 12:18 | 49.869
2025-03-19 | 12:18 | 49.87
2025-03-19 | 12:18 | 49.868
2025-03-19 | 12:18 | 49.871
2025-03-19 | 12:18 | 49.873
2025-03-19 | 12:18 | 49.874
2025-03-19 | 12:18 | 49.879
2025-03-19 | 12:18 | 49.88
2025-03-19 | 12:18 | 49.881
2025-03-19 | 12:18 | 49.883
2025-03-19 | 12:19 | 49.883
2025-03-19 | 12:19 | 49.887
2025-03-19 | 12:19 | 49.886
2025-03-19 | 12:19 | 49.886
2025-03-19 | 12:19 | 49.887
2025-03-19 | 12:19 | 49.887
2025-03-19 | 12:19 | 49.888
2025-03-19 | 12:19 | 49.887
2025-03-19 | 12:19 | 49.888
2025-03-19 | 12:19 | 49.888
2025-03-19 | 12:19 | 49.89
2025-03-19 | 12:19 | 49.894
2025-03-19 | 12:19 | 49.896
2025-03-19 | 12:19 | 49.895
2025-03-19 | 12:19 | 49.898
2025-03-19 | 12:19 | 49.905
2025-03-19 | 12:19 | 49.909
2025-03-19 | 12:19 | 49.909
2025-03-19 | 12:19 | 49.906
2025-03-19 | 12:19 | 49.908
2025-03-19 | 12:19 | 49.908
2025-03-19 | 12:19 | 49.902
2025-03-19 | 12:19 | 49.904
2025-03-19 | 12:19 | 49.902
2025-03-19 | 12:19 | 49.898
2025-03-19 | 12:19 | 49.898
2025-03-19 | 12:19 | 49.901
2025-03-19 | 12:19 | 49.904
2025-03-19 | 12:19 | 49.908
2025-03-19 | 12:19 | 49.91
2025-03-19 | 12:19 | 49.91
2025-03-19 | 12:19 | 49.921
2025-03-19 | 12:19 | 49.925
2025-03-19 | 12:19 | 49.924
2025-03-19 | 12:19 | 49.923
2025-03-19 | 12:19 | 49.926
2025-03-19 | 12:19 | 49.925
2025-03-19 | 12:19 | 49.929
2025-03-19 | 12:19 | 49.927
2025-03-19 | 12:19 | 49.928
2025-03-19 | 12:19 | 49.927
2025-03-19 | 12:19 | 49.925
2025-03-19 | 12:19 | 49.924
2025-03-19 | 12:19 | 49.922
2025-03-19 | 12:19 | 49.921
2025-03-19 | 12:19 | 49.919
2025-03-19 | 12:19 | 49.918
2025-03-19 | 12:19 | 49.918
2025-03-19 | 12:19 | 49.915
2025-03-19 | 12:19 | 49.914
2025-03-19 | 12:19 | 49.916
2025-03-19 | 12:19 | 49.919
2025-03-19 | 12:19 | 49.92
2025-03-19 | 12:19 | 49.921
2025-03-19 | 12:19 | 49.921
2025-03-19 | 12:19 | 49.922
2025-03-19 | 12:19 | 49.922
2025-03-19 | 12:19 | 49.922
2025-03-19 | 12:19 | 49.925
2025-03-19 | 12:20 | 49.926
2025-03-19 | 12:20 | 49.925
2025-03-19 | 12:20 | 49.924
2025-03-19 | 12:20 | 49.925
2025-03-19 | 12:20 | 49.928
2025-03-19 | 12:20 | 49.93
2025-03-19 | 12:20 | 49.932
2025-03-19 | 12:20 | 49.931
2025-03-19 | 12:20 | 49.935
2025-03-19 | 12:20 | 49.934
2025-03-19 | 12:20 | 49.935
2025-03-19 | 12:20 | 49.938
2025-03-19 | 12:20 | 49.938
2025-03-19 | 12:20 | 49.937
2025-03-19 | 12:20 | 49.938
2025-03-19 | 12:20 | 49.941
2025-03-19 | 12:20 | 49.941
2025-03-19 | 12:20 | 49.94
2025-03-19 | 12:20 | 49.94
2025-03-19 | 12:20 | 49.939
2025-03-19 | 12:20 | 49.938
2025-03-19 | 12:20 | 49.939
2025-03-19 | 12:20 | 49.938
2025-03-19 | 12:20 | 49.939
2025-03-19 | 12:20 | 49.939
2025-03-19 | 12:20 | 49.939
2025-03-19 | 12:20 | 49.936
2025-03-19 | 12:20 | 49.934
2025-03-19 | 12:20 | 49.933
2025-03-19 | 12:20 | 49.935
2025-03-19 | 12:20 | 49.938
2025-03-19 | 12:20 | 49.938
2025-03-19 | 12:20 | 49.941
2025-03-19 | 12:20 | 49.942
2025-03-19 | 12:20 | 49.945
2025-03-19 | 12:20 | 49.948
2025-03-19 | 12:20 | 49.951
2025-03-19 | 12:20 | 49.954
2025-03-19 | 12:20 | 49.955
2025-03-19 | 12:20 | 49.955
2025-03-19 | 12:20 | 49.954
2025-03-19 | 12:20 | 49.951
2025-03-19 | 12:20 | 49.95
2025-03-19 | 12:20 | 49.948
2025-03-19 | 12:20 | 49.947
2025-03-19 | 12:20 | 49.945
2025-03-19 | 12:20 | 49.946
2025-03-19 | 12:20 | 49.949
2025-03-19 | 12:20 | 49.951
2025-03-19 | 12:20 | 49.95
2025-03-19 | 12:20 | 49.95
2025-03-19 | 12:20 | 49.953
2025-03-19 | 12:20 | 49.954
2025-03-19 | 12:20 | 49.954
2025-03-19 | 12:20 | 49.956
2025-03-19 | 12:20 | 49.955
2025-03-19 | 12:20 | 49.956
2025-03-19 | 12:20 | 49.956
2025-03-19 | 12:20 | 49.958
2025-03-19 | 12:20 | 49.961
2025-03-19 | 12:20 | 49.961
2025-03-19 | 12:21 | 49.961
2025-03-19 | 12:21 | 49.962
2025-03-19 | 12:21 | 49.962
2025-03-19 | 12:21 | 49.964
2025-03-19 | 12:21 | 49.965
2025-03-19 | 12:21 | 49.969
2025-03-19 | 12:21 | 49.971
2025-03-19 | 12:21 | 49.973
2025-03-19 | 12:21 | 49.972
2025-03-19 | 12:21 | 49.973
2025-03-19 | 12:21 | 49.971
2025-03-19 | 12:21 | 49.971
2025-03-19 | 12:21 | 49.971
2025-03-19 | 12:21 | 49.97
2025-03-19 | 12:21 | 49.972
2025-03-19 | 12:21 | 49.971
2025-03-19 | 12:21 | 49.969
2025-03-19 | 12:21 | 49.971
2025-03-19 | 12:21 | 49.969
2025-03-19 | 12:21 | 49.969
2025-03-19 | 12:21 | 49.967
2025-03-19 | 12:21 | 49.965
2025-03-19 | 12:21 | 49.964
2025-03-19 | 12:21 | 49.965
2025-03-19 | 12:21 | 49.965
2025-03-19 | 12:21 | 49.966
2025-03-19 | 12:21 | 49.967
2025-03-19 | 12:21 | 49.969
2025-03-19 | 12:21 | 49.969
2025-03-19 | 12:21 | 49.971
2025-03-19 | 12:21 | 49.971
2025-03-19 | 12:21 | 49.97
2025-03-19 | 12:21 | 49.969
2025-03-19 | 12:21 | 49.967
2025-03-19 | 12:21 | 49.965
2025-03-19 | 12:21 | 49.964
2025-03-19 | 12:21 | 49.965
2025-03-19 | 12:21 | 49.966
2025-03-19 | 12:21 | 49.966
2025-03-19 | 12:21 | 49.967
2025-03-19 | 12:21 | 49.965
2025-03-19 | 12:21 | 49.967
2025-03-19 | 12:21 | 49.965
2025-03-19 | 12:21 | 49.966
2025-03-19 | 12:21 | 49.968
2025-03-19 | 12:21 | 49.97
2025-03-19 | 12:21 | 49.971
2025-03-19 | 12:21 | 49.973
2025-03-19 | 12:21 | 49.974
2025-03-19 | 12:21 | 49.975
2025-03-19 | 12:21 | 49.975
2025-03-19 | 12:21 | 49.974
2025-03-19 | 12:21 | 49.971
2025-03-19 | 12:21 | 49.97
2025-03-19 | 12:21 | 49.966
2025-03-19 | 12:21 | 49.965
2025-03-19 | 12:21 | 49.965
2025-03-19 | 12:21 | 49.967
2025-03-19 | 12:21 | 49.966
2025-03-19 | 12:22 | 49.966
2025-03-19 | 12:22 | 49.965
2025-03-19 | 12:22 | 49.964
2025-03-19 | 12:22 | 49.963
2025-03-19 | 12:22 | 49.966
2025-03-19 | 12:22 | 49.968
2025-03-19 | 12:22 | 49.968
2025-03-19 | 12:22 | 49.968
2025-03-19 | 12:22 | 49.966
2025-03-19 | 12:22 | 49.965
2025-03-19 | 12:22 | 49.96
2025-03-19 | 12:22 | 49.955
2025-03-19 | 12:22 | 49.953
2025-03-19 | 12:22 | 49.946
2025-03-19 | 12:22 | 49.94
2025-03-19 | 12:22 | 49.934
2025-03-19 | 12:22 | 49.93
2025-03-19 | 12:22 | 49.925
2025-03-19 | 12:22 | 49.92
2025-03-19 | 12:22 | 49.913
2025-03-19 | 12:22 | 49.909
2025-03-19 | 12:22 | 49.904
2025-03-19 | 12:22 | 49.901
2025-03-19 | 12:22 | 49.903
2025-03-19 | 12:22 | 49.902
2025-03-19 | 12:22 | 49.903
2025-03-19 | 12:22 | 49.904
2025-03-19 | 12:22 | 49.904
2025-03-19 | 12:22 | 49.903
2025-03-19 | 12:22 | 49.902
2025-03-19 | 12:22 | 49.899
2025-03-19 | 12:22 | 49.899
2025-03-19 | 12:22 | 49.899
2025-03-19 | 12:22 | 49.902
2025-03-19 | 12:22 | 49.907
2025-03-19 | 12:22 | 49.91
2025-03-19 | 12:22 | 49.912
2025-03-19 | 12:22 | 49.915
2025-03-19 | 12:22 | 49.915
2025-03-19 | 12:22 | 49.913
2025-03-19 | 12:22 | 49.913
2025-03-19 | 12:22 | 49.913
2025-03-19 | 12:22 | 49.914
2025-03-19 | 12:22 | 49.917
2025-03-19 | 12:22 | 49.92
2025-03-19 | 12:22 | 49.92
2025-03-19 | 12:22 | 49.922
2025-03-19 | 12:22 | 49.922
2025-03-19 | 12:22 | 49.922
2025-03-19 | 12:22 | 49.923
2025-03-19 | 12:22 | 49.92
2025-03-19 | 12:22 | 49.915
2025-03-19 | 12:22 | 49.909
2025-03-19 | 12:22 | 49.908
2025-03-19 | 12:22 | 49.909
2025-03-19 | 12:22 | 49.911
2025-03-19 | 12:22 | 49.911
2025-03-19 | 12:22 | 49.91
2025-03-19 | 12:22 | 49.911
2025-03-19 | 12:22 | 49.914
2025-03-19 | 12:22 | 49.915
2025-03-19 | 12:23 | 49.917
2025-03-19 | 12:23 | 49.917
2025-03-19 | 12:23 | 49.919
2025-03-19 | 12:23 | 49.92
2025-03-19 | 12:23 | 49.919
2025-03-19 | 12:23 | 49.918
2025-03-19 | 12:23 | 49.915
2025-03-19 | 12:23 | 49.914
2025-03-19 | 12:23 | 49.909
2025-03-19 | 12:23 | 49.908
2025-03-19 | 12:23 | 49.91
2025-03-19 | 12:23 | 49.911
2025-03-19 | 12:23 | 49.912
2025-03-19 | 12:23 | 49.913
2025-03-19 | 12:23 | 49.914
2025-03-19 | 12:23 | 49.913
2025-03-19 | 12:23 | 49.916
2025-03-19 | 12:23 | 49.918
2025-03-19 | 12:23 | 49.918
2025-03-19 | 12:23 | 49.917
2025-03-19 | 12:23 | 49.917
2025-03-19 | 12:23 | 49.917
2025-03-19 | 12:23 | 49.917
2025-03-19 | 12:23 | 49.915
2025-03-19 | 12:23 | 49.916
2025-03-19 | 12:23 | 49.918
2025-03-19 | 12:23 | 49.921
2025-03-19 | 12:23 | 49.921
2025-03-19 | 12:23 | 49.923
2025-03-19 | 12:23 | 49.924
2025-03-19 | 12:23 | 49.923
2025-03-19 | 12:23 | 49.923
2025-03-19 | 12:23 | 49.925
2025-03-19 | 12:23 | 49.927
2025-03-19 | 12:23 | 49.928
2025-03-19 | 12:23 | 49.926
2025-03-19 | 12:23 | 49.928
2025-03-19 | 12:23 | 49.928
2025-03-19 | 12:23 | 49.929
2025-03-19 | 12:23 | 49.93
2025-03-19 | 12:23 | 49.928
2025-03-19 | 12:23 | 49.928
2025-03-19 | 12:23 | 49.929
2025-03-19 | 12:23 | 49.93
2025-03-19 | 12:23 | 49.93
2025-03-19 | 12:23 | 49.93
2025-03-19 | 12:23 | 49.931
2025-03-19 | 12:23 | 49.932
2025-03-19 | 12:23 | 49.933
2025-03-19 | 12:23 | 49.934
2025-03-19 | 12:23 | 49.934
2025-03-19 | 12:23 | 49.934
2025-03-19 | 12:23 | 49.932
2025-03-19 | 12:23 | 49.931
2025-03-19 | 12:23 | 49.93
2025-03-19 | 12:23 | 49.929
2025-03-19 | 12:23 | 49.926
2025-03-19 | 12:23 | 49.925
2025-03-19 | 12:23 | 49.923
2025-03-19 | 12:24 | 49.923
2025-03-19 | 12:24 | 49.924
2025-03-19 | 12:24 | 49.925
2025-03-19 | 12:24 | 49.926
2025-03-19 | 12:24 | 49.927
2025-03-19 | 12:24 | 49.93
2025-03-19 | 12:24 | 49.931
2025-03-19 | 12:24 | 49.932
2025-03-19 | 12:24 | 49.931
2025-03-19 | 12:24 | 49.932
2025-03-19 | 12:24 | 49.932
2025-03-19 | 12:24 | 49.931
2025-03-19 | 12:24 | 49.933
2025-03-19 | 12:24 | 49.93
2025-03-19 | 12:24 | 49.934
2025-03-19 | 12:24 | 49.933
2025-03-19 | 12:24 | 49.935
2025-03-19 | 12:24 | 49.935
2025-03-19 | 12:24 | 49.933
2025-03-19 | 12:24 | 49.93
2025-03-19 | 12:24 | 49.929
2025-03-19 | 12:24 | 49.927
2025-03-19 | 12:24 | 49.927
2025-03-19 | 12:24 | 49.927
2025-03-19 | 12:24 | 49.929
2025-03-19 | 12:24 | 49.929
2025-03-19 | 12:24 | 49.931
2025-03-19 | 12:24 | 49.933
2025-03-19 | 12:24 | 49.934
2025-03-19 | 12:24 | 49.934
2025-03-19 | 12:24 | 49.937
2025-03-19 | 12:24 | 49.937
2025-03-19 | 12:24 | 49.937
2025-03-19 | 12:24 | 49.941
2025-03-19 | 12:24 | 49.945
2025-03-19 | 12:24 | 49.946
2025-03-19 | 12:24 | 49.946
2025-03-19 | 12:24 | 49.946
2025-03-19 | 12:24 | 49.948
2025-03-19 | 12:24 | 49.951
2025-03-19 | 12:24 | 49.954
2025-03-19 | 12:24 | 49.959
2025-03-19 | 12:24 | 49.962
2025-03-19 | 12:24 | 49.966
2025-03-19 | 12:24 | 49.967
2025-03-19 | 12:24 | 49.971
2025-03-19 | 12:24 | 49.973
2025-03-19 | 12:24 | 49.976
2025-03-19 | 12:24 | 49.978
2025-03-19 | 12:24 | 49.982
2025-03-19 | 12:24 | 49.983
2025-03-19 | 12:24 | 49.986
2025-03-19 | 12:24 | 49.988
2025-03-19 | 12:24 | 49.989
2025-03-19 | 12:24 | 49.992
2025-03-19 | 12:24 | 49.993
2025-03-19 | 12:24 | 49.994
2025-03-19 | 12:24 | 49.996
2025-03-19 | 12:24 | 49.997
2025-03-19 | 12:24 | 49.998
2025-03-19 | 12:24 | 49.998
2025-03-19 | 12:25 | 49.997
2025-03-19 | 12:25 | 49.994
2025-03-19 | 12:25 | 49.995
2025-03-19 | 12:25 | 49.995
2025-03-19 | 12:25 | 49.996
2025-03-19 | 12:25 | 49.998
2025-03-19 | 12:25 | 50
2025-03-19 | 12:25 | 50.002
2025-03-19 | 12:25 | 50.001
2025-03-19 | 12:25 | 50.004
2025-03-19 | 12:25 | 50.002
2025-03-19 | 12:25 | 50.003
2025-03-19 | 12:25 | 50.003
2025-03-19 | 12:25 | 50.004
2025-03-19 | 12:25 | 50.003
2025-03-19 | 12:25 | 50.001
2025-03-19 | 12:25 | 50
2025-03-19 | 12:25 | 50.002
2025-03-19 | 12:25 | 50.003
2025-03-19 | 12:25 | 50.003
2025-03-19 | 12:25 | 50.004
2025-03-19 | 12:25 | 50.004
2025-03-19 | 12:25 | 50.006
2025-03-19 | 12:25 | 50.008
2025-03-19 | 12:25 | 50.01
2025-03-19 | 12:25 | 50.013
2025-03-19 | 12:25 | 50.018
2025-03-19 | 12:25 | 50.022
2025-03-19 | 12:25 | 50.025
2025-03-19 | 12:25 | 50.024
2025-03-19 | 12:25 | 50.02
2025-03-19 | 12:25 | 50.012
2025-03-19 | 12:25 | 50.004
2025-03-19 | 12:25 | 49.999
2025-03-19 | 12:25 | 49.997
2025-03-19 | 12:25 | 49.996
2025-03-19 | 12:25 | 49.997
2025-03-19 | 12:25 | 50.001
2025-03-19 | 12:25 | 50.003
2025-03-19 | 12:25 | 50.003
2025-03-19 | 12:25 | 50.005
2025-03-19 | 12:25 | 50.005
2025-03-19 | 12:25 | 50.007
2025-03-19 | 12:25 | 50.007
2025-03-19 | 12:25 | 50.009
2025-03-19 | 12:25 | 50.008
2025-03-19 | 12:25 | 50.008
2025-03-19 | 12:25 | 50.011
2025-03-19 | 12:25 | 50.013
2025-03-19 | 12:25 | 50.018
2025-03-19 | 12:25 | 50.023
2025-03-19 | 12:25 | 50.025
2025-03-19 | 12:25 | 50.025
2025-03-19 | 12:25 | 50.028
2025-03-19 | 12:25 | 50.031
2025-03-19 | 12:25 | 50.032
2025-03-19 | 12:25 | 50.032
2025-03-19 | 12:25 | 50.032
2025-03-19 | 12:25 | 50.031
2025-03-19 | 12:26 | 50.032
2025-03-19 | 12:26 | 50.034
2025-03-19 | 12:26 | 50.036
2025-03-19 | 12:26 | 50.034
2025-03-19 | 12:26 | 50.033
2025-03-19 | 12:26 | 50.032
2025-03-19 | 12:26 | 50.031
2025-03-19 | 12:26 | 50.027

## 20250319-2
In GMT
Date | Time | Freq
2025-03-19 | 19:53 | 50.154 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-19 | 19:53 | 50.153 | 222 | BRITNED | 676.211
2025-03-19 | 19:53 | 50.154 | 268 | WBURB-2 | 428.156
2025-03-19 | 19:53 | 50.154 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-19 | 19:53 | 50.155 |  | Viking Link | -648.9
2025-03-19 | 19:53 | 50.156 |  | Viking Link | 1398.96
2025-03-19 | 19:53 | 50.157 | 209 | DRAXX-3 | 626.95
2025-03-19 | 19:53 | 50.159 | 154 | CDCL-1 | 391.57
2025-03-19 | 19:53 | 50.159 | 268 | ROCK-1 | 468.495
2025-03-19 | 19:53 | 50.16 | 148 | IFA Bipole1 | 945.473
2025-03-19 | 19:53 | 50.16 | 132 | IFA Bipole1 | 999.1
2025-03-19 | 19:53 | 50.159 | 141 | IFA Bipole2 | 1000
2025-03-19 | 19:53 | 50.158 | 135 | IFA Bipole1 | 996.75
2025-03-19 | 19:53 | 50.156 |  | Viking Link | -780.3
2025-03-19 | 19:53 | 50.154
2025-03-19 | 19:53 | 50.154
2025-03-19 | 19:53 | 50.154
2025-03-19 | 19:53 | 50.155
2025-03-19 | 19:53 | 50.153
2025-03-19 | 19:53 | 50.153 | 130 | HEYM12 | 271.908
2025-03-19 | 19:53 | 50.152 | 228 | HUMR-1 | 303.75
2025-03-19 | 19:53 | 50.153
2025-03-19 | 19:53 | 50.154
2025-03-19 | 19:53 | 50.156
2025-03-19 | 19:53 | 50.157
2025-03-19 | 19:53 | 50.158
2025-03-19 | 19:53 | 50.158
2025-03-19 | 19:53 | 50.159
2025-03-19 | 19:53 | 50.158
2025-03-19 | 19:53 | 50.159
2025-03-19 | 19:53 | 50.159 | 211 | CDCL-1 | 291.5
2025-03-19 | 19:54 | 50.16 | 199 | STAY-2 | 413.125
2025-03-19 | 19:54 | 50.16 | 173 | CDCL-1 | 397.375
2025-03-19 | 19:54 | 50.161 | 248 | SEAB-2 | 361.25
2025-03-19 | 19:54 | 50.161 | 255 | FRANCE | 995.65
2025-03-19 | 19:54 | 50.161 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-19 | 19:54 | 50.161
2025-03-19 | 19:54 | 50.16
2025-03-19 | 19:54 | 50.16
2025-03-19 | 19:54 | 50.159
2025-03-19 | 19:54 | 50.159
2025-03-19 | 19:54 | 50.158
2025-03-19 | 19:54 | 50.158
2025-03-19 | 19:54 | 50.157
2025-03-19 | 19:54 | 50.158
2025-03-19 | 19:54 | 50.158
2025-03-19 | 19:54 | 50.158
2025-03-19 | 19:54 | 50.158
2025-03-19 | 19:54 | 50.157
2025-03-19 | 19:54 | 50.157
2025-03-19 | 19:54 | 50.159
2025-03-19 | 19:54 | 50.157
2025-03-19 | 19:54 | 50.159
2025-03-19 | 19:54 | 50.158
2025-03-19 | 19:54 | 50.158
2025-03-19 | 19:54 | 50.159
2025-03-19 | 19:54 | 50.158
2025-03-19 | 19:54 | 50.156
2025-03-19 | 19:54 | 50.157
2025-03-19 | 19:54 | 50.157
2025-03-19 | 19:54 | 50.159
2025-03-19 | 19:54 | 50.161
2025-03-19 | 19:54 | 50.16
2025-03-19 | 19:54 | 50.155
2025-03-19 | 19:54 | 50.151
2025-03-19 | 19:54 | 50.142
2025-03-19 | 19:54 | 50.131
2025-03-19 | 19:54 | 50.126
2025-03-19 | 19:54 | 50.124
2025-03-19 | 19:54 | 50.124
2025-03-19 | 19:54 | 50.125
2025-03-19 | 19:54 | 50.125
2025-03-19 | 19:54 | 50.128
2025-03-19 | 19:54 | 50.128
2025-03-19 | 19:54 | 50.128
2025-03-19 | 19:54 | 50.127
2025-03-19 | 19:54 | 50.128
2025-03-19 | 19:54 | 50.128
2025-03-19 | 19:54 | 50.128
2025-03-19 | 19:54 | 50.129
2025-03-19 | 19:54 | 50.128
2025-03-19 | 19:54 | 50.127
2025-03-19 | 19:54 | 50.127
2025-03-19 | 19:54 | 50.126
2025-03-19 | 19:54 | 50.127
2025-03-19 | 19:54 | 50.126
2025-03-19 | 19:54 | 50.126
2025-03-19 | 19:54 | 50.125
2025-03-19 | 19:54 | 50.126
2025-03-19 | 19:54 | 50.126
2025-03-19 | 19:54 | 50.127
2025-03-19 | 19:54 | 50.128
2025-03-19 | 19:55 | 50.128
2025-03-19 | 19:55 | 50.127
2025-03-19 | 19:55 | 50.125
2025-03-19 | 19:55 | 50.123
2025-03-19 | 19:55 | 50.122
2025-03-19 | 19:55 | 50.121
2025-03-19 | 19:55 | 50.12
2025-03-19 | 19:55 | 50.12
2025-03-19 | 19:55 | 50.118
2025-03-19 | 19:55 | 50.116
2025-03-19 | 19:55 | 50.117
2025-03-19 | 19:55 | 50.116
2025-03-19 | 19:55 | 50.117
2025-03-19 | 19:55 | 50.116
2025-03-19 | 19:55 | 50.116
2025-03-19 | 19:55 | 50.115
2025-03-19 | 19:55 | 50.116
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.115
2025-03-19 | 19:55 | 50.115
2025-03-19 | 19:55 | 50.115
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.112
2025-03-19 | 19:55 | 50.112
2025-03-19 | 19:55 | 50.112
2025-03-19 | 19:55 | 50.112
2025-03-19 | 19:55 | 50.112
2025-03-19 | 19:55 | 50.112
2025-03-19 | 19:55 | 50.112
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.112
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.115
2025-03-19 | 19:55 | 50.116
2025-03-19 | 19:55 | 50.115
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.114
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.113
2025-03-19 | 19:55 | 50.112
2025-03-19 | 19:55 | 50.111
2025-03-19 | 19:56 | 50.109
2025-03-19 | 19:56 | 50.108
2025-03-19 | 19:56 | 50.108
2025-03-19 | 19:56 | 50.105
2025-03-19 | 19:56 | 50.103
2025-03-19 | 19:56 | 50.101
2025-03-19 | 19:56 | 50.099
2025-03-19 | 19:56 | 50.098
2025-03-19 | 19:56 | 50.099
2025-03-19 | 19:56 | 50.096
2025-03-19 | 19:56 | 50.094
2025-03-19 | 19:56 | 50.092
2025-03-19 | 19:56 | 50.09
2025-03-19 | 19:56 | 50.089
2025-03-19 | 19:56 | 50.087
2025-03-19 | 19:56 | 50.085
2025-03-19 | 19:56 | 50.084
2025-03-19 | 19:56 | 50.083
2025-03-19 | 19:56 | 50.082
2025-03-19 | 19:56 | 50.074
2025-03-19 | 19:56 | 50.066
2025-03-19 | 19:56 | 50.061
2025-03-19 | 19:56 | 50.057
2025-03-19 | 19:56 | 50.053
2025-03-19 | 19:56 | 50.051
2025-03-19 | 19:56 | 50.048
2025-03-19 | 19:56 | 50.048
2025-03-19 | 19:56 | 50.048
2025-03-19 | 19:56 | 50.052
2025-03-19 | 19:56 | 50.052
2025-03-19 | 19:56 | 50.053
2025-03-19 | 19:56 | 50.053
2025-03-19 | 19:56 | 50.053
2025-03-19 | 19:56 | 50.054
2025-03-19 | 19:56 | 50.052
2025-03-19 | 19:56 | 50.052
2025-03-19 | 19:56 | 50.05
2025-03-19 | 19:56 | 50.048
2025-03-19 | 19:56 | 50.044
2025-03-19 | 19:56 | 50.042
2025-03-19 | 19:56 | 50.04
2025-03-19 | 19:56 | 50.038
2025-03-19 | 19:56 | 50.037
2025-03-19 | 19:56 | 50.037
2025-03-19 | 19:56 | 50.039
2025-03-19 | 19:56 | 50.04
2025-03-19 | 19:56 | 50.043
2025-03-19 | 19:56 | 50.043
2025-03-19 | 19:56 | 50.042
2025-03-19 | 19:56 | 50.04
2025-03-19 | 19:56 | 50.038
2025-03-19 | 19:56 | 50.037
2025-03-19 | 19:56 | 50.033
2025-03-19 | 19:56 | 50.032
2025-03-19 | 19:56 | 50.029
2025-03-19 | 19:56 | 50.029
2025-03-19 | 19:56 | 50.029
2025-03-19 | 19:56 | 50.03
2025-03-19 | 19:56 | 50.032
2025-03-19 | 19:56 | 50.032
2025-03-19 | 19:56 | 50.034
2025-03-19 | 19:57 | 50.034
2025-03-19 | 19:57 | 50.034
2025-03-19 | 19:57 | 50.034
2025-03-19 | 19:57 | 50.034
2025-03-19 | 19:57 | 50.033
2025-03-19 | 19:57 | 50.031
2025-03-19 | 19:57 | 50.029
2025-03-19 | 19:57 | 50.028
2025-03-19 | 19:57 | 50.027
2025-03-19 | 19:57 | 50.027
2025-03-19 | 19:57 | 50.026
2025-03-19 | 19:57 | 50.024
2025-03-19 | 19:57 | 50.024
2025-03-19 | 19:57 | 50.025
2025-03-19 | 19:57 | 50.025
2025-03-19 | 19:57 | 50.025
2025-03-19 | 19:57 | 50.026
2025-03-19 | 19:57 | 50.027
2025-03-19 | 19:57 | 50.026
2025-03-19 | 19:57 | 50.026
2025-03-19 | 19:57 | 50.025
2025-03-19 | 19:57 | 50.023
2025-03-19 | 19:57 | 50.026
2025-03-19 | 19:57 | 50.028
2025-03-19 | 19:57 | 50.033
2025-03-19 | 19:57 | 50.035
2025-03-19 | 19:57 | 50.038
2025-03-19 | 19:57 | 50.04
2025-03-19 | 19:57 | 50.042
2025-03-19 | 19:57 | 50.041
2025-03-19 | 19:57 | 50.04
2025-03-19 | 19:57 | 50.039
2025-03-19 | 19:57 | 50.039
2025-03-19 | 19:57 | 50.038
2025-03-19 | 19:57 | 50.038
2025-03-19 | 19:57 | 50.037
2025-03-19 | 19:57 | 50.037
2025-03-19 | 19:57 | 50.038
2025-03-19 | 19:57 | 50.039
2025-03-19 | 19:57 | 50.04
2025-03-19 | 19:57 | 50.038
2025-03-19 | 19:57 | 50.038
2025-03-19 | 19:57 | 50.041
2025-03-19 | 19:57 | 50.044
2025-03-19 | 19:57 | 50.047
2025-03-19 | 19:57 | 50.049
2025-03-19 | 19:57 | 50.051
2025-03-19 | 19:57 | 50.053
2025-03-19 | 19:57 | 50.053
2025-03-19 | 19:57 | 50.054
2025-03-19 | 19:57 | 50.054
2025-03-19 | 19:57 | 50.054
2025-03-19 | 19:57 | 50.054
2025-03-19 | 19:57 | 50.053
2025-03-19 | 19:57 | 50.051
2025-03-19 | 19:57 | 50.051
2025-03-19 | 19:57 | 50.048
2025-03-19 | 19:57 | 50.046
2025-03-19 | 19:57 | 50.046
2025-03-19 | 19:58 | 50.046
2025-03-19 | 19:58 | 50.047
2025-03-19 | 19:58 | 50.045
2025-03-19 | 19:58 | 50.043
2025-03-19 | 19:58 | 50.043
2025-03-19 | 19:58 | 50.043
2025-03-19 | 19:58 | 50.046
2025-03-19 | 19:58 | 50.048
2025-03-19 | 19:58 | 50.05
2025-03-19 | 19:58 | 50.051
2025-03-19 | 19:58 | 50.055
2025-03-19 | 19:58 | 50.057
2025-03-19 | 19:58 | 50.062
2025-03-19 | 19:58 | 50.066
2025-03-19 | 19:58 | 50.069
2025-03-19 | 19:58 | 50.07
2025-03-19 | 19:58 | 50.072
2025-03-19 | 19:58 | 50.074
2025-03-19 | 19:58 | 50.075
2025-03-19 | 19:58 | 50.075
2025-03-19 | 19:58 | 50.077
2025-03-19 | 19:58 | 50.078
2025-03-19 | 19:58 | 50.078
2025-03-19 | 19:58 | 50.08
2025-03-19 | 19:58 | 50.079
2025-03-19 | 19:58 | 50.076
2025-03-19 | 19:58 | 50.073
2025-03-19 | 19:58 | 50.072
2025-03-19 | 19:58 | 50.067
2025-03-19 | 19:58 | 50.065
2025-03-19 | 19:58 | 50.062
2025-03-19 | 19:58 | 50.062
2025-03-19 | 19:58 | 50.061
2025-03-19 | 19:58 | 50.062
2025-03-19 | 19:58 | 50.064
2025-03-19 | 19:58 | 50.063
2025-03-19 | 19:58 | 50.063
2025-03-19 | 19:58 | 50.063
2025-03-19 | 19:58 | 50.061
2025-03-19 | 19:58 | 50.058
2025-03-19 | 19:58 | 50.056
2025-03-19 | 19:58 | 50.055
2025-03-19 | 19:58 | 50.056
2025-03-19 | 19:58 | 50.058
2025-03-19 | 19:58 | 50.058
2025-03-19 | 19:58 | 50.061
2025-03-19 | 19:58 | 50.063
2025-03-19 | 19:58 | 50.065
2025-03-19 | 19:58 | 50.068
2025-03-19 | 19:58 | 50.068
2025-03-19 | 19:58 | 50.069
2025-03-19 | 19:58 | 50.071
2025-03-19 | 19:58 | 50.07
2025-03-19 | 19:58 | 50.071
2025-03-19 | 19:58 | 50.073
2025-03-19 | 19:58 | 50.072
2025-03-19 | 19:58 | 50.073
2025-03-19 | 19:58 | 50.074
2025-03-19 | 19:58 | 50.076
2025-03-19 | 19:58 | 50.077
2025-03-19 | 19:58 | 50.078
2025-03-19 | 19:59 | 50.078
2025-03-19 | 19:59 | 50.08
2025-03-19 | 19:59 | 50.083
2025-03-19 | 19:59 | 50.085
2025-03-19 | 19:59 | 50.085
2025-03-19 | 19:59 | 50.088
2025-03-19 | 19:59 | 50.09
2025-03-19 | 19:59 | 50.091
2025-03-19 | 19:59 | 50.087
2025-03-19 | 19:59 | 50.085
2025-03-19 | 19:59 | 50.084
2025-03-19 | 19:59 | 50.088
2025-03-19 | 19:59 | 50.089
2025-03-19 | 19:59 | 50.092
2025-03-19 | 19:59 | 50.092
2025-03-19 | 19:59 | 50.094
2025-03-19 | 19:59 | 50.093
2025-03-19 | 19:59 | 50.095
2025-03-19 | 19:59 | 50.095
2025-03-19 | 19:59 | 50.096
2025-03-19 | 19:59 | 50.096
2025-03-19 | 19:59 | 50.096
2025-03-19 | 19:59 | 50.094
2025-03-19 | 19:59 | 50.093
2025-03-19 | 19:59 | 50.092
2025-03-19 | 19:59 | 50.092
2025-03-19 | 19:59 | 50.094
2025-03-19 | 19:59 | 50.093
2025-03-19 | 19:59 | 50.094
2025-03-19 | 19:59 | 50.094
2025-03-19 | 19:59 | 50.094
2025-03-19 | 19:59 | 50.095
2025-03-19 | 19:59 | 50.093
2025-03-19 | 19:59 | 50.091
2025-03-19 | 19:59 | 50.09
2025-03-19 | 19:59 | 50.089
2025-03-19 | 19:59 | 50.089
2025-03-19 | 19:59 | 50.089
2025-03-19 | 19:59 | 50.089
2025-03-19 | 19:59 | 50.088
2025-03-19 | 19:59 | 50.087
2025-03-19 | 19:59 | 50.085
2025-03-19 | 19:59 | 50.083
2025-03-19 | 19:59 | 50.082
2025-03-19 | 19:59 | 50.082
2025-03-19 | 19:59 | 50.083
2025-03-19 | 19:59 | 50.083
2025-03-19 | 19:59 | 50.085
2025-03-19 | 19:59 | 50.087
2025-03-19 | 19:59 | 50.088
2025-03-19 | 19:59 | 50.089
2025-03-19 | 19:59 | 50.088
2025-03-19 | 19:59 | 50.086
2025-03-19 | 19:59 | 50.084
2025-03-19 | 19:59 | 50.083
2025-03-19 | 19:59 | 50.082
2025-03-19 | 19:59 | 50.083
2025-03-19 | 19:59 | 50.082
2025-03-19 | 19:59 | 50.081
2025-03-19 | 20:00 | 50.081
2025-03-19 | 20:00 | 50.08
2025-03-19 | 20:00 | 50.078
2025-03-19 | 20:00 | 50.077
2025-03-19 | 20:00 | 50.077
2025-03-19 | 20:00 | 50.077
2025-03-19 | 20:00 | 50.079
2025-03-19 | 20:00 | 50.079
2025-03-19 | 20:00 | 50.078
2025-03-19 | 20:00 | 50.075
2025-03-19 | 20:00 | 50.075
2025-03-19 | 20:00 | 50.075
2025-03-19 | 20:00 | 50.075
2025-03-19 | 20:00 | 50.075
2025-03-19 | 20:00 | 50.072
2025-03-19 | 20:00 | 50.069
2025-03-19 | 20:00 | 50.064
2025-03-19 | 20:00 | 50.058
2025-03-19 | 20:00 | 50.048
2025-03-19 | 20:00 | 50.042
2025-03-19 | 20:00 | 50.036
2025-03-19 | 20:00 | 50.031
2025-03-19 | 20:00 | 50.028
2025-03-19 | 20:00 | 50.024
2025-03-19 | 20:00 | 50.022
2025-03-19 | 20:00 | 50.023
2025-03-19 | 20:00 | 50.023
2025-03-19 | 20:00 | 50.025
2025-03-19 | 20:00 | 50.027
2025-03-19 | 20:00 | 50.029
2025-03-19 | 20:00 | 50.029
2025-03-19 | 20:00 | 50.031
2025-03-19 | 20:00 | 50.031
2025-03-19 | 20:00 | 50.03
2025-03-19 | 20:00 | 50.031
2025-03-19 | 20:00 | 50.032
2025-03-19 | 20:00 | 50.029
2025-03-19 | 20:00 | 50.026
2025-03-19 | 20:00 | 50.024
2025-03-19 | 20:00 | 50.02
2025-03-19 | 20:00 | 50.016
2025-03-19 | 20:00 | 50.014
2025-03-19 | 20:00 | 50.011
2025-03-19 | 20:00 | 50.01
2025-03-19 | 20:00 | 50.007
2025-03-19 | 20:00 | 50.004
2025-03-19 | 20:00 | 49.999
2025-03-19 | 20:00 | 49.995
2025-03-19 | 20:00 | 49.993
2025-03-19 | 20:00 | 49.989
2025-03-19 | 20:00 | 49.983
2025-03-19 | 20:00 | 49.974
2025-03-19 | 20:00 | 49.967
2025-03-19 | 20:00 | 49.962
2025-03-19 | 20:00 | 49.956
2025-03-19 | 20:00 | 49.95
2025-03-19 | 20:00 | 49.947
2025-03-19 | 20:00 | 49.939
2025-03-19 | 20:00 | 49.934
2025-03-19 | 20:00 | 49.931
2025-03-19 | 20:00 | 49.927
2025-03-19 | 20:01 | 49.924
2025-03-19 | 20:01 | 49.925
2025-03-19 | 20:01 | 49.925
2025-03-19 | 20:01 | 49.924
2025-03-19 | 20:01 | 49.921
2025-03-19 | 20:01 | 49.919
2025-03-19 | 20:01 | 49.917
2025-03-19 | 20:01 | 49.918
2025-03-19 | 20:01 | 49.919
2025-03-19 | 20:01 | 49.92
2025-03-19 | 20:01 | 49.918
2025-03-19 | 20:01 | 49.918
2025-03-19 | 20:01 | 49.915
2025-03-19 | 20:01 | 49.913
2025-03-19 | 20:01 | 49.911
2025-03-19 | 20:01 | 49.909
2025-03-19 | 20:01 | 49.909
2025-03-19 | 20:01 | 49.906
2025-03-19 | 20:01 | 49.906
2025-03-19 | 20:01 | 49.905
2025-03-19 | 20:01 | 49.905
2025-03-19 | 20:01 | 49.902
2025-03-19 | 20:01 | 49.901
2025-03-19 | 20:01 | 49.899
2025-03-19 | 20:01 | 49.898
2025-03-19 | 20:01 | 49.899
2025-03-19 | 20:01 | 49.898
2025-03-19 | 20:01 | 49.897
2025-03-19 | 20:01 | 49.896
2025-03-19 | 20:01 | 49.895
2025-03-19 | 20:01 | 49.893
2025-03-19 | 20:01 | 49.894
2025-03-19 | 20:01 | 49.894
2025-03-19 | 20:01 | 49.896
2025-03-19 | 20:01 | 49.896
2025-03-19 | 20:01 | 49.897
2025-03-19 | 20:01 | 49.899
2025-03-19 | 20:01 | 49.899
2025-03-19 | 20:01 | 49.899
2025-03-19 | 20:01 | 49.899
2025-03-19 | 20:01 | 49.898
2025-03-19 | 20:01 | 49.896
2025-03-19 | 20:01 | 49.895
2025-03-19 | 20:01 | 49.893
2025-03-19 | 20:01 | 49.894
2025-03-19 | 20:01 | 49.896

## 20250320-1
In GMT
Date | Time | Freq
2025-03-20 | 17:29 | 49.898 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-20 | 17:29 | 49.899 | 222 | BRITNED | 676.211
2025-03-20 | 17:29 | 49.898 | 268 | WBURB-2 | 428.156
2025-03-20 | 17:29 | 49.899 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-20 | 17:29 | 49.9 |  | Viking Link | -648.9
2025-03-20 | 17:29 | 49.901 |  | Viking Link | 1398.96
2025-03-20 | 17:29 | 49.901 | 209 | DRAXX-3 | 626.95
2025-03-20 | 17:29 | 49.902 | 154 | CDCL-1 | 391.57
2025-03-20 | 17:29 | 49.907 | 268 | ROCK-1 | 468.495
2025-03-20 | 17:29 | 49.91 | 148 | IFA Bipole1 | 945.473
2025-03-20 | 17:29 | 49.913 | 132 | IFA Bipole1 | 999.1
2025-03-20 | 17:29 | 49.914 | 141 | IFA Bipole2 | 1000
2025-03-20 | 17:29 | 49.914 | 135 | IFA Bipole1 | 996.75
2025-03-20 | 17:29 | 49.917 |  | Viking Link | -780.3
2025-03-20 | 17:29 | 49.922
2025-03-20 | 17:29 | 49.925
2025-03-20 | 17:29 | 49.926
2025-03-20 | 17:29 | 49.928
2025-03-20 | 17:29 | 49.93
2025-03-20 | 17:29 | 49.932 | 130 | HEYM12 | 271.908
2025-03-20 | 17:29 | 49.933 | 228 | HUMR-1 | 303.75
2025-03-20 | 17:29 | 49.935
2025-03-20 | 17:29 | 49.937
2025-03-20 | 17:29 | 49.941
2025-03-20 | 17:29 | 49.945
2025-03-20 | 17:29 | 49.948
2025-03-20 | 17:29 | 49.95
2025-03-20 | 17:29 | 49.953
2025-03-20 | 17:29 | 49.953
2025-03-20 | 17:29 | 49.953
2025-03-20 | 17:29 | 49.954 | 211 | CDCL-1 | 291.5
2025-03-20 | 17:29 | 49.954 | 199 | STAY-2 | 413.125
2025-03-20 | 17:29 | 49.953 | 173 | CDCL-1 | 397.375
2025-03-20 | 17:29 | 49.952 | 248 | SEAB-2 | 361.25
2025-03-20 | 17:29 | 49.951 | 255 | FRANCE | 995.65
2025-03-20 | 17:29 | 49.949 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-20 | 17:29 | 49.95
2025-03-20 | 17:29 | 49.95
2025-03-20 | 17:29 | 49.951
2025-03-20 | 17:29 | 49.954
2025-03-20 | 17:30 | 49.958
2025-03-20 | 17:30 | 49.958
2025-03-20 | 17:30 | 49.959
2025-03-20 | 17:30 | 49.961
2025-03-20 | 17:30 | 49.966
2025-03-20 | 17:30 | 49.969
2025-03-20 | 17:30 | 49.971
2025-03-20 | 17:30 | 49.973
2025-03-20 | 17:30 | 49.976
2025-03-20 | 17:30 | 49.976
2025-03-20 | 17:30 | 49.978
2025-03-20 | 17:30 | 49.977
2025-03-20 | 17:30 | 49.977
2025-03-20 | 17:30 | 49.978
2025-03-20 | 17:30 | 49.979
2025-03-20 | 17:30 | 49.983
2025-03-20 | 17:30 | 49.982
2025-03-20 | 17:30 | 49.981
2025-03-20 | 17:30 | 49.98
2025-03-20 | 17:30 | 49.981
2025-03-20 | 17:30 | 49.982
2025-03-20 | 17:30 | 49.972
2025-03-20 | 17:30 | 49.951
2025-03-20 | 17:30 | 49.938
2025-03-20 | 17:30 | 49.929
2025-03-20 | 17:30 | 49.923
2025-03-20 | 17:30 | 49.918
2025-03-20 | 17:30 | 49.915
2025-03-20 | 17:30 | 49.914
2025-03-20 | 17:30 | 49.916
2025-03-20 | 17:30 | 49.917
2025-03-20 | 17:30 | 49.912
2025-03-20 | 17:30 | 49.908
2025-03-20 | 17:30 | 49.907
2025-03-20 | 17:30 | 49.907
2025-03-20 | 17:30 | 49.908
2025-03-20 | 17:30 | 49.909
2025-03-20 | 17:30 | 49.911
2025-03-20 | 17:30 | 49.914
2025-03-20 | 17:30 | 49.917
2025-03-20 | 17:30 | 49.915
2025-03-20 | 17:30 | 49.913
2025-03-20 | 17:30 | 49.911
2025-03-20 | 17:30 | 49.909
2025-03-20 | 17:30 | 49.908
2025-03-20 | 17:30 | 49.911
2025-03-20 | 17:30 | 49.912
2025-03-20 | 17:30 | 49.914
2025-03-20 | 17:30 | 49.915
2025-03-20 | 17:30 | 49.917
2025-03-20 | 17:30 | 49.918
2025-03-20 | 17:30 | 49.92
2025-03-20 | 17:30 | 49.92
2025-03-20 | 17:30 | 49.918
2025-03-20 | 17:30 | 49.918
2025-03-20 | 17:30 | 49.917
2025-03-20 | 17:30 | 49.918
2025-03-20 | 17:30 | 49.92
2025-03-20 | 17:30 | 49.922
2025-03-20 | 17:30 | 49.924
2025-03-20 | 17:30 | 49.924
2025-03-20 | 17:31 | 49.922
2025-03-20 | 17:31 | 49.921
2025-03-20 | 17:31 | 49.922
2025-03-20 | 17:31 | 49.921
2025-03-20 | 17:31 | 49.919
2025-03-20 | 17:31 | 49.916
2025-03-20 | 17:31 | 49.915
2025-03-20 | 17:31 | 49.913
2025-03-20 | 17:31 | 49.911
2025-03-20 | 17:31 | 49.909
2025-03-20 | 17:31 | 49.909
2025-03-20 | 17:31 | 49.907
2025-03-20 | 17:31 | 49.906
2025-03-20 | 17:31 | 49.904
2025-03-20 | 17:31 | 49.903
2025-03-20 | 17:31 | 49.9
2025-03-20 | 17:31 | 49.896
2025-03-20 | 17:31 | 49.894
2025-03-20 | 17:31 | 49.893
2025-03-20 | 17:31 | 49.893
2025-03-20 | 17:31 | 49.892
2025-03-20 | 17:31 | 49.892
2025-03-20 | 17:31 | 49.892
2025-03-20 | 17:31 | 49.892
2025-03-20 | 17:31 | 49.893
2025-03-20 | 17:31 | 49.894
2025-03-20 | 17:31 | 49.895
2025-03-20 | 17:31 | 49.896
2025-03-20 | 17:31 | 49.897
2025-03-20 | 17:31 | 49.898
2025-03-20 | 17:31 | 49.898
2025-03-20 | 17:31 | 49.897
2025-03-20 | 17:31 | 49.896
2025-03-20 | 17:31 | 49.892
2025-03-20 | 17:31 | 49.89
2025-03-20 | 17:31 | 49.889
2025-03-20 | 17:31 | 49.888
2025-03-20 | 17:31 | 49.889
2025-03-20 | 17:31 | 49.889
2025-03-20 | 17:31 | 49.891
2025-03-20 | 17:31 | 49.892
2025-03-20 | 17:31 | 49.894
2025-03-20 | 17:31 | 49.892
2025-03-20 | 17:31 | 49.89
2025-03-20 | 17:31 | 49.889
2025-03-20 | 17:31 | 49.887
2025-03-20 | 17:31 | 49.885
2025-03-20 | 17:31 | 49.885
2025-03-20 | 17:31 | 49.887
2025-03-20 | 17:31 | 49.888
2025-03-20 | 17:31 | 49.89
2025-03-20 | 17:31 | 49.891
2025-03-20 | 17:31 | 49.893
2025-03-20 | 17:31 | 49.893
2025-03-20 | 17:31 | 49.891
2025-03-20 | 17:31 | 49.887
2025-03-20 | 17:31 | 49.879
2025-03-20 | 17:31 | 49.871
2025-03-20 | 17:31 | 49.864
2025-03-20 | 17:32 | 49.859
2025-03-20 | 17:32 | 49.858
2025-03-20 | 17:32 | 49.855
2025-03-20 | 17:32 | 49.852
2025-03-20 | 17:32 | 49.851
2025-03-20 | 17:32 | 49.849
2025-03-20 | 17:32 | 49.85
2025-03-20 | 17:32 | 49.848
2025-03-20 | 17:32 | 49.845
2025-03-20 | 17:32 | 49.843
2025-03-20 | 17:32 | 49.842
2025-03-20 | 17:32 | 49.84
2025-03-20 | 17:32 | 49.839
2025-03-20 | 17:32 | 49.839
2025-03-20 | 17:32 | 49.841
2025-03-20 | 17:32 | 49.842
2025-03-20 | 17:32 | 49.843
2025-03-20 | 17:32 | 49.846
2025-03-20 | 17:32 | 49.848
2025-03-20 | 17:32 | 49.851
2025-03-20 | 17:32 | 49.85
2025-03-20 | 17:32 | 49.85
2025-03-20 | 17:32 | 49.848
2025-03-20 | 17:32 | 49.847
2025-03-20 | 17:32 | 49.847
2025-03-20 | 17:32 | 49.846
2025-03-20 | 17:32 | 49.847
2025-03-20 | 17:32 | 49.846
2025-03-20 | 17:32 | 49.845
2025-03-20 | 17:32 | 49.845
2025-03-20 | 17:32 | 49.845
2025-03-20 | 17:32 | 49.842
2025-03-20 | 17:32 | 49.843
2025-03-20 | 17:32 | 49.845
2025-03-20 | 17:32 | 49.843
2025-03-20 | 17:32 | 49.843
2025-03-20 | 17:32 | 49.842
2025-03-20 | 17:32 | 49.843
2025-03-20 | 17:32 | 49.845
2025-03-20 | 17:32 | 49.844
2025-03-20 | 17:32 | 49.844
2025-03-20 | 17:32 | 49.845
2025-03-20 | 17:32 | 49.845
2025-03-20 | 17:32 | 49.847
2025-03-20 | 17:32 | 49.849
2025-03-20 | 17:32 | 49.851
2025-03-20 | 17:32 | 49.855
2025-03-20 | 17:32 | 49.857
2025-03-20 | 17:32 | 49.857
2025-03-20 | 17:32 | 49.856
2025-03-20 | 17:32 | 49.854
2025-03-20 | 17:32 | 49.852
2025-03-20 | 17:32 | 49.851
2025-03-20 | 17:32 | 49.85
2025-03-20 | 17:32 | 49.848
2025-03-20 | 17:32 | 49.846
2025-03-20 | 17:32 | 49.847
2025-03-20 | 17:32 | 49.846
2025-03-20 | 17:32 | 49.846
2025-03-20 | 17:32 | 49.847
2025-03-20 | 17:32 | 49.85
2025-03-20 | 17:33 | 49.851
2025-03-20 | 17:33 | 49.853
2025-03-20 | 17:33 | 49.858
2025-03-20 | 17:33 | 49.861
2025-03-20 | 17:33 | 49.865
2025-03-20 | 17:33 | 49.87
2025-03-20 | 17:33 | 49.874
2025-03-20 | 17:33 | 49.878
2025-03-20 | 17:33 | 49.88
2025-03-20 | 17:33 | 49.883
2025-03-20 | 17:33 | 49.884
2025-03-20 | 17:33 | 49.885
2025-03-20 | 17:33 | 49.886
2025-03-20 | 17:33 | 49.89
2025-03-20 | 17:33 | 49.891
2025-03-20 | 17:33 | 49.892
2025-03-20 | 17:33 | 49.895
2025-03-20 | 17:33 | 49.896
2025-03-20 | 17:33 | 49.898
2025-03-20 | 17:33 | 49.902
2025-03-20 | 17:33 | 49.904
2025-03-20 | 17:33 | 49.904
2025-03-20 | 17:33 | 49.904
2025-03-20 | 17:33 | 49.907
2025-03-20 | 17:33 | 49.908
2025-03-20 | 17:33 | 49.91
2025-03-20 | 17:33 | 49.909
2025-03-20 | 17:33 | 49.91
2025-03-20 | 17:33 | 49.91
2025-03-20 | 17:33 | 49.91
2025-03-20 | 17:33 | 49.908
2025-03-20 | 17:33 | 49.91
2025-03-20 | 17:33 | 49.909
2025-03-20 | 17:33 | 49.909
2025-03-20 | 17:33 | 49.908
2025-03-20 | 17:33 | 49.908
2025-03-20 | 17:33 | 49.908
2025-03-20 | 17:33 | 49.907
2025-03-20 | 17:33 | 49.904
2025-03-20 | 17:33 | 49.903
2025-03-20 | 17:33 | 49.902
2025-03-20 | 17:33 | 49.902
2025-03-20 | 17:33 | 49.902
2025-03-20 | 17:33 | 49.902
2025-03-20 | 17:33 | 49.902
2025-03-20 | 17:33 | 49.906
2025-03-20 | 17:33 | 49.908
2025-03-20 | 17:33 | 49.911
2025-03-20 | 17:33 | 49.915
2025-03-20 | 17:33 | 49.917
2025-03-20 | 17:33 | 49.918
2025-03-20 | 17:33 | 49.92
2025-03-20 | 17:33 | 49.923
2025-03-20 | 17:33 | 49.925
2025-03-20 | 17:33 | 49.928
2025-03-20 | 17:33 | 49.929
2025-03-20 | 17:33 | 49.93
2025-03-20 | 17:33 | 49.93
2025-03-20 | 17:33 | 49.932
2025-03-20 | 17:34 | 49.935
2025-03-20 | 17:34 | 49.936
2025-03-20 | 17:34 | 49.936
2025-03-20 | 17:34 | 49.933
2025-03-20 | 17:34 | 49.931
2025-03-20 | 17:34 | 49.929
2025-03-20 | 17:34 | 49.926
2025-03-20 | 17:34 | 49.924
2025-03-20 | 17:34 | 49.922
2025-03-20 | 17:34 | 49.924
2025-03-20 | 17:34 | 49.921
2025-03-20 | 17:34 | 49.92
2025-03-20 | 17:34 | 49.918
2025-03-20 | 17:34 | 49.92
2025-03-20 | 17:34 | 49.92
2025-03-20 | 17:34 | 49.922
2025-03-20 | 17:34 | 49.923
2025-03-20 | 17:34 | 49.924
2025-03-20 | 17:34 | 49.925
2025-03-20 | 17:34 | 49.927
2025-03-20 | 17:34 | 49.927
2025-03-20 | 17:34 | 49.928
2025-03-20 | 17:34 | 49.927
2025-03-20 | 17:34 | 49.926
2025-03-20 | 17:34 | 49.928
2025-03-20 | 17:34 | 49.926
2025-03-20 | 17:34 | 49.923
2025-03-20 | 17:34 | 49.923
2025-03-20 | 17:34 | 49.924
2025-03-20 | 17:34 | 49.925
2025-03-20 | 17:34 | 49.924
2025-03-20 | 17:34 | 49.924
2025-03-20 | 17:34 | 49.924
2025-03-20 | 17:34 | 49.926
2025-03-20 | 17:34 | 49.927
2025-03-20 | 17:34 | 49.93
2025-03-20 | 17:34 | 49.932
2025-03-20 | 17:34 | 49.933
2025-03-20 | 17:34 | 49.934
2025-03-20 | 17:34 | 49.935
2025-03-20 | 17:34 | 49.937
2025-03-20 | 17:34 | 49.939
2025-03-20 | 17:34 | 49.942
2025-03-20 | 17:34 | 49.945
2025-03-20 | 17:34 | 49.947
2025-03-20 | 17:34 | 49.949
2025-03-20 | 17:34 | 49.949
2025-03-20 | 17:34 | 49.948
2025-03-20 | 17:34 | 49.951
2025-03-20 | 17:34 | 49.954
2025-03-20 | 17:34 | 49.953
2025-03-20 | 17:34 | 49.952
2025-03-20 | 17:34 | 49.951
2025-03-20 | 17:34 | 49.95
2025-03-20 | 17:34 | 49.951
2025-03-20 | 17:34 | 49.95
2025-03-20 | 17:34 | 49.948
2025-03-20 | 17:34 | 49.948
2025-03-20 | 17:34 | 49.946
2025-03-20 | 17:34 | 49.945
2025-03-20 | 17:34 | 49.942
2025-03-20 | 17:35 | 49.939
2025-03-20 | 17:35 | 49.937
2025-03-20 | 17:35 | 49.935
2025-03-20 | 17:35 | 49.934
2025-03-20 | 17:35 | 49.934
2025-03-20 | 17:35 | 49.935
2025-03-20 | 17:35 | 49.935
2025-03-20 | 17:35 | 49.936
2025-03-20 | 17:35 | 49.937
2025-03-20 | 17:35 | 49.938
2025-03-20 | 17:35 | 49.939
2025-03-20 | 17:35 | 49.94
2025-03-20 | 17:35 | 49.94
2025-03-20 | 17:35 | 49.942
2025-03-20 | 17:35 | 49.942
2025-03-20 | 17:35 | 49.942
2025-03-20 | 17:35 | 49.942
2025-03-20 | 17:35 | 49.94
2025-03-20 | 17:35 | 49.938
2025-03-20 | 17:35 | 49.933
2025-03-20 | 17:35 | 49.933
2025-03-20 | 17:35 | 49.934
2025-03-20 | 17:35 | 49.936
2025-03-20 | 17:35 | 49.936
2025-03-20 | 17:35 | 49.935
2025-03-20 | 17:35 | 49.937
2025-03-20 | 17:35 | 49.939
2025-03-20 | 17:35 | 49.938
2025-03-20 | 17:35 | 49.938
2025-03-20 | 17:35 | 49.938
2025-03-20 | 17:35 | 49.938
2025-03-20 | 17:35 | 49.937
2025-03-20 | 17:35 | 49.938
2025-03-20 | 17:35 | 49.938
2025-03-20 | 17:35 | 49.938
2025-03-20 | 17:35 | 49.939
2025-03-20 | 17:35 | 49.942
2025-03-20 | 17:35 | 49.943
2025-03-20 | 17:35 | 49.945
2025-03-20 | 17:35 | 49.947
2025-03-20 | 17:35 | 49.95
2025-03-20 | 17:35 | 49.953
2025-03-20 | 17:35 | 49.955
2025-03-20 | 17:35 | 49.955
2025-03-20 | 17:35 | 49.953
2025-03-20 | 17:35 | 49.951
2025-03-20 | 17:35 | 49.95
2025-03-20 | 17:35 | 49.949
2025-03-20 | 17:35 | 49.949
2025-03-20 | 17:35 | 49.948
2025-03-20 | 17:35 | 49.948
2025-03-20 | 17:35 | 49.946
2025-03-20 | 17:35 | 49.947
2025-03-20 | 17:35 | 49.945
2025-03-20 | 17:35 | 49.944
2025-03-20 | 17:35 | 49.941
2025-03-20 | 17:35 | 49.938
2025-03-20 | 17:35 | 49.935
2025-03-20 | 17:35 | 49.935
2025-03-20 | 17:36 | 49.935
2025-03-20 | 17:36 | 49.933
2025-03-20 | 17:36 | 49.933
2025-03-20 | 17:36 | 49.933
2025-03-20 | 17:36 | 49.934
2025-03-20 | 17:36 | 49.936
2025-03-20 | 17:36 | 49.938
2025-03-20 | 17:36 | 49.939
2025-03-20 | 17:36 | 49.94
2025-03-20 | 17:36 | 49.942
2025-03-20 | 17:36 | 49.944
2025-03-20 | 17:36 | 49.947
2025-03-20 | 17:36 | 49.95
2025-03-20 | 17:36 | 49.952
2025-03-20 | 17:36 | 49.954
2025-03-20 | 17:36 | 49.955
2025-03-20 | 17:36 | 49.958
2025-03-20 | 17:36 | 49.957
2025-03-20 | 17:36 | 49.957
2025-03-20 | 17:36 | 49.958
2025-03-20 | 17:36 | 49.957
2025-03-20 | 17:36 | 49.959
2025-03-20 | 17:36 | 49.957
2025-03-20 | 17:36 | 49.955
2025-03-20 | 17:36 | 49.955
2025-03-20 | 17:36 | 49.954
2025-03-20 | 17:36 | 49.954
2025-03-20 | 17:36 | 49.953
2025-03-20 | 17:36 | 49.951
2025-03-20 | 17:36 | 49.95
2025-03-20 | 17:36 | 49.95
2025-03-20 | 17:36 | 49.95
2025-03-20 | 17:36 | 49.952
2025-03-20 | 17:36 | 49.953
2025-03-20 | 17:36 | 49.956
2025-03-20 | 17:36 | 49.956
2025-03-20 | 17:36 | 49.957
2025-03-20 | 17:36 | 49.958
2025-03-20 | 17:36 | 49.958
2025-03-20 | 17:36 | 49.959
2025-03-20 | 17:36 | 49.959
2025-03-20 | 17:36 | 49.961
2025-03-20 | 17:36 | 49.961
2025-03-20 | 17:36 | 49.962
2025-03-20 | 17:36 | 49.961
2025-03-20 | 17:36 | 49.961
2025-03-20 | 17:36 | 49.961
2025-03-20 | 17:36 | 49.96
2025-03-20 | 17:36 | 49.958
2025-03-20 | 17:36 | 49.955
2025-03-20 | 17:36 | 49.951
2025-03-20 | 17:36 | 49.949
2025-03-20 | 17:36 | 49.949
2025-03-20 | 17:36 | 49.95
2025-03-20 | 17:36 | 49.953
2025-03-20 | 17:36 | 49.955
2025-03-20 | 17:36 | 49.955
2025-03-20 | 17:36 | 49.956
2025-03-20 | 17:36 | 49.956
2025-03-20 | 17:36 | 49.957
2025-03-20 | 17:36 | 49.957
2025-03-20 | 17:37 | 49.958
2025-03-20 | 17:37 | 49.958
2025-03-20 | 17:37 | 49.956
2025-03-20 | 17:37 | 49.957
2025-03-20 | 17:37 | 49.957
2025-03-20 | 17:37 | 49.957
2025-03-20 | 17:37 | 49.954
2025-03-20 | 17:37 | 49.952
2025-03-20 | 17:37 | 49.95
2025-03-20 | 17:37 | 49.947
2025-03-20 | 17:37 | 49.945
2025-03-20 | 17:37 | 49.944
2025-03-20 | 17:37 | 49.943
2025-03-20 | 17:37 | 49.943
2025-03-20 | 17:37 | 49.943
2025-03-20 | 17:37 | 49.944
2025-03-20 | 17:37 | 49.941
2025-03-20 | 17:37 | 49.94
2025-03-20 | 17:37 | 49.94
2025-03-20 | 17:37 | 49.942
2025-03-20 | 17:37 | 49.943
2025-03-20 | 17:37 | 49.944
2025-03-20 | 17:37 | 49.945
2025-03-20 | 17:37 | 49.949
2025-03-20 | 17:37 | 49.951
2025-03-20 | 17:37 | 49.955
2025-03-20 | 17:37 | 49.957
2025-03-20 | 17:37 | 49.958
2025-03-20 | 17:37 | 49.957
2025-03-20 | 17:37 | 49.954
2025-03-20 | 17:37 | 49.949
2025-03-20 | 17:37 | 49.946
2025-03-20 | 17:37 | 49.942
2025-03-20 | 17:37 | 49.943
2025-03-20 | 17:37 | 49.941
2025-03-20 | 17:37 | 49.943
2025-03-20 | 17:37 | 49.942
2025-03-20 | 17:37 | 49.946
2025-03-20 | 17:37 | 49.948
2025-03-20 | 17:37 | 49.951
2025-03-20 | 17:37 | 49.951
2025-03-20 | 17:37 | 49.949
2025-03-20 | 17:37 | 49.947
2025-03-20 | 17:37 | 49.946
2025-03-20 | 17:37 | 49.945
2025-03-20 | 17:37 | 49.949
2025-03-20 | 17:37 | 49.951
2025-03-20 | 17:37 | 49.952
2025-03-20 | 17:37 | 49.951
2025-03-20 | 17:37 | 49.952
2025-03-20 | 17:37 | 49.951
2025-03-20 | 17:37 | 49.952
2025-03-20 | 17:37 | 49.954
2025-03-20 | 17:37 | 49.957
2025-03-20 | 17:37 | 49.96
2025-03-20 | 17:37 | 49.962
2025-03-20 | 17:37 | 49.959
2025-03-20 | 17:37 | 49.958
2025-03-20 | 17:37 | 49.955
2025-03-20 | 17:38 | 49.951
2025-03-20 | 17:38 | 49.948
2025-03-20 | 17:38 | 49.945
2025-03-20 | 17:38 | 49.943
2025-03-20 | 17:38 | 49.942
2025-03-20 | 17:38 | 49.94
2025-03-20 | 17:38 | 49.938
2025-03-20 | 17:38 | 49.935
2025-03-20 | 17:38 | 49.93
2025-03-20 | 17:38 | 49.926
2025-03-20 | 17:38 | 49.926
2025-03-20 | 17:38 | 49.925
2025-03-20 | 17:38 | 49.928
2025-03-20 | 17:38 | 49.932
2025-03-20 | 17:38 | 49.935
2025-03-20 | 17:38 | 49.934
2025-03-20 | 17:38 | 49.934
2025-03-20 | 17:38 | 49.934
2025-03-20 | 17:38 | 49.935
2025-03-20 | 17:38 | 49.936
2025-03-20 | 17:38 | 49.939
2025-03-20 | 17:38 | 49.942
2025-03-20 | 17:38 | 49.942
2025-03-20 | 17:38 | 49.943
2025-03-20 | 17:38 | 49.944
2025-03-20 | 17:38 | 49.943
2025-03-20 | 17:38 | 49.945
2025-03-20 | 17:38 | 49.945
2025-03-20 | 17:38 | 49.946
2025-03-20 | 17:38 | 49.946
2025-03-20 | 17:38 | 49.943
2025-03-20 | 17:38 | 49.94
2025-03-20 | 17:38 | 49.94
2025-03-20 | 17:38 | 49.94
2025-03-20 | 17:38 | 49.941
2025-03-20 | 17:38 | 49.941
2025-03-20 | 17:38 | 49.94
2025-03-20 | 17:38 | 49.937
2025-03-20 | 17:38 | 49.934
2025-03-20 | 17:38 | 49.93
2025-03-20 | 17:38 | 49.927
2025-03-20 | 17:38 | 49.926
2025-03-20 | 17:38 | 49.924
2025-03-20 | 17:38 | 49.92
2025-03-20 | 17:38 | 49.921
2025-03-20 | 17:38 | 49.919
2025-03-20 | 17:38 | 49.921
2025-03-20 | 17:38 | 49.92
2025-03-20 | 17:38 | 49.92
2025-03-20 | 17:38 | 49.92
2025-03-20 | 17:38 | 49.921
2025-03-20 | 17:38 | 49.922
2025-03-20 | 17:38 | 49.921
2025-03-20 | 17:38 | 49.922
2025-03-20 | 17:38 | 49.927
2025-03-20 | 17:38 | 49.933
2025-03-20 | 17:38 | 49.939
2025-03-20 | 17:38 | 49.943
2025-03-20 | 17:38 | 49.945
2025-03-20 | 17:38 | 49.947
2025-03-20 | 17:38 | 49.947
2025-03-20 | 17:39 | 49.947
2025-03-20 | 17:39 | 49.948
2025-03-20 | 17:39 | 49.947
2025-03-20 | 17:39 | 49.945
2025-03-20 | 17:39 | 49.944
2025-03-20 | 17:39 | 49.945
2025-03-20 | 17:39 | 49.947
2025-03-20 | 17:39 | 49.95
2025-03-20 | 17:39 | 49.951
2025-03-20 | 17:39 | 49.954
2025-03-20 | 17:39 | 49.955
2025-03-20 | 17:39 | 49.955
2025-03-20 | 17:39 | 49.953
2025-03-20 | 17:39 | 49.951
2025-03-20 | 17:39 | 49.949
2025-03-20 | 17:39 | 49.951
2025-03-20 | 17:39 | 49.952
2025-03-20 | 17:39 | 49.954
2025-03-20 | 17:39 | 49.955
2025-03-20 | 17:39 | 49.956
2025-03-20 | 17:39 | 49.957
2025-03-20 | 17:39 | 49.958
2025-03-20 | 17:39 | 49.957
2025-03-20 | 17:39 | 49.955
2025-03-20 | 17:39 | 49.953
2025-03-20 | 17:39 | 49.953
2025-03-20 | 17:39 | 49.951
2025-03-20 | 17:39 | 49.95
2025-03-20 | 17:39 | 49.946
2025-03-20 | 17:39 | 49.947
2025-03-20 | 17:39 | 49.946
2025-03-20 | 17:39 | 49.95
2025-03-20 | 17:39 | 49.952
2025-03-20 | 17:39 | 49.951
2025-03-20 | 17:39 | 49.952
2025-03-20 | 17:39 | 49.952
2025-03-20 | 17:39 | 49.951
2025-03-20 | 17:39 | 49.951
2025-03-20 | 17:39 | 49.952
2025-03-20 | 17:39 | 49.955
2025-03-20 | 17:39 | 49.955
2025-03-20 | 17:39 | 49.957
2025-03-20 | 17:39 | 49.956
2025-03-20 | 17:39 | 49.957
2025-03-20 | 17:39 | 49.961
2025-03-20 | 17:39 | 49.964
2025-03-20 | 17:39 | 49.966
2025-03-20 | 17:39 | 49.968
2025-03-20 | 17:39 | 49.969
2025-03-20 | 17:39 | 49.97
2025-03-20 | 17:39 | 49.969
2025-03-20 | 17:39 | 49.971
2025-03-20 | 17:39 | 49.974
2025-03-20 | 17:39 | 49.976
2025-03-20 | 17:39 | 49.978
2025-03-20 | 17:39 | 49.98
2025-03-20 | 17:39 | 49.982
2025-03-20 | 17:39 | 49.985
2025-03-20 | 17:39 | 49.984
2025-03-20 | 17:40 | 49.983
2025-03-20 | 17:40 | 49.979
2025-03-20 | 17:40 | 49.976
2025-03-20 | 17:40 | 49.973
2025-03-20 | 17:40 | 49.971
2025-03-20 | 17:40 | 49.971
2025-03-20 | 17:40 | 49.972
2025-03-20 | 17:40 | 49.973
2025-03-20 | 17:40 | 49.974
2025-03-20 | 17:40 | 49.976
2025-03-20 | 17:40 | 49.976
2025-03-20 | 17:40 | 49.977
2025-03-20 | 17:40 | 49.976
2025-03-20 | 17:40 | 49.974
2025-03-20 | 17:40 | 49.971
2025-03-20 | 17:40 | 49.971
2025-03-20 | 17:40 | 49.973
2025-03-20 | 17:40 | 49.972
2025-03-20 | 17:40 | 49.974
2025-03-20 | 17:40 | 49.977
2025-03-20 | 17:40 | 49.979
2025-03-20 | 17:40 | 49.98
2025-03-20 | 17:40 | 49.982
2025-03-20 | 17:40 | 49.983
2025-03-20 | 17:40 | 49.984
2025-03-20 | 17:40 | 49.984
2025-03-20 | 17:40 | 49.984
2025-03-20 | 17:40 | 49.981
2025-03-20 | 17:40 | 49.981
2025-03-20 | 17:40 | 49.981
2025-03-20 | 17:40 | 49.983
2025-03-20 | 17:40 | 49.983
2025-03-20 | 17:40 | 49.982
2025-03-20 | 17:40 | 49.981
2025-03-20 | 17:40 | 49.979
2025-03-20 | 17:40 | 49.977
2025-03-20 | 17:40 | 49.976
2025-03-20 | 17:40 | 49.977
2025-03-20 | 17:40 | 49.979
2025-03-20 | 17:40 | 49.98
2025-03-20 | 17:40 | 49.98
2025-03-20 | 17:40 | 49.979
2025-03-20 | 17:40 | 49.98
2025-03-20 | 17:40 | 49.981
2025-03-20 | 17:40 | 49.982
2025-03-20 | 17:40 | 49.983
2025-03-20 | 17:40 | 49.984
2025-03-20 | 17:40 | 49.984
2025-03-20 | 17:40 | 49.985
2025-03-20 | 17:40 | 49.986
2025-03-20 | 17:40 | 49.987
2025-03-20 | 17:40 | 49.987
2025-03-20 | 17:40 | 49.986
2025-03-20 | 17:40 | 49.985
2025-03-20 | 17:40 | 49.982
2025-03-20 | 17:40 | 49.979
2025-03-20 | 17:40 | 49.978
2025-03-20 | 17:40 | 49.975
2025-03-20 | 17:40 | 49.973
2025-03-20 | 17:40 | 49.97
2025-03-20 | 17:40 | 49.965
2025-03-20 | 17:41 | 49.963
2025-03-20 | 17:41 | 49.962
2025-03-20 | 17:41 | 49.964
2025-03-20 | 17:41 | 49.968
2025-03-20 | 17:41 | 49.973
2025-03-20 | 17:41 | 49.976
2025-03-20 | 17:41 | 49.978
2025-03-20 | 17:41 | 49.981
2025-03-20 | 17:41 | 49.981
2025-03-20 | 17:41 | 49.98
2025-03-20 | 17:41 | 49.981
2025-03-20 | 17:41 | 49.979
2025-03-20 | 17:41 | 49.978
2025-03-20 | 17:41 | 49.977
2025-03-20 | 17:41 | 49.977
2025-03-20 | 17:41 | 49.977
2025-03-20 | 17:41 | 49.974
2025-03-20 | 17:41 | 49.973
2025-03-20 | 17:41 | 49.972
2025-03-20 | 17:41 | 49.97
2025-03-20 | 17:41 | 49.97
2025-03-20 | 17:41 | 49.969
2025-03-20 | 17:41 | 49.967
2025-03-20 | 17:41 | 49.965
2025-03-20 | 17:41 | 49.965
2025-03-20 | 17:41 | 49.964
2025-03-20 | 17:41 | 49.962
2025-03-20 | 17:41 | 49.958
2025-03-20 | 17:41 | 49.955
2025-03-20 | 17:41 | 49.951
2025-03-20 | 17:41 | 49.947
2025-03-20 | 17:41 | 49.94
2025-03-20 | 17:41 | 49.935
2025-03-20 | 17:41 | 49.934
2025-03-20 | 17:41 | 49.931
2025-03-20 | 17:41 | 49.93
2025-03-20 | 17:41 | 49.932
2025-03-20 | 17:41 | 49.931
2025-03-20 | 17:41 | 49.932
2025-03-20 | 17:41 | 49.933
2025-03-20 | 17:41 | 49.935
2025-03-20 | 17:41 | 49.937
2025-03-20 | 17:41 | 49.938
2025-03-20 | 17:41 | 49.938
2025-03-20 | 17:41 | 49.936
2025-03-20 | 17:41 | 49.936
2025-03-20 | 17:41 | 49.936
2025-03-20 | 17:41 | 49.937
2025-03-20 | 17:41 | 49.936
2025-03-20 | 17:41 | 49.936
2025-03-20 | 17:41 | 49.937
2025-03-20 | 17:41 | 49.939
2025-03-20 | 17:41 | 49.938
2025-03-20 | 17:41 | 49.936
2025-03-20 | 17:41 | 49.932
2025-03-20 | 17:41 | 49.932
2025-03-20 | 17:41 | 49.931
2025-03-20 | 17:41 | 49.93
2025-03-20 | 17:41 | 49.928
2025-03-20 | 17:42 | 49.927
2025-03-20 | 17:42 | 49.927
2025-03-20 | 17:42 | 49.928
2025-03-20 | 17:42 | 49.932
2025-03-20 | 17:42 | 49.936
2025-03-20 | 17:42 | 49.939
2025-03-20 | 17:42 | 49.942
2025-03-20 | 17:42 | 49.945
2025-03-20 | 17:42 | 49.946
2025-03-20 | 17:42 | 49.946
2025-03-20 | 17:42 | 49.946
2025-03-20 | 17:42 | 49.942
2025-03-20 | 17:42 | 49.941
2025-03-20 | 17:42 | 49.939
2025-03-20 | 17:42 | 49.94
2025-03-20 | 17:42 | 49.94
2025-03-20 | 17:42 | 49.942
2025-03-20 | 17:42 | 49.942
2025-03-20 | 17:42 | 49.942
2025-03-20 | 17:42 | 49.942
2025-03-20 | 17:42 | 49.944
2025-03-20 | 17:42 | 49.944
2025-03-20 | 17:42 | 49.942
2025-03-20 | 17:42 | 49.94
2025-03-20 | 17:42 | 49.94
2025-03-20 | 17:42 | 49.938
2025-03-20 | 17:42 | 49.937
2025-03-20 | 17:42 | 49.936
2025-03-20 | 17:42 | 49.937
2025-03-20 | 17:42 | 49.938
2025-03-20 | 17:42 | 49.941
2025-03-20 | 17:42 | 49.944
2025-03-20 | 17:42 | 49.947
2025-03-20 | 17:42 | 49.949
2025-03-20 | 17:42 | 49.951
2025-03-20 | 17:42 | 49.953
2025-03-20 | 17:42 | 49.954
2025-03-20 | 17:42 | 49.953
2025-03-20 | 17:42 | 49.955
2025-03-20 | 17:42 | 49.955
2025-03-20 | 17:42 | 49.955
2025-03-20 | 17:42 | 49.958
2025-03-20 | 17:42 | 49.959
2025-03-20 | 17:42 | 49.958
2025-03-20 | 17:42 | 49.957
2025-03-20 | 17:42 | 49.956
2025-03-20 | 17:42 | 49.955
2025-03-20 | 17:42 | 49.954
2025-03-20 | 17:42 | 49.956
2025-03-20 | 17:42 | 49.957
2025-03-20 | 17:42 | 49.961
2025-03-20 | 17:42 | 49.965
2025-03-20 | 17:42 | 49.97
2025-03-20 | 17:42 | 49.971
2025-03-20 | 17:42 | 49.974
2025-03-20 | 17:42 | 49.975
2025-03-20 | 17:42 | 49.977
2025-03-20 | 17:42 | 49.98
2025-03-20 | 17:42 | 49.982
2025-03-20 | 17:42 | 49.986
2025-03-20 | 17:42 | 49.987
2025-03-20 | 17:43 | 49.99
2025-03-20 | 17:43 | 49.996
2025-03-20 | 17:43 | 50.004
2025-03-20 | 17:43 | 50.014
2025-03-20 | 17:43 | 50.022
2025-03-20 | 17:43 | 50.03
2025-03-20 | 17:43 | 50.034
2025-03-20 | 17:43 | 50.04
2025-03-20 | 17:43 | 50.042
2025-03-20 | 17:43 | 50.044
2025-03-20 | 17:43 | 50.044
2025-03-20 | 17:43 | 50.043
2025-03-20 | 17:43 | 50.041
2025-03-20 | 17:43 | 50.042
2025-03-20 | 17:43 | 50.04
2025-03-20 | 17:43 | 50.039
2025-03-20 | 17:43 | 50.036
2025-03-20 | 17:43 | 50.037
2025-03-20 | 17:43 | 50.037
2025-03-20 | 17:43 | 50.038
2025-03-20 | 17:43 | 50.04
2025-03-20 | 17:43 | 50.042
2025-03-20 | 17:43 | 50.044
2025-03-20 | 17:43 | 50.048
2025-03-20 | 17:43 | 50.051
2025-03-20 | 17:43 | 50.054
2025-03-20 | 17:43 | 50.056
2025-03-20 | 17:43 | 50.058
2025-03-20 | 17:43 | 50.061
2025-03-20 | 17:43 | 50.061
2025-03-20 | 17:43 | 50.062
2025-03-20 | 17:43 | 50.06
2025-03-20 | 17:43 | 50.056
2025-03-20 | 17:43 | 50.055
2025-03-20 | 17:43 | 50.053
2025-03-20 | 17:43 | 50.051
2025-03-20 | 17:43 | 50.052
2025-03-20 | 17:43 | 50.052
2025-03-20 | 17:43 | 50.053
2025-03-20 | 17:43 | 50.056
2025-03-20 | 17:43 | 50.058
2025-03-20 | 17:43 | 50.06
2025-03-20 | 17:43 | 50.063
2025-03-20 | 17:43 | 50.064
2025-03-20 | 17:43 | 50.066
2025-03-20 | 17:43 | 50.069
2025-03-20 | 17:43 | 50.069
2025-03-20 | 17:43 | 50.072
2025-03-20 | 17:43 | 50.073
2025-03-20 | 17:43 | 50.075
2025-03-20 | 17:43 | 50.074
2025-03-20 | 17:43 | 50.074
2025-03-20 | 17:43 | 50.074
2025-03-20 | 17:43 | 50.072
2025-03-20 | 17:43 | 50.07
2025-03-20 | 17:43 | 50.07
2025-03-20 | 17:43 | 50.068
2025-03-20 | 17:43 | 50.067
2025-03-20 | 17:43 | 50.064
2025-03-20 | 17:44 | 50.064
2025-03-20 | 17:44 | 50.066
2025-03-20 | 17:44 | 50.068
2025-03-20 | 17:44 | 50.068

## 20250320-2
In GMT
Date | Time | Freq
2025-03-20 | 23:48 | 50.037 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-20 | 23:48 | 50.04 | 222 | BRITNED | 676.211
2025-03-20 | 23:48 | 50.039 | 268 | WBURB-2 | 428.156
2025-03-20 | 23:48 | 50.041 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-20 | 23:48 | 50.046 |  | Viking Link | -648.9
2025-03-20 | 23:48 | 50.054 |  | Viking Link | 1398.96
2025-03-20 | 23:48 | 50.058 | 209 | DRAXX-3 | 626.95
2025-03-20 | 23:48 | 50.056 | 154 | CDCL-1 | 391.57
2025-03-20 | 23:49 | 50.051 | 268 | ROCK-1 | 468.495
2025-03-20 | 23:49 | 50.052 | 148 | IFA Bipole1 | 945.473
2025-03-20 | 23:49 | 50.052 | 132 | IFA Bipole1 | 999.1
2025-03-20 | 23:49 | 50.056 | 141 | IFA Bipole2 | 1000
2025-03-20 | 23:49 | 50.062 | 135 | IFA Bipole1 | 996.75
2025-03-20 | 23:49 | 50.065 |  | Viking Link | -780.3
2025-03-20 | 23:49 | 50.069
2025-03-20 | 23:49 | 50.067
2025-03-20 | 23:49 | 50.067
2025-03-20 | 23:49 | 50.063
2025-03-20 | 23:49 | 50.058
2025-03-20 | 23:49 | 50.058 | 130 | HEYM12 | 271.908
2025-03-20 | 23:49 | 50.054 | 228 | HUMR-1 | 303.75
2025-03-20 | 23:49 | 50.055
2025-03-20 | 23:49 | 50.056
2025-03-20 | 23:49 | 50.053
2025-03-20 | 23:49 | 50.049
2025-03-20 | 23:49 | 50.05
2025-03-20 | 23:49 | 50.052
2025-03-20 | 23:49 | 50.052
2025-03-20 | 23:49 | 50.048
2025-03-20 | 23:49 | 50.045
2025-03-20 | 23:49 | 50.045 | 211 | CDCL-1 | 291.5
2025-03-20 | 23:49 | 50.053 | 199 | STAY-2 | 413.125
2025-03-20 | 23:49 | 50.063 | 173 | CDCL-1 | 397.375
2025-03-20 | 23:49 | 50.067 | 248 | SEAB-2 | 361.25
2025-03-20 | 23:49 | 50.064 | 255 | FRANCE | 995.65
2025-03-20 | 23:49 | 50.063 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-20 | 23:49 | 50.063
2025-03-20 | 23:49 | 50.061
2025-03-20 | 23:49 | 50.053
2025-03-20 | 23:49 | 50.048
2025-03-20 | 23:49 | 50.042
2025-03-20 | 23:49 | 50.051
2025-03-20 | 23:49 | 50.058
2025-03-20 | 23:49 | 50.054
2025-03-20 | 23:49 | 50.048
2025-03-20 | 23:49 | 50.04
2025-03-20 | 23:49 | 50.034
2025-03-20 | 23:49 | 50.043
2025-03-20 | 23:49 | 50.048
2025-03-20 | 23:49 | 50.05
2025-03-20 | 23:49 | 50.045
2025-03-20 | 23:49 | 50.039
2025-03-20 | 23:49 | 50.045
2025-03-20 | 23:49 | 50.05
2025-03-20 | 23:49 | 50.049
2025-03-20 | 23:49 | 50.041
2025-03-20 | 23:49 | 50.033
2025-03-20 | 23:49 | 50.03
2025-03-20 | 23:49 | 50.023
2025-03-20 | 23:49 | 50.028
2025-03-20 | 23:49 | 50.04
2025-03-20 | 23:49 | 50.13
2025-03-20 | 23:49 | 50.052
2025-03-20 | 23:49 | 50.079
2025-03-20 | 23:49 | 50.084
2025-03-20 | 23:49 | 50.078
2025-03-20 | 23:49 | 50.066
2025-03-20 | 23:50 | 50.061
2025-03-20 | 23:50 | 50.061
2025-03-20 | 23:50 | 50.072
2025-03-20 | 23:50 | 50.072
2025-03-20 | 23:50 | 50.072
2025-03-20 | 23:50 | 50.068
2025-03-20 | 23:50 | 50.068
2025-03-20 | 23:50 | 50.068
2025-03-20 | 23:50 | 50.066
2025-03-20 | 23:50 | 50.064
2025-03-20 | 23:50 | 50.063
2025-03-20 | 23:50 | 50.063
2025-03-20 | 23:50 | 50.062
2025-03-20 | 23:50 | 50.059
2025-03-20 | 23:50 | 50.058
2025-03-20 | 23:50 | 50.061
2025-03-20 | 23:50 | 50.059
2025-03-20 | 23:50 | 50.059
2025-03-20 | 23:50 | 50.056
2025-03-20 | 23:50 | 50.057
2025-03-20 | 23:50 | 50.054
2025-03-20 | 23:50 | 50.048
2025-03-20 | 23:50 | 50.044
2025-03-20 | 23:50 | 50.043
2025-03-20 | 23:50 | 50.047
2025-03-20 | 23:50 | 50.053
2025-03-20 | 23:50 | 50.056
2025-03-20 | 23:50 | 50.056
2025-03-20 | 23:50 | 50.05
2025-03-20 | 23:50 | 50.041
2025-03-20 | 23:50 | 50.035
2025-03-20 | 23:50 | 50.032
2025-03-20 | 23:50 | 50.034
2025-03-20 | 23:50 | 50.044
2025-03-20 | 23:50 | 50.047
2025-03-20 | 23:50 | 50.049
2025-03-20 | 23:50 | 50.045
2025-03-20 | 23:50 | 50.047
2025-03-20 | 23:50 | 50.045
2025-03-20 | 23:50 | 50.047
2025-03-20 | 23:50 | 50.045
2025-03-20 | 23:50 | 50.043
2025-03-20 | 23:50 | 50.042
2025-03-20 | 23:50 | 50.042
2025-03-20 | 23:50 | 50.041
2025-03-20 | 23:50 | 50.037
2025-03-20 | 23:50 | 50.034
2025-03-20 | 23:50 | 50.037
2025-03-20 | 23:50 | 50.037
2025-03-20 | 23:50 | 50.038
2025-03-20 | 23:50 | 50.032
2025-03-20 | 23:50 | 50.028
2025-03-20 | 23:50 | 50.034
2025-03-20 | 23:50 | 50.041
2025-03-20 | 23:50 | 50.044
2025-03-20 | 23:50 | 50.045
2025-03-20 | 23:50 | 50.046
2025-03-20 | 23:50 | 50.045
2025-03-20 | 23:50 | 50.046
2025-03-20 | 23:50 | 50.043
2025-03-20 | 23:50 | 50.041
2025-03-20 | 23:51 | 50.04
2025-03-20 | 23:51 | 50.04
2025-03-20 | 23:51 | 50.037
2025-03-20 | 23:51 | 50.031
2025-03-20 | 23:51 | 50.029
2025-03-20 | 23:51 | 50.025
2025-03-20 | 23:51 | 50.028
2025-03-20 | 23:51 | 50.028
2025-03-20 | 23:51 | 50.03
2025-03-20 | 23:51 | 50.031
2025-03-20 | 23:51 | 50.035
2025-03-20 | 23:51 | 50.035
2025-03-20 | 23:51 | 50.033
2025-03-20 | 23:51 | 50.031
2025-03-20 | 23:51 | 50.03
2025-03-20 | 23:51 | 50.03
2025-03-20 | 23:51 | 50.028
2025-03-20 | 23:51 | 50.027
2025-03-20 | 23:51 | 50.029
2025-03-20 | 23:51 | 50.028
2025-03-20 | 23:51 | 50.028
2025-03-20 | 23:51 | 50.029
2025-03-20 | 23:51 | 50.03
2025-03-20 | 23:51 | 50.027
2025-03-20 | 23:51 | 50.026
2025-03-20 | 23:51 | 50.025
2025-03-20 | 23:51 | 50.025
2025-03-20 | 23:51 | 50.023
2025-03-20 | 23:51 | 50.023
2025-03-20 | 23:51 | 50.026
2025-03-20 | 23:51 | 50.026
2025-03-20 | 23:51 | 50.03
2025-03-20 | 23:51 | 50.037
2025-03-20 | 23:51 | 50.042
2025-03-20 | 23:51 | 50.042
2025-03-20 | 23:51 | 50.043
2025-03-20 | 23:51 | 50.042
2025-03-20 | 23:51 | 50.042
2025-03-20 | 23:51 | 50.046
2025-03-20 | 23:51 | 50.048
2025-03-20 | 23:51 | 50.046
2025-03-20 | 23:51 | 50.043
2025-03-20 | 23:51 | 50.042
2025-03-20 | 23:51 | 50.043
2025-03-20 | 23:51 | 50.046
2025-03-20 | 23:51 | 50.042
2025-03-20 | 23:51 | 50.039
2025-03-20 | 23:51 | 50.039
2025-03-20 | 23:51 | 50.042
2025-03-20 | 23:51 | 50.045
2025-03-20 | 23:51 | 50.044
2025-03-20 | 23:51 | 50.045
2025-03-20 | 23:51 | 50.048
2025-03-20 | 23:51 | 50.05
2025-03-20 | 23:51 | 50.051
2025-03-20 | 23:51 | 50.053
2025-03-20 | 23:51 | 50.053
2025-03-20 | 23:51 | 50.052
2025-03-20 | 23:51 | 50.052
2025-03-20 | 23:52 | 50.048
2025-03-20 | 23:52 | 50.046
2025-03-20 | 23:52 | 50.048
2025-03-20 | 23:52 | 50.047
2025-03-20 | 23:52 | 50.045
2025-03-20 | 23:52 | 50.047
2025-03-20 | 23:52 | 50.045
2025-03-20 | 23:52 | 50.048
2025-03-20 | 23:52 | 50.053
2025-03-20 | 23:52 | 50.057
2025-03-20 | 23:52 | 50.053
2025-03-20 | 23:52 | 50.056
2025-03-20 | 23:52 | 50.059
2025-03-20 | 23:52 | 50.06
2025-03-20 | 23:52 | 50.054
2025-03-20 | 23:52 | 50.05
2025-03-20 | 23:52 | 50.051
2025-03-20 | 23:52 | 50.05
2025-03-20 | 23:52 | 50.046
2025-03-20 | 23:52 | 50.043
2025-03-20 | 23:52 | 50.044
2025-03-20 | 23:52 | 50.045
2025-03-20 | 23:52 | 50.043
2025-03-20 | 23:52 | 50.044
2025-03-20 | 23:52 | 50.048
2025-03-20 | 23:52 | 50.05
2025-03-20 | 23:52 | 50.049
2025-03-20 | 23:52 | 50.048
2025-03-20 | 23:52 | 50.049
2025-03-20 | 23:52 | 50.049
2025-03-20 | 23:52 | 50.044
2025-03-20 | 23:52 | 50.038
2025-03-20 | 23:52 | 50.035
2025-03-20 | 23:52 | 50.034
2025-03-20 | 23:52 | 50.038
2025-03-20 | 23:52 | 50.044
2025-03-20 | 23:52 | 50.045
2025-03-20 | 23:52 | 50.04
2025-03-20 | 23:52 | 50.034
2025-03-20 | 23:52 | 50.036
2025-03-20 | 23:52 | 50.038
2025-03-20 | 23:52 | 50.04
2025-03-20 | 23:52 | 50.042
2025-03-20 | 23:52 | 50.04
2025-03-20 | 23:52 | 50.042
2025-03-20 | 23:52 | 50.046
2025-03-20 | 23:52 | 50.045
2025-03-20 | 23:52 | 50.044
2025-03-20 | 23:52 | 50.042
2025-03-20 | 23:52 | 50.039
2025-03-20 | 23:52 | 50.039
2025-03-20 | 23:52 | 50.043
2025-03-20 | 23:52 | 50.042
2025-03-20 | 23:52 | 50.041
2025-03-20 | 23:52 | 50.038
2025-03-20 | 23:52 | 50.035
2025-03-20 | 23:52 | 50.036
2025-03-20 | 23:52 | 50.039
2025-03-20 | 23:52 | 50.041
2025-03-20 | 23:52 | 50.04
2025-03-20 | 23:52 | 50.04
2025-03-20 | 23:53 | 50.039
2025-03-20 | 23:53 | 50.039
2025-03-20 | 23:53 | 50.037
2025-03-20 | 23:53 | 50.035
2025-03-20 | 23:53 | 50.036
2025-03-20 | 23:53 | 50.037
2025-03-20 | 23:53 | 50.038
2025-03-20 | 23:53 | 50.039
2025-03-20 | 23:53 | 50.04
2025-03-20 | 23:53 | 50.041
2025-03-20 | 23:53 | 50.039
2025-03-20 | 23:53 | 50.039
2025-03-20 | 23:53 | 50.035
2025-03-20 | 23:53 | 50.031
2025-03-20 | 23:53 | 50.03
2025-03-20 | 23:53 | 50.033
2025-03-20 | 23:53 | 50.037
2025-03-20 | 23:53 | 50.042
2025-03-20 | 23:53 | 50.042
2025-03-20 | 23:53 | 50.039
2025-03-20 | 23:53 | 50.039
2025-03-20 | 23:53 | 50.035
2025-03-20 | 23:53 | 50.032
2025-03-20 | 23:53 | 50.031
2025-03-20 | 23:53 | 50.032
2025-03-20 | 23:53 | 50.034
2025-03-20 | 23:53 | 50.036
2025-03-20 | 23:53 | 50.036
2025-03-20 | 23:53 | 50.037
2025-03-20 | 23:53 | 50.037
2025-03-20 | 23:53 | 50.035
2025-03-20 | 23:53 | 50.034
2025-03-20 | 23:53 | 50.033
2025-03-20 | 23:53 | 50.03
2025-03-20 | 23:53 | 50.033
2025-03-20 | 23:53 | 50.033
2025-03-20 | 23:53 | 50.031
2025-03-20 | 23:53 | 50.027
2025-03-20 | 23:53 | 50.025
2025-03-20 | 23:53 | 50.023
2025-03-20 | 23:53 | 50.025
2025-03-20 | 23:53 | 50.025
2025-03-20 | 23:53 | 50.026
2025-03-20 | 23:53 | 50.026
2025-03-20 | 23:53 | 50.027
2025-03-20 | 23:53 | 50.028
2025-03-20 | 23:53 | 50.028
2025-03-20 | 23:53 | 50.029
2025-03-20 | 23:53 | 50.033
2025-03-20 | 23:53 | 50.032
2025-03-20 | 23:53 | 50.026
2025-03-20 | 23:53 | 50.026
2025-03-20 | 23:53 | 50.032
2025-03-20 | 23:53 | 50.034
2025-03-20 | 23:53 | 50.033
2025-03-20 | 23:53 | 50.029
2025-03-20 | 23:53 | 50.03
2025-03-20 | 23:53 | 50.031
2025-03-20 | 23:53 | 50.031
2025-03-20 | 23:54 | 50.033
2025-03-20 | 23:54 | 50.034
2025-03-20 | 23:54 | 50.03
2025-03-20 | 23:54 | 50.028
2025-03-20 | 23:54 | 50.029
2025-03-20 | 23:54 | 50.029
2025-03-20 | 23:54 | 50.028
2025-03-20 | 23:54 | 50.029
2025-03-20 | 23:54 | 50.029
2025-03-20 | 23:54 | 50.03
2025-03-20 | 23:54 | 50.029
2025-03-20 | 23:54 | 50.034
2025-03-20 | 23:54 | 50.039
2025-03-20 | 23:54 | 50.04
2025-03-20 | 23:54 | 50.038
2025-03-20 | 23:54 | 50.037
2025-03-20 | 23:54 | 50.036
2025-03-20 | 23:54 | 50.033
2025-03-20 | 23:54 | 50.028
2025-03-20 | 23:54 | 50.025
2025-03-20 | 23:54 | 50.026
2025-03-20 | 23:54 | 50.028
2025-03-20 | 23:54 | 50.028
2025-03-20 | 23:54 | 50.029
2025-03-20 | 23:54 | 50.027
2025-03-20 | 23:54 | 50.026
2025-03-20 | 23:54 | 50.022
2025-03-20 | 23:54 | 50.02
2025-03-20 | 23:54 | 50.023
2025-03-20 | 23:54 | 50.023
2025-03-20 | 23:54 | 50.02
2025-03-20 | 23:54 | 50.015
2025-03-20 | 23:54 | 50.011
2025-03-20 | 23:54 | 50.016
2025-03-20 | 23:54 | 50.025
2025-03-20 | 23:54 | 50.031
2025-03-20 | 23:54 | 50.031
2025-03-20 | 23:54 | 50.027
2025-03-20 | 23:54 | 50.024
2025-03-20 | 23:54 | 50.02
2025-03-20 | 23:54 | 50.017
2025-03-20 | 23:54 | 50.019
2025-03-20 | 23:54 | 50.023
2025-03-20 | 23:54 | 50.027
2025-03-20 | 23:54 | 50.031
2025-03-20 | 23:54 | 50.038
2025-03-20 | 23:54 | 50.039
2025-03-20 | 23:54 | 50.035
2025-03-20 | 23:54 | 50.035
2025-03-20 | 23:54 | 50.037
2025-03-20 | 23:54 | 50.036
2025-03-20 | 23:54 | 50.036
2025-03-20 | 23:54 | 50.036
2025-03-20 | 23:54 | 50.033
2025-03-20 | 23:54 | 50.029
2025-03-20 | 23:54 | 50.03
2025-03-20 | 23:54 | 50.039
2025-03-20 | 23:54 | 50.047
2025-03-20 | 23:54 | 50.053
2025-03-20 | 23:54 | 50.057
2025-03-20 | 23:54 | 50.058
2025-03-20 | 23:55 | 50.056
2025-03-20 | 23:55 | 50.055
2025-03-20 | 23:55 | 50.052
2025-03-20 | 23:55 | 50.051
2025-03-20 | 23:55 | 50.05
2025-03-20 | 23:55 | 50.05
2025-03-20 | 23:55 | 50.049
2025-03-20 | 23:55 | 50.045
2025-03-20 | 23:55 | 50.042
2025-03-20 | 23:55 | 50.038
2025-03-20 | 23:55 | 50.035
2025-03-20 | 23:55 | 50.035
2025-03-20 | 23:55 | 50.037
2025-03-20 | 23:55 | 50.044
2025-03-20 | 23:55 | 50.045
2025-03-20 | 23:55 | 50.042
2025-03-20 | 23:55 | 50.043
2025-03-20 | 23:55 | 50.049
2025-03-20 | 23:55 | 50.051
2025-03-20 | 23:55 | 50.053
2025-03-20 | 23:55 | 50.053
2025-03-20 | 23:55 | 50.056
2025-03-20 | 23:55 | 50.057
2025-03-20 | 23:55 | 50.055
2025-03-20 | 23:55 | 50.054
2025-03-20 | 23:55 | 50.051
2025-03-20 | 23:55 | 50.048
2025-03-20 | 23:55 | 50.045
2025-03-20 | 23:55 | 50.044
2025-03-20 | 23:55 | 50.043
2025-03-20 | 23:55 | 50.04
2025-03-20 | 23:55 | 50.038
2025-03-20 | 23:55 | 50.037
2025-03-20 | 23:55 | 50.04
2025-03-20 | 23:55 | 50.041
2025-03-20 | 23:55 | 50.046
2025-03-20 | 23:55 | 50.051
2025-03-20 | 23:55 | 50.054
2025-03-20 | 23:55 | 50.055
2025-03-20 | 23:55 | 50.058
2025-03-20 | 23:55 | 50.061
2025-03-20 | 23:55 | 50.061
2025-03-20 | 23:55 | 50.062
2025-03-20 | 23:55 | 50.06
2025-03-20 | 23:55 | 50.058
2025-03-20 | 23:55 | 50.058
2025-03-20 | 23:55 | 50.054
2025-03-20 | 23:55 | 50.054
2025-03-20 | 23:55 | 50.055
2025-03-20 | 23:55 | 50.058
2025-03-20 | 23:55 | 50.055
2025-03-20 | 23:55 | 50.051
2025-03-20 | 23:55 | 50.05
2025-03-20 | 23:55 | 50.05
2025-03-20 | 23:55 | 50.049
2025-03-20 | 23:55 | 50.048
2025-03-20 | 23:55 | 50.049
2025-03-20 | 23:55 | 50.054
2025-03-20 | 23:55 | 50.055
2025-03-20 | 23:56 | 50.054
2025-03-20 | 23:56 | 50.058
2025-03-20 | 23:56 | 50.058
2025-03-20 | 23:56 | 50.056
2025-03-20 | 23:56 | 50.054
2025-03-20 | 23:56 | 50.054
2025-03-20 | 23:56 | 50.055
2025-03-20 | 23:56 | 50.055
2025-03-20 | 23:56 | 50.057
2025-03-20 | 23:56 | 50.058
2025-03-20 | 23:56 | 50.058
2025-03-20 | 23:56 | 50.058
2025-03-20 | 23:56 | 50.058
2025-03-20 | 23:56 | 50.057
2025-03-20 | 23:56 | 50.059
2025-03-20 | 23:56 | 50.06
2025-03-20 | 23:56 | 50.06
2025-03-20 | 23:56 | 50.058
2025-03-20 | 23:56 | 50.059
2025-03-20 | 23:56 | 50.06
2025-03-20 | 23:56 | 50.064
2025-03-20 | 23:56 | 50.066
2025-03-20 | 23:56 | 50.066
2025-03-20 | 23:56 | 50.067
2025-03-20 | 23:56 | 50.069
2025-03-20 | 23:56 | 50.067
2025-03-20 | 23:56 | 50.066
2025-03-20 | 23:56 | 50.063
2025-03-20 | 23:56 | 50.063
2025-03-20 | 23:56 | 50.062
2025-03-20 | 23:56 | 50.062
2025-03-20 | 23:56 | 50.06
2025-03-20 | 23:56 | 50.058
2025-03-20 | 23:56 | 50.059
2025-03-20 | 23:56 | 50.059
2025-03-20 | 23:56 | 50.058
2025-03-20 | 23:56 | 50.059
2025-03-20 | 23:56 | 50.058
2025-03-20 | 23:56 | 50.055
2025-03-20 | 23:56 | 50.053
2025-03-20 | 23:56 | 50.053
2025-03-20 | 23:56 | 50.057
2025-03-20 | 23:56 | 50.061
2025-03-20 | 23:56 | 50.063
2025-03-20 | 23:56 | 50.064
2025-03-20 | 23:56 | 50.065
2025-03-20 | 23:56 | 50.066
2025-03-20 | 23:56 | 50.065
2025-03-20 | 23:56 | 50.067
2025-03-20 | 23:56 | 50.071
2025-03-20 | 23:56 | 50.074
2025-03-20 | 23:56 | 50.072
2025-03-20 | 23:56 | 50.071
2025-03-20 | 23:56 | 50.067
2025-03-20 | 23:56 | 50.067
2025-03-20 | 23:56 | 50.07
2025-03-20 | 23:56 | 50.073
2025-03-20 | 23:56 | 50.075
2025-03-20 | 23:56 | 50.08
2025-03-20 | 23:56 | 50.086
2025-03-20 | 23:56 | 50.094
2025-03-20 | 23:57 | 50.099
2025-03-20 | 23:57 | 50.102
2025-03-20 | 23:57 | 50.102
2025-03-20 | 23:57 | 50.103
2025-03-20 | 23:57 | 50.103
2025-03-20 | 23:57 | 50.104
2025-03-20 | 23:57 | 50.104
2025-03-20 | 23:57 | 50.106
2025-03-20 | 23:57 | 50.105
2025-03-20 | 23:57 | 50.103
2025-03-20 | 23:57 | 50.103
2025-03-20 | 23:57 | 50.104
2025-03-20 | 23:57 | 50.104
2025-03-20 | 23:57 | 50.105
2025-03-20 | 23:57 | 50.105
2025-03-20 | 23:57 | 50.107
2025-03-20 | 23:57 | 50.106
2025-03-20 | 23:57 | 50.107
2025-03-20 | 23:57 | 50.109
2025-03-20 | 23:57 | 50.11
2025-03-20 | 23:57 | 50.11
2025-03-20 | 23:57 | 50.11
2025-03-20 | 23:57 | 50.108
2025-03-20 | 23:57 | 50.105
2025-03-20 | 23:57 | 50.103
2025-03-20 | 23:57 | 50.105
2025-03-20 | 23:57 | 50.106
2025-03-20 | 23:57 | 50.109
2025-03-20 | 23:57 | 50.112
2025-03-20 | 23:57 | 50.112
2025-03-20 | 23:57 | 50.109
2025-03-20 | 23:57 | 50.107
2025-03-20 | 23:57 | 50.109
2025-03-20 | 23:57 | 50.112
2025-03-20 | 23:57 | 50.112
2025-03-20 | 23:57 | 50.111
2025-03-20 | 23:57 | 50.108
2025-03-20 | 23:57 | 50.109
2025-03-20 | 23:57 | 50.109
2025-03-20 | 23:57 | 50.11
2025-03-20 | 23:57 | 50.108
2025-03-20 | 23:57 | 50.107
2025-03-20 | 23:57 | 50.105
2025-03-20 | 23:57 | 50.107
2025-03-20 | 23:57 | 50.11
2025-03-20 | 23:57 | 50.11
2025-03-20 | 23:57 | 50.111
2025-03-20 | 23:57 | 50.113
2025-03-20 | 23:57 | 50.112
2025-03-20 | 23:57 | 50.112
2025-03-20 | 23:57 | 50.11
2025-03-20 | 23:57 | 50.109
2025-03-20 | 23:57 | 50.108
2025-03-20 | 23:57 | 50.107
2025-03-20 | 23:57 | 50.106
2025-03-20 | 23:57 | 50.106
2025-03-20 | 23:57 | 50.107
2025-03-20 | 23:57 | 50.106
2025-03-20 | 23:57 | 50.105
2025-03-20 | 23:58 | 50.105
2025-03-20 | 23:58 | 50.106
2025-03-20 | 23:58 | 50.11
2025-03-20 | 23:58 | 50.111
2025-03-20 | 23:58 | 50.112
2025-03-20 | 23:58 | 50.109
2025-03-20 | 23:58 | 50.107
2025-03-20 | 23:58 | 50.108
2025-03-20 | 23:58 | 50.11
2025-03-20 | 23:58 | 50.109
2025-03-20 | 23:58 | 50.107
2025-03-20 | 23:58 | 50.105
2025-03-20 | 23:58 | 50.106
2025-03-20 | 23:58 | 50.107
2025-03-20 | 23:58 | 50.107
2025-03-20 | 23:58 | 50.108
2025-03-20 | 23:58 | 50.112
2025-03-20 | 23:58 | 50.113
2025-03-20 | 23:58 | 50.112
2025-03-20 | 23:58 | 50.11
2025-03-20 | 23:58 | 50.108
2025-03-20 | 23:58 | 50.106
2025-03-20 | 23:58 | 50.108
2025-03-20 | 23:58 | 50.107
2025-03-20 | 23:58 | 50.105
2025-03-20 | 23:58 | 50.102
2025-03-20 | 23:58 | 50.105
2025-03-20 | 23:58 | 50.106
2025-03-20 | 23:58 | 50.108
2025-03-20 | 23:58 | 50.108
2025-03-20 | 23:58 | 50.107
2025-03-20 | 23:58 | 50.106
2025-03-20 | 23:58 | 50.106
2025-03-20 | 23:58 | 50.104
2025-03-20 | 23:58 | 50.101
2025-03-20 | 23:58 | 50.104
2025-03-20 | 23:58 | 50.104
2025-03-20 | 23:58 | 50.102
2025-03-20 | 23:58 | 50.099
2025-03-20 | 23:58 | 50.098
2025-03-20 | 23:58 | 50.099
2025-03-20 | 23:58 | 50.098
2025-03-20 | 23:58 | 50.097
2025-03-20 | 23:58 | 50.095
2025-03-20 | 23:58 | 50.095
2025-03-20 | 23:58 | 50.095
2025-03-20 | 23:58 | 50.093
2025-03-20 | 23:58 | 50.092
2025-03-20 | 23:58 | 50.09
2025-03-20 | 23:58 | 50.09
2025-03-20 | 23:58 | 50.089
2025-03-20 | 23:58 | 50.091
2025-03-20 | 23:58 | 50.094
2025-03-20 | 23:58 | 50.099
2025-03-20 | 23:58 | 50.1
2025-03-20 | 23:58 | 50.098
2025-03-20 | 23:58 | 50.097
2025-03-20 | 23:58 | 50.096
2025-03-20 | 23:58 | 50.099
2025-03-20 | 23:58 | 50.101
2025-03-20 | 23:58 | 50.102
2025-03-20 | 23:59 | 50.1
2025-03-20 | 23:59 | 50.098
2025-03-20 | 23:59 | 50.098
2025-03-20 | 23:59 | 50.099
2025-03-20 | 23:59 | 50.102
2025-03-20 | 23:59 | 50.104
2025-03-20 | 23:59 | 50.104
2025-03-20 | 23:59 | 50.103
2025-03-20 | 23:59 | 50.102
2025-03-20 | 23:59 | 50.102
2025-03-20 | 23:59 | 50.102
2025-03-20 | 23:59 | 50.104
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.107
2025-03-20 | 23:59 | 50.107
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.102
2025-03-20 | 23:59 | 50.1
2025-03-20 | 23:59 | 50.101
2025-03-20 | 23:59 | 50.101
2025-03-20 | 23:59 | 50.102
2025-03-20 | 23:59 | 50.102
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.106
2025-03-20 | 23:59 | 50.107
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.106
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.107
2025-03-20 | 23:59 | 50.106
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.106
2025-03-20 | 23:59 | 50.108
2025-03-20 | 23:59 | 50.108
2025-03-20 | 23:59 | 50.109
2025-03-20 | 23:59 | 50.109
2025-03-20 | 23:59 | 50.11
2025-03-20 | 23:59 | 50.109
2025-03-20 | 23:59 | 50.111
2025-03-20 | 23:59 | 50.112
2025-03-20 | 23:59 | 50.115
2025-03-20 | 23:59 | 50.115
2025-03-20 | 23:59 | 50.116
2025-03-20 | 23:59 | 50.115
2025-03-20 | 23:59 | 50.117
2025-03-20 | 23:59 | 50.114
2025-03-20 | 23:59 | 50.111
2025-03-20 | 23:59 | 50.11
2025-03-20 | 23:59 | 50.11
2025-03-20 | 23:59 | 50.108
2025-03-20 | 23:59 | 50.106
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.105
2025-03-20 | 23:59 | 50.106
2025-03-20 | 23:59 | 50.104
2025-03-20 | 24:00 | 50.105
2025-03-20 | 24:00 | 50.106
2025-03-20 | 24:00 | 50.107
2025-03-20 | 24:00 | 50.106
2025-03-20 | 24:00 | 50.104
2025-03-20 | 24:00 | 50.103
2025-03-20 | 24:00 | 50.103
2025-03-20 | 24:00 | 50.102
2025-03-20 | 24:00 | 50.103
2025-03-20 | 24:00 | 50.104
2025-03-20 | 24:00 | 50.107
2025-03-20 | 24:00 | 50.109
2025-03-20 | 24:00 | 50.112
2025-03-20 | 24:00 | 50.112
2025-03-20 | 24:00 | 50.113
2025-03-20 | 24:00 | 50.115
2025-03-20 | 24:00 | 50.114
2025-03-20 | 24:00 | 50.112
2025-03-20 | 24:00 | 50.112
2025-03-20 | 24:00 | 50.113
2025-03-20 | 24:00 | 50.112
2025-03-20 | 24:00 | 50.112
2025-03-20 | 24:00 | 50.111
2025-03-20 | 24:00 | 50.111
2025-03-20 | 24:00 | 50.11
2025-03-20 | 24:00 | 50.11
2025-03-20 | 24:00 | 50.111
2025-03-20 | 24:00 | 50.112
2025-03-20 | 24:00 | 50.114
2025-03-20 | 24:00 | 50.117
2025-03-21 | 0:00 | 50.113
2025-03-21 | 0:00 | 50.089
2025-03-21 | 0:00 | 50.072
2025-03-21 | 0:00 | 50.061
2025-03-21 | 0:00 | 50.06
2025-03-21 | 0:00 | 50.066
2025-03-21 | 0:00 | 50.07
2025-03-21 | 0:00 | 50.074
2025-03-21 | 0:00 | 50.076
2025-03-21 | 0:00 | 50.073
2025-03-21 | 0:00 | 50.068
2025-03-21 | 0:00 | 50.064
2025-03-21 | 0:00 | 50.064
2025-03-21 | 0:00 | 50.065
2025-03-21 | 0:00 | 50.065
2025-03-21 | 0:00 | 50.063
2025-03-21 | 0:00 | 50.062
2025-03-21 | 0:00 | 50.062
2025-03-21 | 0:00 | 50.061
2025-03-21 | 0:00 | 50.06
2025-03-21 | 0:00 | 50.062
2025-03-21 | 0:00 | 50.063
2025-03-21 | 0:00 | 50.061
2025-03-21 | 0:00 | 50.06
2025-03-21 | 0:00 | 50.062
2025-03-21 | 0:00 | 50.065
2025-03-21 | 0:00 | 50.069
2025-03-21 | 0:00 | 50.072
2025-03-21 | 0:00 | 50.073
2025-03-21 | 0:00 | 50.072
2025-03-21 | 0:00 | 50.069
2025-03-21 | 0:01 | 50.068
2025-03-21 | 0:01 | 50.068
2025-03-21 | 0:01 | 50.069
2025-03-21 | 0:01 | 50.067
2025-03-21 | 0:01 | 50.066
2025-03-21 | 0:01 | 50.066
2025-03-21 | 0:01 | 50.067
2025-03-21 | 0:01 | 50.066
2025-03-21 | 0:01 | 50.066
2025-03-21 | 0:01 | 50.066
2025-03-21 | 0:01 | 50.064
2025-03-21 | 0:01 | 50.061
2025-03-21 | 0:01 | 50.061
2025-03-21 | 0:01 | 50.063
2025-03-21 | 0:01 | 50.064
2025-03-21 | 0:01 | 50.065
2025-03-21 | 0:01 | 50.066
2025-03-21 | 0:01 | 50.064
2025-03-21 | 0:01 | 50.062
2025-03-21 | 0:01 | 50.061
2025-03-21 | 0:01 | 50.061
2025-03-21 | 0:01 | 50.062
2025-03-21 | 0:01 | 50.063
2025-03-21 | 0:01 | 50.063
2025-03-21 | 0:01 | 50.064
2025-03-21 | 0:01 | 50.065
2025-03-21 | 0:01 | 50.065
2025-03-21 | 0:01 | 50.067
2025-03-21 | 0:01 | 50.07
2025-03-21 | 0:01 | 50.07
2025-03-21 | 0:01 | 50.069
2025-03-21 | 0:01 | 50.069
2025-03-21 | 0:01 | 50.067
2025-03-21 | 0:01 | 50.066
2025-03-21 | 0:01 | 50.066
2025-03-21 | 0:01 | 50.065
2025-03-21 | 0:01 | 50.063
2025-03-21 | 0:01 | 50.063
2025-03-21 | 0:01 | 50.061
2025-03-21 | 0:01 | 50.062
2025-03-21 | 0:01 | 50.064
2025-03-21 | 0:01 | 50.064
2025-03-21 | 0:01 | 50.062
2025-03-21 | 0:01 | 50.062
2025-03-21 | 0:01 | 50.064
2025-03-21 | 0:01 | 50.062
2025-03-21 | 0:01 | 50.063
2025-03-21 | 0:01 | 50.065
2025-03-21 | 0:01 | 50.067
2025-03-21 | 0:01 | 50.067
2025-03-21 | 0:01 | 50.062
2025-03-21 | 0:01 | 50.057
2025-03-21 | 0:01 | 50.053
2025-03-21 | 0:01 | 50.053
2025-03-21 | 0:01 | 50.053
2025-03-21 | 0:01 | 50.058
2025-03-21 | 0:01 | 50.065
2025-03-21 | 0:01 | 50.067
2025-03-21 | 0:01 | 50.066
2025-03-21 | 0:02 | 50.067
2025-03-21 | 0:02 | 50.069
2025-03-21 | 0:02 | 50.069
2025-03-21 | 0:02 | 50.068
2025-03-21 | 0:02 | 50.066
2025-03-21 | 0:02 | 50.061
2025-03-21 | 0:02 | 50.056
2025-03-21 | 0:02 | 50.052
2025-03-21 | 0:02 | 50.052
2025-03-21 | 0:02 | 50.055
2025-03-21 | 0:02 | 50.063
2025-03-21 | 0:02 | 50.064
2025-03-21 | 0:02 | 50.065
2025-03-21 | 0:02 | 50.062
2025-03-21 | 0:02 | 50.062
2025-03-21 | 0:02 | 50.059
2025-03-21 | 0:02 | 50.056
2025-03-21 | 0:02 | 50.052
2025-03-21 | 0:02 | 50.047
2025-03-21 | 0:02 | 50.041
2025-03-21 | 0:02 | 50.036
2025-03-21 | 0:02 | 50.037
2025-03-21 | 0:02 | 50.035
2025-03-21 | 0:02 | 50.033
2025-03-21 | 0:02 | 50.031
2025-03-21 | 0:02 | 50.03
2025-03-21 | 0:02 | 50.035
2025-03-21 | 0:02 | 50.039
2025-03-21 | 0:02 | 50.04
2025-03-21 | 0:02 | 50.041
2025-03-21 | 0:02 | 50.041
2025-03-21 | 0:02 | 50.039
2025-03-21 | 0:02 | 50.039
2025-03-21 | 0:02 | 50.038
2025-03-21 | 0:02 | 50.035
2025-03-21 | 0:02 | 50.033
2025-03-21 | 0:02 | 50.034
2025-03-21 | 0:02 | 50.031
2025-03-21 | 0:02 | 50.029
2025-03-21 | 0:02 | 50.027
2025-03-21 | 0:02 | 50.026
2025-03-21 | 0:02 | 50.023
2025-03-21 | 0:02 | 50.025
2025-03-21 | 0:02 | 50.023
2025-03-21 | 0:02 | 50.024
2025-03-21 | 0:02 | 50.023
2025-03-21 | 0:02 | 50.022
2025-03-21 | 0:02 | 50.024
2025-03-21 | 0:02 | 50.026
2025-03-21 | 0:02 | 50.028
2025-03-21 | 0:02 | 50.029
2025-03-21 | 0:02 | 50.03
2025-03-21 | 0:02 | 50.027
2025-03-21 | 0:02 | 50.026
2025-03-21 | 0:02 | 50.029
2025-03-21 | 0:02 | 50.034
2025-03-21 | 0:02 | 50.036
2025-03-21 | 0:02 | 50.037
2025-03-21 | 0:02 | 50.038
2025-03-21 | 0:02 | 50.039
2025-03-21 | 0:02 | 50.038
2025-03-21 | 0:03 | 50.034
2025-03-21 | 0:03 | 50.031
2025-03-21 | 0:03 | 50.031
2025-03-21 | 0:03 | 50.032
2025-03-21 | 0:03 | 50.032
2025-03-21 | 0:03 | 50.032
2025-03-21 | 0:03 | 50.032
2025-03-21 | 0:03 | 50.029
2025-03-21 | 0:03 | 50.028
2025-03-21 | 0:03 | 50.027
2025-03-21 | 0:03 | 50.026
2025-03-21 | 0:03 | 50.021
2025-03-21 | 0:03 | 50.016
2025-03-21 | 0:03 | 50.014
2025-03-21 | 0:03 | 50.013
2025-03-21 | 0:03 | 50.009
2025-03-21 | 0:03 | 50.005
2025-03-21 | 0:03 | 49.999
2025-03-21 | 0:03 | 49.991
2025-03-21 | 0:03 | 49.991
2025-03-21 | 0:03 | 49.994
2025-03-21 | 0:03 | 49.999
2025-03-21 | 0:03 | 50.004
2025-03-21 | 0:03 | 50.007
2025-03-21 | 0:03 | 50.011
2025-03-21 | 0:03 | 50.013
2025-03-21 | 0:03 | 50.014
2025-03-21 | 0:03 | 50.013
2025-03-21 | 0:03 | 50.013
2025-03-21 | 0:03 | 50.013
2025-03-21 | 0:03 | 50.009
2025-03-21 | 0:03 | 50.002
2025-03-21 | 0:03 | 49.996
2025-03-21 | 0:03 | 49.992
2025-03-21 | 0:03 | 49.989
2025-03-21 | 0:03 | 49.985
2025-03-21 | 0:03 | 49.983
2025-03-21 | 0:03 | 49.983
2025-03-21 | 0:03 | 49.986
2025-03-21 | 0:03 | 49.991
2025-03-21 | 0:03 | 49.996
2025-03-21 | 0:03 | 50
2025-03-21 | 0:03 | 50.007
2025-03-21 | 0:03 | 50.012
2025-03-21 | 0:03 | 50.017
2025-03-21 | 0:03 | 50.021
2025-03-21 | 0:03 | 50.023
2025-03-21 | 0:03 | 50.024
2025-03-21 | 0:03 | 50.022
2025-03-21 | 0:03 | 50.018
2025-03-21 | 0:03 | 50.013
2025-03-21 | 0:03 | 50.008
2025-03-21 | 0:03 | 50.002
2025-03-21 | 0:03 | 49.999
2025-03-21 | 0:03 | 49.994
2025-03-21 | 0:03 | 49.989
2025-03-21 | 0:03 | 49.987
2025-03-21 | 0:03 | 49.982
2025-03-21 | 0:03 | 49.983
2025-03-21 | 0:04 | 49.982
2025-03-21 | 0:04 | 49.983
2025-03-21 | 0:04 | 49.983
2025-03-21 | 0:04 | 49.983
2025-03-21 | 0:04 | 49.982
2025-03-21 | 0:04 | 49.98
2025-03-21 | 0:04 | 49.978
2025-03-21 | 0:04 | 49.975
2025-03-21 | 0:04 | 49.975
2025-03-21 | 0:04 | 49.974
2025-03-21 | 0:04 | 49.972
2025-03-21 | 0:04 | 49.97
2025-03-21 | 0:04 | 49.966
2025-03-21 | 0:04 | 49.964
2025-03-21 | 0:04 | 49.965
2025-03-21 | 0:04 | 49.967
2025-03-21 | 0:04 | 49.965
2025-03-21 | 0:04 | 49.964
2025-03-21 | 0:04 | 49.963

## 20250323-1
In GMT
Date | Time | Freq
2025-03-23 | 8:46 | 49.942 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-23 | 8:46 | 49.941 | 222 | BRITNED | 676.211
2025-03-23 | 8:46 | 49.941 | 268 | WBURB-2 | 428.156
2025-03-23 | 8:46 | 49.943 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-23 | 8:46 | 49.943 |  | Viking Link | -648.9
2025-03-23 | 8:46 | 49.942 |  | Viking Link | 1398.96
2025-03-23 | 8:46 | 49.942 | 209 | DRAXX-3 | 626.95
2025-03-23 | 8:46 | 49.942 | 154 | CDCL-1 | 391.57
2025-03-23 | 8:46 | 49.94 | 268 | ROCK-1 | 468.495
2025-03-23 | 8:46 | 49.938 | 148 | IFA Bipole1 | 945.473
2025-03-23 | 8:46 | 49.937 | 132 | IFA Bipole1 | 999.1
2025-03-23 | 8:46 | 49.937 | 141 | IFA Bipole2 | 1000
2025-03-23 | 8:46 | 49.937 | 135 | IFA Bipole1 | 996.75
2025-03-23 | 8:46 | 49.937 |  | Viking Link | -780.3
2025-03-23 | 8:46 | 49.94
2025-03-23 | 8:46 | 49.944
2025-03-23 | 8:46 | 49.947
2025-03-23 | 8:46 | 49.95
2025-03-23 | 8:46 | 49.952
2025-03-23 | 8:46 | 49.951 | 130 | HEYM12 | 271.908
2025-03-23 | 8:46 | 49.952 | 228 | HUMR-1 | 303.75
2025-03-23 | 8:47 | 49.949
2025-03-23 | 8:47 | 49.949
2025-03-23 | 8:47 | 49.949
2025-03-23 | 8:47 | 49.947
2025-03-23 | 8:47 | 49.945
2025-03-23 | 8:47 | 49.944
2025-03-23 | 8:47 | 49.948
2025-03-23 | 8:47 | 49.948
2025-03-23 | 8:47 | 49.949
2025-03-23 | 8:47 | 49.95 | 211 | CDCL-1 | 291.5
2025-03-23 | 8:47 | 49.955 | 199 | STAY-2 | 413.125
2025-03-23 | 8:47 | 49.955 | 173 | CDCL-1 | 397.375
2025-03-23 | 8:47 | 49.955 | 248 | SEAB-2 | 361.25
2025-03-23 | 8:47 | 49.959 | 255 | FRANCE | 995.65
2025-03-23 | 8:47 | 49.962 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-23 | 8:47 | 49.963
2025-03-23 | 8:47 | 49.962
2025-03-23 | 8:47 | 49.965
2025-03-23 | 8:47 | 49.963
2025-03-23 | 8:47 | 49.961
2025-03-23 | 8:47 | 49.961
2025-03-23 | 8:47 | 49.961
2025-03-23 | 8:47 | 49.96
2025-03-23 | 8:47 | 49.958
2025-03-23 | 8:47 | 49.957
2025-03-23 | 8:47 | 49.957
2025-03-23 | 8:47 | 49.957
2025-03-23 | 8:47 | 49.956
2025-03-23 | 8:47 | 49.957
2025-03-23 | 8:47 | 49.955
2025-03-23 | 8:47 | 49.951
2025-03-23 | 8:47 | 49.946
2025-03-23 | 8:47 | 49.944
2025-03-23 | 8:47 | 49.942
2025-03-23 | 8:47 | 49.941
2025-03-23 | 8:47 | 49.939
2025-03-23 | 8:47 | 49.938
2025-03-23 | 8:47 | 49.94
2025-03-23 | 8:47 | 49.941
2025-03-23 | 8:47 | 49.94
2025-03-23 | 8:47 | 49.914
2025-03-23 | 8:47 | 49.883
2025-03-23 | 8:47 | 49.873
2025-03-23 | 8:47 | 49.874
2025-03-23 | 8:47 | 49.878
2025-03-23 | 8:47 | 49.88
2025-03-23 | 8:47 | 49.88
2025-03-23 | 8:47 | 49.881
2025-03-23 | 8:47 | 49.882
2025-03-23 | 8:47 | 49.881
2025-03-23 | 8:47 | 49.878
2025-03-23 | 8:47 | 49.876
2025-03-23 | 8:47 | 49.876
2025-03-23 | 8:47 | 49.874
2025-03-23 | 8:47 | 49.874
2025-03-23 | 8:47 | 49.875
2025-03-23 | 8:47 | 49.877
2025-03-23 | 8:47 | 49.875
2025-03-23 | 8:47 | 49.872
2025-03-23 | 8:48 | 49.873
2025-03-23 | 8:48 | 49.871
2025-03-23 | 8:48 | 49.868
2025-03-23 | 8:48 | 49.864
2025-03-23 | 8:48 | 49.863
2025-03-23 | 8:48 | 49.866
2025-03-23 | 8:48 | 49.863
2025-03-23 | 8:48 | 49.862
2025-03-23 | 8:48 | 49.864
2025-03-23 | 8:48 | 49.862
2025-03-23 | 8:48 | 49.857
2025-03-23 | 8:48 | 49.856
2025-03-23 | 8:48 | 49.859
2025-03-23 | 8:48 | 49.86
2025-03-23 | 8:48 | 49.855
2025-03-23 | 8:48 | 49.856
2025-03-23 | 8:48 | 49.857
2025-03-23 | 8:48 | 49.857
2025-03-23 | 8:48 | 49.857
2025-03-23 | 8:48 | 49.854
2025-03-23 | 8:48 | 49.855
2025-03-23 | 8:48 | 49.856
2025-03-23 | 8:48 | 49.853
2025-03-23 | 8:48 | 49.856
2025-03-23 | 8:48 | 49.857
2025-03-23 | 8:48 | 49.855
2025-03-23 | 8:48 | 49.852
2025-03-23 | 8:48 | 49.849
2025-03-23 | 8:48 | 49.851
2025-03-23 | 8:48 | 49.848
2025-03-23 | 8:48 | 49.845
2025-03-23 | 8:48 | 49.841
2025-03-23 | 8:48 | 49.842
2025-03-23 | 8:48 | 49.841
2025-03-23 | 8:48 | 49.843
2025-03-23 | 8:48 | 49.843
2025-03-23 | 8:48 | 49.842
2025-03-23 | 8:48 | 49.842
2025-03-23 | 8:48 | 49.84
2025-03-23 | 8:48 | 49.843
2025-03-23 | 8:48 | 49.845
2025-03-23 | 8:48 | 49.842
2025-03-23 | 8:48 | 49.842
2025-03-23 | 8:48 | 49.845
2025-03-23 | 8:48 | 49.845
2025-03-23 | 8:48 | 49.841
2025-03-23 | 8:48 | 49.844
2025-03-23 | 8:48 | 49.845
2025-03-23 | 8:48 | 49.847
2025-03-23 | 8:48 | 49.844
2025-03-23 | 8:48 | 49.848
2025-03-23 | 8:48 | 49.848
2025-03-23 | 8:48 | 49.852
2025-03-23 | 8:48 | 49.855
2025-03-23 | 8:48 | 49.855
2025-03-23 | 8:48 | 49.854
2025-03-23 | 8:48 | 49.857
2025-03-23 | 8:48 | 49.861
2025-03-23 | 8:48 | 49.864
2025-03-23 | 8:48 | 49.868
2025-03-23 | 8:48 | 49.869
2025-03-23 | 8:49 | 49.866
2025-03-23 | 8:49 | 49.862
2025-03-23 | 8:49 | 49.862
2025-03-23 | 8:49 | 49.862
2025-03-23 | 8:49 | 49.863
2025-03-23 | 8:49 | 49.865
2025-03-23 | 8:49 | 49.867
2025-03-23 | 8:49 | 49.867
2025-03-23 | 8:49 | 49.867
2025-03-23 | 8:49 | 49.866
2025-03-23 | 8:49 | 49.866
2025-03-23 | 8:49 | 49.867
2025-03-23 | 8:49 | 49.869
2025-03-23 | 8:49 | 49.871
2025-03-23 | 8:49 | 49.872
2025-03-23 | 8:49 | 49.872
2025-03-23 | 8:49 | 49.87
2025-03-23 | 8:49 | 49.872
2025-03-23 | 8:49 | 49.873
2025-03-23 | 8:49 | 49.872
2025-03-23 | 8:49 | 49.877
2025-03-23 | 8:49 | 49.879
2025-03-23 | 8:49 | 49.882
2025-03-23 | 8:49 | 49.881
2025-03-23 | 8:49 | 49.879
2025-03-23 | 8:49 | 49.881
2025-03-23 | 8:49 | 49.881
2025-03-23 | 8:49 | 49.88
2025-03-23 | 8:49 | 49.881
2025-03-23 | 8:49 | 49.881
2025-03-23 | 8:49 | 49.88
2025-03-23 | 8:49 | 49.878
2025-03-23 | 8:49 | 49.882
2025-03-23 | 8:49 | 49.882
2025-03-23 | 8:49 | 49.882
2025-03-23 | 8:49 | 49.879
2025-03-23 | 8:49 | 49.883
2025-03-23 | 8:49 | 49.884
2025-03-23 | 8:49 | 49.885
2025-03-23 | 8:49 | 49.885
2025-03-23 | 8:49 | 49.888
2025-03-23 | 8:49 | 49.892
2025-03-23 | 8:49 | 49.891
2025-03-23 | 8:49 | 49.888
2025-03-23 | 8:49 | 49.891
2025-03-23 | 8:49 | 49.892
2025-03-23 | 8:49 | 49.895
2025-03-23 | 8:49 | 49.896
2025-03-23 | 8:49 | 49.896
2025-03-23 | 8:49 | 49.895
2025-03-23 | 8:49 | 49.894
2025-03-23 | 8:49 | 49.894
2025-03-23 | 8:49 | 49.896
2025-03-23 | 8:49 | 49.897
2025-03-23 | 8:49 | 49.898
2025-03-23 | 8:49 | 49.899
2025-03-23 | 8:49 | 49.902
2025-03-23 | 8:49 | 49.903
2025-03-23 | 8:49 | 49.901
2025-03-23 | 8:50 | 49.903
2025-03-23 | 8:50 | 49.906
2025-03-23 | 8:50 | 49.907
2025-03-23 | 8:50 | 49.907
2025-03-23 | 8:50 | 49.907
2025-03-23 | 8:50 | 49.909
2025-03-23 | 8:50 | 49.909
2025-03-23 | 8:50 | 49.91
2025-03-23 | 8:50 | 49.91
2025-03-23 | 8:50 | 49.909
2025-03-23 | 8:50 | 49.91
2025-03-23 | 8:50 | 49.91
2025-03-23 | 8:50 | 49.913
2025-03-23 | 8:50 | 49.915
2025-03-23 | 8:50 | 49.913
2025-03-23 | 8:50 | 49.91
2025-03-23 | 8:50 | 49.91
2025-03-23 | 8:50 | 49.911
2025-03-23 | 8:50 | 49.91
2025-03-23 | 8:50 | 49.914
2025-03-23 | 8:50 | 49.922
2025-03-23 | 8:50 | 49.925
2025-03-23 | 8:50 | 49.923
2025-03-23 | 8:50 | 49.922
2025-03-23 | 8:50 | 49.921
2025-03-23 | 8:50 | 49.923
2025-03-23 | 8:50 | 49.922
2025-03-23 | 8:50 | 49.921
2025-03-23 | 8:50 | 49.92
2025-03-23 | 8:50 | 49.92
2025-03-23 | 8:50 | 49.916
2025-03-23 | 8:50 | 49.915
2025-03-23 | 8:50 | 49.916
2025-03-23 | 8:50 | 49.917
2025-03-23 | 8:50 | 49.918
2025-03-23 | 8:50 | 49.918
2025-03-23 | 8:50 | 49.921
2025-03-23 | 8:50 | 49.923
2025-03-23 | 8:50 | 49.92
2025-03-23 | 8:50 | 49.918
2025-03-23 | 8:50 | 49.917
2025-03-23 | 8:50 | 49.916
2025-03-23 | 8:50 | 49.915
2025-03-23 | 8:50 | 49.918
2025-03-23 | 8:50 | 49.917
2025-03-23 | 8:50 | 49.918
2025-03-23 | 8:50 | 49.917
2025-03-23 | 8:50 | 49.919
2025-03-23 | 8:50 | 49.917
2025-03-23 | 8:50 | 49.914
2025-03-23 | 8:50 | 49.91
2025-03-23 | 8:50 | 49.911
2025-03-23 | 8:50 | 49.912
2025-03-23 | 8:50 | 49.91
2025-03-23 | 8:50 | 49.906
2025-03-23 | 8:50 | 49.906
2025-03-23 | 8:50 | 49.904
2025-03-23 | 8:50 | 49.902
2025-03-23 | 8:50 | 49.901
2025-03-23 | 8:50 | 49.903
2025-03-23 | 8:50 | 49.903
2025-03-23 | 8:51 | 49.902
2025-03-23 | 8:51 | 49.901
2025-03-23 | 8:51 | 49.902
2025-03-23 | 8:51 | 49.903
2025-03-23 | 8:51 | 49.903
2025-03-23 | 8:51 | 49.904
2025-03-23 | 8:51 | 49.907
2025-03-23 | 8:51 | 49.906
2025-03-23 | 8:51 | 49.903
2025-03-23 | 8:51 | 49.901
2025-03-23 | 8:51 | 49.899
2025-03-23 | 8:51 | 49.897
2025-03-23 | 8:51 | 49.897
2025-03-23 | 8:51 | 49.899
2025-03-23 | 8:51 | 49.9
2025-03-23 | 8:51 | 49.898
2025-03-23 | 8:51 | 49.899
2025-03-23 | 8:51 | 49.899
2025-03-23 | 8:51 | 49.9
2025-03-23 | 8:51 | 49.9
2025-03-23 | 8:51 | 49.901
2025-03-23 | 8:51 | 49.902
2025-03-23 | 8:51 | 49.903
2025-03-23 | 8:51 | 49.904
2025-03-23 | 8:51 | 49.905
2025-03-23 | 8:51 | 49.905
2025-03-23 | 8:51 | 49.905
2025-03-23 | 8:51 | 49.905
2025-03-23 | 8:51 | 49.905
2025-03-23 | 8:51 | 49.907
2025-03-23 | 8:51 | 49.904
2025-03-23 | 8:51 | 49.904
2025-03-23 | 8:51 | 49.905
2025-03-23 | 8:51 | 49.907
2025-03-23 | 8:51 | 49.905
2025-03-23 | 8:51 | 49.905
2025-03-23 | 8:51 | 49.907
2025-03-23 | 8:51 | 49.909
2025-03-23 | 8:51 | 49.911
2025-03-23 | 8:51 | 49.912
2025-03-23 | 8:51 | 49.915
2025-03-23 | 8:51 | 49.918
2025-03-23 | 8:51 | 49.917
2025-03-23 | 8:51 | 49.916
2025-03-23 | 8:51 | 49.916
2025-03-23 | 8:51 | 49.918
2025-03-23 | 8:51 | 49.917
2025-03-23 | 8:51 | 49.916
2025-03-23 | 8:51 | 49.915
2025-03-23 | 8:51 | 49.914
2025-03-23 | 8:51 | 49.911
2025-03-23 | 8:51 | 49.909
2025-03-23 | 8:51 | 49.908
2025-03-23 | 8:51 | 49.908
2025-03-23 | 8:51 | 49.906
2025-03-23 | 8:51 | 49.904
2025-03-23 | 8:51 | 49.905
2025-03-23 | 8:51 | 49.902
2025-03-23 | 8:51 | 49.899
2025-03-23 | 8:52 | 49.898
2025-03-23 | 8:52 | 49.901
2025-03-23 | 8:52 | 49.901
2025-03-23 | 8:52 | 49.903
2025-03-23 | 8:52 | 49.906
2025-03-23 | 8:52 | 49.907
2025-03-23 | 8:52 | 49.906
2025-03-23 | 8:52 | 49.903
2025-03-23 | 8:52 | 49.901
2025-03-23 | 8:52 | 49.901
2025-03-23 | 8:52 | 49.901
2025-03-23 | 8:52 | 49.904
2025-03-23 | 8:52 | 49.906
2025-03-23 | 8:52 | 49.906
2025-03-23 | 8:52 | 49.903
2025-03-23 | 8:52 | 49.901
2025-03-23 | 8:52 | 49.9
2025-03-23 | 8:52 | 49.898
2025-03-23 | 8:52 | 49.896
2025-03-23 | 8:52 | 49.897
2025-03-23 | 8:52 | 49.9
2025-03-23 | 8:52 | 49.9
2025-03-23 | 8:52 | 49.899
2025-03-23 | 8:52 | 49.897
2025-03-23 | 8:52 | 49.897
2025-03-23 | 8:52 | 49.898
2025-03-23 | 8:52 | 49.899
2025-03-23 | 8:52 | 49.9
2025-03-23 | 8:52 | 49.899
2025-03-23 | 8:52 | 49.897
2025-03-23 | 8:52 | 49.894
2025-03-23 | 8:52 | 49.894
2025-03-23 | 8:52 | 49.895
2025-03-23 | 8:52 | 49.895
2025-03-23 | 8:52 | 49.894
2025-03-23 | 8:52 | 49.896
2025-03-23 | 8:52 | 49.893
2025-03-23 | 8:52 | 49.892
2025-03-23 | 8:52 | 49.892
2025-03-23 | 8:52 | 49.895
2025-03-23 | 8:52 | 49.897
2025-03-23 | 8:52 | 49.898
2025-03-23 | 8:52 | 49.9
2025-03-23 | 8:52 | 49.9
2025-03-23 | 8:52 | 49.9
2025-03-23 | 8:52 | 49.899
2025-03-23 | 8:52 | 49.9
2025-03-23 | 8:52 | 49.899
2025-03-23 | 8:52 | 49.895
2025-03-23 | 8:52 | 49.889
2025-03-23 | 8:52 | 49.887
2025-03-23 | 8:52 | 49.886
2025-03-23 | 8:52 | 49.886
2025-03-23 | 8:52 | 49.886
2025-03-23 | 8:52 | 49.887
2025-03-23 | 8:52 | 49.888
2025-03-23 | 8:52 | 49.888
2025-03-23 | 8:52 | 49.887
2025-03-23 | 8:52 | 49.889
2025-03-23 | 8:52 | 49.89
2025-03-23 | 8:52 | 49.89
2025-03-23 | 8:53 | 49.89
2025-03-23 | 8:53 | 49.89
2025-03-23 | 8:53 | 49.894
2025-03-23 | 8:53 | 49.895
2025-03-23 | 8:53 | 49.895
2025-03-23 | 8:53 | 49.895
2025-03-23 | 8:53 | 49.896
2025-03-23 | 8:53 | 49.894
2025-03-23 | 8:53 | 49.894
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.891
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.891
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.893
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.894
2025-03-23 | 8:53 | 49.895
2025-03-23 | 8:53 | 49.894
2025-03-23 | 8:53 | 49.894
2025-03-23 | 8:53 | 49.895
2025-03-23 | 8:53 | 49.894
2025-03-23 | 8:53 | 49.893
2025-03-23 | 8:53 | 49.895
2025-03-23 | 8:53 | 49.899
2025-03-23 | 8:53 | 49.9
2025-03-23 | 8:53 | 49.9
2025-03-23 | 8:53 | 49.9
2025-03-23 | 8:53 | 49.899
2025-03-23 | 8:53 | 49.897
2025-03-23 | 8:53 | 49.897
2025-03-23 | 8:53 | 49.895
2025-03-23 | 8:53 | 49.896
2025-03-23 | 8:53 | 49.893
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.891
2025-03-23 | 8:53 | 49.893
2025-03-23 | 8:53 | 49.893
2025-03-23 | 8:53 | 49.889
2025-03-23 | 8:53 | 49.89
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.891
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.891
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.889
2025-03-23 | 8:53 | 49.891
2025-03-23 | 8:53 | 49.893
2025-03-23 | 8:53 | 49.891
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.893
2025-03-23 | 8:53 | 49.892
2025-03-23 | 8:53 | 49.889
2025-03-23 | 8:54 | 49.888
2025-03-23 | 8:54 | 49.891
2025-03-23 | 8:54 | 49.893
2025-03-23 | 8:54 | 49.893
2025-03-23 | 8:54 | 49.894
2025-03-23 | 8:54 | 49.894
2025-03-23 | 8:54 | 49.896
2025-03-23 | 8:54 | 49.896
2025-03-23 | 8:54 | 49.896
2025-03-23 | 8:54 | 49.898
2025-03-23 | 8:54 | 49.896
2025-03-23 | 8:54 | 49.895
2025-03-23 | 8:54 | 49.895
2025-03-23 | 8:54 | 49.896
2025-03-23 | 8:54 | 49.894
2025-03-23 | 8:54 | 49.894
2025-03-23 | 8:54 | 49.894
2025-03-23 | 8:54 | 49.891
2025-03-23 | 8:54 | 49.891
2025-03-23 | 8:54 | 49.891
2025-03-23 | 8:54 | 49.89
2025-03-23 | 8:54 | 49.89
2025-03-23 | 8:54 | 49.892
2025-03-23 | 8:54 | 49.891
2025-03-23 | 8:54 | 49.889
2025-03-23 | 8:54 | 49.889
2025-03-23 | 8:54 | 49.89
2025-03-23 | 8:54 | 49.89
2025-03-23 | 8:54 | 49.892
2025-03-23 | 8:54 | 49.891
2025-03-23 | 8:54 | 49.89
2025-03-23 | 8:54 | 49.889
2025-03-23 | 8:54 | 49.888
2025-03-23 | 8:54 | 49.888
2025-03-23 | 8:54 | 49.887
2025-03-23 | 8:54 | 49.886
2025-03-23 | 8:54 | 49.886
2025-03-23 | 8:54 | 49.885
2025-03-23 | 8:54 | 49.885
2025-03-23 | 8:54 | 49.886
2025-03-23 | 8:54 | 49.887
2025-03-23 | 8:54 | 49.888
2025-03-23 | 8:54 | 49.889
2025-03-23 | 8:54 | 49.889
2025-03-23 | 8:54 | 49.89
2025-03-23 | 8:54 | 49.889
2025-03-23 | 8:54 | 49.888
2025-03-23 | 8:54 | 49.89
2025-03-23 | 8:54 | 49.889
2025-03-23 | 8:54 | 49.887
2025-03-23 | 8:54 | 49.885
2025-03-23 | 8:54 | 49.884
2025-03-23 | 8:54 | 49.886
2025-03-23 | 8:54 | 49.885
2025-03-23 | 8:54 | 49.883
2025-03-23 | 8:54 | 49.882
2025-03-23 | 8:54 | 49.882
2025-03-23 | 8:54 | 49.882
2025-03-23 | 8:54 | 49.884
2025-03-23 | 8:54 | 49.885
2025-03-23 | 8:54 | 49.886
2025-03-23 | 8:55 | 49.883
2025-03-23 | 8:55 | 49.883
2025-03-23 | 8:55 | 49.884
2025-03-23 | 8:55 | 49.885
2025-03-23 | 8:55 | 49.881
2025-03-23 | 8:55 | 49.879
2025-03-23 | 8:55 | 49.881
2025-03-23 | 8:55 | 49.882
2025-03-23 | 8:55 | 49.884
2025-03-23 | 8:55 | 49.885
2025-03-23 | 8:55 | 49.886
2025-03-23 | 8:55 | 49.889
2025-03-23 | 8:55 | 49.89
2025-03-23 | 8:55 | 49.891
2025-03-23 | 8:55 | 49.892
2025-03-23 | 8:55 | 49.892
2025-03-23 | 8:55 | 49.891
2025-03-23 | 8:55 | 49.89
2025-03-23 | 8:55 | 49.888
2025-03-23 | 8:55 | 49.887
2025-03-23 | 8:55 | 49.885
2025-03-23 | 8:55 | 49.886
2025-03-23 | 8:55 | 49.886
2025-03-23 | 8:55 | 49.885
2025-03-23 | 8:55 | 49.884
2025-03-23 | 8:55 | 49.882
2025-03-23 | 8:55 | 49.884
2025-03-23 | 8:55 | 49.883
2025-03-23 | 8:55 | 49.882
2025-03-23 | 8:55 | 49.885
2025-03-23 | 8:55 | 49.883
2025-03-23 | 8:55 | 49.883
2025-03-23 | 8:55 | 49.883
2025-03-23 | 8:55 | 49.886
2025-03-23 | 8:55 | 49.887
2025-03-23 | 8:55 | 49.885
2025-03-23 | 8:55 | 49.882
2025-03-23 | 8:55 | 49.885
2025-03-23 | 8:55 | 49.884
2025-03-23 | 8:55 | 49.883
2025-03-23 | 8:55 | 49.884
2025-03-23 | 8:55 | 49.887
2025-03-23 | 8:55 | 49.888
2025-03-23 | 8:55 | 49.888
2025-03-23 | 8:55 | 49.888
2025-03-23 | 8:55 | 49.888
2025-03-23 | 8:55 | 49.887
2025-03-23 | 8:55 | 49.887
2025-03-23 | 8:55 | 49.887
2025-03-23 | 8:55 | 49.885
2025-03-23 | 8:55 | 49.884
2025-03-23 | 8:55 | 49.874
2025-03-23 | 8:55 | 49.87
2025-03-23 | 8:55 | 49.872
2025-03-23 | 8:55 | 49.873
2025-03-23 | 8:55 | 49.874
2025-03-23 | 8:55 | 49.875
2025-03-23 | 8:55 | 49.875
2025-03-23 | 8:55 | 49.873
2025-03-23 | 8:56 | 49.873
2025-03-23 | 8:56 | 49.876
2025-03-23 | 8:56 | 49.876
2025-03-23 | 8:56 | 49.873
2025-03-23 | 8:56 | 49.871
2025-03-23 | 8:56 | 49.873
2025-03-23 | 8:56 | 49.872
2025-03-23 | 8:56 | 49.872
2025-03-23 | 8:56 | 49.873
2025-03-23 | 8:56 | 49.875
2025-03-23 | 8:56 | 49.875
2025-03-23 | 8:56 | 49.873
2025-03-23 | 8:56 | 49.872
2025-03-23 | 8:56 | 49.875
2025-03-23 | 8:56 | 49.876
2025-03-23 | 8:56 | 49.878
2025-03-23 | 8:56 | 49.877
2025-03-23 | 8:56 | 49.877
2025-03-23 | 8:56 | 49.877
2025-03-23 | 8:56 | 49.875
2025-03-23 | 8:56 | 49.874
2025-03-23 | 8:56 | 49.874
2025-03-23 | 8:56 | 49.87
2025-03-23 | 8:56 | 49.869
2025-03-23 | 8:56 | 49.869
2025-03-23 | 8:56 | 49.871
2025-03-23 | 8:56 | 49.87
2025-03-23 | 8:56 | 49.87
2025-03-23 | 8:56 | 49.871
2025-03-23 | 8:56 | 49.872
2025-03-23 | 8:56 | 49.872
2025-03-23 | 8:56 | 49.872
2025-03-23 | 8:56 | 49.873
2025-03-23 | 8:56 | 49.875
2025-03-23 | 8:56 | 49.875
2025-03-23 | 8:56 | 49.874
2025-03-23 | 8:56 | 49.875
2025-03-23 | 8:56 | 49.875
2025-03-23 | 8:56 | 49.873
2025-03-23 | 8:56 | 49.869
2025-03-23 | 8:56 | 49.87
2025-03-23 | 8:56 | 49.87
2025-03-23 | 8:56 | 49.867
2025-03-23 | 8:56 | 49.869
2025-03-23 | 8:56 | 49.871
2025-03-23 | 8:56 | 49.871
2025-03-23 | 8:56 | 49.869
2025-03-23 | 8:56 | 49.873
2025-03-23 | 8:56 | 49.874
2025-03-23 | 8:56 | 49.875
2025-03-23 | 8:56 | 49.874
2025-03-23 | 8:56 | 49.876
2025-03-23 | 8:56 | 49.878
2025-03-23 | 8:56 | 49.879
2025-03-23 | 8:56 | 49.876
2025-03-23 | 8:56 | 49.876
2025-03-23 | 8:56 | 49.876
2025-03-23 | 8:56 | 49.874
2025-03-23 | 8:56 | 49.87
2025-03-23 | 8:56 | 49.87
2025-03-23 | 8:56 | 49.87
2025-03-23 | 8:57 | 49.869
2025-03-23 | 8:57 | 49.869
2025-03-23 | 8:57 | 49.871
2025-03-23 | 8:57 | 49.872
2025-03-23 | 8:57 | 49.876
2025-03-23 | 8:57 | 49.877
2025-03-23 | 8:57 | 49.878
2025-03-23 | 8:57 | 49.878
2025-03-23 | 8:57 | 49.876
2025-03-23 | 8:57 | 49.876
2025-03-23 | 8:57 | 49.879
2025-03-23 | 8:57 | 49.882
2025-03-23 | 8:57 | 49.882
2025-03-23 | 8:57 | 49.884
2025-03-23 | 8:57 | 49.885
2025-03-23 | 8:57 | 49.885
2025-03-23 | 8:57 | 49.881
2025-03-23 | 8:57 | 49.881
2025-03-23 | 8:57 | 49.88
2025-03-23 | 8:57 | 49.881
2025-03-23 | 8:57 | 49.88
2025-03-23 | 8:57 | 49.883
2025-03-23 | 8:57 | 49.883
2025-03-23 | 8:57 | 49.883
2025-03-23 | 8:57 | 49.882
2025-03-23 | 8:57 | 49.884
2025-03-23 | 8:57 | 49.885
2025-03-23 | 8:57 | 49.885
2025-03-23 | 8:57 | 49.883
2025-03-23 | 8:57 | 49.883
2025-03-23 | 8:57 | 49.882
2025-03-23 | 8:57 | 49.882
2025-03-23 | 8:57 | 49.88
2025-03-23 | 8:57 | 49.883
2025-03-23 | 8:57 | 49.884
2025-03-23 | 8:57 | 49.882
2025-03-23 | 8:57 | 49.88
2025-03-23 | 8:57 | 49.882
2025-03-23 | 8:57 | 49.884
2025-03-23 | 8:57 | 49.881
2025-03-23 | 8:57 | 49.882
2025-03-23 | 8:57 | 49.883
2025-03-23 | 8:57 | 49.882
2025-03-23 | 8:57 | 49.878
2025-03-23 | 8:57 | 49.877
2025-03-23 | 8:57 | 49.878
2025-03-23 | 8:57 | 49.875
2025-03-23 | 8:57 | 49.873
2025-03-23 | 8:57 | 49.875
2025-03-23 | 8:57 | 49.878
2025-03-23 | 8:57 | 49.878
2025-03-23 | 8:57 | 49.877
2025-03-23 | 8:57 | 49.879
2025-03-23 | 8:57 | 49.882
2025-03-23 | 8:57 | 49.883
2025-03-23 | 8:57 | 49.886
2025-03-23 | 8:57 | 49.888
2025-03-23 | 8:57 | 49.888
2025-03-23 | 8:57 | 49.887
2025-03-23 | 8:58 | 49.885
2025-03-23 | 8:58 | 49.886
2025-03-23 | 8:58 | 49.888
2025-03-23 | 8:58 | 49.888
2025-03-23 | 8:58 | 49.884
2025-03-23 | 8:58 | 49.886
2025-03-23 | 8:58 | 49.888
2025-03-23 | 8:58 | 49.887
2025-03-23 | 8:58 | 49.887
2025-03-23 | 8:58 | 49.888
2025-03-23 | 8:58 | 49.887
2025-03-23 | 8:58 | 49.886
2025-03-23 | 8:58 | 49.887
2025-03-23 | 8:58 | 49.89
2025-03-23 | 8:58 | 49.892
2025-03-23 | 8:58 | 49.891
2025-03-23 | 8:58 | 49.893
2025-03-23 | 8:58 | 49.894
2025-03-23 | 8:58 | 49.894
2025-03-23 | 8:58 | 49.891
2025-03-23 | 8:58 | 49.895
2025-03-23 | 8:58 | 49.894
2025-03-23 | 8:58 | 49.895
2025-03-23 | 8:58 | 49.892
2025-03-23 | 8:58 | 49.891
2025-03-23 | 8:58 | 49.89
2025-03-23 | 8:58 | 49.888
2025-03-23 | 8:58 | 49.886
2025-03-23 | 8:58 | 49.885
2025-03-23 | 8:58 | 49.886
2025-03-23 | 8:58 | 49.885
2025-03-23 | 8:58 | 49.883
2025-03-23 | 8:58 | 49.884
2025-03-23 | 8:58 | 49.886
2025-03-23 | 8:58 | 49.883
2025-03-23 | 8:58 | 49.883
2025-03-23 | 8:58 | 49.884
2025-03-23 | 8:58 | 49.883
2025-03-23 | 8:58 | 49.883
2025-03-23 | 8:58 | 49.887
2025-03-23 | 8:58 | 49.888
2025-03-23 | 8:58 | 49.888
2025-03-23 | 8:58 | 49.886
2025-03-23 | 8:58 | 49.886
2025-03-23 | 8:58 | 49.886
2025-03-23 | 8:58 | 49.887
2025-03-23 | 8:58 | 49.887
2025-03-23 | 8:58 | 49.888
2025-03-23 | 8:58 | 49.888
2025-03-23 | 8:58 | 49.891
2025-03-23 | 8:58 | 49.892
2025-03-23 | 8:58 | 49.892
2025-03-23 | 8:58 | 49.894
2025-03-23 | 8:58 | 49.892
2025-03-23 | 8:58 | 49.893
2025-03-23 | 8:58 | 49.893
2025-03-23 | 8:58 | 49.897
2025-03-23 | 8:58 | 49.899
2025-03-23 | 8:58 | 49.897
2025-03-23 | 8:58 | 49.899
2025-03-23 | 8:58 | 49.9
2025-03-23 | 8:59 | 49.902
2025-03-23 | 8:59 | 49.906
2025-03-23 | 8:59 | 49.907
2025-03-23 | 8:59 | 49.909
2025-03-23 | 8:59 | 49.908
2025-03-23 | 8:59 | 49.908
2025-03-23 | 8:59 | 49.91
2025-03-23 | 8:59 | 49.91
2025-03-23 | 8:59 | 49.913
2025-03-23 | 8:59 | 49.916
2025-03-23 | 8:59 | 49.92
2025-03-23 | 8:59 | 49.922
2025-03-23 | 8:59 | 49.923
2025-03-23 | 8:59 | 49.925
2025-03-23 | 8:59 | 49.927
2025-03-23 | 8:59 | 49.928
2025-03-23 | 8:59 | 49.928
2025-03-23 | 8:59 | 49.927
2025-03-23 | 8:59 | 49.926
2025-03-23 | 8:59 | 49.925
2025-03-23 | 8:59 | 49.924
2025-03-23 | 8:59 | 49.925
2025-03-23 | 8:59 | 49.926
2025-03-23 | 8:59 | 49.927
2025-03-23 | 8:59 | 49.93
2025-03-23 | 8:59 | 49.934
2025-03-23 | 8:59 | 49.938
2025-03-23 | 8:59 | 49.938
2025-03-23 | 8:59 | 49.938
2025-03-23 | 8:59 | 49.938
2025-03-23 | 8:59 | 49.939
2025-03-23 | 8:59 | 49.938
2025-03-23 | 8:59 | 49.936
2025-03-23 | 8:59 | 49.939
2025-03-23 | 8:59 | 49.942
2025-03-23 | 8:59 | 49.939
2025-03-23 | 8:59 | 49.94
2025-03-23 | 8:59 | 49.943
2025-03-23 | 8:59 | 49.945
2025-03-23 | 8:59 | 49.944
2025-03-23 | 8:59 | 49.943
2025-03-23 | 8:59 | 49.94
2025-03-23 | 8:59 | 49.94
2025-03-23 | 8:59 | 49.94
2025-03-23 | 8:59 | 49.941
2025-03-23 | 8:59 | 49.944
2025-03-23 | 8:59 | 49.946
2025-03-23 | 8:59 | 49.943
2025-03-23 | 8:59 | 49.942
2025-03-23 | 8:59 | 49.943
2025-03-23 | 8:59 | 49.94
2025-03-23 | 8:59 | 49.936
2025-03-23 | 8:59 | 49.936
2025-03-23 | 8:59 | 49.939
2025-03-23 | 8:59 | 49.939
2025-03-23 | 8:59 | 49.938
2025-03-23 | 8:59 | 49.938
2025-03-23 | 8:59 | 49.942
2025-03-23 | 8:59 | 49.94
2025-03-23 | 9:00 | 49.937
2025-03-23 | 9:00 | 49.937
2025-03-23 | 9:00 | 49.937
2025-03-23 | 9:00 | 49.937
2025-03-23 | 9:00 | 49.936
2025-03-23 | 9:00 | 49.938
2025-03-23 | 9:00 | 49.939
2025-03-23 | 9:00 | 49.941
2025-03-23 | 9:00 | 49.942
2025-03-23 | 9:00 | 49.944
2025-03-23 | 9:00 | 49.942
2025-03-23 | 9:00 | 49.941
2025-03-23 | 9:00 | 49.94
2025-03-23 | 9:00 | 49.941
2025-03-23 | 9:00 | 49.94
2025-03-23 | 9:00 | 49.938
2025-03-23 | 9:00 | 49.935
2025-03-23 | 9:00 | 49.938
2025-03-23 | 9:00 | 49.939
2025-03-23 | 9:00 | 49.942
2025-03-23 | 9:00 | 49.944
2025-03-23 | 9:00 | 49.944
2025-03-23 | 9:00 | 49.945
2025-03-23 | 9:00 | 49.941
2025-03-23 | 9:00 | 49.938
2025-03-23 | 9:00 | 49.934
2025-03-23 | 9:00 | 49.933
2025-03-23 | 9:00 | 49.934
2025-03-23 | 9:00 | 49.935
2025-03-23 | 9:00 | 49.94
2025-03-23 | 9:00 | 49.946
2025-03-23 | 9:00 | 49.95
2025-03-23 | 9:00 | 49.948
2025-03-23 | 9:00 | 49.95
2025-03-23 | 9:00 | 49.953
2025-03-23 | 9:00 | 49.955
2025-03-23 | 9:00 | 49.956
2025-03-23 | 9:00 | 49.961
2025-03-23 | 9:00 | 49.962
2025-03-23 | 9:00 | 49.962
2025-03-23 | 9:00 | 49.961
2025-03-23 | 9:00 | 49.96
2025-03-23 | 9:00 | 49.961
2025-03-23 | 9:00 | 49.958
2025-03-23 | 9:00 | 49.956
2025-03-23 | 9:00 | 49.954
2025-03-23 | 9:00 | 49.955
2025-03-23 | 9:00 | 49.956
2025-03-23 | 9:00 | 49.956
2025-03-23 | 9:00 | 49.959
2025-03-23 | 9:00 | 49.961
2025-03-23 | 9:00 | 49.963
2025-03-23 | 9:00 | 49.967
2025-03-23 | 9:00 | 49.97
2025-03-23 | 9:00 | 49.975
2025-03-23 | 9:00 | 49.975
2025-03-23 | 9:00 | 49.975
2025-03-23 | 9:00 | 49.973
2025-03-23 | 9:00 | 49.971
2025-03-23 | 9:00 | 49.971
2025-03-23 | 9:00 | 49.974
2025-03-23 | 9:01 | 49.971
2025-03-23 | 9:01 | 49.97
2025-03-23 | 9:01 | 49.966
2025-03-23 | 9:01 | 49.963
2025-03-23 | 9:01 | 49.959
2025-03-23 | 9:01 | 49.955
2025-03-23 | 9:01 | 49.958
2025-03-23 | 9:01 | 49.96
2025-03-23 | 9:01 | 49.959
2025-03-23 | 9:01 | 49.957
2025-03-23 | 9:01 | 49.957
2025-03-23 | 9:01 | 49.956
2025-03-23 | 9:01 | 49.954
2025-03-23 | 9:01 | 49.954
2025-03-23 | 9:01 | 49.956
2025-03-23 | 9:01 | 49.956
2025-03-23 | 9:01 | 49.956
2025-03-23 | 9:01 | 49.955
2025-03-23 | 9:01 | 49.959
2025-03-23 | 9:01 | 49.962
2025-03-23 | 9:01 | 49.962
2025-03-23 | 9:01 | 49.962
2025-03-23 | 9:01 | 49.963
2025-03-23 | 9:01 | 49.963
2025-03-23 | 9:01 | 49.963
2025-03-23 | 9:01 | 49.962
2025-03-23 | 9:01 | 49.964
2025-03-23 | 9:01 | 49.964
2025-03-23 | 9:01 | 49.964
2025-03-23 | 9:01 | 49.969
2025-03-23 | 9:01 | 49.971
2025-03-23 | 9:01 | 49.972
2025-03-23 | 9:01 | 49.971
2025-03-23 | 9:01 | 49.97
2025-03-23 | 9:01 | 49.97
2025-03-23 | 9:01 | 49.969
2025-03-23 | 9:01 | 49.968
2025-03-23 | 9:01 | 49.968
2025-03-23 | 9:01 | 49.97
2025-03-23 | 9:01 | 49.971
2025-03-23 | 9:01 | 49.972
2025-03-23 | 9:01 | 49.973
2025-03-23 | 9:01 | 49.975
2025-03-23 | 9:01 | 49.975
2025-03-23 | 9:01 | 49.975
2025-03-23 | 9:01 | 49.975
2025-03-23 | 9:01 | 49.971
2025-03-23 | 9:01 | 49.969
2025-03-23 | 9:01 | 49.967
2025-03-23 | 9:01 | 49.968
2025-03-23 | 9:01 | 49.967
2025-03-23 | 9:01 | 49.965
2025-03-23 | 9:01 | 49.964
2025-03-23 | 9:01 | 49.965
2025-03-23 | 9:01 | 49.967
2025-03-23 | 9:01 | 49.968
2025-03-23 | 9:01 | 49.97
2025-03-23 | 9:01 | 49.973
2025-03-23 | 9:01 | 49.973
2025-03-23 | 9:02 | 49.974
2025-03-23 | 9:02 | 49.976
2025-03-23 | 9:02 | 49.975
2025-03-23 | 9:02 | 49.975
2025-03-23 | 9:02 | 49.973
2025-03-23 | 9:02 | 49.973
2025-03-23 | 9:02 | 49.973
2025-03-23 | 9:02 | 49.973
2025-03-23 | 9:02 | 49.972
2025-03-23 | 9:02 | 49.971
2025-03-23 | 9:02 | 49.972
2025-03-23 | 9:02 | 49.969
2025-03-23 | 9:02 | 49.968
2025-03-23 | 9:02 | 49.969
2025-03-23 | 9:02 | 49.969
2025-03-23 | 9:02 | 49.969
2025-03-23 | 9:02 | 49.97
2025-03-23 | 9:02 | 49.97
2025-03-23 | 9:02 | 49.969
2025-03-23 | 9:02 | 49.967
2025-03-23 | 9:02 | 49.964
2025-03-23 | 9:02 | 49.962
2025-03-23 | 9:02 | 49.958
2025-03-23 | 9:02 | 49.956
2025-03-23 | 9:02 | 49.956
2025-03-23 | 9:02 | 49.958
2025-03-23 | 9:02 | 49.958
2025-03-23 | 9:02 | 49.957
2025-03-23 | 9:02 | 49.955
2025-03-23 | 9:02 | 49.957
2025-03-23 | 9:02 | 49.957
2025-03-23 | 9:02 | 49.954
2025-03-23 | 9:02 | 49.953
2025-03-23 | 9:02 | 49.952
2025-03-23 | 9:02 | 49.951
2025-03-23 | 9:02 | 49.95
2025-03-23 | 9:02 | 49.948
2025-03-23 | 9:02 | 49.95
2025-03-23 | 9:02 | 49.951
2025-03-23 | 9:02 | 49.952
2025-03-23 | 9:02 | 49.962
2025-03-23 | 9:02 | 49.969
2025-03-23 | 9:02 | 49.972
2025-03-23 | 9:02 | 49.973
2025-03-23 | 9:02 | 49.973
2025-03-23 | 9:02 | 49.975
2025-03-23 | 9:02 | 49.973
2025-03-23 | 9:02 | 49.971
2025-03-23 | 9:02 | 49.971
2025-03-23 | 9:02 | 49.971
2025-03-23 | 9:02 | 49.972
2025-03-23 | 9:02 | 49.972
2025-03-23 | 9:02 | 49.974
2025-03-23 | 9:02 | 49.973
2025-03-23 | 9:02 | 49.97
2025-03-23 | 9:02 | 49.972
2025-03-23 | 9:02 | 49.974
2025-03-23 | 9:02 | 49.974
2025-03-23 | 9:02 | 49.971
2025-03-23 | 9:02 | 49.968
2025-03-23 | 9:02 | 49.966
2025-03-23 | 9:03 | 49.963
2025-03-23 | 9:03 | 49.96
2025-03-23 | 9:03 | 49.96
2025-03-23 | 9:03 | 49.962
2025-03-23 | 9:03 | 49.964
2025-03-23 | 9:03 | 49.967
2025-03-23 | 9:03 | 49.971
2025-03-23 | 9:03 | 49.973
2025-03-23 | 9:03 | 49.972
2025-03-23 | 9:03 | 49.969
2025-03-23 | 9:03 | 49.969
2025-03-23 | 9:03 | 49.969
2025-03-23 | 9:03 | 49.969
2025-03-23 | 9:03 | 49.968
2025-03-23 | 9:03 | 49.97
2025-03-23 | 9:03 | 49.971
2025-03-23 | 9:03 | 49.972
2025-03-23 | 9:03 | 49.973
2025-03-23 | 9:03 | 49.974
2025-03-23 | 9:03 | 49.975
2025-03-23 | 9:03 | 49.977
2025-03-23 | 9:03 | 49.979
2025-03-23 | 9:03 | 49.983
2025-03-23 | 9:03 | 49.983
2025-03-23 | 9:03 | 49.983
2025-03-23 | 9:03 | 49.982
2025-03-23 | 9:03 | 49.984
2025-03-23 | 9:03 | 49.982
2025-03-23 | 9:03 | 49.981
2025-03-23 | 9:03 | 49.979
2025-03-23 | 9:03 | 49.977
2025-03-23 | 9:03 | 49.977
2025-03-23 | 9:03 | 49.976
2025-03-23 | 9:03 | 49.974
2025-03-23 | 9:03 | 49.973
2025-03-23 | 9:03 | 49.973
2025-03-23 | 9:03 | 49.973
2025-03-23 | 9:03 | 49.974
2025-03-23 | 9:03 | 49.977
2025-03-23 | 9:03 | 49.977
2025-03-23 | 9:03 | 49.978
2025-03-23 | 9:03 | 49.978
2025-03-23 | 9:03 | 49.981
2025-03-23 | 9:03 | 49.979
2025-03-23 | 9:03 | 49.978
2025-03-23 | 9:03 | 49.977
2025-03-23 | 9:03 | 49.976
2025-03-23 | 9:03 | 49.973
2025-03-23 | 9:03 | 49.971
2025-03-23 | 9:03 | 49.972
2025-03-23 | 9:03 | 49.973
2025-03-23 | 9:03 | 49.973
2025-03-23 | 9:03 | 49.973
2025-03-23 | 9:03 | 49.974
2025-03-23 | 9:03 | 49.974
2025-03-23 | 9:03 | 49.976
2025-03-23 | 9:03 | 49.978
2025-03-23 | 9:03 | 49.978
2025-03-23 | 9:03 | 49.979
2025-03-23 | 9:04 | 49.978
2025-03-23 | 9:04 | 49.978
2025-03-23 | 9:04 | 49.977
2025-03-23 | 9:04 | 49.977
2025-03-23 | 9:04 | 49.976
2025-03-23 | 9:04 | 49.978
2025-03-23 | 9:04 | 49.977
2025-03-23 | 9:04 | 49.974
2025-03-23 | 9:04 | 49.972
2025-03-23 | 9:04 | 49.973
2025-03-23 | 9:04 | 49.974
2025-03-23 | 9:04 | 49.973
2025-03-23 | 9:04 | 49.97
2025-03-23 | 9:04 | 49.968
2025-03-23 | 9:04 | 49.97
2025-03-23 | 9:04 | 49.97
2025-03-23 | 9:04 | 49.97
2025-03-23 | 9:04 | 49.972
2025-03-23 | 9:04 | 49.972
2025-03-23 | 9:04 | 49.972
2025-03-23 | 9:04 | 49.972
2025-03-23 | 9:04 | 49.975
2025-03-23 | 9:04 | 49.975
2025-03-23 | 9:04 | 49.972
2025-03-23 | 9:04 | 49.971
2025-03-23 | 9:04 | 49.971
2025-03-23 | 9:04 | 49.971
2025-03-23 | 9:04 | 49.968
2025-03-23 | 9:04 | 49.965
2025-03-23 | 9:04 | 49.965
2025-03-23 | 9:04 | 49.965
2025-03-23 | 9:04 | 49.963
2025-03-23 | 9:04 | 49.961
2025-03-23 | 9:04 | 49.963
2025-03-23 | 9:04 | 49.963
2025-03-23 | 9:04 | 49.964
2025-03-23 | 9:04 | 49.963
2025-03-23 | 9:04 | 49.961
2025-03-23 | 9:04 | 49.961
2025-03-23 | 9:04 | 49.962
2025-03-23 | 9:04 | 49.966
2025-03-23 | 9:04 | 49.967
2025-03-23 | 9:04 | 49.968
2025-03-23 | 9:04 | 49.967
2025-03-23 | 9:04 | 49.966
2025-03-23 | 9:04 | 49.965
2025-03-23 | 9:04 | 49.961
2025-03-23 | 9:04 | 49.958
2025-03-23 | 9:04 | 49.96
2025-03-23 | 9:04 | 49.962
2025-03-23 | 9:04 | 49.958
2025-03-23 | 9:04 | 49.956
2025-03-23 | 9:04 | 49.957
2025-03-23 | 9:04 | 49.957
2025-03-23 | 9:04 | 49.958
2025-03-23 | 9:04 | 49.958
2025-03-23 | 9:04 | 49.961
2025-03-23 | 9:04 | 49.962
2025-03-23 | 9:04 | 49.96
2025-03-23 | 9:04 | 49.958
2025-03-23 | 9:04 | 49.959
2025-03-23 | 9:05 | 49.959
2025-03-23 | 9:05 | 49.955
2025-03-23 | 9:05 | 49.955
2025-03-23 | 9:05 | 49.956
2025-03-23 | 9:05 | 49.957
2025-03-23 | 9:05 | 49.953
2025-03-23 | 9:05 | 49.952
2025-03-23 | 9:05 | 49.95
2025-03-23 | 9:05 | 49.947
2025-03-23 | 9:05 | 49.945
2025-03-23 | 9:05 | 49.942
2025-03-23 | 9:05 | 49.937
2025-03-23 | 9:05 | 49.935
2025-03-23 | 9:05 | 49.933
2025-03-23 | 9:05 | 49.934
2025-03-23 | 9:05 | 49.936
2025-03-23 | 9:05 | 49.937
2025-03-23 | 9:05 | 49.938
2025-03-23 | 9:05 | 49.941
2025-03-23 | 9:05 | 49.942
2025-03-23 | 9:05 | 49.942
2025-03-23 | 9:05 | 49.94
2025-03-23 | 9:05 | 49.938
2025-03-23 | 9:05 | 49.939
2025-03-23 | 9:05 | 49.941
2025-03-23 | 9:05 | 49.942
2025-03-23 | 9:05 | 49.942
2025-03-23 | 9:05 | 49.941
2025-03-23 | 9:05 | 49.94
2025-03-23 | 9:05 | 49.94
2025-03-23 | 9:05 | 49.94
2025-03-23 | 9:05 | 49.938
2025-03-23 | 9:05 | 49.936
2025-03-23 | 9:05 | 49.937
2025-03-23 | 9:05 | 49.939
2025-03-23 | 9:05 | 49.938
2025-03-23 | 9:05 | 49.938
2025-03-23 | 9:05 | 49.938
2025-03-23 | 9:05 | 49.94
2025-03-23 | 9:05 | 49.938
2025-03-23 | 9:05 | 49.939
2025-03-23 | 9:05 | 49.937
2025-03-23 | 9:05 | 49.938
2025-03-23 | 9:05 | 49.936
2025-03-23 | 9:05 | 49.933
2025-03-23 | 9:05 | 49.933
2025-03-23 | 9:05 | 49.932
2025-03-23 | 9:05 | 49.932
2025-03-23 | 9:05 | 49.93
2025-03-23 | 9:05 | 49.93
2025-03-23 | 9:05 | 49.93
2025-03-23 | 9:05 | 49.928
2025-03-23 | 9:05 | 49.93
2025-03-23 | 9:05 | 49.935
2025-03-23 | 9:05 | 49.939
2025-03-23 | 9:05 | 49.94
2025-03-23 | 9:05 | 49.94
2025-03-23 | 9:05 | 49.942
2025-03-23 | 9:05 | 49.942
2025-03-23 | 9:06 | 49.942
2025-03-23 | 9:06 | 49.945
2025-03-23 | 9:06 | 49.947
2025-03-23 | 9:06 | 49.952
2025-03-23 | 9:06 | 49.955
2025-03-23 | 9:06 | 49.954
2025-03-23 | 9:06 | 49.953
2025-03-23 | 9:06 | 49.952
2025-03-23 | 9:06 | 49.95
2025-03-23 | 9:06 | 49.947
2025-03-23 | 9:06 | 49.949
2025-03-23 | 9:06 | 49.946
2025-03-23 | 9:06 | 49.942
2025-03-23 | 9:06 | 49.941
2025-03-23 | 9:06 | 49.942
2025-03-23 | 9:06 | 49.941
2025-03-23 | 9:06 | 49.941
2025-03-23 | 9:06 | 49.942
2025-03-23 | 9:06 | 49.943
2025-03-23 | 9:06 | 49.946
2025-03-23 | 9:06 | 49.949
2025-03-23 | 9:06 | 49.952
2025-03-23 | 9:06 | 49.954
2025-03-23 | 9:06 | 49.954
2025-03-23 | 9:06 | 49.952
2025-03-23 | 9:06 | 49.952
2025-03-23 | 9:06 | 49.95
2025-03-23 | 9:06 | 49.948
2025-03-23 | 9:06 | 49.949
2025-03-23 | 9:06 | 49.95
2025-03-23 | 9:06 | 49.95
2025-03-23 | 9:06 | 49.948
2025-03-23 | 9:06 | 49.946
2025-03-23 | 9:06 | 49.948
2025-03-23 | 9:06 | 49.949
2025-03-23 | 9:06 | 49.948
2025-03-23 | 9:06 | 49.945
2025-03-23 | 9:06 | 49.945
2025-03-23 | 9:06 | 49.947
2025-03-23 | 9:06 | 49.948
2025-03-23 | 9:06 | 49.949
2025-03-23 | 9:06 | 49.953
2025-03-23 | 9:06 | 49.953
2025-03-23 | 9:06 | 49.952
2025-03-23 | 9:06 | 49.952
2025-03-23 | 9:06 | 49.951
2025-03-23 | 9:06 | 49.95
2025-03-23 | 9:06 | 49.948
2025-03-23 | 9:06 | 49.949
2025-03-23 | 9:06 | 49.951
2025-03-23 | 9:06 | 49.95
2025-03-23 | 9:06 | 49.952
2025-03-23 | 9:06 | 49.952
2025-03-23 | 9:06 | 49.953
2025-03-23 | 9:06 | 49.951
2025-03-23 | 9:06 | 49.951
2025-03-23 | 9:06 | 49.952
2025-03-23 | 9:06 | 49.955
2025-03-23 | 9:06 | 49.955
2025-03-23 | 9:06 | 49.955
2025-03-23 | 9:06 | 49.96
2025-03-23 | 9:07 | 49.963
2025-03-23 | 9:07 | 49.963
2025-03-23 | 9:07 | 49.964
2025-03-23 | 9:07 | 49.967
2025-03-23 | 9:07 | 49.97
2025-03-23 | 9:07 | 49.972
2025-03-23 | 9:07 | 49.975
2025-03-23 | 9:07 | 49.975
2025-03-23 | 9:07 | 49.975
2025-03-23 | 9:07 | 49.975
2025-03-23 | 9:07 | 49.975
2025-03-23 | 9:07 | 49.975
2025-03-23 | 9:07 | 49.974
2025-03-23 | 9:07 | 49.974
2025-03-23 | 9:07 | 49.971
2025-03-23 | 9:07 | 49.971
2025-03-23 | 9:07 | 49.968
2025-03-23 | 9:07 | 49.966
2025-03-23 | 9:07 | 49.966
2025-03-23 | 9:07 | 49.967
2025-03-23 | 9:07 | 49.97
2025-03-23 | 9:07 | 49.967
2025-03-23 | 9:07 | 49.968
2025-03-23 | 9:07 | 49.966
2025-03-23 | 9:07 | 49.966
2025-03-23 | 9:07 | 49.963
2025-03-23 | 9:07 | 49.962
2025-03-23 | 9:07 | 49.962
2025-03-23 | 9:07 | 49.959
2025-03-23 | 9:07 | 49.96
2025-03-23 | 9:07 | 49.959
2025-03-23 | 9:07 | 49.958
2025-03-23 | 9:07 | 49.958
2025-03-23 | 9:07 | 49.959
2025-03-23 | 9:07 | 49.96
2025-03-23 | 9:07 | 49.958
2025-03-23 | 9:07 | 49.957
2025-03-23 | 9:07 | 49.955
2025-03-23 | 9:07 | 49.956
2025-03-23 | 9:07 | 49.955
2025-03-23 | 9:07 | 49.955
2025-03-23 | 9:07 | 49.954
2025-03-23 | 9:07 | 49.955
2025-03-23 | 9:07 | 49.955
2025-03-23 | 9:07 | 49.954
2025-03-23 | 9:07 | 49.953
2025-03-23 | 9:07 | 49.95
2025-03-23 | 9:07 | 49.949
2025-03-23 | 9:07 | 49.948
2025-03-23 | 9:07 | 49.948
2025-03-23 | 9:07 | 49.948
2025-03-23 | 9:07 | 49.949
2025-03-23 | 9:07 | 49.95
2025-03-23 | 9:07 | 49.949
2025-03-23 | 9:07 | 49.95
2025-03-23 | 9:07 | 49.949
2025-03-23 | 9:07 | 49.949
2025-03-23 | 9:07 | 49.949
2025-03-23 | 9:07 | 49.95
2025-03-23 | 9:08 | 49.949
2025-03-23 | 9:08 | 49.951
2025-03-23 | 9:08 | 49.951
2025-03-23 | 9:08 | 49.953
2025-03-23 | 9:08 | 49.954
2025-03-23 | 9:08 | 49.955
2025-03-23 | 9:08 | 49.955
2025-03-23 | 9:08 | 49.954
2025-03-23 | 9:08 | 49.951
2025-03-23 | 9:08 | 49.949
2025-03-23 | 9:08 | 49.947
2025-03-23 | 9:08 | 49.947
2025-03-23 | 9:08 | 49.943
2025-03-23 | 9:08 | 49.944
2025-03-23 | 9:08 | 49.947
2025-03-23 | 9:08 | 49.942
2025-03-23 | 9:08 | 49.941
2025-03-23 | 9:08 | 49.937
2025-03-23 | 9:08 | 49.942
2025-03-23 | 9:08 | 49.938
2025-03-23 | 9:08 | 49.938
2025-03-23 | 9:08 | 49.936
2025-03-23 | 9:08 | 49.933
2025-03-23 | 9:08 | 49.931
2025-03-23 | 9:08 | 49.93
2025-03-23 | 9:08 | 49.931
2025-03-23 | 9:08 | 49.934
2025-03-23 | 9:08 | 49.934
2025-03-23 | 9:08 | 49.933
2025-03-23 | 9:08 | 49.933
2025-03-23 | 9:08 | 49.934
2025-03-23 | 9:08 | 49.934
2025-03-23 | 9:08 | 49.933
2025-03-23 | 9:08 | 49.933
2025-03-23 | 9:08 | 49.933
2025-03-23 | 9:08 | 49.933
2025-03-23 | 9:08 | 49.934
2025-03-23 | 9:08 | 49.934
2025-03-23 | 9:08 | 49.932
2025-03-23 | 9:08 | 49.929
2025-03-23 | 9:08 | 49.928
2025-03-23 | 9:08 | 49.93
2025-03-23 | 9:08 | 49.932
2025-03-23 | 9:08 | 49.93
2025-03-23 | 9:08 | 49.926
2025-03-23 | 9:08 | 49.928
2025-03-23 | 9:08 | 49.93
2025-03-23 | 9:08 | 49.929
2025-03-23 | 9:08 | 49.927
2025-03-23 | 9:08 | 49.928
2025-03-23 | 9:08 | 49.928
2025-03-23 | 9:08 | 49.926
2025-03-23 | 9:08 | 49.925
2025-03-23 | 9:08 | 49.928
2025-03-23 | 9:08 | 49.929
2025-03-23 | 9:08 | 49.928
2025-03-23 | 9:08 | 49.929
2025-03-23 | 9:08 | 49.926
2025-03-23 | 9:08 | 49.924
2025-03-23 | 9:08 | 49.924
2025-03-23 | 9:08 | 49.93
2025-03-23 | 9:09 | 49.932
2025-03-23 | 9:09 | 49.931
2025-03-23 | 9:09 | 49.931
2025-03-23 | 9:09 | 49.93
2025-03-23 | 9:09 | 49.929
2025-03-23 | 9:09 | 49.928
2025-03-23 | 9:09 | 49.927
2025-03-23 | 9:09 | 49.925
2025-03-23 | 9:09 | 49.925
2025-03-23 | 9:09 | 49.923
2025-03-23 | 9:09 | 49.922
2025-03-23 | 9:09 | 49.924
2025-03-23 | 9:09 | 49.924
2025-03-23 | 9:09 | 49.923
2025-03-23 | 9:09 | 49.925
2025-03-23 | 9:09 | 49.927
2025-03-23 | 9:09 | 49.928
2025-03-23 | 9:09 | 49.929
2025-03-23 | 9:09 | 49.929
2025-03-23 | 9:09 | 49.932
2025-03-23 | 9:09 | 49.931
2025-03-23 | 9:09 | 49.931
2025-03-23 | 9:09 | 49.929
2025-03-23 | 9:09 | 49.93
2025-03-23 | 9:09 | 49.928
2025-03-23 | 9:09 | 49.923
2025-03-23 | 9:09 | 49.923
2025-03-23 | 9:09 | 49.922
2025-03-23 | 9:09 | 49.921
2025-03-23 | 9:09 | 49.923
2025-03-23 | 9:09 | 49.925
2025-03-23 | 9:09 | 49.925
2025-03-23 | 9:09 | 49.925
2025-03-23 | 9:09 | 49.928
2025-03-23 | 9:09 | 49.931
2025-03-23 | 9:09 | 49.932
2025-03-23 | 9:09 | 49.933
2025-03-23 | 9:09 | 49.937
2025-03-23 | 9:09 | 49.938
2025-03-23 | 9:09 | 49.937
2025-03-23 | 9:09 | 49.936
2025-03-23 | 9:09 | 49.934
2025-03-23 | 9:09 | 49.933
2025-03-23 | 9:09 | 49.933
2025-03-23 | 9:09 | 49.93
2025-03-23 | 9:09 | 49.927
2025-03-23 | 9:09 | 49.931
2025-03-23 | 9:09 | 49.933
2025-03-23 | 9:09 | 49.93
2025-03-23 | 9:09 | 49.93
2025-03-23 | 9:09 | 49.931
2025-03-23 | 9:09 | 49.928
2025-03-23 | 9:09 | 49.927
2025-03-23 | 9:09 | 49.927
2025-03-23 | 9:09 | 49.927
2025-03-23 | 9:09 | 49.929
2025-03-23 | 9:09 | 49.932
2025-03-23 | 9:09 | 49.933
2025-03-23 | 9:09 | 49.935
2025-03-23 | 9:10 | 49.935
2025-03-23 | 9:10 | 49.935
2025-03-23 | 9:10 | 49.936
2025-03-23 | 9:10 | 49.932
2025-03-23 | 9:10 | 49.928
2025-03-23 | 9:10 | 49.93
2025-03-23 | 9:10 | 49.929
2025-03-23 | 9:10 | 49.932
2025-03-23 | 9:10 | 49.933
2025-03-23 | 9:10 | 49.93
2025-03-23 | 9:10 | 49.931
2025-03-23 | 9:10 | 49.933
2025-03-23 | 9:10 | 49.933
2025-03-23 | 9:10 | 49.935
2025-03-23 | 9:10 | 49.936
2025-03-23 | 9:10 | 49.938
2025-03-23 | 9:10 | 49.937
2025-03-23 | 9:10 | 49.939
2025-03-23 | 9:10 | 49.937
2025-03-23 | 9:10 | 49.937
2025-03-23 | 9:10 | 49.939
2025-03-23 | 9:10 | 49.936
2025-03-23 | 9:10 | 49.937
2025-03-23 | 9:10 | 49.935
2025-03-23 | 9:10 | 49.933
2025-03-23 | 9:10 | 49.932
2025-03-23 | 9:10 | 49.933
2025-03-23 | 9:10 | 49.931
2025-03-23 | 9:10 | 49.931
2025-03-23 | 9:10 | 49.932
2025-03-23 | 9:10 | 49.93
2025-03-23 | 9:10 | 49.926
2025-03-23 | 9:10 | 49.926
2025-03-23 | 9:10 | 49.929
2025-03-23 | 9:10 | 49.929
2025-03-23 | 9:10 | 49.93
2025-03-23 | 9:10 | 49.932
2025-03-23 | 9:10 | 49.933
2025-03-23 | 9:10 | 49.931
2025-03-23 | 9:10 | 49.927
2025-03-23 | 9:10 | 49.928
2025-03-23 | 9:10 | 49.927
2025-03-23 | 9:10 | 49.931
2025-03-23 | 9:10 | 49.931
2025-03-23 | 9:10 | 49.934
2025-03-23 | 9:10 | 49.937
2025-03-23 | 9:10 | 49.937
2025-03-23 | 9:10 | 49.934
2025-03-23 | 9:10 | 49.933
2025-03-23 | 9:10 | 49.934
2025-03-23 | 9:10 | 49.931
2025-03-23 | 9:10 | 49.929
2025-03-23 | 9:10 | 49.928
2025-03-23 | 9:10 | 49.929
2025-03-23 | 9:10 | 49.927
2025-03-23 | 9:10 | 49.928
2025-03-23 | 9:10 | 49.929
2025-03-23 | 9:10 | 49.93
2025-03-23 | 9:10 | 49.93
2025-03-23 | 9:10 | 49.929
2025-03-23 | 9:10 | 49.931
2025-03-23 | 9:11 | 49.936
2025-03-23 | 9:11 | 49.94
2025-03-23 | 9:11 | 49.943
2025-03-23 | 9:11 | 49.944
2025-03-23 | 9:11 | 49.946
2025-03-23 | 9:11 | 49.943
2025-03-23 | 9:11 | 49.944
2025-03-23 | 9:11 | 49.948
2025-03-23 | 9:11 | 49.949
2025-03-23 | 9:11 | 49.948
2025-03-23 | 9:11 | 49.947
2025-03-23 | 9:11 | 49.952
2025-03-23 | 9:11 | 49.956
2025-03-23 | 9:11 | 49.956
2025-03-23 | 9:11 | 49.958
2025-03-23 | 9:11 | 49.962
2025-03-23 | 9:11 | 49.965
2025-03-23 | 9:11 | 49.959
2025-03-23 | 9:11 | 49.959
2025-03-23 | 9:11 | 49.961
2025-03-23 | 9:11 | 49.958
2025-03-23 | 9:11 | 49.957
2025-03-23 | 9:11 | 49.955
2025-03-23 | 9:11 | 49.958
2025-03-23 | 9:11 | 49.955
2025-03-23 | 9:11 | 49.955
2025-03-23 | 9:11 | 49.951
2025-03-23 | 9:11 | 49.95
2025-03-23 | 9:11 | 49.949
2025-03-23 | 9:11 | 49.951
2025-03-23 | 9:11 | 49.949
2025-03-23 | 9:11 | 49.95
2025-03-23 | 9:11 | 49.948
2025-03-23 | 9:11 | 49.948
2025-03-23 | 9:11 | 49.951
2025-03-23 | 9:11 | 49.956
2025-03-23 | 9:11 | 49.957
2025-03-23 | 9:11 | 49.955
2025-03-23 | 9:11 | 49.957
2025-03-23 | 9:11 | 49.958
2025-03-23 | 9:11 | 49.958
2025-03-23 | 9:11 | 49.955
2025-03-23 | 9:11 | 49.957
2025-03-23 | 9:11 | 49.957
2025-03-23 | 9:11 | 49.959
2025-03-23 | 9:11 | 49.957
2025-03-23 | 9:11 | 49.959
2025-03-23 | 9:11 | 49.962
2025-03-23 | 9:11 | 49.964
2025-03-23 | 9:11 | 49.962
2025-03-23 | 9:11 | 49.961
2025-03-23 | 9:11 | 49.96
2025-03-23 | 9:11 | 49.959
2025-03-23 | 9:11 | 49.962
2025-03-23 | 9:11 | 49.966
2025-03-23 | 9:11 | 49.967
2025-03-23 | 9:11 | 49.969
2025-03-23 | 9:11 | 49.975
2025-03-23 | 9:11 | 49.978
2025-03-23 | 9:12 | 49.979
2025-03-23 | 9:12 | 49.978
2025-03-23 | 9:12 | 49.98
2025-03-23 | 9:12 | 49.978
2025-03-23 | 9:12 | 49.978
2025-03-23 | 9:12 | 49.974
2025-03-23 | 9:12 | 49.974
2025-03-23 | 9:12 | 49.974
2025-03-23 | 9:12 | 49.974
2025-03-23 | 9:12 | 49.975
2025-03-23 | 9:12 | 49.977
2025-03-23 | 9:12 | 49.977
2025-03-23 | 9:12 | 49.976
2025-03-23 | 9:12 | 49.975
2025-03-23 | 9:12 | 49.976
2025-03-23 | 9:12 | 49.976
2025-03-23 | 9:12 | 49.976
2025-03-23 | 9:12 | 49.977
2025-03-23 | 9:12 | 49.981
2025-03-23 | 9:12 | 49.981
2025-03-23 | 9:12 | 49.982
2025-03-23 | 9:12 | 49.983
2025-03-23 | 9:12 | 49.988
2025-03-23 | 9:12 | 49.99
2025-03-23 | 9:12 | 49.992
2025-03-23 | 9:12 | 49.994
2025-03-23 | 9:12 | 49.998
2025-03-23 | 9:12 | 50.003
2025-03-23 | 9:12 | 50.005
2025-03-23 | 9:12 | 50.012
2025-03-23 | 9:12 | 50.016
2025-03-23 | 9:12 | 50.017
2025-03-23 | 9:12 | 50.018
2025-03-23 | 9:12 | 50.017
2025-03-23 | 9:12 | 50.013
2025-03-23 | 9:12 | 50.01
2025-03-23 | 9:12 | 50.01
2025-03-23 | 9:12 | 50.009
2025-03-23 | 9:12 | 50.01
2025-03-23 | 9:12 | 50.01
2025-03-23 | 9:12 | 50.011
2025-03-23 | 9:12 | 50.02
2025-03-23 | 9:12 | 50.02
2025-03-23 | 9:12 | 50.016
2025-03-23 | 9:12 | 50.014
2025-03-23 | 9:12 | 50.016
2025-03-23 | 9:12 | 50.019
2025-03-23 | 9:12 | 50.02
2025-03-23 | 9:12 | 50.019
2025-03-23 | 9:12 | 50.019
2025-03-23 | 9:12 | 50.018
2025-03-23 | 9:12 | 50.015
2025-03-23 | 9:12 | 50.014
2025-03-23 | 9:12 | 50.017
2025-03-23 | 9:12 | 50.018
2025-03-23 | 9:12 | 50.019
2025-03-23 | 9:12 | 50.021
2025-03-23 | 9:12 | 50.022
2025-03-23 | 9:12 | 50.021
2025-03-23 | 9:12 | 50.017
2025-03-23 | 9:12 | 50.015
2025-03-23 | 9:13 | 50.018
2025-03-23 | 9:13 | 50.018
2025-03-23 | 9:13 | 50.015
2025-03-23 | 9:13 | 50.013
2025-03-23 | 9:13 | 50.014
2025-03-23 | 9:13 | 50.017
2025-03-23 | 9:13 | 50.024
2025-03-23 | 9:13 | 50.028
2025-03-23 | 9:13 | 50.028
2025-03-23 | 9:13 | 50.026
2025-03-23 | 9:13 | 50.024
2025-03-23 | 9:13 | 50.023
2025-03-23 | 9:13 | 50.022
2025-03-23 | 9:13 | 50.019
2025-03-23 | 9:13 | 50.02
2025-03-23 | 9:13 | 50.022
2025-03-23 | 9:13 | 50.024
2025-03-23 | 9:13 | 50.025
2025-03-23 | 9:13 | 50.025
2025-03-23 | 9:13 | 50.024
2025-03-23 | 9:13 | 50.022
2025-03-23 | 9:13 | 50.023
2025-03-23 | 9:13 | 50.024
2025-03-23 | 9:13 | 50.028
2025-03-23 | 9:13 | 50.032
2025-03-23 | 9:13 | 50.031
2025-03-23 | 9:13 | 50.031

## 20250324-1
In GMT
Date | Time | Freq
2025-03-24 | 10:30 | 50.053 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-03-24 | 10:30 | 50.038 | 222 | BRITNED | 676.211
2025-03-24 | 10:30 | 50.03 | 268 | WBURB-2 | 428.156
2025-03-24 | 10:30 | 50.023 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-03-24 | 10:30 | 50.02 |  | Viking Link | -648.9
2025-03-24 | 10:30 | 50.019 |  | Viking Link | 1398.96
2025-03-24 | 10:30 | 50.017 | 209 | DRAXX-3 | 626.95
2025-03-24 | 10:30 | 50.015 | 154 | CDCL-1 | 391.57
2025-03-24 | 10:30 | 50.014 | 268 | ROCK-1 | 468.495
2025-03-24 | 10:30 | 50.015 | 148 | IFA Bipole1 | 945.473
2025-03-24 | 10:30 | 50.017 | 132 | IFA Bipole1 | 999.1
2025-03-24 | 10:30 | 50.016 | 141 | IFA Bipole2 | 1000
2025-03-24 | 10:30 | 50.017 | 135 | IFA Bipole1 | 996.75
2025-03-24 | 10:30 | 50.015 |  | Viking Link | -780.3
2025-03-24 | 10:30 | 50.014
2025-03-24 | 10:30 | 50.014
2025-03-24 | 10:30 | 50.016
2025-03-24 | 10:30 | 50.018
2025-03-24 | 10:30 | 50.019
2025-03-24 | 10:30 | 50.016 | 130 | HEYM12 | 271.908
2025-03-24 | 10:30 | 50.013 | 228 | HUMR-1 | 303.75
2025-03-24 | 10:30 | 50.011
2025-03-24 | 10:30 | 50.01
2025-03-24 | 10:30 | 50.008
2025-03-24 | 10:30 | 50.007
2025-03-24 | 10:30 | 50.007
2025-03-24 | 10:30 | 50.01
2025-03-24 | 10:30 | 50.013
2025-03-24 | 10:30 | 50.014
2025-03-24 | 10:30 | 50.017
2025-03-24 | 10:30 | 50.02 | 211 | CDCL-1 | 291.5
2025-03-24 | 10:31 | 50.022 | 199 | STAY-2 | 413.125
2025-03-24 | 10:31 | 50.027 | 173 | CDCL-1 | 397.375
2025-03-24 | 10:31 | 50.029 | 248 | SEAB-2 | 361.25
2025-03-24 | 10:31 | 50.029 | 255 | FRANCE | 995.65
2025-03-24 | 10:31 | 50.029 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-03-24 | 10:31 | 50.031
2025-03-24 | 10:31 | 50.032
2025-03-24 | 10:31 | 50.035
2025-03-24 | 10:31 | 50.037
2025-03-24 | 10:31 | 50.038
2025-03-24 | 10:31 | 50.037
2025-03-24 | 10:31 | 50.033
2025-03-24 | 10:31 | 50.031
2025-03-24 | 10:31 | 50.028
2025-03-24 | 10:31 | 50.027
2025-03-24 | 10:31 | 50.024
2025-03-24 | 10:31 | 50.02
2025-03-24 | 10:31 | 50.019
2025-03-24 | 10:31 | 50.016
2025-03-24 | 10:31 | 50.015
2025-03-24 | 10:31 | 50.013
2025-03-24 | 10:31 | 50.011
2025-03-24 | 10:31 | 50.013
2025-03-24 | 10:31 | 50.014
2025-03-24 | 10:31 | 50.015
2025-03-24 | 10:31 | 50.014
2025-03-24 | 10:31 | 50.014
2025-03-24 | 10:31 | 50.014
2025-03-24 | 10:31 | 50.013
2025-03-24 | 10:31 | 50.014
2025-03-24 | 10:31 | 50.014
2025-03-24 | 10:31 | 50.014
2025-03-24 | 10:31 | 50.014
2025-03-24 | 10:31 | 50.016
2025-03-24 | 10:31 | 50.015
2025-03-24 | 10:31 | 50.012
2025-03-24 | 10:31 | 50.01
2025-03-24 | 10:31 | 50.007
2025-03-24 | 10:31 | 50.005
2025-03-24 | 10:31 | 50.001
2025-03-24 | 10:31 | 49.998
2025-03-24 | 10:31 | 49.996
2025-03-24 | 10:31 | 49.993
2025-03-24 | 10:31 | 49.99
2025-03-24 | 10:31 | 49.987
2025-03-24 | 10:31 | 49.985
2025-03-24 | 10:31 | 49.985
2025-03-24 | 10:31 | 49.987
2025-03-24 | 10:31 | 49.988
2025-03-24 | 10:31 | 49.991
2025-03-24 | 10:31 | 49.993
2025-03-24 | 10:31 | 49.996
2025-03-24 | 10:31 | 49.999
2025-03-24 | 10:31 | 50
2025-03-24 | 10:31 | 50.003
2025-03-24 | 10:31 | 50.003
2025-03-24 | 10:31 | 50.005
2025-03-24 | 10:31 | 50.007
2025-03-24 | 10:31 | 50.009
2025-03-24 | 10:32 | 50.01
2025-03-24 | 10:32 | 50.01
2025-03-24 | 10:32 | 50.01
2025-03-24 | 10:32 | 50.009
2025-03-24 | 10:32 | 50.01
2025-03-24 | 10:32 | 50.009
2025-03-24 | 10:32 | 50.009
2025-03-24 | 10:32 | 50.013
2025-03-24 | 10:32 | 50.015
2025-03-24 | 10:32 | 50.018
2025-03-24 | 10:32 | 50.021
2025-03-24 | 10:32 | 50.022
2025-03-24 | 10:32 | 50.022
2025-03-24 | 10:32 | 50.022
2025-03-24 | 10:32 | 50.02
2025-03-24 | 10:32 | 50.02
2025-03-24 | 10:32 | 50.017
2025-03-24 | 10:32 | 50.014
2025-03-24 | 10:32 | 50.012
2025-03-24 | 10:32 | 50.015
2025-03-24 | 10:32 | 50.016
2025-03-24 | 10:32 | 50.017
2025-03-24 | 10:32 | 50.016
2025-03-24 | 10:32 | 50.015
2025-03-24 | 10:32 | 50.015
2025-03-24 | 10:32 | 50.013
2025-03-24 | 10:32 | 50.012
2025-03-24 | 10:32 | 50.01
2025-03-24 | 10:32 | 50.009
2025-03-24 | 10:32 | 50.006
2025-03-24 | 10:32 | 50.005
2025-03-24 | 10:32 | 50.003
2025-03-24 | 10:32 | 49.996
2025-03-24 | 10:32 | 49.992
2025-03-24 | 10:32 | 49.986
2025-03-24 | 10:32 | 49.984
2025-03-24 | 10:32 | 49.982
2025-03-24 | 10:32 | 49.982
2025-03-24 | 10:32 | 49.983
2025-03-24 | 10:32 | 49.985
2025-03-24 | 10:32 | 49.984
2025-03-24 | 10:32 | 49.983
2025-03-24 | 10:32 | 49.979
2025-03-24 | 10:32 | 49.978
2025-03-24 | 10:32 | 49.977
2025-03-24 | 10:32 | 49.976
2025-03-24 | 10:32 | 49.974
2025-03-24 | 10:32 | 49.974
2025-03-24 | 10:32 | 49.975
2025-03-24 | 10:32 | 49.977
2025-03-24 | 10:32 | 49.978
2025-03-24 | 10:32 | 49.977
2025-03-24 | 10:32 | 49.976
2025-03-24 | 10:32 | 49.977