## Sheet1
Category | Example Scenarios |  | Existing |  | New |  | TIA Required? |  | Outcome check
|  |  | Installed Capacity (Original Proposal) | Export Capacity (WACM1) | Installed Capacity (Original Proposal) | Export Capacity (WACM1) | Installed Capacity (Original Proposal) | Export Capacity (WACM1)
A new generation connection | 1 | New generation connection with 0MW export capacity | N/A | N/A | 4MW | 0MW | No | No | Same
| 2 | New generation connection with 6MW installed capacity and 0 MW export capacity | N/A | N/A | 6MW | 0MW | Yes | No | Different
Changes to an existing connection with 0 MW export and installed capacity below the 5MW threshold | 3 | Existing connection with 2MW installed capacity increasing to 4MW | 2MW | 0MW* | 4MW | 0MW | No | No | Same
| 4 | Existing connection with 2MW installed capacity increasing to 6MW | 2MW | 0MW* | 6MW | 0MW | Yes | No | Different
Changes to an existing connection with 0 MW export capacity and installed capacity above the 5MW threshold | 5 | Existing connection with 6MW installed capacity increasing to 12MW | 6MW | 0MW* | 12MW | 0MW | Yes | No | Different
A new generation connection | 6 | New generation connection with 4MW installed capacity and 4MW export capacity | N/A | N/A | 4MW | 4MW | No | No | Same
| 7 | New generation connection with 6MW installed capacity and 6MW export capacity | N/A | N/A | 6MW | 6MW | Yes | Yes | Same
| 8 | New generation connection with 6MW installed capacity but only 3MW export | N/A | N/A | 6MW | 3MW | Yes | No | Different
Changes to an existing connection with both export and installed capacities below the 5MW threshold | 9 | Existing connection with 2MW installed capacity and 2MW export capacity increasing to 4MW installed capacity and 4MW export capacity | 2MW | 2MW | 4MW | 4MW | No | No | Same
| 10 | Existing connection with 2MW installed capacity and 2MW export capacity to increasing to 6MW installed capacity and 6MW export capacity | 2MW | 2MW | 6MW | 6MW | Yes | Yes | Same
| 11 | Existing connection with 2MW installed capacity and 2MW export capacity increasing to 6MW installed capacity and 4MW export capacity | 2MW | 2MW | 6MW | 4MW | Yes | No | Different
| 12 | Existing connection with 4MW installed capacity and 4MW export capacity increasing to 6MW installed capacity and 4MW export capacity | 4MW | 4MW | 6MW | 4MW | Yes | No | Different
Changes to an existing connection with both export and installed capacities above the 5MW threshold | 13 | Existing connection with 6MW of installed capacity and 6MW of export capacity increasing to 8MW of installed capacity and 8MW of export capacity | 6MW | 6MW | 8MW | 8MW | Yes | Yes | Same
Changes to an existing connection with installed capacity only above the 5MW threshold | 14 | Existing connection with 6MW installed capacity with 2MW export capacity increasing to 4MW export capacity | 6MW | 2MW | 6MW | 4MW | Yes | No | Different
| 15 | Existing connection with 6MW installed capacity with 2MW export increasing installed capacity to 8MW and export capacity to 4MW | 6MW | 2MW | 8MW | 4MW | Yes | No | Different
| 16 | Existing connection with 6MW installed capacity with 2MW export, increasing installed capacity to 8MW and export capacity to 6MW | 6MW | 2MW | 8MW | 6MW | Yes | Yes | Same
Changes to an existing connection wanting to reduce capacity | 17 | Existing connection with 6MW of installed capacity and 6MW of export capacity reducing to 4MW of installed capacity and 4MW of export capacity | 6MW | 6MW | 4MW | 4MW | No | No | Same
| 18 | Existing connection with 6MW of both export and installed capacity reducing export capacity to 4MW with no change to installed capacity | 6MW | 6MW | 6MW | 4MW | No | No | Same
Assumptions:
The term "existing connection" means sites which are already energised or are have a contracted DNO connection offer but not yet energised
All of the scenarios listed assume that there are no fault level issues at GSP, where fault level issues are known a TIA must take place
All of the scenarios listed also apply to existing demand connections seeking to add generation
Where the installed capacity is greater than the export capacity, export limiting schemes will be installed to limit the export from the customers site.