## Note
Long-term 2029
Stability: Site Effectiveness Information
Version Control
| V1 | Initial Version Published at EOI Stage. This document relates to the Stability Service as part of the Long-term 2029 tender | 24 March 2025
This document contains the following information for the acceptable sites within each region of need for the Stability Service. System Impedance - The fault level for the connection points permissible as part of the Long Term 2029 Stability Service Fault Impedance - The fault impedance for faults at the reference node(s) as seen by the connection point. Effectiveness Factors - The effectiveness of the Short-Circuit Level injected at the connection point to the reference node.
Notes:
1 | Substations are at transmission voltage level
2 | For substations which are run solid, just one busbar is shown. For substations that are run split, multiple busbars will be shown representing the electrical nodes of the split
3 | Effectiveness factors show how effective a solution will be based on its location to provide short circuit current contribution to the NESO regions of need, please be aware that some locations may be effective across multiple regions. In the effectiveness factors tab, the sites in yellow cells are the most effective towards the region of need they are within.
4 | Short circuit current contribution is based on positive sequence RMS reactive current value at 40ms after fault initiation.
5 | The substations included within each of the regions of need have been identified based on their overall effectiveness at contributing to the main reference point of each region, with the view to ensure that each region is defined, with reduced interactivity between regions.
This data has been supplied at the EOI stage to help inform tenders of possible sites that would be effective towards meting NESO's stability requirement. The data provided in the System Impedance and Fault Impedance tabs will need to be used at the Feasibility Study stage. Further information for this will be provided at the ITT stage of the tender. The overall effectiveness depends on two factors, the fault current injection to the remote fault at the point of connection (a combination of the System and Fault Impedance) then the overall effectiveness of this fault current injection towards the reference site (Effective Factors)
Information that is supplied to Tenderers as part of this tender process is supplied in good faith. The information contained in this document or any other document in the EOI Pack and in any related written or oral communication is believed to be correct at the time of issue. NESO will not accept any liability for its accuracy, adequacy or completeness and no warranty is given as such. Any reliance by a Tenderer or any third party on the information provided by NESO as part of this document or any other document in the EOI Pack is at the Tenderer’s and/or third party’s risk.

## System Impedance
Region | Substation Location | Substation Code | Voltage Level (kV)
|  |  |  | Sk'' (MVA) | X/R ratio (peak) | Z (Ohm) | R (Ohm) | X (Ohm) | Z angle (degree)
North East of England | Aldwarke 275kV | ALDW2/ALDW2 MC1 | 275 | 3861 | 13.5 | 19.5869 | 1.4469 | 19.5334 | 85.7636
North East of England | Blyth 275kV | BLYT2/BLYT2 M1 | 275 | 4677 | 14.669 | 16.1696 | 1.0997 | 16.1321 | 86.1001
North East of England | Blyth 400 kV | BLYT4/BLYT4 M1 | 400 | 4840.54 | 15.055 | 33.0542 | 2.1907 | 32.9815 | 86.1998
North East of England | Bradford West 275kV | BRAW2/BRAW2 MC1 | 275 | 3780.94 | 17.23 | 20.0016 | 1.1589 | 19.968 | 86.6784
North East of England | Bradford West 400kV | BRAW4/BRAW4A | 400 | 3528.77 | 17.118 | 45.3416 | 2.6443 | 45.2644 | 86.6567
North East of England | Brinsworth 275kV | BRIN2/BRIN2 M2 | 275 | 3889.46 | 12.953 | 19.4436 | 1.4966 | 19.3859 | 85.5854
North East of England | Brinsworth 275kV | BRIN2/BRIN2 R1 | 275 | 3477.44 | 12.224 | 21.7473 | 1.7731 | 21.6749 | 85.3233
North East of England | Brinsworth 400kV | BRIN4/BRIN4_R2 | 400 | 4901.79 | 18.013 | 32.6411 | 1.8093 | 32.591 | 86.8225
North East of England | Chesterfield 400kV | CHTE4/CHTE4_M1 | 400 | 4625.21 | 17.819 | 34.593 | 1.9383 | 34.5387 | 86.7879
North East of England | Cottam 400kV | COTT4/COTT4 M1 | 400 | 5814.69 | 19.679 | 27.5165 | 1.3965 | 27.4811 | 87.091
North East of England | Cottam 400kV | COTT4/COTT4 R3/4 | 400 | 5974.16 | 19.764 | 26.782 | 1.3534 | 26.7478 | 87.1035
North East of England | Creyke Beck 400kV | CREB4/CREB4 MB1 | 400 | 5677.75 | 20.788 | 28.1802 | 1.354 | 28.1476 | 87.2459
North East of England | Drax 400kV | DRAX4/DRAX4 M2 | 400 | 5255.74 | 19.209 | 30.4429 | 1.5827 | 30.4017 | 87.0199
North East of England | Drax 400kV | DRAX4/DRAX4 R4/5/6 | 400 | 5277.08 | 19.911 | 30.3198 | 1.5208 | 30.2816 | 87.1248
North East of England | Eggborough 400kV | EGGB4/EGGB4 M2 | 400 | 5076.29 | 18.486 | 31.5191 | 1.7025 | 31.4731 | 86.9036
North East of England | Eggborough 400kV | EGGB4/EGGB4 R1 | 400 | 5116.95 | 19.307 | 31.2686 | 1.6174 | 31.2268 | 87.035
North East of England | Elland 275kV | ELLA2/ELLA2 MC4 | 275 | 3792.77 | 15.67 | 19.9393 | 1.2699 | 19.8988 | 86.3486
North East of England | Ferrybridge 275kV | FERR2/FERR2 M1 | 275 | 3743.25 | 18.545 | 20.203 | 1.0878 | 20.1737 | 86.9134
North East of England | Ferrybridge 275kV | FERR2/FERR2 R2 | 275 | 3763.82 | 19.55 | 20.0926 | 1.0264 | 20.0664 | 87.0718
North East of England | Fourstones 275kV | FOUR2/FOUR2 MC1 | 275 | 3610.04 | 9.699 | 20.9485 | 2.1485 | 20.8381 | 84.1134
North East of England | Grimsby West 400kV | GRIW4/GRIW4 MC1 | 400 | 5688.02 | 21.365 | 28.1293 | 1.3152 | 28.0985 | 87.3202
North East of England | Greystones A 275kV | GRST2A/GRST2A M1 | 275 | 3887.29 | 20.868 | 19.4544 | 0.93119 | 19.4321 | 87.2565
North East of England | Greystones B 275kV | GRST2B/GRST2B M3 | 275 | 3895.98 | 20.986 | 19.411 | 0.9239 | 19.389 | 87.2719
North East of England | Harker 400kV GIS | HARKG4/HARKG R6 | 400 | 4422.03 | 12.797 | 36.1825 | 2.8188 | 36.0725 | 85.5318
North East of England | Hartmoor 275kV | HARM2/HARM2 MC3 | 275 | 4021.87 | 14.405 | 18.8034 | 1.3022 | 18.7583 | 86.0289
North East of England | Hartlepool 275kV | HATL2/HATL2 M1 | 275 | 4241.89 | 15.393 | 17.8281 | 1.1558 | 17.7906 | 86.283
North East of England | Hawthorn Pit 275kV | HAWP2/HAWP2 MC1 | 275 | 4481.84 | 15.714 | 16.8737 | 1.0716 | 16.8396 | 86.3587
North East of England | Hedon 275kV | HEDO2/HEDO2 R1 | 275 | 4097.17 | 20.521 | 18.4579 | 0.8984 | 18.436 | 87.2102
North East of England | High Marnham 275kV | HIGM2/HIGM2 R5 | 275 | 4249.37 | 16.973 | 17.7968 | 1.0467 | 17.7659 | 86.6282
North East of England | High Marnham 400kV | HIGM4/HIGM4 MC1 | 400 | 5558.37 | 18.559 | 28.7854 | 1.5488 | 28.7437 | 86.9158
North East of England | Humber Refinery 400kV | HUMR4/HUMR4 M1 | 400 | 7012.22 | 26.112 | 22.8173 | 0.87318 | 22.8006 | 87.8068
North East of England | Jordanthorpe 275kV | JORD2/JORD2 MC1 | 275 | 3241.34 | 11.222 | 23.3314 | 2.0709 | 23.2393 | 84.9078
North East of England | Keadby 400kV | KEAD4/KEAD4 M3 | 400 | 6314.49 | 22.639 | 25.3385 | 1.1182 | 25.3139 | 87.4708
North East of England | Keadby 400kV | KEAD4/KEAD4 R2 | 400 | 6119.45 | 22.758 | 26.1461 | 1.1478 | 26.1209 | 87.484
North East of England | Keadby 400kV | KEAD4/KEAD4 R3 | 400 | 5340.7 | 18.76 | 29.9586 | 1.5947 | 29.9161 | 86.9487
North East of England | Killingholme 400kV | KILL4/KILL4 M1 | 400 | 6895.13 | 25.434 | 23.2048 | 0.91165 | 23.1869 | 87.7484
North East of England | Kirkstall 275kV | KIRK2/KIRK2 MC3 | 275 | 3548.09 | 16.418 | 21.3143 | 1.2958 | 21.2749 | 86.5145
North East of England | Knaresborough 275KV | KNAR2/KNAR2 MC2 | 275 | 3698.93 | 12.386 | 20.4451 | 1.6453 | 20.3788 | 85.3842
North East of England | Lackenby 275kV | LACK2/LACK2 M1 | 275 | 3731.72 | 17.027 | 20.2655 | 1.1881 | 20.2306 | 86.6389
North East of England | Lackenby 400kV | LACK4/LACK4 M1 | 400 | 4931.13 | 16.16 | 32.4469 | 2.004 | 32.385 | 86.459
North East of England | Creyke Beck B 400kV | CREBB4/M2 | 400 | 5841.06 | 20.633 | 27.3923 | 1.326 | 27.3602 | 87.2253
North East of England | Monk Fryston 275kV | MONF2/MONF2 M1 | 275 | 3831.17 | 20.331 | 19.7394 | 0.96973 | 19.7156 | 87.1841
North East of England | Monk Fryston 275kV | MONF2/MONF2 R1 | 275 | 3655.04 | 25.585 | 20.6906 | 0.80808 | 20.6748 | 87.7617
North East of England | Monk Fryston 400kV | MONF4/MONF4 MC2 | 400 | 4873.71 | 18.149 | 32.8292 | 1.8061 | 32.7795 | 86.8462
North East of England | Monk Fryston Substation-New 400kV | MONFN4/MONFN4 M4 | 400 | 4873.71 | 18.149 | 32.8292 | 1.8061 | 32.7795 | 86.8462
North East of England | Monk Fryston Substation-New 400kV | MONFN4/MONFN4 M5 | 400 | 4871.13 | 18.991 | 32.8466 | 1.7272 | 32.8011 | 86.9858
North East of England | Neepsend 275kV | NEEP2/NEEP2 M2 | 275 | 3447.71 | 12.863 | 21.9348 | 1.7001 | 21.8689 | 85.5546
North East of England | Norton 275kV | NORT2/NORT2 M1 | 275 | 4175.61 | 18.267 | 18.1111 | 0.98998 | 18.084 | 86.8666
North East of England | Norton 400kV | NORT4/NORT4 M1 | 400 | 5222.56 | 16.304 | 30.6363 | 1.8755 | 30.5789 | 86.4902
North East of England | Offerton 275kV | OFFE2/OFFE2 MC1 | 275 | 4235.93 | 14.073 | 17.8532 | 1.2654 | 17.8083 | 85.9355
North East of England | Osbaldwick 400kV | OSBA4/OSBA4 MC1 | 400 | 4677.45 | 17.541 | 34.2067 | 1.9469 | 34.1512 | 86.7371
North East of England | Osbaldwick 400kV | OSBA4/OSBA4 MC3/4 | 400 | 5047.62 | 18.162 | 31.6981 | 1.7427 | 31.6502 | 86.8485
North East of England | Pitsmoor 275kV | PITS2/PITS2 MC2 | 275 | 3441.43 | 12.364 | 21.9749 | 1.7715 | 21.9034 | 85.376
North East of England | Poppleton 275kV | POPP2/POPP2 MC1 | 275 | 4462.96 | 17.006 | 16.945 | 0.9947 | 16.9158 | 86.6347
North East of England | Hawthorn Pit 400kV | HAWP4/R2 | 400 | 4740.78 | 15.885 | 33.7497 | 2.1204 | 33.683 | 86.3978
North East of England | Saltend North 275kV | SAEN2/SAEN2 MC2 | 275 | 4097.79 | 20.522 | 18.4551 | 0.89822 | 18.4332 | 87.2103
North East of England | Saltend South 275kV | SAES2/SAES2 M | 275 | 4098.7 | 20.516 | 18.451 | 0.89828 | 18.4291 | 87.2095
North East of England | Saltholme 275kV | SALH2/SALH2 MC1 | 275 | 4088.99 | 15.336 | 18.4948 | 1.2034 | 18.4556 | 86.2692
North East of England | South Humber Bank 400kV | SHBA4/SHBA4 M1 | 400 | 6018.48 | 22.176 | 26.5848 | 1.1976 | 26.5578 | 87.4181
North East of England | Sheffield City 275kV | SHEC2/SHEC2 MC1 | 275 | 3342.63 | 12.066 | 22.6244 | 1.8686 | 22.5471 | 85.2623
North East of England | Skelton Grange 275kV | SKLG2/SKLG2 MC4 | 275 | 3664.01 | 17.223 | 20.64 | 1.1964 | 20.6053 | 86.677
North East of England | Spennymoor 400kV | SPEN4/SPEN4 MC2 | 400 | 4804.01 | 15.587 | 33.3055 | 2.1324 | 33.2372 | 86.3292
North East of England | Spennymoor 400kV | SPEN4/SPEN4 MC3 | 400 | 4827.05 | 15.561 | 33.1465 | 2.1257 | 33.0783 | 86.323
North East of England | South Shields 275kV | SSHI2/SSHI2 MC1 | 275 | 4251.53 | 13.419 | 17.7877 | 1.3219 | 17.7385 | 85.7381
North East of England | Stella West 275kV | STEW2/STEW2 M1 | 275 | 4864.11 | 15.043 | 15.5476 | 1.0313 | 15.5133 | 86.1968
North East of England | Stella West 400kV | STEW4/STEW4 M1 | 400 | 5253.3 | 16.051 | 30.457 | 1.8938 | 30.3981 | 86.435
North East of England | Stocksbridge 400kV | STSB4/STSB4 MC1 | 400 | 4354.09 | 16.056 | 36.7471 | 2.2843 | 36.676 | 86.4361
North East of England | Templeborough 275kV | TEMP2/TEMP2 MC2 | 275 | 3412.14 | 12.045 | 22.1635 | 1.8338 | 22.0875 | 85.2541
North East of England | Templeborough 275kV | TEMP2/TEMP2 MC3 | 275 | 3416.08 | 12.103 | 22.1379 | 1.8229 | 22.0628 | 85.2767
North East of England | Thorpe Marsh 275kV | THOM2/THOM2 M1 | 275 | 4179.3 | 19.322 | 18.0951 | 0.93525 | 18.0709 | 87.0373
North East of England | Thorpe Marsh 400kV | THOM4/THOM4 MC3 | 400 | 5096.32 | 18.785 | 31.3952 | 1.6689 | 31.3508 | 86.9528
North East of England | Thorpe Marsh 400kV | THOM4/THOM4 R6 | 400 | 5116 | 17.663 | 31.2744 | 1.7678 | 31.2244 | 86.7596
North East of England | Thornton 400kV | THTO4/THTO4 M1 | 400 | 5498.24 | 20.006 | 29.1002 | 1.4528 | 29.0639 | 87.1385
North East of England | Thornton 400kV | THTO4/THTO4 M2 | 400 | 5394.92 | 19.369 | 29.6575 | 1.5291 | 29.6181 | 87.0445
North East of England | Thornton 400kV | THTO4/THTO4 R1/2 | 400 | 4777.07 | 18.169 | 33.4933 | 1.8406 | 33.4427 | 86.8497
North East of England | Thurcroft 275kV | THUR2/THUR2 MC2 | 275 | 3977.14 | 12.214 | 19.0149 | 1.5516 | 18.9515 | 85.3194
North East of England | Tinsley Park 275kV | TINP2/TINP2 M1 | 275 | 3700.77 | 12.36 | 20.4349 | 1.6479 | 20.3684 | 85.3745
North East of England | Tinsley Park 275kV | TINP2/TINP2 M2 | 275 | 3702.64 | 12.378 | 20.4246 | 1.6447 | 20.3583 | 85.3812
North East of England | Tod Point 275kV | TODP2/TODP2 MC1 | 275 | 3773.92 | 15.833 | 20.0388 | 1.2631 | 19.999 | 86.386
North East of England | Tynemouth 275kV | TYNE2/TYNE2 MC1 | 275 | 4180.22 | 12.988 | 18.0912 | 1.3888 | 18.0378 | 85.5972
North East of England | West Boldon 275kV | WBOL2/WBOL2 MC2 | 275 | 4393.82 | 14.129 | 17.2117 | 1.2151 | 17.1687 | 85.9516
North East of England | West Burton 400kV | WBUR4/WBUR4 M1 | 400 | 5993.05 | 21.553 | 26.6976 | 1.2374 | 26.6689 | 87.3435
North East of England | West Burton 400kV | WBUR4/WBUR4 R3/4 | 400 | 5837.51 | 20.551 | 27.4089 | 1.3321 | 27.3766 | 87.2142
North East of England | Wincobank 275kV | WIBA2/WIBA2 MC1 | 275 | 3417.73 | 12.175 | 22.1273 | 1.8113 | 22.053 | 85.3045
North East of England | Wilton 275kV | WILT2/WILT2A | 275 | 3870.73 | 20.995 | 19.5377 | 0.92953 | 19.5155 | 87.273
North East of England | Wilton 275kV | WILT2/WILT2B | 275 | 3870.73 | 20.995 | 19.5377 | 0.92953 | 19.5155 | 87.273
North East of England | Wilton 275kV | WILT2/WILT2C | 275 | 3879.28 | 21.114 | 19.4946 | 0.92227 | 19.4728 | 87.2884
North East of England | Wilton 275kV | WILT2/WILT2D | 275 | 3879.34 | 21.113 | 19.4943 | 0.9223 | 19.4725 | 87.2883
North East of England | West Melton 275kV | WMEL2/WMEL2 MC1 | 275 | 4261.51 | 14.881 | 17.7461 | 1.1898 | 17.7061 | 86.1555
North East of England | York North 275kV | OVER2/YORK2 M1 | 275 | 4718.25 | 19.026 | 16.0282 | 0.84127 | 16.0061 | 86.9913
South Wales and West England | Abham 400kV | ABHA4/ABHA4A | 400 | 4467.05 | 13.076 | 35.8178 | 2.7312 | 35.7135 | 85.6268
South Wales and West England | Abham 400kV | ABHA4/ABHA4B | 400 | 4464.83 | 13.072 | 35.8356 | 2.7334 | 35.7312 | 85.6254
South Wales and West England | Aberthaw 275kV | ABTH2/ABTH2 M1 | 275 | 4270.67 | 14.367 | 17.708 | 1.2296 | 17.6653 | 86.0184
South Wales and West England | Alverdiscott 400kV GIS | ALVE4A/ALVE4 M4 | 400 | 4529.69 | 13.002 | 35.3225 | 2.7087 | 35.2185 | 85.602
South Wales and West England | Axminster 400kV | AXMI4/AXMI4 MC1 | 400 | 4796.01 | 14.796 | 33.3611 | 2.2496 | 33.2851 | 86.1335
South Wales and West England | Baglan Bay 275kV | BAGB2/BAGB2 R1 | 275 | 3638.66 | 13.828 | 20.7838 | 1.4991 | 20.7296 | 85.8637
South Wales and West England | Bramley 400kV | BRLE4/BRLE4 M1 | 400 | 6117.97 | 18.226 | 26.1525 | 1.4327 | 26.1132 | 86.8595
South Wales and West England | Bridgwater 400kV | BRWA4A | 400 | 7889.22 | 10.029 | 20.2808 | 2.0122 | 20.1808 | 84.3058
South Wales and West England | Bridgwater 400kV | BRWA4B | 400 | 7903.26 | 10.032 | 20.2448 | 2.0081 | 20.145 | 84.3075
South Wales and West England | Cardiff East 275kV | CARE2/CARE2 MC1 | 275 | 3821.38 | 12.681 | 19.79 | 1.5558 | 19.7287 | 85.4911
South Wales and West England | Chickerell 400kV | CHIC4/CHIC4 MB2 | 400 | 4864.01 | 15.012 | 32.8947 | 2.1864 | 32.8219 | 86.189
South Wales and West England | Chickerell 400kV | CHIC4/CHIC4 R1/2 | 400 | 4807.62 | 15.011 | 33.2805 | 2.2122 | 33.2069 | 86.1887
South Wales and West England | Cilfynydd 400kV | CILF4/CILF4 M2 | 400 | 5145.67 | 15.389 | 31.0941 | 2.0163 | 31.0287 | 86.2821
South Wales and West England | Cowley 400kV | COWL4/COWL4 M1 | 400 | 6141.79 | 18.715 | 26.051 | 1.39 | 26.0139 | 86.9414
South Wales and West England | Didcot 400kV | DIDC4/DIDC4 R1/2 | 400 | 6084.59 | 18.393 | 26.2959 | 1.4276 | 26.2572 | 86.888
South Wales and West England | Exeter Main 400kV | EXET4/EXET4 R1 | 400 | 5191.19 | 14.44 | 30.8214 | 2.1293 | 30.7478 | 86.0385
South Wales and West England | Feckenham 400kV | FECK4/FECK4 R2 | 400 | 5167.17 | 15.847 | 30.9647 | 1.9501 | 30.9033 | 86.3892
South Wales and West England | Fleet 400kV | FLEE4/FLEE4 MC1 | 400 | 6057.96 | 18.025 | 26.4115 | 1.463 | 26.371 | 86.8246
South Wales and West England | Hinkley Point 275kV | HINP2/HINP2 R1 | 275 | 2707.12 | 27.134 | 27.9356 | 1.0288 | 27.9166 | 87.8894
South Wales and West England | Hinkley Point 400kV | HINP4/HINP4 R3/4 | 400 | 5335.12 | 14.853 | 29.99 | 2.0146 | 29.9222 | 86.1483
South Wales and West England | Imperial Park 400kV | IMPP4/IMPP4 MC2 | 400 | 4891.97 | 15.232 | 32.7067 | 2.1426 | 32.6364 | 86.2439
South Wales and West England | Indian Queens 400kV | INDQ4/INDQ4 MC2 | 400 | 4325.31 | 12.063 | 36.9916 | 3.056 | 36.8651 | 85.2611
South Wales and West England | Iron Acton 275kV | IROA2/IROA2 MC3 | 275 | 4457.51 | 14.497 | 16.9657 | 1.1675 | 16.9255 | 86.054
South Wales and West England | Langage 400kV | LAGA4/LAGA4 M2 | 400 | 4555.68 | 12.9 | 35.121 | 2.7144 | 35.0159 | 85.5673
South Wales and West England | Landulph 400kV | LAND4/LAND4 MC2 | 400 | 4278.41 | 12.379 | 37.3971 | 3.0112 | 37.2756 | 85.3816
South Wales and West England | Landulph 400kV | LAND4/LAND4 MC3 | 400 | 4274.31 | 12.363 | 37.4329 | 3.018 | 37.3111 | 85.3756
South Wales and West England | Margam 275kV | MAGA2/MAGA2 MC1 | 275 | 3755.48 | 13.06 | 20.1372 | 1.5374 | 20.0785 | 85.6214
South Wales and West England | Melksham 400kV | MELK4/MELK4 M1 | 400 | 5670.08 | 15.768 | 28.2183 | 1.786 | 28.1617 | 86.3712
South Wales and West England | Minety 400kV | MITY4/MITY4 MC3 | 400 | 5508.63 | 15.255 | 29.0453 | 1.8999 | 28.9831 | 86.2495
South Wales and West England | New Woolavington | ---- | 400 | 7903.26 | 10.032 | 20.2448 | 2.0081 | 20.145 | 84.3075
South Wales and West England | Pembroke 400kV | PEMB4/PEMB4 M2 | 400 | 4214.79 | 14.648 | 37.9616 | 2.5856 | 37.8734 | 86.0946
South Wales and West England | Pont Abraham 400kV | POAB4/POAB4 R1 | 400 | 4382.25 | 14.884 | 36.5109 | 2.4475 | 36.4288 | 86.1563
South Wales and West England | Pyle 275kV | PYLE2/PYLE2 MC1 | 275 | 3862.78 | 12.8 | 19.5779 | 1.5249 | 19.5184 | 85.5328
South Wales and West England | Rassau 400kV | RASS4/RASS4 M2 | 400 | 4806.41 | 15.186 | 33.2889 | 2.1873 | 33.2169 | 86.2325
South Wales and West England | Rhigos 400KV | RHIG4/RHIG4 M2 | 400 | 4712.78 | 15.047 | 33.9502 | 2.2513 | 33.8755 | 86.1978
South Wales and West England | Sandford 400kV | SAFO4/SAFO4 M2 | 400 | 5029.73 | 14.76 | 31.8109 | 2.1503 | 31.7381 | 86.1241
South Wales and West England | Seabank 400kV | SEAB4/SEAB4 M2 | 400 | 5265.57 | 15.343 | 30.3861 | 1.9763 | 30.3217 | 86.2709
South Wales and West England | Shurton 400kV | SHUR4/SHUR4 M1 | 400 | 5342.51 | 14.856 | 29.9485 | 2.0114 | 29.8809 | 86.1491
South Wales and West England | Swansea North 275kV | SWAN2/SWAN2 MC3 | 275 | 2895.49 | 21.016 | 26.1182 | 1.2414 | 26.0887 | 87.2758
South Wales and West England | Swansea North 400kV | SWAN4/SWAN4 M1 | 400 | 4150.02 | 14.754 | 38.554 | 2.6071 | 38.4658 | 86.1225
South Wales and West England | Swansea North 400kV | SWAN4/SWAN4 R3 | 400 | 4565.62 | 15.029 | 35.0445 | 2.3266 | 34.9672 | 86.1933
South Wales and West England | Taunton 400kV | TAUN4/TAUN4 M1 | 400 | 5042.97 | 14.033 | 31.7273 | 2.2552 | 31.6471 | 85.924
South Wales and West England | Taunton 400kV | TAUN4/TAUN4 M2 | 400 | 5065.37 | 14.016 | 31.587 | 2.2479 | 31.5069 | 85.919
South Wales and West England | Tremorfa 275kV | TREM2/TREM2 MC1 | 275 | 3882.82 | 12.466 | 19.4768 | 1.5574 | 19.4145 | 85.4137
South Wales and West England | Culham Jet 400kV | CULJ4/Term406 | 400 | 6054.28 | 18.32 | 26.4276 | 1.4404 | 26.3883 | 86.8756
South Wales and West England | Upper Boat 275kV | UPPB2/UPPB2 MC3 | 275 | 3918.58 | 14.949 | 19.2991 | 1.2881 | 19.256 | 86.173
South Wales and West England | Upper Boat 275kV | UPPB2/UPPB2 MC4 | 275 | 3924.83 | 14.981 | 19.2684 | 1.2833 | 19.2256 | 86.1811
South Wales and West England | Uskmouth 275kV | USKM2/USKM2 M1 | 275 | 4411.65 | 14.819 | 17.1421 | 1.1541 | 17.1032 | 86.1395
South Wales and West England | Walham 400kV | WALH4/WALH4 MC2 | 400 | 5110.45 | 15.291 | 31.3084 | 2.0431 | 31.2417 | 86.2583
South Wales and West England | Whitson 275kV | WHSO2/WHSO2 M2 | 275 | 4302.17 | 14.175 | 17.5783 | 1.237 | 17.5348 | 85.9647
South Wales and West England | Whitson 275kV | WHSO2/WHSO2 R1 | 275 | 4442.66 | 15.372 | 17.0225 | 1.105 | 16.9866 | 86.278
South West | Abham 400kV | ABHA4/ABHA4A | 400 | 4467.05 | 13.076 | 35.8178 | 2.7312 | 35.7135 | 85.6268
South West | Abham 400kV | ABHA4/ABHA4B | 400 | 4464.83 | 13.072 | 35.8356 | 2.7334 | 35.7312 | 85.6254
South West | Alverdiscott 400kV GIS | ALVE4A/ALVE4 M4 | 400 | 4529.69 | 13.002 | 35.3225 | 2.7087 | 35.2185 | 85.602
South West | Axminster 400kV | AXMI4/AXMI4 MC1 | 400 | 4796.01 | 14.796 | 33.3611 | 2.2496 | 33.2851 | 86.1335
South West | Chickerell 400kV | CHIC4/CHIC4 MB2 | 400 | 4864.01 | 15.012 | 32.8947 | 2.1864 | 32.8219 | 86.189
South West | Chickerell 400kV | CHIC4/CHIC4 R1/2 | 400 | 4807.62 | 15.011 | 33.2805 | 2.2122 | 33.2069 | 86.1887
South West | Exeter Main 400kV | EXET4/EXET4 R1 | 400 | 5191.19 | 14.44 | 30.8214 | 2.1293 | 30.7478 | 86.0385
South West | Hinkley Point 275kV | HINP2/HINP2 M2 | 275 | 2748.39 | 26.52 | 27.5161 | 1.0368 | 27.4966 | 87.8405
South West | Hinkley Point 275kV | HINP2/HINP2 R1 | 275 | 2707.12 | 27.134 | 27.9356 | 1.0288 | 27.9166 | 87.8894
South West | Hinkley Point 400kV | HINP4/HINP4 R3/4 | 400 | 5335.12 | 14.853 | 29.99 | 2.0146 | 29.9222 | 86.1483
South West | Indian Queens 400kV | INDQ4/INDQ4 MC2 | 400 | 4325.31 | 12.063 | 36.9916 | 3.056 | 36.8651 | 85.2611
South West | Langage 400kV | LAGA4/LAGA4 M2 | 400 | 4555.68 | 12.9 | 35.121 | 2.7144 | 35.0159 | 85.5673
South West | Landulph 400kV | LAND4/LAND4 MC2 | 400 | 4278.41 | 12.379 | 37.3971 | 3.0112 | 37.2756 | 85.3816
South West | Landulph 400kV | LAND4/LAND4 MC3 | 400 | 4274.31 | 12.363 | 37.4329 | 3.018 | 37.3111 | 85.3756
South West | Mannington 400kV | MANN4/MANN4 R5 | 400 | 5548.11 | 15.775 | 28.8386 | 1.8245 | 28.7809 | 86.3728
South West | Nursling 400kV | NURS4/NURS4A | 400 | 5527.22 | 16.109 | 28.9476 | 1.7935 | 28.892 | 86.4478
South West | Sandford 400kV | SAFO4/SAFO4 M2 | 400 | 5029.73 | 14.76 | 31.8109 | 2.1503 | 31.7381 | 86.1241
South West | Seabank 400kV | SEAB4/SEAB4 M2 | 400 | 5265.57 | 15.343 | 30.3861 | 1.9763 | 30.3217 | 86.2709
South West | Shurton 400kV | SHUR4/SHUR4 M1 | 400 | 5342.51 | 14.856 | 29.9485 | 2.0114 | 29.8809 | 86.1491
South West | Taunton 400kV | TAUN4/TAUN4 M1 | 400 | 5042.97 | 14.033 | 31.7273 | 2.2552 | 31.6471 | 85.924
South West | Taunton 400kV | TAUN4/TAUN4 M2 | 400 | 5065.37 | 14.016 | 31.587 | 2.2479 | 31.5069 | 85.919
South Coast | Canterbury 400kV | CANT4/CANT4 MC1 | 400 | 6169.83 | 17.495 | 25.9326 | 1.4799 | 25.8904 | 86.7286
South Coast | Cleve Hill 400kV | CLEH4/CLEH4 M1 | 400 | 6090.16 | 17.806 | 26.2719 | 1.4731 | 26.2306 | 86.7856
South Coast | Dungeness 275kV | DUNG2/DUNG2 R2 | 275 | 4536.85 | 22.01 | 16.6691 | 0.75656 | 16.6519 | 87.3986
South Coast | Dungeness 400kV | DUNG4/DUNG4 M1 | 400 | 5857.99 | 16.209 | 27.3131 | 1.6819 | 27.2613 | 86.4697
South Coast | Kemsley 400kV | KEMS4/KEMS4 R2 | 400 | 6599.4 | 18.965 | 24.2446 | 1.2766 | 24.211 | 86.9817
South Coast | Little Horsted 400kV | LHOR4/LHOR4A | 400 | 5576.25 | 16.066 | 28.6931 | 1.7825 | 28.6377 | 86.4383
South Coast | Ninfield 400kV | NINF4/NINF4 R1 | 400 | 5767.88 | 16.208 | 27.7398 | 1.7082 | 27.6872 | 86.4694
South Coast | Richborough 400kV | RICH4/RICH4 M1 | 400 | 5699.3 | 15.847 | 28.0736 | 1.768 | 28.0179 | 86.3892
South Coast | Sellindge 400kV Compound A | SELL4A/SELL4A R1 | 400 | 5996.32 | 16.619 | 26.683 | 1.6027 | 26.6349 | 86.5565
South Coast | Sellindge 400kV Compound B | SELL4B/SELL4B R4 | 400 | 5994.29 | 16.611 | 26.6921 | 1.604 | 26.6438 | 86.5549
South West Scotland | Blackhill 132kV | SPTL\BLAH1- | 132 | 1495.16 | 14.49 | 11.6536 | 0.80234 | 11.6259 | 86.0521
South West Scotland | Breezy Hill 132kV | SPTL\BREE1- | 132 | 1475.28 | 8.138 | 11.8106 | 1.4405 | 11.7225 | 82.9946
South West Scotland | Glenglass 132kV | SPTL\GLGL1A | 132 | 1244.89 | 10.423 | 13.9964 | 1.3367 | 13.9324 | 84.5197
South West Scotland | New Cumnock 132kV | SPTL\NECU1- | 132 | 1817.58 | 23.605 | 9.5864 | 0.40575 | 9.5778 | 87.5742
East Scotland | Abernethy 132kV | ABNE1Q | 132 | 1408.97 | 2.827 | 12.3665 | 4.124 | 11.6586 | 70.5197
East Scotland | Amulree 132kV | AMUL1G | 132 | 1306.39 | 2.693 | 13.3375 | 4.6429 | 12.5033 | 69.6284
East Scotland | Arbroath 132kV | ARBR1Q | 132 | 1256.76 | 3.88 | 13.8642 | 3.4602 | 13.4255 | 75.5476
East Scotland | Birkhill 132kV | BIHI1R | 132 | 2587.96 | 7.615 | 6.7327 | 0.87661 | 6.6754 | 82.5187
East Scotland | Brechin 132kV | BREC1R | 132 | 1207.9 | 2.68 | 14.425 | 5.0429 | 13.5149 | 69.5377
East Scotland | Bridge of Dun 132kV | BRID1R | 132 | 1046.12 | 2.492 | 16.6558 | 6.2029 | 15.4577 | 68.1352
East Scotland | Burghmuir 132kV | BUMU1R | 132 | 1205.34 | 2.595 | 14.4557 | 5.198 | 13.4888 | 68.9255
East Scotland | Charlestown 132kV | CHAR1T | 132 | 2677.93 | 7.359 | 6.5065 | 0.87611 | 6.4473 | 82.2616
East Scotland | Clunie 132kV | CLUN1T | 132 | 1929.65 | 4.461 | 9.0296 | 1.9751 | 8.811 | 77.3652
East Scotland | Coupar Angus 132kV | COUA1Q | 132 | 1818.19 | 5.538 | 9.5832 | 1.7029 | 9.4306 | 79.7644
East Scotland | Denside 132kV | DENS1R | 132 | 1895.71 | 6.837 | 9.1913 | 1.3302 | 9.0945 | 81.6788
East Scotland | Dudhope 132kV | DUDH1R | 132 | 2562.92 | 6.412 | 6.7985 | 1.0476 | 6.7173 | 81.1357
East Scotland | Fasqope 132kV | FASQ1- | 132 | 1161.28 | 2.716 | 15.0041 | 5.1841 | 14.0801 | 69.7869
East Scotland | Fasque 132kV | FASQ1J | 132 | 785.82 | 2.895 | 22.173 | 7.2394 | 20.9579 | 70.9439
East Scotland | Fiddes 132kV | FIDD1B | 132 | 1108.5 | 2.861 | 15.7185 | 5.1864 | 14.8383 | 70.734
East Scotland | Glenagnes 132kV | GLAG1R | 132 | 2571.31 | 6.486 | 6.7763 | 1.0326 | 6.6972 | 81.2353
East Scotland | Lunanhead 132kV | LUNA1R | 132 | 1414.43 | 5.81 | 12.3187 | 2.0895 | 12.1402 | 80.2341
East Scotland | Lyndhurst 132kV | LYND1R | 132 | 2402.91 | 5.57 | 7.2512 | 1.2813 | 7.1371 | 79.8219
East Scotland | Milton of Craigie 132kV | MILC1V | 132 | 2626.01 | 7.326 | 6.6352 | 0.89738 | 6.5742 | 82.2272
East Scotland | Tealing 132kV | TEAL1- | 132 | 2846.49 | 9.175 | 6.1212 | 0.66324 | 6.0852 | 83.7798
North East Scotland | Blackhillock 132kV | BLHI1K | 132 | 2938.57 | 14.661 | 5.9294 | 0.4035 | 5.9157 | 86.098
North East Scotland | Blackhillock 275kV | BLHI2J | 275 | 5764.69 | 9.411 | 13.1187 | 1.3862 | 13.0452 | 83.9346
North East Scotland | Blackhillock 400kV | BLHI4- | 400 | 5515.11 | 9.922 | 29.0112 | 2.9092 | 28.865 | 84.2448
North East Scotland | Cainford 275kV | CAIN2- | 275 | 5172.45 | 8.918 | 14.6207 | 1.6293 | 14.5297 | 83.602
North East Scotland | Clayhill 132kV | CLAY1Q | 132 | 2587.38 | 7.817 | 6.7342 | 0.85452 | 6.6798 | 82.71
North East Scotland | Craigiebuckler 132kV | CRAI1R | 132 | 2673.74 | 8.284 | 6.5167 | 0.78099 | 6.4697 | 83.1169
North East Scotland | Dyce 132kV | DYCE1U | 132 | 1738 | 6.247 | 10.0253 | 1.5846 | 9.8993 | 80.9054
North East Scotland | Elchies 132kV | ELCH1- | 132 | 1216.14 | 5.865 | 14.3273 | 2.4081 | 14.1235 | 80.3239
North East Scotland | Fetteresso 132kV | FETT1- | 132 | 2744.63 | 16.137 | 6.3484 | 0.39265 | 6.3362 | 86.454
North East Scotland | Fetteresso 400kV | FETT4R | 400 | 6152.98 | 9.417 | 26.0037 | 2.7459 | 25.8583 | 83.9384
North East Scotland | Fiddes 132kV | FIDD1R | 132 | 1283.33 | 3.066 | 13.5772 | 4.21 | 12.908 | 71.9359
North East Scotland | Foggieton 132kV | FOGG1Q | 132 | 2360.66 | 5.828 | 7.381 | 1.2482 | 7.2747 | 80.2637
North East Scotland | Fraserburgh 132kV | FRAS1Q | 132 | 1052.27 | 5.082 | 16.5585 | 3.197 | 16.2469 | 78.868
North East Scotland | Glendye 132kV | GLDY1- | 132 | 1288.57 | 6.835 | 13.522 | 1.9575 | 13.3795 | 81.6764
North East Scotland | Inverugie 132kV | INRU1S | 132 | 1880.21 | 12.751 | 9.267 | 0.72455 | 9.2387 | 85.5157
North East Scotland | Keith 132kV | KEIT1K | 132 | 2747.54 | 13.493 | 6.3417 | 0.46871 | 6.3243 | 85.7614
North East Scotland | Keith 275kV | KEIT2Q | 275 | 5653.12 | 9.169 | 13.3776 | 1.4504 | 13.2987 | 83.7757
North East Scotland | Kinmuck 275kV | KINM2B | 275 | 3994.6 | 8.962 | 18.9318 | 2.0994 | 18.815 | 83.6331
North East Scotland | Kintore 132kV | KINT1U | 132 | 2766.73 | 9.943 | 6.2977 | 0.6302 | 6.2661 | 84.2569
North East Scotland | Kintore 275kV | KINT2J | 275 | 5819.21 | 9.355 | 12.9958 | 1.3813 | 12.9221 | 83.8986
North East Scotland | Kintore 400kV | KINT4K | 400 | 6073.08 | 9.537 | 26.3458 | 2.7474 | 26.2021 | 84.0141
North East Scotland | Lumbs 132kV | LUMB1Q | 132 | 1362.55 | 6.404 | 12.7878 | 1.9729 | 12.6347 | 81.1248
North East Scotland | Macduff 132kV | MACD1R | 132 | 903.01 | 3.851 | 19.2955 | 4.8497 | 18.6761 | 75.4433
North East Scotland | New Deer 400kV | NEDE4K | 400 | 5470.07 | 9.477 | 29.2501 | 3.0694 | 29.0886 | 83.9765
North East Scotland | Peterhead 132kV | PEHE1- | 132 | 1963.19 | 14.355 | 8.8754 | 0.61678 | 8.8539 | 86.0151
North East Scotland | Peterhead 275kV | PEHE2V | 275 | 4556.81 | 9.054 | 16.596 | 1.8219 | 16.4957 | 83.6973
North East Scotland | Peterhead 400kV | PEHE4J | 400 | 5041.78 | 9.435 | 31.7348 | 3.3448 | 31.5581 | 83.9499
North East Scotland | Peterhead Grange 132kV | PEHG1R | 132 | 1565.49 | 9.748 | 11.1301 | 1.1358 | 11.072 | 84.1428
North East Scotland | Persley 132kV | PERS1R | 132 | 2683.36 | 8.582 | 6.4934 | 0.75154 | 6.4497 | 83.3537
North East Scotland | Persley 275kV | PERS2R | 275 | 4275.54 | 9.001 | 17.6878 | 1.9531 | 17.5797 | 83.6605
North East Scotland | Redmoss 132kV | REDM1R | 132 | 2488.01 | 6.926 | 7.0032 | 1.0008 | 6.9313 | 81.7842
North East Scotland | Rothienorman 400kV | ROTI4K | 400 | 5817.12 | 9.527 | 27.505 | 2.8713 | 27.3547 | 84.0079
North East Scotland | St Fergus 132kV | SFER1M | 132 | 1677.49 | 10.407 | 10.3869 | 0.9935 | 10.3393 | 84.5113
North East Scotland | Strichen 132kV | STRI1Q | 132 | 1104.73 | 5.248 | 15.7722 | 2.9523 | 15.4934 | 79.2117
North East Scotland | Tarland 132kV | TARL1Q | 132 | 893.95 | 3.874 | 19.491 | 4.8716 | 18.8724 | 75.5261
North East Scotland | Willowdale 132kV | WOHI1R | 132 | 2646.66 | 7.874 | 6.5834 | 0.82943 | 6.5309 | 82.7622
North Scotland | Brora 132kV | BROR1- | 132 | 1342.38 | 3.084 | 12.9799 | 4.0036 | 12.3471 | 72.0345
North Scotland | Connagill 132kV | CONN1C | 132 | 1919.24 | 16.821 | 9.0786 | 0.53877 | 9.0626 | 86.5978
North Scotland | Connagill 275kV | CONN2K | 275 | 3592.84 | 11.431 | 21.0488 | 1.8344 | 20.9687 | 85.0004
North Scotland | Dounreay 132kV | DOUN1- | 132 | 1544.9 | 20.104 | 11.2784 | 0.56031 | 11.2645 | 87.1524
North Scotland | Dounreay 275kV | DOUN2- | 275 | 3952.93 | 12.312 | 19.1314 | 1.5488 | 19.0686 | 85.3565
North Scotland | Boulfruich 132kV | DUBE1Q | 132 | 1248.89 | 3.332 | 13.9516 | 4.0104 | 13.3628 | 73.2944
North Scotland | Gills Bay 132kV | GILB1M | 132 | 1631.67 | 12.781 | 10.6786 | 0.83296 | 10.6461 | 85.5262
North Scotland | Gordonbush 275kV | GORW2- | 275 | 3307.21 | 10.016 | 22.8667 | 2.2717 | 22.7536 | 84.2985
North Scotland | Limekilns 132kV | LIMK1A | 132 | 1532.28 | 19.581 | 11.3713 | 0.57997 | 11.3565 | 87.0764
North Scotland | Meygen 132kV | MEYG1- | 132 | 1625.22 | 12.559 | 10.721 | 0.85096 | 10.6872 | 85.4475
North Scotland | Mybster 132kV | MYBS1R | 132 | 1696.29 | 6.466 | 10.2718 | 1.5699 | 10.1511 | 81.2086
North Scotland | Mybster 132kV | MYBS1S | 132 | 1317.47 | 16.593 | 13.2253 | 0.7956 | 13.2014 | 86.5512
North Scotland | Spittal 132kV | SPIT1M | 132 | 1425.24 | 18.111 | 12.2253 | 0.67399 | 12.2067 | 86.8396
North Scotland | Spittal 275kV | SPIT2J | 275 | 3361.18 | 10.905 | 22.4995 | 2.0546 | 22.4055 | 84.7606
North Scotland | Spittal 400kV | SPIT4J | 400 | 2705.72 | 12.892 | 59.134 | 4.5731 | 58.9569 | 85.5646
North Scotland | Strathy North 132kV | STNO1C | 132 | 1321.38 | 7.46 | 13.1862 | 1.7519 | 13.0693 | 82.3651
North Scotland | Strathy South 132kV | STSO1A | 132 | 1170.98 | 6.55 | 14.8798 | 2.2457 | 14.7094 | 81.3196
North Scotland | Strathy Wood 132kV | STWO1- | 132 | 1161.27 | 5.561 | 15.0043 | 2.6555 | 14.7674 | 79.8058
North Scotland | Thurso South 132kV | THUS1M | 132 | 2083.17 | 15.652 | 8.3642 | 0.5333 | 8.3472 | 86.3444
North Scotland | Thurso South 275kV | THUS2K | 275 | 3409.58 | 11.435 | 22.1802 | 1.9323 | 22.0958 | 85.0022

## Fault Impedance
Fault Location
Region | Substation Location | Busbar | Voltage Level (kV) | Lackenby 400kV (LACK4 M1) |  | Creyke Beck 400kV CREB4 MB1 |  | Minety 400kV MITY4 MC3 |  | Seabank 400kV SEAB4 M2 |  | Exeter Main 400kV EXET4 R1 |  | Indian Queens 400kV INDQ MC2 |  | Richborough 400kV RICH4 M1 |  | Glengas 132kV GLGL1A |  | Tealing 132kV TEAL1- |  | Peterhead 400kV PEHE4J |  | Spittal 275kV SPIT2J |  | Spittal 400kV SPIT4J
|  |  |  | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm) | Rf(Ohm) | Xf(Ohm)
North East England | Aldwarke 275kV | ALDW2/ALDW2 MC1 | 275 | 0.50311 | 6.7919 | 0.26137 | 3.5285
North East England | Blyth 275kV | BLYT2/BLYT2 M1 | 275 | 0.28707 | 4.211 | 0.52469 | 7.6967
North East England | Blyth 400 kV | BLYT4/BLYT4 M1 | 400 | 0.63238 | 9.5204 | 1.1235 | 16.9149
North East England | Bradford West 275kV | BRAW2/BRAW2 MC1 | 275 | 0.35998 | 6.2024 | 0.21747 | 3.747
North East England | Bradford West 400kV | BRAW4/BRAW4A | 400 | 0.77652 | 13.2924 | 0.52632 | 9.0095
North East England | Brinsworth 275kV | BRIN2/BRIN2 M2 | 275 | 0.52584 | 6.8113 | 0.26826 | 3.4748
North East England | Brinsworth 275kV | BRIN2/BRIN2 R1 | 275 | 0.61976 | 7.576 | 0.33023 | 4.0367
North East England | Brinsworth 400kV | BRIN4/BRIN4_R2 | 400 | 0.61279 | 11.0382 | 0.3118 | 5.6165
North East England | Chesterfield 400kV | CHTE4/CHTE4_M1 | 400 | 0.66694 | 11.8843 | 0.3367 | 5.9997
North East England | Cottam 400kV | COTT4/COTT4 M1 | 400 | 0.68781 | 13.5354 | 0.34912 | 6.8703
North East England | Cottam 400kV | COTT4/COTT4 R3/4 | 400 | 0.70655 | 13.9642 | 0.32367 | 6.3969
North East England | Creyke Beck 400kV | CREB4/CREB4 MB1 | 400 | 0.49322 | 10.253 | 0 | 0
North East England | Drax 400kV | DRAX4/DRAX4 M2 | 400 | 0.49433 | 9.4956 | 0.28369 | 5.4494
North East England | Drax 400kV | DRAX4/DRAX4 R4/5/6 | 400 | 0.44154 | 8.7914 | 0.21726 | 4.3259
North East England | Eggborough 400kV | EGGB4/EGGB4 M2 | 400 | 0.523 | 9.6682 | 0.30754 | 5.6852
North East England | Eggborough 400kV | EGGB4/EGGB4 R1 | 400 | 0.47496 | 9.1701 | 0.24382 | 4.7074
North East England | Elland 275kV | ELLA2/ELLA2 MC4 | 275 | 0.39881 | 6.2494 | 0.23829 | 3.734
North East England | Ferrybridge 275kV | FERR2/FERR2 M1 | 275 | 0.33977 | 6.301 | 0.19954 | 3.7005
North East England | Ferrybridge 275kV | FERR2/FERR2 R2 | 275 | 0.31355 | 6.1299 | 0.18113 | 3.5411
North East England | Fourstones 275kV | FOUR2/FOUR2 MC1 | 275 | 0.73152 | 7.095 | 1.1877 | 11.5192
North East England | Grimsby West 400kV | GRIW4/GRIW4 MC1 | 400 | 0.7724 | 16.5023 | 0.3454 | 7.3794
North East England | Greystones A 275kV | GRST2A/GRST2A M1 | 275 | 0 | 0 | 0.22127 | 4.6175
North East England | Greystones B 275kV | GRST2B/GRST2B M3 | 275 | 0 | 0 | 0.21954 | 4.6073
North East England | Harker 400kV GIS | HARKG4/HARKG R6 | 400 | 1.1626 | 14.8774 | 1.7946 | 22.966
North East England | Hartmoor 275kV | HARM2/HARM2 MC3 | 275 | 0.19286 | 2.7782 | 0.4647 | 6.6939
North East England | Hartlepool 275kV | HATL2/HATL2 M1 | 275 | 0.15018 | 2.3118 | 0.39352 | 6.0574
North East England | Hawthorn Pit 275kV | HAWP2/HAWP2 MC1 | 275 | 0.1759 | 2.7641 | 0.40039 | 6.2917
North East England | Hedon 275kV | HEDO2/HEDO2 R1 | 275 | 0.33228 | 6.8188 | 0.05028 | 1.0318
North East England | High Marnham 275kV | HIGM2/HIGM2 R5 | 275 | 0.41518 | 7.0468 | 0.20534 | 3.4852
North East England | High Marnham 400kV | HIGM4/HIGM4 MC1 | 400 | 0.75253 | 13.9661 | 0.37756 | 7.0072
North East England | Humber Refinery 400kV | HUMR4/HUMR4 M1 | 400 | 0.58699 | 15.3275 | 0.29417 | 7.6815
North East England | Jordanthorpe 275kV | JORD2/JORD2 MC1 | 275 | 0.72383 | 8.1228 | 0.38568 | 4.3281
North East England | Keadby 400kV | KEAD4/KEAD4 M3 | 400 | 0.58895 | 13.3333 | 0.27258 | 6.171
North East England | Keadby 400kV | KEAD4/KEAD4 R2 | 400 | 0.58602 | 13.3367 | 0.22188 | 5.0496
North East England | Keadby 400kV | KEAD4/KEAD4 R3 | 400 | 0.61402 | 11.519 | 0.31283 | 5.8687
North East England | Killingholme 400kV | KILL4/KILL4 M1 | 400 | 0.58777 | 14.9494 | 0.28474 | 7.2421
North East England | Kirkstall 275kV | KIRK2/KIRK2 MC3 | 275 | 0.40473 | 6.6449 | 0.24133 | 3.9622
North East England | Knaresborough 275KV | KNAR2/KNAR2 MC2 | 275 | 0.41907 | 5.1906 | 0.27903 | 3.4561
North East England | Lackenby 275kV | LACK2/LACK2 M1 | 275 | 0.092184 | 1.5696 | 0.35691 | 6.0771
North East England | Lackenby 400kV | LACK4/LACK4 M1 | 400 | 0 | 0 | 0.48236 | 7.7949
North East England | Creyke Beck B 400kV | CREBB4/M2 | 400 | 0.40961 | 8.4516 | 0.10907 | 2.2504
North East England | Monk Fryston 275kV | MONF2/MONF2 M1 | 275 | 0.29624 | 6.0228 | 0.16979 | 3.452
North East England | Monk Fryston 275kV | MONF2/MONF2 R1 | 275 | 0.24686 | 6.3158 | 0.14597 | 3.7346
North East England | Monk Fryston 400kV | MONF4/MONF4 MC2 | 400 | 0.54254 | 9.8466 | 0.32626 | 5.9212
North East England | Monk Fryston Substation-New 400kV | MONFN4/MONFN4 M4 | 400 | 0.54254 | 9.8466 | 0.32626 | 5.9212
North East England | Monk Fryston Substation-New 400kV | MONFN4/MONFN4 M5 | 400 | 0.50144 | 9.5229 | 0.26496 | 5.0318
North East England | Neepsend 275kV | NEEP2/NEEP2 M2 | 275 | 0.59424 | 7.6438 | 0.31663 | 4.0728
North East England | Norton 275kV | NORT2/NORT2 M1 | 275 | 0.12236 | 2.2351 | 0.32125 | 5.8683
North East England | Norton 400kV | NORT4/NORT4 M1 | 400 | 0.23181 | 3.7794 | 0.58257 | 9.4983
North East England | Offerton 275kV | OFFE2/OFFE2 MC1 | 275 | 0.23035 | 3.2417 | 0.49701 | 6.9944
North East England | Osbaldwick 400kV | OSBA4/OSBA4 MC1 | 400 | 0.46862 | 8.22 | 0.35986 | 6.3123
North East England | Osbaldwick 400kV | OSBA4/OSBA4 MC3/4 | 400 | 0.38513 | 6.9947 | 0.24215 | 4.3979
North East England | Pitsmoor 275kV | PITS2/PITS2 MC2 | 275 | 0.6192 | 7.6558 | 0.32993 | 4.0793
North East England | Poppleton 275kV | POPP2/POPP2 MC1 | 275 | 0.23181 | 3.9422 | 0.17279 | 2.9384
North East England | Hawthorn Pit 400kV | HAWP4/R2 | 400 | 0.28369 | 4.5063 | 0.69929 | 11.1082
North East England | Saltend North 275kV | SAEN2/SAEN2 MC2 | 275 | 0.33222 | 6.8178 | 0.051272 | 1.0522
North East England | Saltend South 275kV | SAES2/SAES2 M | 275 | 0.33224 | 6.8162 | 0.050273 | 1.0314
North East England | Saltholme 275kV | SALH2/SALH2 MC1 | 275 | 0.15638 | 2.3982 | 0.40328 | 6.1847
North East England | South Humber Bank 400kV | SHBA4/SHBA4 M1 | 400 | 0.7309 | 16.2084 | 0.33975 | 7.5344
North East England | Sheffield City 275kV | SHEC2/SHEC2 MC1 | 275 | 0.65314 | 7.8808 | 0.34802 | 4.1992
North East England | Skelton Grange 275kV | SKLG2/SKLG2 MC4 | 275 | 0.37367 | 6.4358 | 0.21945 | 3.7797
North East England | Spennymoor 400kV | SPEN4/SPEN4 MC2 | 400 | 0.36455 | 5.6822 | 0.79671 | 12.4183
North East England | Spennymoor 400kV | SPEN4/SPEN4 MC3 | 400 | 0.36926 | 5.746 | 0.79824 | 12.4214
North East England | South Shields 275kV | SSHI2/SSHI2 MC1 | 275 | 0.2746 | 3.6848 | 0.5558 | 7.4582
North East England | Stella West 275kV | STEW2/STEW2 M1 | 275 | 0.32566 | 4.8989 | 0.54559 | 8.2073
North East England | Stella West 400kV | STEW4/STEW4 M1 | 400 | 0.53105 | 8.5239 | 0.95404 | 15.3133
North East England | Stocksbridge 400kV | STSB4/STSB4 MC1 | 400 | 0.75332 | 12.0953 | 0.42542 | 6.8305
North East England | Templeborough 275kV | TEMP2/TEMP2 MC2 | 275 | 0.64095 | 7.7202 | 0.34152 | 4.1136
North East England | Templeborough 275kV | TEMP2/TEMP2 MC3 | 275 | 0.63716 | 7.7115 | 0.3395 | 4.109
North East England | Thorpe Marsh 275kV | THOM2/THOM2 M1 | 275 | 0.30349 | 5.8641 | 0.15479 | 2.9908
North East England | Thorpe Marsh 400kV | THOM4/THOM4 MC3 | 400 | 0.50983 | 9.5771 | 0.25824 | 4.851
North East England | Thorpe Marsh 400kV | THOM4/THOM4 R6 | 400 | 0.61147 | 10.8004 | 0.3218 | 5.6839
North East England | Thornton 400kV | THTO4/THTO4 M1 | 400 | 0.39319 | 7.8661 | 0.16321 | 3.2652
North East England | Thornton 400kV | THTO4/THTO4 M2 | 400 | 0.36806 | 7.1289 | 0.17559 | 3.401
North East England | Thornton 400kV | THTO4/THTO4 R1/2 | 400 | 0.4952 | 8.9973 | 0.33506 | 6.0877
North East England | Thurcroft 275kV | THUR2/THUR2 MC2 | 275 | 0.548 | 6.6933 | 0.28028 | 3.4234
North East England | Tinsley Park 275kV | TINP2/TINP2 M1 | 275 | 0.579 | 7.1565 | 0.29538 | 3.6509
North East England | Tinsley Park 275kV | TINP2/TINP2 M2 | 275 | 0.57787 | 7.1529 | 0.29481 | 3.6491
North East England | Tod Point 275kV | TODP2/TODP2 MC1 | 275 | 0.11283 | 1.7864 | 0.39235 | 6.212
North East England | Tynemouth 275kV | TYNE2/TYNE2 MC1 | 275 | 0.309 | 4.0133 | 0.6066 | 7.8786
North East England | West Boldon 275kV | WBOL2/WBOL2 MC2 | 275 | 0.24186 | 3.4173 | 0.49874 | 7.0467
North East England | West Burton 400kV | WBUR4/WBUR4 M1 | 400 | 0.62614 | 13.4951 | 0.31128 | 6.7089
North East England | West Burton 400kV | WBUR4/WBUR4 R3/4 | 400 | 0.63848 | 13.1213 | 0.32475 | 6.6739
North East England | Wincobank 275kV | WIBA2/WIBA2 MC1 | 275 | 0.63311 | 7.7081 | 0.33734 | 4.1071
North East England | Wilton 275kV | WILT2/WILT2A | 275 | 0 | 0 | 0.22088 | 4.6374
North East England | Wilton 275kV | WILT2/WILT2B | 275 | 0 | 0 | 0.22088 | 4.6374
North East England | Wilton 275kV | WILT2/WILT2C | 275 | 0 | 0 | 0.21915 | 4.6272
North East England | Wilton 275kV | WILT2/WILT2D | 275 | 0 | 0 | 0.21916 | 4.6271
North East England | West Melton 275kV | WMEL2/WMEL2 MC1 | 275 | 0.40941 | 6.0924 | 0.21162 | 3.1491
North East England | York North 275kV | OVER2/YORK2 M1 | 275 | 0.19606 | 3.7302 | 0.14614 | 2.7804
South Wales and West England | Abham 400kV | ABHA4/ABHA4A | 400 |  |  |  |  | 0.43358 | 5.6695 | 0.48198 | 6.3024
South Wales and West England | Abham 400kV | ABHA4/ABHA4B | 400 |  |  |  |  | 0.43393 | 5.6723 | 0.48237 | 6.3055
South Wales and West England | Aberthaw 275kV | ABTH2/ABTH2 M1 | 275 |  |  |  |  | 0.16767 | 2.4089 | 0.22554 | 3.2404
South Wales and West England | Alverdiscott 400kV GIS | ALVE4A/ALVE4 M4 | 400 |  |  |  |  | 0.39405 | 5.1234 | 0.41192 | 5.3558
South Wales and West England | Axminster 400kV | AXMI4/AXMI4 MC1 | 400 |  |  |  |  | 0.41265 | 6.1056 | 0.50726 | 7.5055
South Wales and West England | Baglan Bay 275kV | BAGB2/BAGB2 R1 | 275 |  |  |  |  | 0.22005 | 3.0429 | 0.3027 | 4.1858
South Wales and West England | Bramley 400kV | BRLE4/BRLE4 M1 | 400 |  |  |  |  | 0.36493 | 6.6512
South Wales and West England | Bridgwater 400kV | BRWA4A | 400 |  |  |  |  | 0.6285 | 6.3032 | 0.51253 | 5.1401
South Wales and West England | Bridgwater 400kV | BRWAB | 400 |  |  |  |  | 0.63066 | 6.3267 | 0.51147 | 5.131
South Wales and West England | Cardiff East 275kV | CARE2/CARE2 MC1 | 275 |  |  |  |  | 0.20216 | 2.5636 | 0.27455 | 3.4815
South Wales and West England | Chickerell 400kV | CHIC4/CHIC4 MB2 | 400 |  |  |  |  | 0.44148 | 6.6275 | 0.58119 | 8.7248
South Wales and West England | Chickerell 400kV | CHIC4/CHIC4 R1/2 | 400 |  |  |  |  | 0.4531 | 6.8014 | 0.59515 | 8.9338
South Wales and West England | Cilfynydd 400kV | CILF4/CILF4 M2 | 400 |  |  |  |  | 0.29068 | 4.4732 | 0.38405 | 5.9102
South Wales and West England | Cowley 400kV | COWL4/COWL4 M1 | 400 |  |  |  |  | 0.40819 | 7.6393
South Wales and West England | Didcot 400kV | DIDC4/DIDC4 R1/2 | 400 |  |  |  |  | 0.405 | 7.4491
South Wales and West England | Exeter Main 400kV | EXET4/EXET4 R1 | 400 |  |  |  |  | 0.34089 | 4.9225 | 0.38761 | 5.5971
South Wales and West England | Feckenham 400kV | FECK4/FECK4 R2 | 400 |  |  |  |  | 0.68517 | 10.8579
South Wales and West England | Fleet 400kV | FLEE4/FLEE4 MC1 | 400 |  |  |  |  | 0.3819 | 6.8837
South Wales and West England | Hinkley Point 275kV | HINP2/HINP2 R1 | 275 |  |  |  |  | 0.12586 | 3.4152 | 0.11432 | 3.1018
South Wales and West England | Hinkley Point 400kV | HINP4/HINP4 R3/4 | 400 |  |  |  |  | 0.24391 | 3.6229 | 0.22136 | 3.2878
South Wales and West England | Imperial Park 400kV | IMPP4/IMPP4 MC2 | 400 |  |  |  |  | 0.27296 | 4.1577 | 0.43264 | 6.59
South Wales and West England | Indian Queens 400kV | INDQ4/INDQ4 MC2 | 400 |  |  |  |  | 0.46474 | 5.6062 | 0.50163 | 6.0512
South Wales and West England | Iron Acton 275kV | IROA2/IROA2 MC3 | 275 |  |  |  |  | 0.12113 | 1.7561 | 0.21744 | 3.1522
South Wales and West England | Langage 400kV | LAGA4/LAGA4 M2 | 400 |  |  |  |  | 0.42727 | 5.5118 | 0.47152 | 6.0826
South Wales and West England | Landulph 400kV | LAND4/LAND4 MC2 | 400 |  |  |  |  | 0.47802 | 5.9175 | 0.52307 | 6.4751
South Wales and West England | Landulph 400kV | LAND4/LAND4 MC3 | 400 |  |  |  |  | 0.46698 | 5.7733 | 0.51182 | 6.3276
South Wales and West England | Margam 275kV | MAGA2/MAGA2 MC1 | 275 |  |  |  |  | 0.21963 | 2.8684 | 0.3016 | 3.9388
South Wales and West England | Melksham 400kV | MELK4/MELK4 M1 | 400 |  |  |  |  | 0.14273 | 2.2505 | 0.40005 | 6.3079
South Wales and West England | Minety 400kV | MITY4/MITY4 MC3 | 400 |  |  |  |  | 0 | 0 | 0.56431 | 8.6085
South Wales and West England | New Woolavington 400kV | ----- | 400 |  |  |  |  | 0.63066 | 6.3267 | 0.51147 | 5.131
South Wales and West England | Pembroke 400kV | PEMB4/PEMB4 M2 | 400 |  |  |  |  | 0.41046 | 6.0123 | 0.57527 | 8.4266
South Wales and West England | Pont Abraham 400kV | POAB4/POAB4 R1 | 400 |  |  |  |  | 0.39513 | 5.8811 | 0.55926 | 8.324
South Wales and West England | Pyle 275kV | PYLE2/PYLE2 MC1 | 275 |  |  |  |  | 0.21386 | 2.7375 | 0.29262 | 3.7455
South Wales and West England | Rassau 400kV | RASS4/RASS4 M2 | 400 |  |  |  |  | 0.36796 | 5.5879 | 0.52648 | 7.9951
South Wales and West England | Rhigos 400KV | RHIG4/RHIG4 M2 | 400 |  |  |  |  | 0.33938 | 5.1067 | 0.46438 | 6.9876
South Wales and West England | Sandford 400kV | SAFO4/SAFO4 M2 | 400 |  |  |  |  | 0.25227 | 3.7235 | 0.10842 | 1.6002
South Wales and West England | Seabank 400kV | SEAB4/SEAB4 M2 | 400 |  |  |  |  | 0.22447 | 3.4441 | 0 | 0
South Wales and West England | Shurton 400kV | SHUR4/SHUR4 M1 | 400 |  |  |  |  | 0.24606 | 3.6555 | 0.22597 | 3.357
South Wales and West England | Swansea North 275kV | SWAN2/SWAN2 MC3 | 275 |  |  |  |  | 0.19208 | 4.0368 | 0.2615 | 5.4957
South Wales and West England | Swansea North 400kV | SWAN4/SWAN4 M1 | 400 |  |  |  |  | 0.39648 | 5.8496 | 0.53778 | 7.9344
South Wales and West England | Swansea North 400kV | SWAN4/SWAN4 R3 | 400 |  |  |  |  | 0.37876 | 5.6923 | 0.53164 | 7.9901
South Wales and West England | Taunton 400kV | TAUN4/TAUN4 M1 | 400 |  |  |  |  | 0.31336 | 4.3974 | 0.31923 | 4.4797
South Wales and West England | Taunton 400kV | TAUN4/TAUN4 M2 | 400 |  |  |  |  | 0.30944 | 4.3371 | 0.3182 | 4.4599
South Wales and West England | Tremorfa 275kV | TREM2/TREM2 MC1 | 275 |  |  |  |  | 0.19446 | 2.4241 | 0.26625 | 3.3191
South Wales and West England | Culham Jet 400kV | CULJ4/Term406 | 400 |  |  |  |  | 0.4134 | 7.5735 | 0.74203 | 13.594
South Wales and West England | Upper Boat 275kV | UPPB2/UPPB2 MC3 | 275 |  |  |  |  | 0.17899 | 2.6757 | 0.23809 | 3.5592
South Wales and West England | Upper Boat 275kV | UPPB2/UPPB2 MC4 | 275 |  |  |  |  | 0.17666 | 2.6465 | 0.2372 | 3.5535
South Wales and West England | Uskmouth 275kV | USKM2/USKM2 M1 | 275 |  |  |  |  | 0.13974 | 2.0708 | 0.19101 | 2.8306
South Wales and West England | Walham 400kV | WALH4/WALH4 MC2 | 400 |  |  |  |  | 0.49808 | 7.6161 | 0.8184 | 12.5142
South Wales and West England | Whitson 275kV | WHSO2/WHSO2 M2 | 275 |  |  |  |  | 0.14822 | 2.101 | 0.20641 | 2.9259
South Wales and West England | Whitson 275kV | WHSO2/WHSO2 R1 | 275 |  |  |  |  | 0.13379 | 2.0567 | 0.1784 | 2.7423
South West | Abham 400kV | ABHA4/ABHA4A | 400 | [8 empty] | 0.047234 | 0.61763 | 0.69136 | 9.0403
South West | Abham 400kV | ABHA4/ABHA4B | 400 | [8 empty] | 0.047272 | 0.61794 | 0.68763 | 8.9887
South West | Alverdiscott 400kV GIS | ALVE4A/ALVE4 M4 | 400 | [8 empty] | 0.23554 | 3.0625 | 0.60672 | 7.8886
South West | Bridgwater 400kV | BRWA4A | 400 | [8 empty] | 0.8665 | 8.6901
South West | Bridgwater 400kV | BRWAB | 400 | [8 empty] | 0.86882 | 8.716
South West | Axminster 400kV | AXMI4/AXMI4 MC1 | 400 | [8 empty] | 0.16413 | 2.4285 | 1.2274 | 18.1602
South West | Chickerell 400kV | CHIC4/CHIC4 MB2 | 400 | [8 empty] | 0.32959 | 4.9478
South West | Chickerell 400kV | CHIC4/CHIC4 R1/2 | 400 | [8 empty] | 0.33935 | 5.094
South West | Exeter Main 400kV | EXET4/EXET4 R1 | 400 | [8 empty] | 0 | 0 | 0.91693 | 13.2405
South West | Hinkley Point 275kV | HINP2/HINP2 R1 | 275 | [8 empty] | 0.23509 | 6.379
South West | Hinkley Point 400kV | HINP4/HINP4 R3/4 | 400 | [8 empty] | 0.45729 | 6.7922
South West | Indian Queens 400kV | INDQ4/INDQ4 MC2 | 400 | [8 empty] | 0.15746 | 1.8995 | 0 | 0
South West | Langage 400kV | LAGA4/LAGA4 M2 | 400 | [8 empty] | 0.072459 | 0.93472 | 0.47901 | 6.1793
South West | Landulph 400kV | LAND4/LAND4 MC2 | 400 | [8 empty] | 0.10598 | 1.312 | 0.37217 | 4.6071
South West | Landulph 400kV | LAND4/LAND4 MC3 | 400 | [8 empty] | 0.099767 | 1.2334 | 0.36161 | 4.4706
South West | Mannington 400kV | MANN4/MANN4 R5 | 400 | [8 empty] | 0.52362 | 8.2601
South West | New Woolavington 400kV | ----- | 400 | [8 empty] | 0.86882 | 8.716
South West | Nursling 400kV | NURS4/NURS4A | 400 | [8 empty] | 0.70442 | 11.3476
South West | Sandford 400kV | SAFO4/SAFO4 M2 | 400 | [8 empty] | 0.62427 | 9.2143
South West | Seabank 400kV | SEAB4/SEAB4 M2 | 400 | [8 empty] | 0.70523 | 10.8204
South West | Shurton 400kV | SHUR4/SHUR4 M1 | 400 | [8 empty] | 0.45053 | 6.693
South West | Taunton 400kV | TAUN4/TAUN4 M1 | 400 | [8 empty] | 0.26176 | 3.6733 | 1.1057 | 15.517
South West | Taunton 400kV | TAUN4/TAUN4 M2 | 400 | [8 empty] | 0.25812 | 3.6179 | 1.0922 | 15.3087
South Coast | Canterbury 400kV | CANT4/CANT4 MC1 | 400 | [12 empty] | 0.21918 | 3.8345
South Coast | Cleve Hill 400kV | CLEH4/CLEH4 M1 | 400 | [12 empty] | 0.33439 | 5.9542
South Coast | Dungeness 275kV | DUNG2/DUNG2 R2 | 275 | [12 empty] | 0.18678 | 4.1111
South Coast | Dungeness 400kV | DUNG4/DUNG4 M1 | 400 | [12 empty] | 0.41522 | 6.7303
South Coast | Kemsley 400kV | KEMS4/KEMS4 R2 | 400 | [12 empty] | 0.53419 | 10.1308
South Coast | Little Horsted 400kV | LHOR4/LHOR4A | 400 | [12 empty] | 0.69664 | 11.1922
South Coast | Ninfield 400kV | NINF4/NINF4 R1 | 400 | [12 empty] | 0.5755 | 9.3278
South Coast | Richborough 400kV | RICH4/RICH4 M1 | 400 | [12 empty] | 0 | 0
South Coast | Sellindge 400kV Compound A | SELL4A/SELL4A R1 | 400 | [12 empty] | 0.30983 | 5.149
South Coast | Sellindge 400kV Compound B | SELL4B/SELL4B R4 | 400 | [12 empty] | 0.31008 | 5.1507
South West Scotland | Blackhill 132kV | SPTL\BLAH1- | 132 | [14 empty] | 0.18455 | 2.6741
South West Scotland | Breezy Hill 132kV | SPTL\BREE1- | 132 | [14 empty] | 0.78591 | 6.3957
South West Scotland | Glenglass 132kV | SPTL\GLGL1A | 132 | [14 empty] | 0 | 0
South West Scotland | New Cumnock 132kV | SPTL\NECU1- | 132 | [14 empty] | 0.22138 | 5.2256
East Scotland | Abernethy 132kV | ABNE1Q | 132 | [16 empty] | 0.89303 | 2.5246
East Scotland | Amulree 132kV | AMUL1G | 132 | [16 empty] | 2.2972 | 6.1862
East Scotland | Arbroath 132kV | ARBR1Q | 132 | [16 empty] | 0.13295 | 0.51583
East Scotland | Birkhill 132kV | BIHI1R | 132 | [16 empty] | 0.038432 | 0.29266
East Scotland | Brechin 132kV | BREC1R | 132 | [16 empty] | 1.206 | 3.2322
East Scotland | Bridge of Dun 132kV | BRID1R | 132 | [16 empty] | 1.4835 | 3.6968
East Scotland | Burghmuir 132kV | BUMU1R | 132 | [16 empty] | 1.7792 | 4.617
East Scotland | Charlestown 132kV | CHAR1T | 132 | [16 empty] | 0.041282 | 0.3038
East Scotland | Clunie 132kV | CLUN1T | 132 | [16 empty] | 1.4361 | 6.4066
East Scotland | Coupar Angus 132kV | COUA1Q | 132 | [16 empty] | 0.29347 | 1.6252
East Scotland | Denside 132kV | DENS1R | 132 | [16 empty] | 0.0013315 | 0.0091036
East Scotland | Dudhope 132kV | DUDH1R | 132 | [16 empty] | 0.037996 | 0.24363
East Scotland | Fasqope 132kV | FASQ1- | 132 | [16 empty] | 1.2478 | 3.389
East Scotland | Fasque 132kV | FASQ1J | 132 | [16 empty] | 1.7313 | 5.0122
East Scotland | Fiddes 132kV | FIDD1B | 132 | [16 empty] | 2.805 | 8.025
East Scotland | Glenagnes 132kV | GLAG1R | 132 | [16 empty] | 0.039673 | 0.25732
East Scotland | Lunanhead 132kV | LUNA1R | 132 | [16 empty] | 0.0041875 | 0.024329
East Scotland | Lyndhurst 132kV | LYND1R | 132 | [16 empty] | 0.060378 | 0.3363
East Scotland | Milton of Craigie 132kV | MILC1V | 132 | [16 empty] | 0.023955 | 0.17549
East Scotland | Tealing 132kV | TEAL1- | 132 | [16 empty] | 0 | 0
North East Scotland | Blackhillock 132kV | BLHI1K | 132 | [18 empty] | 0.16083 | 2.358
North East Scotland | Blackhillock 275kV | BLHI2J | 275 | [18 empty] | 0.54443 | 5.1236
North East Scotland | Blackhillock 400kV | BLHI4- | 400 | [18 empty] | 0.76403 | 7.5807
North East Scotland | Cainford 275kV | CAIN2- | 275 | [18 empty] | 0.61799 | 5.5113
North East Scotland | Clayhill 132kV | CLAY1Q | 132 | [18 empty] | 0.33562 | 2.6235
North East Scotland | Craigiebuckler 132kV | CRAI1R | 132 | [18 empty] | 0.30978 | 2.5662
North East Scotland | Dyce 132kV | DYCE1U | 132 | [18 empty] | 0.61015 | 3.8116
North East Scotland | Elchies 132kV | ELCH1- | 132 | [18 empty] | 0.95517 | 5.602
North East Scotland | Fetteresso 132kV | FETT1- | 132 | [18 empty] | 0.19603 | 3.1634
North East Scotland | Fetteresso 400kV | FETT4R | 400 | [18 empty] | 1.3161 | 12.3936
North East Scotland | Fiddes 132kV | FIDD1R | 132 | [18 empty] | 2.5913 | 7.945
North East Scotland | Foggieton 132kV | FOGG1Q | 132 | [18 empty] | 0.49268 | 2.8713
North East Scotland | Fraserburgh 132kV | FRAS1Q | 132 | [18 empty] | 0.44008 | 2.2365
North East Scotland | Glendye 132kV | GLDY1- | 132 | [18 empty] | 0.97289 | 6.6497
North East Scotland | Inverugie 132kV | INRU1S | 132 | [18 empty] | 0.093226 | 1.1887
North East Scotland | Keith 132kV | KEIT1K | 132 | [18 empty] | 0.18683 | 2.5209
North East Scotland | Keith 275kV | KEIT2Q | 275 | [18 empty] | 0.56966 | 5.2232
North East Scotland | Kinmuck 275kV | KINM2B | 275 | [18 empty] | 0.37923 | 3.3987
North East Scotland | Kintore 132kV | KINT1U | 132 | [18 empty] | 0.24024 | 2.3887
North East Scotland | Kintore 275kV | KINT2J | 275 | [18 empty] | 0.46044 | 4.3074
North East Scotland | Kintore 400kV | KINT4K | 400 | [18 empty] | 0.86761 | 8.2744
North East Scotland | Lumbs 132kV | LUMB1Q | 132 | [18 empty] | 0.26904 | 1.7229
North East Scotland | Macduff 132kV | MACD1R | 132 | [18 empty] | 1.9712 | 7.5913
North East Scotland | New Deer 400kV | NEDE4K | 400 | [18 empty] | 0.38713 | 3.6688
North East Scotland | Peterhead 132kV | PEHE1- | 132 | [18 empty] | 0.07936 | 1.1392
North East Scotland | Peterhead 275kV | PEHE2V | 275 | [18 empty] | 0.19795 | 1.7922
North East Scotland | Peterhead 400kV | PEHE4J | 400 | [18 empty] | 0 | 0
North East Scotland | Peterhead Grange 132kV | PEHG1R | 132 | [18 empty] | 0.1505 | 1.4671
North East Scotland | Persley 132kV | PERS1R | 132 | [18 empty] | 0.29227 | 2.5082
North East Scotland | Persley 275kV | PERS2R | 275 | [18 empty] | 0.50982 | 4.5889
North East Scotland | Redmoss 132kV | REDM1R | 132 | [18 empty] | 0.395 | 2.7358
North East Scotland | Rothienorman 400kV | ROTI4K | 400 | [18 empty] | 0.61328 | 5.8428
North East Scotland | St Fergus 132kV | SFER1M | 132 | [18 empty] | 0.13292 | 1.3833
North East Scotland | Strichen 132kV | STRI1Q | 132 | [18 empty] | 0.40258 | 2.1127
North East Scotland | Tarland 132kV | TARL1Q | 132 | [18 empty] | 2.0092 | 7.7835
North East Scotland | Willowdale 132kV | WOHI1R | 132 | [18 empty] | 0.32738 | 2.5778
North Scotland | Brora 132kV | BROR1- | 132 | [20 empty] | 3.4658 | 10.6885
North Scotland | Connagill 132kV | CONN1C | 132 | [20 empty] | 0.18247 | 3.0694 | 0.3775 | 6.35
North Scotland | Connagill 275kV | CONN2K | 275 | [20 empty] | 0.61472 | 7.0269 | 1.2642 | 14.4514
North Scotland | Dounreay 132kV | DOUN1- | 132 | [20 empty] | 0.15346 | 3.0852 | 0.35076 | 7.0517
North Scotland | Dounreay 275kV | DOUN2- | 275 | [20 empty] | 0.40922 | 5.0383 | 0.92927 | 11.4412
North Scotland | Boulfruich 132kV | DUBE1Q | 132 | [20 empty] | 1.5212 | 5.0686 | 3.0626 | 10.2047
North Scotland | Gills Bay 132kV | GILB1M | 132 | [20 empty] | 0.12008 | 1.5348 | 0.38127 | 4.873
North Scotland | Gordonbush 275kV | GORW2- | 275 | [20 empty] | 1.9119 | 19.1499
North Scotland | Limekilns 132kV | LIMK1A | 132 | [20 empty] | 0.15885 | 3.1104 | 0.36307 | 7.1093
North Scotland | Meygen 132kV | MEYG1- | 132 | [20 empty] | 0.12379 | 1.5547 | 0.39132 | 4.9145
North Scotland | Mybster 132kV | MYBS1R | 132 | [20 empty] | 0.33996 | 2.1982 | 0.86785 | 5.6115
North Scotland | Mybster 132kV | MYBS1S | 132 | [20 empty] | 0.002394 | 0.039723 | 0.21277 | 3.5304
North Scotland | Spittal 132kV | SPIT1M | 132 | [20 empty] | 0.0020281 | 0.03673 | 0.18024 | 3.2644
North Scotland | Spittal 275kV | SPIT2J | 275 | [20 empty] | 0 | 0 | 0.53959 | 5.8843
North Scotland | Spittal 400kV | SPIT4J | 400 | [20 empty] | 0.0045777 | 0.059016 | 0 | 0
North Scotland | Strathy North 132kV | STNO1C | 132 | [20 empty] | 0.59965 | 4.4734 | 1.2377 | 9.2333
North Scotland | Strathy South 132kV | STSO1A | 132 | [20 empty] | 0.77678 | 5.0879
North Scotland | Strathy Wood 132kV | STWO1- | 132 | [20 empty] | 0.91373 | 5.0813 | 1.8838 | 10.476
North Scotland | Thurso South 132kV | THUS1M | 132 | [20 empty] | 0.06998 | 1.0953 | 0.23404 | 3.6631
North Scotland | Thurso South 275kV | THUS2K | 275 | [20 empty] | 0.20284 | 2.3195 | 0.76268 | 8.7212

## Effectiveness Factors
|  |  |  | England and Wales | [6 empty] | Scotland
Effectiveness to
|  |  |  | North East England Region |  | South Wales and West England |  | South West England |  | South East England | South West Scotland | East Scotland | North East Scotland | North Scotland
Region | Busbar | Substation/Nodes | Voltage Level (kV) | Lackenby 400kV | Creyke Beck 400kV | Minety 400kV | Seabank 400kV | Exeter Main 400kV | Indian Queens 400kV | Richborough 400kV | Glenglas 132kV | Tealing 132kV | Peterhead 400kV | Spittal 275kV | Spittal 400kV
North East England | ALDW2 MC1 | Aldwarke 275kV | 275 | 71.8092 | 78.1697
North East England | BLYT2 M1 | Blyth 275kV | 275 | 81.0534 | 77.3778
North East England | BLYT4 M1 | Blyth 400kV | 400 | 79.9537 | 76.5505
North East England | BRAW2 MC1 | Bradford West 275kV | 275 | 75.0349 | 80.4175
North East England | BRIN2 R1/M1 | Brinsworth 275kV | 275 | 72.4324 | 78.4782
North East England | BRIN2 R2/M2 | Brinsworth 275kV | 275 | 70.5759 | 77.3764
North East England | BRIN4_R2 | Brinsworth 400kV | 400 | 71.5346 | 78.3959
North East England | CHTE4_M1 | Chesterfield 400kV | 400 | 70.9608 | 77.851
North East England | COTT4 M1/2 | Cottam 400kV | 400 | 53.2238 | 59.9698
North East England | COTT4 R1/2/3/4 and M3/4 | Cottam 400kV | 400 | 52.8815 | 63.7075
North East England | CREB4 MB1 | Creyke Beck 400kV | 400 | 74.6153 | 100
North East England | M2 | Creyke Beck B 400kV | 400 | 77.5829 | 92.5775
North East England | DRAX4 M1/2/3 and RB1/2/3 | Drax 400kV | 400 | 72.9926 | 78.3788
North East England | DRAX4 M4/5/6 and RB4/5/6 | Drax 400kV | 400 | 76.7143 | 84.8463
North East England | EGGB4 M1/M2 | Eggborough 400kV | 400 | 73.5034 | 78.8283
North East England | EGGB4 R1/R2 | Eggborough 400kV | 400 | 76.1868 | 83.7479
North East England | ELLA2 MC4 | Elland 275kV | 275 | 74.5766 | 79.937
North East England | FERR2 M1/2 | Ferrybridge 275kV | 275 | 74.5941 | 80.0248
North East England | FERR2 R1/R2 | Ferrybridge 275kV | 275 | 75.574 | 81.5209
North East England | FOUR2 MC1 | Fourstones 275kV | 275 | 76.6753 | 75.7355
North East England | GRST2A M1 | Greystones A 275kV | 275 | 99.1078 | 85.8985
North East England | GRST2B M3 | Greystones B 275kV | 275 | 99.1187 | 85.9089
North East England | GRIW4 MC1 | Grimsby West 400kV | 400 | 61.8543 | 76.5771
North East England | HARKG R6 | Harker 400kV GIS | 400 | 73.7315 | 77.2369
North East England | HATL2 M1 | Hartlepool 275kV | 275 | 89.4041 | 82.8404
North East England | HARM2 MC3 | Hartmoor 275kV | 275 | 88.0164 | 82.0021
North East England | HAWP2 MC1 | Hawthorn Pit 275kV | 275 | 86.9034 | 81.5383
North East England | HEDO2 R1 | Hedon 275kV | 275 | 75.0833 | 95.4125
North East England | HIGM2 R5 | High Marnham 275kV | 275 | 66.3395 | 73.8225
North East England | HIGM4 MC1 | High Marnham 400kV | 400 | 58.0418 | 66.6954
North East England | HUMR4 M1 | Humber Refinery 400kV | 400 | 60.402 | 74.2064
North East England | JORD2 MC1 | Jordanthorpe 275kV | 275 | 72.5081 | 78.529
North East England | KEAD4 R3 | Keadby 400kV | 400 | 65.4595 | 71.6666
North East England | KEAD4 M3 | Keadby 400kV | 400 | 63.9707 | 76.9385
North East England | KEAD4 M2 R2 | Keadby 400kV | 400 | 62.1857 | 77.8057
North East England | KILL4 M1 | Killingholme 400kV | 400 | 61.3111 | 75.4402
North East England | KIRK2 MC3 | Kirkstall 275kV | 275 | 74.9368 | 80.3186
North East England | KNAR2 MC2 | Knaresborough | 275 | 78.7254 | 83.8036
North East England | LACK4 M1 | Lackenby 400kV | 400 | 100 | 86.6895
North East England | LACK2 M1 | Lackenby 400kV | 275 | 93.7473 | 84.5604
North East England | MONFN4 M4 | Monk Fryston 400kV | 400 | 74.2658 | 79.5399
North East England | Monk Fryston R1/R2 | Monk Fryston 275kV | 275 | 74.2432 | 79.5958
North East England | Monk Fryston M1/M2 | Monk Fryston 275kV | 275 | 75.6629 | 81.6903
North East England | NEEP2 M2 | Neepsend 275kV | 275 | 72.4748 | 78.4439
North East England | NORT2 M1 | Norton 275kV | 275 | 89.5917 | 83.4518
North East England | NORT4 M1 | Norton 275kV | 400 | 88.8975 | 83.4897
North East England | OFFE2 MC1 | Offerton 275kV | 275 | 85.7859 | 80.7415
North East England | OSBA4 MC1 | Osbaldwick 400kV | 400 | 78.8133 | 82.0021
North East England | OSBA4 MC3/4 | Osbaldwick 400kV | 400 | 82.1965 | 89.2396
North East England | PITS2 MC2 | Pitsmoor 275kV | 275 | 72.4898 | 78.4999
North East England | POPP2 MC1 | Poppleton 275kV | 275 | 80.5683 | 84.9817
North East England | SAEN2 MC2 | Saltend North 275kV | 275 | 75.0715 | 95.2608
North East England | SAES2 M | Saltend South 275kV | 275 | 75.0768 | 95.3286
North East England | SALH2 MC1 | Salthome 275kV | 275 | 89.3399 | 83.0633
North East England | SHEC2 MC1 | Sheffield City 275kV | 275 | 72.482 | 78.4603
North East England | SKLG2 MC4 | Skelton Grange 275kV | 275 | 74.9302 | 80.443
North East England | SHBA4 M1 | South Humber Bank 400kV | 400 | 61.64 | 76.1163
North East England | SSHI2 MC1 | South Shields 275kV | 275 | 84.2501 | 79.6499
North East England | SPEN4 MC1/2 | Spennymoor 400kV | 400 | 85.7661 | 81.0838
North East England | SPEN4 MC3/4 | Spennymoor 400kV | 400 | 85.5662 | 80.8951
North East England | STEW4 M1 | Stella West 400kV | 400 | 79.7939 | 76.4753
North East England | STEW2 M1 | Stella West 275kV | 275 | 77.5509 | 74.9972
North East England | STSB4 MC1 | Stocksbridge 400kV | 400 | 71.9722 | 77.2719
North East England | TEMP2 MC3 | Templeborough 275kV | 275 | 72.468 | 78.4997
North East England | TEMP2 MC1/2 | Templeborough 275kV | 275 | 72.4672 | 78.4995
North East England | Thornton M1/M4 400kV | Thornton 400kV | 400 | 79.5005 | 89.7367
North East England | Thornton M2/M3 400kV | Thornton 400kV | 400 | 81.4993 | 90.8845
North East England | Thornton RB1/RB2 400kV | Thornton 400kV | 400 | 76.4142 | 80.4129
North East England | THOM2 M1 | Thorpe Marsh 275kV | 275 | 73.599 | 80.6563
North East England | THOM4 MC1/2/3/4 | Thorpe Marsh 400kV | 400 | 74.9191 | 82.3541
North East England | THOM4 R5/6 M5/M6 | Thorpe Marsh 400kV | 400 | 70.0088 | 76.1777
North East England | THUR2 MC2 | Thurcroft 275kV | 275 | 70.3813 | 77.1641
North East England | TINP2 M1 | Tinsley Park 275kV | 275 | 70.5914 | 77.3545
North East England | TINP2 M2 | Tinsley Park 275kV | 275 | 70.5562 | 77.3927
North East England | TODP2 MC1 | Tod Point 275kV | 275 | 92.687 | 84.1297
North East England | TYNE2 MC1 | Tynemouth MC1 275kV | 275 | 83.2067 | 78.8844
North East England | WBOL2 MC2 | West Boldon MC2 | 275 | 84.8099 | 80.0472
North East England | WBUR4 M1 | West Burton 400kV | 400 | 58.5833 | 68.2425
North East England | WBUR4 R3/4 | West Burton 400kV | 400 | 55.2459 | 61.9443
North East England | WMEL2 MC1 | West Melton 275kV | 275 | 71.4006 | 77.9365
North East England | WILT2A | Wilton 275kV | 275 | 99.1206 | 85.9105
North East England | WIBA2 MC1 | Wincobank 275kV | 275 | 72.4872 | 78.5061
North East England | YORK2 M1 | York North 275kV | 275 | 80.5611 | 84.9806
South Wales and West England | ABTH2 M1 | Aberthaw 275kV | 275 |  |  | 66.2854 | 68.2807
South Wales and West England | ABHA4B | Abham 400kV | 400 |  |  | 59.1695 | 65.2841 | 95.5661 | 73.3429
South Wales and West England | ABHA4A | Abham 400kV | 400 |  |  | 59.1755 | 65.2899 | 95.5832 | 73.3182
South Wales and West England | ALVE4 M4 | Alverdiscott 400kV GIS | 400 |  |  | 62.305 | 69.6511 | 85.8606 | 76.7646
South Wales and West England | AXMI4 MC1 | Axminster 400kV | 400 |  |  | 56.2942 | 60.0241 | 88.6799 | 53.1731
South Wales and West England | BAGB2 R1 | Baglan Bay 275kV | 275 |  |  | 66.1627 | 67.5534
South Wales and West England | BRLE4 M1 | Bramley 400kV | 400 |  |  | 53.6795
South Wales and West England | BRWA4A | Bridgwater 400kV | 400 |  |  | 69.2 | 75 | 66.7
South Wales and West England | BRWA4B | Bridgwater 400kV | 400 |  |  | 69.2 | 75 | 66.7
South Wales and West England | CARE2 MC1 | Cardiff East 275kV | 275 |  |  | 68.2865 | 70.3674
South Wales and West England | CHIC4 MB2 | Chickerell 400kV | 400 |  |  | 52.3288 | 53.8958 | 76.7121
South Wales and West England | CHIC4 R1/2 | Chickerell 400kV | 400 |  |  | 53.0153 | 54.6202 | 77.8024
South Wales and West England | CILF4 M2 | Cilfynydd 400kV | 400 |  |  | 67.3331 | 69.6948
South Wales and West England | COWL4 M1 | Cowley 400kV | 400 |  |  | 53.3507
South Wales and West England | Term406 | Culham Jet 400kV | 400 |  |  | 53.3835
South Wales and West England | DIDC4 R1/2 | Didcot 400kV | 400 |  |  | 53.4059
South Wales and West England | EXET4 R1 | Exeter Main 400kV | 400 |  |  | 60.0354 | 65.8611
South Wales and West England | FECK4 R2 | Feckenham 400kV | 400 |  |  | 59.6824
South Wales and West England | FLEE4 MC1 | Fleet 400kV | 400 |  |  | 50.8315
South Wales and West England | HINP2 R1 | Hinkley Point 275kV | 275 |  |  | 69.8942 | 79.7554 | 71.6413
South Wales and West England | HINP4 R3/4 | Hinkley Point 400kV | 400 |  |  | 69.8701 | 79.6579 | 71.5641
South Wales and West England | IMPP4 MC2 | Imperial Park 400kV | 400 |  |  | 70.9264 | 68.6419
South Wales and West England | INDQ4 MC2 | Indian Queens 400kV | 400 |  |  | 59.1128 | 65.7779 | 88.6006 | 100
South Wales and West England | IROA2 MC3 | Iron Acton 275kV | 275 |  |  | 71.8661 | 67.3742
South Wales and West England | LAND4 MC1/MC2 | Landulph 400kV | 400 |  |  | 58.6126 | 64.9564 | 91.5801 | 85.2791
South Wales and West England | LAND4 MC3/MC4 | Landulph 400kV | 400 |  |  | 58.5007 | 64.8239 | 91.3642 | 85.1046
South Wales and West England | LAGA4 M2 | Langage 400kV | 400 |  |  | 58.8507 | 65.088 | 93.3469 | 79.9161
South Wales and West England | MAGA2 MC1 | Margam 275kV | 275 |  |  | 66.4088 | 68.0303
South Wales and West England | MELK4 M1 | Melksham 400kV | 400 |  |  | 81.3063 | 66.7644
South Wales and West England | MITY4 MC3 | Minety 400kV | 400 |  |  | 100 | 60.6017
South Wales and West England | ----- | New Woolavington 400kV | 400 |  |  | 69.2 | 75 | 66.7
South Wales and West England | PEMB4 M2 | Pembroke 400kV | 400 |  |  | 63.359 | 64.153
South Wales and West England | POAB4 R1 | Pont Abraham 400kV | 400 |  |  | 64.6762 | 65.0276
South Wales and West England | PYLE2 MC1 | Pyle 275kV | 275 |  |  | 66.4785 | 68.2125
South Wales and West England | RASS4 M2 | Rassau 400kV | 400 |  |  | 64.796 | 64.6165
South Wales and West England | RHIG4 M2 | Rhigos 400KV | 400 |  |  | 66.4087 | 67.9135
South Wales and West England | SAFO4 M2 | Sandford 400kV | 400 |  |  | 71.0063 | 90.0687
South Wales and West England | SEAB4 M2 | Seabank 400kV | 400 |  |  | 72.4305 | 100
South Wales and West England | SHUR4 M1 | Shurton 400kV | 400 |  |  | 69.8157 | 79.2116 | 71.8219
South Wales and West England | SWAN2 MC3 | Swansea North 275kV | 275 |  |  | 65.6734 | 67.2429
South Wales and West England | SWAN4 M3/M4 R3/4 | Swansea North 400kV | 400 |  |  | 64.5482 | 64.8804
South Wales and West England | SWAN4 M1/M2 | Swansea North 400kV | 400 |  |  | 65.7936 | 67.4782
South Wales and West England | TAUN4 M1 | Taunton 400kV | 400 |  |  | 65.2403 | 73.0626 | 83.8484 | 57.5626
South Wales and West England | TAUN4 M2 | Taunton 400kV | 400 |  |  | 64.9592 | 72.738 | 83.4615 | 57.2899
South Wales and West England | TREM2 MC1 | Tremorfa 275kV | 275 |  |  | 68.4118 | 70.4559
South Wales and West England | UPPB2 MC2/3 | Upperboat 275kV | 275 |  |  | 65.9632 | 68.1068
South Wales and West England | UPPB2 MC1/4 | Upperboat 275kV | 275 |  |  | 65.738 | 67.8758
South Wales and West England | USKM2 M1 | Uskmouth 275kV | 275 |  |  | 69.1832 | 71.27
South Wales and West England | WALH4 MC2 | Walham 400kV | 400 |  |  | 59.3874 | 51.9571
South Wales and West England | WHSO2 M2 | Whitson 275kV | 275 |  |  | 69.3103 | 70.9381
South Wales and West England | WHSO2 R1 | Whitson 275kV | 275 |  |  | 69.3967 | 71.9339
South West England | ABHA4B | Abham 400kV | 400 |  |  | 59.1695 | 65.2841 | 95.5661 | 73.3429
South West England | ABHA4A | Abham 400kV | 400 |  |  | 59.1755 | 65.2899 | 95.5832 | 73.3182
South West England | ALVE4 M4 | Alverdiscott 400kV GIS | 400 |  |  | 62.305 | 69.6511 | 85.8606 | 76.7646
South West England | AXMI4 MC1 | Axminster 400kV | 400 |  |  | 56.2942 | 60.0241 | 88.6799 | 53.1731
South West England | BRWA4A | Bridgwater 400kV | 400 |  |  | 69.2 | 75 | 66.7
South West England | BRWA4B | Bridgwater 400kV | 400 |  |  | 69.2 | 75 | 66.7
South West England | CHIC4 MB2 | Chickerell 400kV | 400 |  |  | 52.3288 | 53.8958 | 76.7121
South West England | CHIC4 R1/2 | Chickerell 400kV | 400 |  |  | 53.0153 | 54.6202 | 77.8024
South West England | EXET4 R1 | Exeter Main 400kV | 400 |  |  |  |  | 100 | 60.2172
South West England | HINP2 R1 | Hinkley Point 275kV | 275 |  |  | 69.8942 | 79.7554 | 71.6413
South West England | HINP4 R3/4 | Hinkley Point 400kV | 400 |  |  | 69.8701 | 79.6579 | 71.5641
South West England | INDQ4 MC2 | Indian Queens 400kV | 400 |  |  | 59.1128 | 65.7779 | 88.6006 | 100
South West England | LAND4 MC1/MC2 | Landulph 400kV | 400 |  |  | 58.6126 | 64.9564 | 91.5801 | 85.2791
South West England | LAND4 MC3/MC4 | Landulph 400kV | 400 |  |  | 58.5007 | 64.8239 | 91.3642 | 85.1046
South West England | LAGA4 M2 | Langage 400kV | 400 |  |  | 58.8507 | 65.088 | 93.3469 | 79.9161
South West England | MANN4 R5 | Mannington 400kV | 400 |  |  |  |  | 61.0227
South West England | ----- | New Woolavington 400kV | 400 |  |  | 69.2 | 75 | 66.7
South West England | NURS4A | Nursling 400kV | 400 |  |  |  |  | 50.9941
South West England | SAFO4 M2 | Sandford 400kV | 400 |  |  |  |  | 65.1192
South West England | SEAB4 M2 | Seabank 400kV | 400 |  |  |  |  | 59.1925
South West England | SHUR4 M1 | Shurton 400kV | 400 |  |  | 69.8157 | 79.2116 | 71.8219
South West England | TAUN4 M1 | Taunton 400kV | 400 |  |  | 65.2403 | 73.0626 | 83.8484 | 57.5626
South West England | TAUN4 M2 | Taunton 400kV | 400 |  |  | 64.9592 | 72.738 | 83.4615 | 57.2899
South East England | CANT4 MC1 | Canterbury 400kV | 400 | [6 empty] | 78.8043
South East England | CLEH4 M1 | Cleve Hill 400kV | 400 | [6 empty] | 70.5149
South East England | DUNG2 R2 | Dungeness 275kV | 275 | [6 empty] | 65.3949
South East England | DUNG4 M1 | Dungeness 400kV | 400 | [6 empty] | 65.4188
South East England | KEMS4 R2 | Kemsley 400kV | 400 | [6 empty] | 52.8418
South East England | ----- | New Kemsley 400kV | 400 | [6 empty] | 52.8
South East England | LHOR4A | Little Horsted 400kV | 400 | [6 empty] | 50.3609
South East England | NINF4 R1 | Ninfield 400kV | 400 | [6 empty] | 55.5916
South East England | RICH4 M1 | Richborough 400kV | 400 | [6 empty] | 100
South East England | SELL4A R1 | Sellindge 400kV Compound A | 400 | [6 empty] | 71.5156
South East England | SELL4B R4 | Sellindge 400kV Compound B | 400 | [6 empty] | 71.5164
South West Scotland | SPTL\BLAH1- | Blackhill 132kV | 132 | [7 empty] | 80.016
South West Scotland | SPTL\BREE1- | Breezy Hill 132kV | 132 | [7 empty] | 61.7836
South West Scotland | SPTL\GLGL1A | Glenglass 132kV | 132 | [7 empty] | 100
South West Scotland | SPTL\NECU1- | New Cumnock 132kV | 132 | [7 empty] | 62.3786
East Scotland | ABNE1Q | Abernethy 132kV | 132 | [8 empty] | 81.1111
East Scotland | AMUL1G | Amulree 132kV | 132 | [8 empty] | 64.2446
East Scotland | ARBR1Q | Arbroath 132kV | 132 | [8 empty] | 95.1909
East Scotland | BIHI1R | Birkhill 132kV | 132 | [8 empty] | 95.624
East Scotland | BREC1R | Brechin 132kV | 132 | [8 empty] | 75.3419
East Scotland | BRID1R | Bridge of Dun 132kV | 132 | [8 empty] | 75.1951
East Scotland | BUMU1R | Burghmuir 132kV | 132 | [8 empty] | 72.6573
East Scotland | CHAR1T | Charlestown 132kV | 132 | [8 empty] | 95.4371
East Scotland | CLUN1T | Clunie 132kV | 132 | [8 empty] | 54.5674
East Scotland | COUA1Q | Coupar Angus 132kV | 132 | [8 empty] | 84.7598
East Scotland | DENS1R | Denside 132kV | 132 | [8 empty] | 99.7016
East Scotland | DUDH1R | Dudhope 132kV | 132 | [8 empty] | 96.4213
East Scotland | FASQ1- | Fasqope 132kV | 132 | [8 empty] | 75.203
East Scotland | FASQ1J | Fasque 132kV | 132 | [8 empty] | 73.8412
East Scotland | FIDD1B | Fiddes 132kV | 132 | [8 empty] | 53.1276
East Scotland | GLAG1R | Glenagnes 132kV | 132 | [8 empty] | 96.1869
East Scotland | LUNA1R | Lunanhead 132kV | 132 | [8 empty] | 100
East Scotland | LYND1R | Lyndhurst 132kV | 132 | [8 empty] | 95.3928
East Scotland | MILC1V | Milton of Craigie 132kV | 132 | [8 empty] | 97.3585
East Scotland | TEAL1- | Tealing 132kV | 132 | [8 empty] | 100
North East Scotland | BLHI1K | Blackhillock 132kV | 132 | [9 empty] | 55.9014
North East Scotland | BLHI2J | Blackhillock 275kV | 275 | [9 empty] | 59.5936
North East Scotland | BLHI4- | Blackhillock 400kV | 400 | [9 empty] | 66.8186
North East Scotland | CAIN2- | Cainford 275kV | 275 | [9 empty] | 61.1174
North East Scotland | CLAY1Q | Clayhill 132kV | 132 | [9 empty] | 70.5432
North East Scotland | CRAI1R | Craigiebuckler 132kV | 132 | [9 empty] | 70.2277
North East Scotland | DYCE1U | Dyce 132kV | 132 | [9 empty] | 69.5513
North East Scotland | ELCH1- | Elchies 132kV | 132 | [9 empty] | 52.9534
North East Scotland | FETT1- | Fetteresso 132kV | 132 | [9 empty] | 60.2711
North East Scotland | FETT4R | Fetteresso 400kV | 400 | [9 empty] | 61.2706
North East Scotland | FIDD1R | Fiddes 132kV | 132 | [9 empty] | 58.2522
North East Scotland | FOGG1Q | Foggieton 132kV | 132 | [9 empty] | 69.9086
North East Scotland | FRAS1Q | Fraserburgh 132kV | 132 | [9 empty] | 90.229
North East Scotland | GLDY1- | Glendye 132kV | 132 | [9 empty] | 56.5352
North East Scotland | INRU1S | Inverugie 132kV | 132 | [9 empty] | 90.4537
North East Scotland | KEIT1K | Keith 132kV | 132 | [9 empty] | 55.9138
North East Scotland | KEIT2Q | Keith 275kV | 275 | [9 empty] | 59.5291
North East Scotland | KINM2B | Kinmuck 275kV | 275 | [9 empty] | 82.331
North East Scotland | KINT1U | Kintore 132kV | 132 | [9 empty] | 69.7143
North East Scotland | KINT2J | Kintore 275kV | 275 | [9 empty] | 68.4704
North East Scotland | KINT4K | Kintore 400kV | 400 | [9 empty] | 69.2418
North East Scotland | LUMB1Q | Lumbs 132kV | 132 | [9 empty] | 90.4582
North East Scotland | MACD1R | Macduff 132kV | 132 | [9 empty] | 55.0245
North East Scotland | NEDE4K | New Deer 400kV | 400 | [9 empty] | 83.745
North East Scotland | PEHE1- | Peterhead 132kV | 132 | [9 empty] | 90.4397
North East Scotland | PEHE2V | Peterhead 275kV | 275 | [9 empty] | 89.1782
North East Scotland | PEHE4J | Peterhead 400kV | 400 | [9 empty] | 100
North East Scotland | PEHG1R | Peterhead Grange 132kV | 132 | [9 empty] | 90.3891
North East Scotland | PERS1R | Persley 132kV | 132 | [9 empty] | 70.7745
North East Scotland | PERS2R | Persley 275kV | 275 | [9 empty] | 75.3712
North East Scotland | REDM1R | Redmoss 132kV | 132 | [9 empty] | 70.4314
North East Scotland | ROTI4K | Rothienorman 400kV | 400 | [9 empty] | 75.3131
North East Scotland | SFER1M | St Fergus 132kV | 132 | [9 empty] | 90.6578
North East Scotland | STRI1Q | Strichen 132kV | 132 | [9 empty] | 90.2756
North East Scotland | TARL1Q | Tarland 132kV | 132 | [9 empty] | 68.2608
North East Scotland | WOHI1R | Willowdale 132kV | 132 | [9 empty] | 70.3976
North Scotland | BROR1- | Brora 132kV | 132 | [10 empty] | 50.2383
North Scotland | CONN1C | Connagill 132kV | 132 | [10 empty] | 67.5749 | 52.2062
North Scotland | CONN2K | Connagill 275kV | 275 | [10 empty] | 72.397 | 56.5752
North Scotland | DOUN1- | Dounreay 132kV | 132 | [10 empty] | 75.7473 | 59.021
North Scotland | DOUN2- | Dounreay 275kV | 275 | [10 empty] | 77.1078 | 60.4792
North Scotland | DUBE1Q | Boulfruich 132kV | 132 | [10 empty] | 73.72 | 57.7389
North Scotland | GILB1M | Gills Bay 132kV | 132 | [10 empty] | 88.4439 | 69.6897
North Scotland | GORW2- | Gordonbush 275kV | 275 | [10 empty] | 51.041
North Scotland | LIMK1A | Limekilns 132kV | 132 | [10 empty] | 75.7095 | 58.9872
North Scotland | MEYG1- | Meygen 132kV | 132 | [10 empty] | 88.2001 | 69.486
North Scotland | MYBS1R | Mybster 132kV | 132 | [10 empty] | 85.6578 | 67.7011
North Scotland | MYBS1S | Mybster 132kV | 132 | [10 empty] | 96.7702 | 76.1604
North Scotland | SPIT1M | Spittal 132kV | 132 | [10 empty] | 97.5297 | 76.8596
North Scotland | SPIT2J | Spittal 275kV | 275 | [10 empty] | 100 | 79.0658
North Scotland | SPIT4J | Spittal 400kV | 400 | [10 empty] | 96.0619 | 100
North Scotland | STNO1C | Strathy North 132kV | 132 | [10 empty] | 66.6749 | 51.3547
North Scotland | STSO1A | Strathy South 132kV | 132 | [10 empty] | 63.5216
North Scotland | STWO1- | Strathy Wood 132kV | 132 | [10 empty] | 66.1076 | 50.8442
North Scotland | THUS1M | Thurso South 132kV | 132 | [10 empty] | 89.4315 | 70.522
North Scotland | THUS2K | Thurso South 275kV | 275 | [10 empty] | 89.7582 | 70.877

## ProcInspection (hidden)
Procurement Excel Wookbook Inspection
Date: | 2025-03-21 15:00
UserName: | alexandra.millar
Workbook Secure: | TRUE
HyperLinks List
| Worksheet Name | No of Embedded Documents | Is Worksheet Hidden | HyperLinks | Protected | External Excel Links | Worksheet Name | Cell Reference | HyperLink
| Note | 0 | No | 0 | Yes
| System Impedance | 0 | No | 0 | Yes
| Fault Impedance | 0 | No | 0 | Yes
| Effectiveness Factors | 0 | No | 0 | Yes