## Version
Date | Version | Details
2025-04-15 | 1 | This file only contains the indicative reporting associated with draft data for GC0151 for April 2025. This file will be updated in May 2025 to reflect the full data set.
2025-05-15 | 2 | This file only contains the indicative reporting associated with data for GC0151 for April 2025. This file is updated in May 2025 to reflect the full data set.
2025-05-30 | 3 | This file only contains the indicative reporting associated with data for GC0105 & GC0151 for April 2025.

## Notes
Subject | Notes
RoCoF | RoCoF=(frequency_500ms - frequency_0ms)/500ms RoCoF is calculated using 500ms sliding window. Note that smaller losses will have less accurate ROCOF calculations The RoCoF figure in this report is from external service
System Inertia | Monitoring which transmission-connected generators are running and adding an estimate of inertia from embedded generation and demand
Data 'N/A' | N/A: data not applicable or potentially unreliable. For example, there maybe events when the loss of infeed or exfeed is not instantaneous (over long time period), the calculated RoCoF may not be indicative. For some events, during a disturbance the data may potentially be unreliable. NGESO will apply engineering judgement to determine whether the derived/calculated data is suitable for sharing.
MW trip/loss of all generation/ interconnection related to the incident | Positive sign: indicates a loss of infeed, generator or importing interconnector. Negative sign: indicates a loss of outfeed, exporting interconnector.

## Transmission Faults (GC0151)
Location | Network Operator | Date Time | Voltage Trace (Refer to sheet) | Notes
Hornsea Two 220kV Export Cable 2 Trip | OFTO | 2025-04-03 07:46
Drax - Keadby - Thorpe Marsh 400kV circuit | NGET | 2025-04-08 03:50 | V20250408-1
Kintore - Rothienorman 2 400kV circuit | SHETL | 2025-04-09 07:18
Neilston - Elderslie - Johnstone 1 132kV circuit | SPT | 2025-04-17 04:38
St Fergus 132kV BB2 - SF2/ SM2/ SA2 | SHETL | 2025-04-18 18:01
Drax 400kV Main Busbar 3 and Main Busbar 4 | NGET | 2025-04-23 17:15
Brora 1TO 33kV | SHETL | 2025-04-24 05:25
Heysham 132kV Reserve Busbar 1, Reserve Busbar 2, and Main Busbar 2 | NGET | 2025-04-27 18:13

## System Incidents (GC0105)
|  |  | Date and time of the incident | System frequency trace (1-second interval) for the incident | System frequency immediately before the incident | System frequency immediately after the incident | Maximum/Minimum rate of change of frequency (RoCoF) of the incident | System inertia at the time of the incident | Where known, MW trip/loss of all generation/ interconnection related to the incident |  | Where known, MW trip/loss of all Embedded Generation(EG) related to the incident | Where known, MW trip/loss of all DNO demand related to the incident; |  | Transmission fault associated with the incident; | Any transient voltage dip (loss % and duration) at the local substation associated with the incident | Any other data to gain a clearer understanding of the incident and its potential implications
Reference | Name | Notes | Date Time | System Frequency (Refer to sheet) | Pre-Event Frequency (Hz) | Post-Event Frequency (Hz) | RoCoF (Hz/s) | System Inertia (GVAs) | Generation/Interconnection (MW) |  | EG (MW) | Demand (MW) |  | Transmission fault | Voltage Dip | Additional data
20250419-1 | Trip of DRAX-1 |  | 2025-04-19 19:39 | 20250419-1 | 50.069 | 49.884 | -0.043144 | 163 | DRAX-1 | 647.7
20250419-2 | Trip of KEAD-2 |  | 2025-04-19 20:14 | 20250419-2 | 49.942 | 49.787 | -0.081916 | 163 | KEAD-2 | 822.66
20250423-1 | Trip of DRAX-3 |  | 2025-04-23 17:15 | 20250423-1 | 49.986 | 49.816 | -0.13486 | 247 | DRAX-3 | 643.65
20250426-1 | Trip of KEAD-2 |  | 2025-04-26 23:33 | 20250426-1 | 50.031 | 49.895 | -0.035865 | 126 | KEAD-2 | 363.06
20250427-1 | Trip of VIKING LINK | Importing from DK to GB | 2025-04-27 03:05 | 20250427-1 | 49.961 | 49.774 | -0.18258 | 113 | VIKING LINK | 986.9
20250427-2 | Trip of IFA BP2 | Importing from FR to GB | 2025-04-27 10:32 | 20250427-2 | 49.937 | 49.837 | -0.097635 | 124 | IFA BP2 | 552.3
20250427-3 | Loss of Demand | Loss of demand of ENWL fed via Trimpell 132kV substation | 2025-04-27 18:13 | 20250427-3 | [7 empty] | ENWL | 3.5 | Loss of Heysham 132kV substation
20250429-1 | Trip of IFA BP1 | Importing from FR to GB | 2025-04-29 16:25 | 20250429-1 | 49.971 | 49.778 | -0.13249 | 191 | IFA BP1 | 1002.6

## 20250419-1
In GMT
Date | Time | Freq
2025-04-19 | 19:38 | 50.083 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-04-19 | 19:38 | 50.082 | 222 | BRITNED | 676.211
2025-04-19 | 19:38 | 50.08 | 268 | WBURB-2 | 428.156
2025-04-19 | 19:38 | 50.079 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-04-19 | 19:38 | 50.077 |  | Viking Link | -648.9
2025-04-19 | 19:38 | 50.074 |  | Viking Link | 1398.96
2025-04-19 | 19:38 | 50.074 | 209 | DRAXX-3 | 626.95
2025-04-19 | 19:38 | 50.076 | 154 | CDCL-1 | 391.57
2025-04-19 | 19:38 | 50.075 | 268 | ROCK-1 | 468.495
2025-04-19 | 19:38 | 50.074 | 148 | IFA Bipole1 | 945.473
2025-04-19 | 19:38 | 50.073 | 132 | IFA Bipole1 | 999.1
2025-04-19 | 19:38 | 50.073 | 141 | IFA Bipole2 | 1000
2025-04-19 | 19:38 | 50.075 | 135 | IFA Bipole1 | 996.75
2025-04-19 | 19:38 | 50.074 |  | Viking Link | -780.3
2025-04-19 | 19:38 | 50.074
2025-04-19 | 19:38 | 50.074
2025-04-19 | 19:38 | 50.073
2025-04-19 | 19:38 | 50.073
2025-04-19 | 19:38 | 50.074
2025-04-19 | 19:38 | 50.075 | 130 | HEYM12 | 271.908
2025-04-19 | 19:38 | 50.076 | 228 | HUMR-1 | 303.75
2025-04-19 | 19:38 | 50.076
2025-04-19 | 19:38 | 50.079
2025-04-19 | 19:38 | 50.083
2025-04-19 | 19:38 | 50.086
2025-04-19 | 19:38 | 50.084
2025-04-19 | 19:38 | 50.084
2025-04-19 | 19:38 | 50.084
2025-04-19 | 19:38 | 50.084
2025-04-19 | 19:38 | 50.08
2025-04-19 | 19:38 | 50.078 | 211 | CDCL-1 | 291.5
2025-04-19 | 19:38 | 50.077 | 199 | STAY-2 | 413.125
2025-04-19 | 19:38 | 50.077 | 173 | CDCL-1 | 397.375
2025-04-19 | 19:38 | 50.074 | 248 | SEAB-2 | 361.25
2025-04-19 | 19:38 | 50.076 | 255 | FRANCE | 995.65
2025-04-19 | 19:39 | 50.077 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-04-19 | 19:39 | 50.079
2025-04-19 | 19:39 | 50.079
2025-04-19 | 19:39 | 50.081
2025-04-19 | 19:39 | 50.085
2025-04-19 | 19:39 | 50.089
2025-04-19 | 19:39 | 50.087
2025-04-19 | 19:39 | 50.088
2025-04-19 | 19:39 | 50.089
2025-04-19 | 19:39 | 50.089
2025-04-19 | 19:39 | 50.086
2025-04-19 | 19:39 | 50.085
2025-04-19 | 19:39 | 50.085
2025-04-19 | 19:39 | 50.082
2025-04-19 | 19:39 | 50.078
2025-04-19 | 19:39 | 50.075
2025-04-19 | 19:39 | 50.074
2025-04-19 | 19:39 | 50.071
2025-04-19 | 19:39 | 50.069
2025-04-19 | 19:39 | 50.064
2025-04-19 | 19:39 | 50.053
2025-04-19 | 19:39 | 50.029
2025-04-19 | 19:39 | 50.006
2025-04-19 | 19:39 | 49.99
2025-04-19 | 19:39 | 49.977
2025-04-19 | 19:39 | 49.967
2025-04-19 | 19:39 | 49.948
2025-04-19 | 19:39 | 49.915
2025-04-19 | 19:39 | 49.896
2025-04-19 | 19:39 | 49.886
2025-04-19 | 19:39 | 49.884
2025-04-19 | 19:39 | 49.886
2025-04-19 | 19:39 | 49.888
2025-04-19 | 19:39 | 49.887
2025-04-19 | 19:39 | 49.888
2025-04-19 | 19:39 | 49.889
2025-04-19 | 19:39 | 49.89
2025-04-19 | 19:39 | 49.89
2025-04-19 | 19:39 | 49.889
2025-04-19 | 19:39 | 49.889
2025-04-19 | 19:39 | 49.887
2025-04-19 | 19:39 | 49.885
2025-04-19 | 19:39 | 49.884
2025-04-19 | 19:39 | 49.885
2025-04-19 | 19:39 | 49.884
2025-04-19 | 19:39 | 49.884
2025-04-19 | 19:39 | 49.884
2025-04-19 | 19:39 | 49.885
2025-04-19 | 19:39 | 49.886
2025-04-19 | 19:39 | 49.886
2025-04-19 | 19:39 | 49.885
2025-04-19 | 19:39 | 49.886
2025-04-19 | 19:39 | 49.885
2025-04-19 | 19:39 | 49.884
2025-04-19 | 19:39 | 49.884
2025-04-19 | 19:39 | 49.884
2025-04-19 | 19:39 | 49.883
2025-04-19 | 19:39 | 49.882
2025-04-19 | 19:39 | 49.881
2025-04-19 | 19:40 | 49.88
2025-04-19 | 19:40 | 49.878
2025-04-19 | 19:40 | 49.878
2025-04-19 | 19:40 | 49.88
2025-04-19 | 19:40 | 49.882
2025-04-19 | 19:40 | 49.881
2025-04-19 | 19:40 | 49.881
2025-04-19 | 19:40 | 49.884
2025-04-19 | 19:40 | 49.886
2025-04-19 | 19:40 | 49.887
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.889
2025-04-19 | 19:40 | 49.891
2025-04-19 | 19:40 | 49.893
2025-04-19 | 19:40 | 49.894
2025-04-19 | 19:40 | 49.893
2025-04-19 | 19:40 | 49.893
2025-04-19 | 19:40 | 49.893
2025-04-19 | 19:40 | 49.893
2025-04-19 | 19:40 | 49.892
2025-04-19 | 19:40 | 49.891
2025-04-19 | 19:40 | 49.889
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.887
2025-04-19 | 19:40 | 49.89
2025-04-19 | 19:40 | 49.892
2025-04-19 | 19:40 | 49.89
2025-04-19 | 19:40 | 49.889
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.887
2025-04-19 | 19:40 | 49.885
2025-04-19 | 19:40 | 49.885
2025-04-19 | 19:40 | 49.885
2025-04-19 | 19:40 | 49.883
2025-04-19 | 19:40 | 49.882
2025-04-19 | 19:40 | 49.885
2025-04-19 | 19:40 | 49.885
2025-04-19 | 19:40 | 49.885
2025-04-19 | 19:40 | 49.885
2025-04-19 | 19:40 | 49.886
2025-04-19 | 19:40 | 49.887
2025-04-19 | 19:40 | 49.887
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.889
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.887
2025-04-19 | 19:40 | 49.887
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.887
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.888
2025-04-19 | 19:40 | 49.887
2025-04-19 | 19:40 | 49.886
2025-04-19 | 19:40 | 49.886
2025-04-19 | 19:40 | 49.886
2025-04-19 | 19:40 | 49.885
2025-04-19 | 19:40 | 49.886
2025-04-19 | 19:41 | 49.89
2025-04-19 | 19:41 | 49.892
2025-04-19 | 19:41 | 49.89
2025-04-19 | 19:41 | 49.89
2025-04-19 | 19:41 | 49.893
2025-04-19 | 19:41 | 49.895
2025-04-19 | 19:41 | 49.895
2025-04-19 | 19:41 | 49.896
2025-04-19 | 19:41 | 49.896
2025-04-19 | 19:41 | 49.9
2025-04-19 | 19:41 | 49.899
2025-04-19 | 19:41 | 49.9
2025-04-19 | 19:41 | 49.899
2025-04-19 | 19:41 | 49.899
2025-04-19 | 19:41 | 49.9
2025-04-19 | 19:41 | 49.903
2025-04-19 | 19:41 | 49.909
2025-04-19 | 19:41 | 49.908
2025-04-19 | 19:41 | 49.907
2025-04-19 | 19:41 | 49.908
2025-04-19 | 19:41 | 49.907
2025-04-19 | 19:41 | 49.907
2025-04-19 | 19:41 | 49.904
2025-04-19 | 19:41 | 49.905
2025-04-19 | 19:41 | 49.907
2025-04-19 | 19:41 | 49.906
2025-04-19 | 19:41 | 49.905
2025-04-19 | 19:41 | 49.906
2025-04-19 | 19:41 | 49.908
2025-04-19 | 19:41 | 49.908
2025-04-19 | 19:41 | 49.903
2025-04-19 | 19:41 | 49.894
2025-04-19 | 19:41 | 49.889
2025-04-19 | 19:41 | 49.887
2025-04-19 | 19:41 | 49.885
2025-04-19 | 19:41 | 49.886
2025-04-19 | 19:41 | 49.887
2025-04-19 | 19:41 | 49.886
2025-04-19 | 19:41 | 49.885
2025-04-19 | 19:41 | 49.885
2025-04-19 | 19:41 | 49.886
2025-04-19 | 19:41 | 49.886
2025-04-19 | 19:41 | 49.887
2025-04-19 | 19:41 | 49.889
2025-04-19 | 19:41 | 49.887
2025-04-19 | 19:41 | 49.887
2025-04-19 | 19:41 | 49.889
2025-04-19 | 19:41 | 49.89
2025-04-19 | 19:41 | 49.89
2025-04-19 | 19:41 | 49.891
2025-04-19 | 19:41 | 49.891
2025-04-19 | 19:41 | 49.893
2025-04-19 | 19:41 | 49.895
2025-04-19 | 19:41 | 49.896
2025-04-19 | 19:41 | 49.898
2025-04-19 | 19:41 | 49.9
2025-04-19 | 19:41 | 49.9
2025-04-19 | 19:41 | 49.899
2025-04-19 | 19:41 | 49.898
2025-04-19 | 19:42 | 49.897
2025-04-19 | 19:42 | 49.896
2025-04-19 | 19:42 | 49.895
2025-04-19 | 19:42 | 49.894
2025-04-19 | 19:42 | 49.895
2025-04-19 | 19:42 | 49.895
2025-04-19 | 19:42 | 49.896
2025-04-19 | 19:42 | 49.897
2025-04-19 | 19:42 | 49.897
2025-04-19 | 19:42 | 49.895
2025-04-19 | 19:42 | 49.896
2025-04-19 | 19:42 | 49.895
2025-04-19 | 19:42 | 49.896
2025-04-19 | 19:42 | 49.894
2025-04-19 | 19:42 | 49.893
2025-04-19 | 19:42 | 49.893
2025-04-19 | 19:42 | 49.892
2025-04-19 | 19:42 | 49.89
2025-04-19 | 19:42 | 49.89
2025-04-19 | 19:42 | 49.89
2025-04-19 | 19:42 | 49.89
2025-04-19 | 19:42 | 49.892
2025-04-19 | 19:42 | 49.896
2025-04-19 | 19:42 | 49.897
2025-04-19 | 19:42 | 49.895
2025-04-19 | 19:42 | 49.895
2025-04-19 | 19:42 | 49.894
2025-04-19 | 19:42 | 49.893
2025-04-19 | 19:42 | 49.891
2025-04-19 | 19:42 | 49.891
2025-04-19 | 19:42 | 49.891
2025-04-19 | 19:42 | 49.889
2025-04-19 | 19:42 | 49.887
2025-04-19 | 19:42 | 49.884
2025-04-19 | 19:42 | 49.884
2025-04-19 | 19:42 | 49.885
2025-04-19 | 19:42 | 49.885
2025-04-19 | 19:42 | 49.883
2025-04-19 | 19:42 | 49.883
2025-04-19 | 19:42 | 49.884
2025-04-19 | 19:42 | 49.881
2025-04-19 | 19:42 | 49.879
2025-04-19 | 19:42 | 49.878
2025-04-19 | 19:42 | 49.878
2025-04-19 | 19:42 | 49.877
2025-04-19 | 19:42 | 49.878
2025-04-19 | 19:42 | 49.879
2025-04-19 | 19:42 | 49.878
2025-04-19 | 19:42 | 49.876
2025-04-19 | 19:42 | 49.877
2025-04-19 | 19:42 | 49.879
2025-04-19 | 19:42 | 49.88
2025-04-19 | 19:42 | 49.88
2025-04-19 | 19:42 | 49.879
2025-04-19 | 19:42 | 49.879
2025-04-19 | 19:42 | 49.88
2025-04-19 | 19:42 | 49.88
2025-04-19 | 19:42 | 49.88
2025-04-19 | 19:42 | 49.882
2025-04-19 | 19:42 | 49.882
2025-04-19 | 19:42 | 49.883
2025-04-19 | 19:43 | 49.886
2025-04-19 | 19:43 | 49.887
2025-04-19 | 19:43 | 49.887
2025-04-19 | 19:43 | 49.887
2025-04-19 | 19:43 | 49.887
2025-04-19 | 19:43 | 49.889
2025-04-19 | 19:43 | 49.888
2025-04-19 | 19:43 | 49.888
2025-04-19 | 19:43 | 49.891
2025-04-19 | 19:43 | 49.892
2025-04-19 | 19:43 | 49.892
2025-04-19 | 19:43 | 49.891
2025-04-19 | 19:43 | 49.892
2025-04-19 | 19:43 | 49.891
2025-04-19 | 19:43 | 49.889
2025-04-19 | 19:43 | 49.89
2025-04-19 | 19:43 | 49.891
2025-04-19 | 19:43 | 49.889
2025-04-19 | 19:43 | 49.888
2025-04-19 | 19:43 | 49.889
2025-04-19 | 19:43 | 49.887
2025-04-19 | 19:43 | 49.887
2025-04-19 | 19:43 | 49.887
2025-04-19 | 19:43 | 49.887
2025-04-19 | 19:43 | 49.885
2025-04-19 | 19:43 | 49.882
2025-04-19 | 19:43 | 49.88
2025-04-19 | 19:43 | 49.881
2025-04-19 | 19:43 | 49.881
2025-04-19 | 19:43 | 49.879
2025-04-19 | 19:43 | 49.873
2025-04-19 | 19:43 | 49.864
2025-04-19 | 19:43 | 49.862
2025-04-19 | 19:43 | 49.86
2025-04-19 | 19:43 | 49.86
2025-04-19 | 19:43 | 49.859
2025-04-19 | 19:43 | 49.858
2025-04-19 | 19:43 | 49.856
2025-04-19 | 19:43 | 49.856
2025-04-19 | 19:43 | 49.857
2025-04-19 | 19:43 | 49.858
2025-04-19 | 19:43 | 49.857
2025-04-19 | 19:43 | 49.857
2025-04-19 | 19:43 | 49.858
2025-04-19 | 19:43 | 49.856
2025-04-19 | 19:43 | 49.853
2025-04-19 | 19:43 | 49.851
2025-04-19 | 19:43 | 49.851
2025-04-19 | 19:43 | 49.85
2025-04-19 | 19:43 | 49.847
2025-04-19 | 19:43 | 49.847
2025-04-19 | 19:43 | 49.85
2025-04-19 | 19:43 | 49.851
2025-04-19 | 19:43 | 49.851
2025-04-19 | 19:43 | 49.853
2025-04-19 | 19:43 | 49.856
2025-04-19 | 19:43 | 49.855
2025-04-19 | 19:43 | 49.853
2025-04-19 | 19:43 | 49.854
2025-04-19 | 19:44 | 49.855
2025-04-19 | 19:44 | 49.857
2025-04-19 | 19:44 | 49.863
2025-04-19 | 19:44 | 49.865
2025-04-19 | 19:44 | 49.864
2025-04-19 | 19:44 | 49.865
2025-04-19 | 19:44 | 49.867
2025-04-19 | 19:44 | 49.872
2025-04-19 | 19:44 | 49.874
2025-04-19 | 19:44 | 49.872
2025-04-19 | 19:44 | 49.872
2025-04-19 | 19:44 | 49.873
2025-04-19 | 19:44 | 49.87
2025-04-19 | 19:44 | 49.867
2025-04-19 | 19:44 | 49.867
2025-04-19 | 19:44 | 49.868
2025-04-19 | 19:44 | 49.867
2025-04-19 | 19:44 | 49.864
2025-04-19 | 19:44 | 49.863
2025-04-19 | 19:44 | 49.862
2025-04-19 | 19:44 | 49.861
2025-04-19 | 19:44 | 49.86
2025-04-19 | 19:44 | 49.863
2025-04-19 | 19:44 | 49.865
2025-04-19 | 19:44 | 49.862
2025-04-19 | 19:44 | 49.857
2025-04-19 | 19:44 | 49.854
2025-04-19 | 19:44 | 49.851
2025-04-19 | 19:44 | 49.852
2025-04-19 | 19:44 | 49.851
2025-04-19 | 19:44 | 49.851
2025-04-19 | 19:44 | 49.847
2025-04-19 | 19:44 | 49.852
2025-04-19 | 19:44 | 49.855
2025-04-19 | 19:44 | 49.859
2025-04-19 | 19:44 | 49.86
2025-04-19 | 19:44 | 49.859
2025-04-19 | 19:44 | 49.859
2025-04-19 | 19:44 | 49.858
2025-04-19 | 19:44 | 49.857
2025-04-19 | 19:44 | 49.855
2025-04-19 | 19:44 | 49.855
2025-04-19 | 19:44 | 49.86
2025-04-19 | 19:44 | 49.863
2025-04-19 | 19:44 | 49.861
2025-04-19 | 19:44 | 49.858
2025-04-19 | 19:44 | 49.858
2025-04-19 | 19:44 | 49.858
2025-04-19 | 19:44 | 49.857
2025-04-19 | 19:44 | 49.856
2025-04-19 | 19:44 | 49.856
2025-04-19 | 19:44 | 49.854
2025-04-19 | 19:44 | 49.853
2025-04-19 | 19:44 | 49.853
2025-04-19 | 19:44 | 49.852
2025-04-19 | 19:44 | 49.853
2025-04-19 | 19:44 | 49.854
2025-04-19 | 19:44 | 49.857
2025-04-19 | 19:44 | 49.859
2025-04-19 | 19:44 | 49.861
2025-04-19 | 19:44 | 49.864
2025-04-19 | 19:45 | 49.867
2025-04-19 | 19:45 | 49.867
2025-04-19 | 19:45 | 49.867
2025-04-19 | 19:45 | 49.867
2025-04-19 | 19:45 | 49.868
2025-04-19 | 19:45 | 49.87
2025-04-19 | 19:45 | 49.871
2025-04-19 | 19:45 | 49.873
2025-04-19 | 19:45 | 49.874
2025-04-19 | 19:45 | 49.875
2025-04-19 | 19:45 | 49.877
2025-04-19 | 19:45 | 49.877
2025-04-19 | 19:45 | 49.877
2025-04-19 | 19:45 | 49.876
2025-04-19 | 19:45 | 49.873
2025-04-19 | 19:45 | 49.871
2025-04-19 | 19:45 | 49.87
2025-04-19 | 19:45 | 49.869
2025-04-19 | 19:45 | 49.867
2025-04-19 | 19:45 | 49.869
2025-04-19 | 19:45 | 49.87
2025-04-19 | 19:45 | 49.868
2025-04-19 | 19:45 | 49.864
2025-04-19 | 19:45 | 49.863
2025-04-19 | 19:45 | 49.862
2025-04-19 | 19:45 | 49.861
2025-04-19 | 19:45 | 49.859
2025-04-19 | 19:45 | 49.86
2025-04-19 | 19:45 | 49.864
2025-04-19 | 19:45 | 49.865
2025-04-19 | 19:45 | 49.862
2025-04-19 | 19:45 | 49.863
2025-04-19 | 19:45 | 49.864
2025-04-19 | 19:45 | 49.865
2025-04-19 | 19:45 | 49.866
2025-04-19 | 19:45 | 49.866
2025-04-19 | 19:45 | 49.867
2025-04-19 | 19:45 | 49.867
2025-04-19 | 19:45 | 49.868
2025-04-19 | 19:45 | 49.871
2025-04-19 | 19:45 | 49.87
2025-04-19 | 19:45 | 49.87
2025-04-19 | 19:45 | 49.871
2025-04-19 | 19:45 | 49.873
2025-04-19 | 19:45 | 49.872
2025-04-19 | 19:45 | 49.872
2025-04-19 | 19:45 | 49.873
2025-04-19 | 19:45 | 49.875
2025-04-19 | 19:45 | 49.877
2025-04-19 | 19:45 | 49.877
2025-04-19 | 19:45 | 49.876
2025-04-19 | 19:45 | 49.878
2025-04-19 | 19:45 | 49.877
2025-04-19 | 19:45 | 49.875
2025-04-19 | 19:45 | 49.874
2025-04-19 | 19:45 | 49.874
2025-04-19 | 19:45 | 49.874
2025-04-19 | 19:45 | 49.874
2025-04-19 | 19:45 | 49.874
2025-04-19 | 19:46 | 49.875
2025-04-19 | 19:46 | 49.877
2025-04-19 | 19:46 | 49.878
2025-04-19 | 19:46 | 49.879
2025-04-19 | 19:46 | 49.881
2025-04-19 | 19:46 | 49.88
2025-04-19 | 19:46 | 49.88
2025-04-19 | 19:46 | 49.883
2025-04-19 | 19:46 | 49.885
2025-04-19 | 19:46 | 49.886
2025-04-19 | 19:46 | 49.885
2025-04-19 | 19:46 | 49.885
2025-04-19 | 19:46 | 49.883
2025-04-19 | 19:46 | 49.882
2025-04-19 | 19:46 | 49.882
2025-04-19 | 19:46 | 49.882
2025-04-19 | 19:46 | 49.882
2025-04-19 | 19:46 | 49.88
2025-04-19 | 19:46 | 49.88
2025-04-19 | 19:46 | 49.883
2025-04-19 | 19:46 | 49.885
2025-04-19 | 19:46 | 49.883
2025-04-19 | 19:46 | 49.883
2025-04-19 | 19:46 | 49.882
2025-04-19 | 19:46 | 49.881
2025-04-19 | 19:46 | 49.88
2025-04-19 | 19:46 | 49.88
2025-04-19 | 19:46 | 49.879
2025-04-19 | 19:46 | 49.876
2025-04-19 | 19:46 | 49.874
2025-04-19 | 19:46 | 49.872
2025-04-19 | 19:46 | 49.872
2025-04-19 | 19:46 | 49.871
2025-04-19 | 19:46 | 49.87
2025-04-19 | 19:46 | 49.869
2025-04-19 | 19:46 | 49.867
2025-04-19 | 19:46 | 49.863
2025-04-19 | 19:46 | 49.862
2025-04-19 | 19:46 | 49.864
2025-04-19 | 19:46 | 49.863
2025-04-19 | 19:46 | 49.86
2025-04-19 | 19:46 | 49.856
2025-04-19 | 19:46 | 49.856
2025-04-19 | 19:46 | 49.857
2025-04-19 | 19:46 | 49.858
2025-04-19 | 19:46 | 49.859
2025-04-19 | 19:46 | 49.86
2025-04-19 | 19:46 | 49.862
2025-04-19 | 19:46 | 49.862
2025-04-19 | 19:46 | 49.86
2025-04-19 | 19:46 | 49.861
2025-04-19 | 19:46 | 49.862
2025-04-19 | 19:46 | 49.861
2025-04-19 | 19:46 | 49.861
2025-04-19 | 19:46 | 49.862
2025-04-19 | 19:46 | 49.864
2025-04-19 | 19:46 | 49.863
2025-04-19 | 19:46 | 49.864
2025-04-19 | 19:46 | 49.866
2025-04-19 | 19:46 | 49.864
2025-04-19 | 19:46 | 49.864
2025-04-19 | 19:47 | 49.864
2025-04-19 | 19:47 | 49.862
2025-04-19 | 19:47 | 49.86
2025-04-19 | 19:47 | 49.859
2025-04-19 | 19:47 | 49.86
2025-04-19 | 19:47 | 49.863
2025-04-19 | 19:47 | 49.863
2025-04-19 | 19:47 | 49.861
2025-04-19 | 19:47 | 49.861
2025-04-19 | 19:47 | 49.863
2025-04-19 | 19:47 | 49.862
2025-04-19 | 19:47 | 49.864
2025-04-19 | 19:47 | 49.864
2025-04-19 | 19:47 | 49.864
2025-04-19 | 19:47 | 49.862
2025-04-19 | 19:47 | 49.861
2025-04-19 | 19:47 | 49.861
2025-04-19 | 19:47 | 49.859
2025-04-19 | 19:47 | 49.857
2025-04-19 | 19:47 | 49.857
2025-04-19 | 19:47 | 49.858
2025-04-19 | 19:47 | 49.857
2025-04-19 | 19:47 | 49.857
2025-04-19 | 19:47 | 49.857
2025-04-19 | 19:47 | 49.857
2025-04-19 | 19:47 | 49.854
2025-04-19 | 19:47 | 49.851
2025-04-19 | 19:47 | 49.852
2025-04-19 | 19:47 | 49.853
2025-04-19 | 19:47 | 49.852
2025-04-19 | 19:47 | 49.85
2025-04-19 | 19:47 | 49.853
2025-04-19 | 19:47 | 49.854
2025-04-19 | 19:47 | 49.852
2025-04-19 | 19:47 | 49.851
2025-04-19 | 19:47 | 49.851
2025-04-19 | 19:47 | 49.853
2025-04-19 | 19:47 | 49.853
2025-04-19 | 19:47 | 49.852
2025-04-19 | 19:47 | 49.851
2025-04-19 | 19:47 | 49.852
2025-04-19 | 19:47 | 49.851
2025-04-19 | 19:47 | 49.85
2025-04-19 | 19:47 | 49.853
2025-04-19 | 19:47 | 49.858
2025-04-19 | 19:47 | 49.859
2025-04-19 | 19:47 | 49.859
2025-04-19 | 19:47 | 49.86
2025-04-19 | 19:47 | 49.86
2025-04-19 | 19:47 | 49.86
2025-04-19 | 19:47 | 49.859
2025-04-19 | 19:47 | 49.861
2025-04-19 | 19:47 | 49.862
2025-04-19 | 19:47 | 49.862
2025-04-19 | 19:47 | 49.863
2025-04-19 | 19:47 | 49.863
2025-04-19 | 19:47 | 49.862
2025-04-19 | 19:47 | 49.861
2025-04-19 | 19:47 | 49.862
2025-04-19 | 19:48 | 49.865
2025-04-19 | 19:48 | 49.867
2025-04-19 | 19:48 | 49.868
2025-04-19 | 19:48 | 49.867
2025-04-19 | 19:48 | 49.868
2025-04-19 | 19:48 | 49.866
2025-04-19 | 19:48 | 49.865
2025-04-19 | 19:48 | 49.864
2025-04-19 | 19:48 | 49.864
2025-04-19 | 19:48 | 49.865
2025-04-19 | 19:48 | 49.863
2025-04-19 | 19:48 | 49.86
2025-04-19 | 19:48 | 49.86
2025-04-19 | 19:48 | 49.86
2025-04-19 | 19:48 | 49.861
2025-04-19 | 19:48 | 49.859
2025-04-19 | 19:48 | 49.858
2025-04-19 | 19:48 | 49.854
2025-04-19 | 19:48 | 49.854
2025-04-19 | 19:48 | 49.856
2025-04-19 | 19:48 | 49.856
2025-04-19 | 19:48 | 49.855
2025-04-19 | 19:48 | 49.854
2025-04-19 | 19:48 | 49.853
2025-04-19 | 19:48 | 49.852
2025-04-19 | 19:48 | 49.849
2025-04-19 | 19:48 | 49.847
2025-04-19 | 19:48 | 49.849
2025-04-19 | 19:48 | 49.851
2025-04-19 | 19:48 | 49.85
2025-04-19 | 19:48 | 49.849
2025-04-19 | 19:48 | 49.848
2025-04-19 | 19:48 | 49.848
2025-04-19 | 19:48 | 49.848
2025-04-19 | 19:48 | 49.849
2025-04-19 | 19:48 | 49.852
2025-04-19 | 19:48 | 49.852
2025-04-19 | 19:48 | 49.852
2025-04-19 | 19:48 | 49.853
2025-04-19 | 19:48 | 49.853
2025-04-19 | 19:48 | 49.852
2025-04-19 | 19:48 | 49.851
2025-04-19 | 19:48 | 49.852
2025-04-19 | 19:48 | 49.853
2025-04-19 | 19:48 | 49.853
2025-04-19 | 19:48 | 49.855
2025-04-19 | 19:48 | 49.858
2025-04-19 | 19:48 | 49.861
2025-04-19 | 19:48 | 49.862
2025-04-19 | 19:48 | 49.864
2025-04-19 | 19:48 | 49.869
2025-04-19 | 19:48 | 49.871
2025-04-19 | 19:48 | 49.871
2025-04-19 | 19:48 | 49.872
2025-04-19 | 19:48 | 49.873
2025-04-19 | 19:48 | 49.873
2025-04-19 | 19:48 | 49.873
2025-04-19 | 19:48 | 49.871
2025-04-19 | 19:48 | 49.871
2025-04-19 | 19:48 | 49.868
2025-04-19 | 19:48 | 49.864
2025-04-19 | 19:49 | 49.863
2025-04-19 | 19:49 | 49.862
2025-04-19 | 19:49 | 49.863
2025-04-19 | 19:49 | 49.863
2025-04-19 | 19:49 | 49.864
2025-04-19 | 19:49 | 49.866
2025-04-19 | 19:49 | 49.864
2025-04-19 | 19:49 | 49.862
2025-04-19 | 19:49 | 49.86
2025-04-19 | 19:49 | 49.862
2025-04-19 | 19:49 | 49.862
2025-04-19 | 19:49 | 49.863
2025-04-19 | 19:49 | 49.866
2025-04-19 | 19:49 | 49.869
2025-04-19 | 19:49 | 49.866
2025-04-19 | 19:49 | 49.867
2025-04-19 | 19:49 | 49.868
2025-04-19 | 19:49 | 49.868
2025-04-19 | 19:49 | 49.868
2025-04-19 | 19:49 | 49.868
2025-04-19 | 19:49 | 49.867
2025-04-19 | 19:49 | 49.866
2025-04-19 | 19:49 | 49.866
2025-04-19 | 19:49 | 49.867
2025-04-19 | 19:49 | 49.869
2025-04-19 | 19:49 | 49.869
2025-04-19 | 19:49 | 49.868
2025-04-19 | 19:49 | 49.872
2025-04-19 | 19:49 | 49.875
2025-04-19 | 19:49 | 49.875
2025-04-19 | 19:49 | 49.873
2025-04-19 | 19:49 | 49.874
2025-04-19 | 19:49 | 49.878
2025-04-19 | 19:49 | 49.878
2025-04-19 | 19:49 | 49.876
2025-04-19 | 19:49 | 49.876
2025-04-19 | 19:49 | 49.877
2025-04-19 | 19:49 | 49.878
2025-04-19 | 19:49 | 49.876
2025-04-19 | 19:49 | 49.877
2025-04-19 | 19:49 | 49.878
2025-04-19 | 19:49 | 49.875
2025-04-19 | 19:49 | 49.874
2025-04-19 | 19:49 | 49.875
2025-04-19 | 19:49 | 49.876
2025-04-19 | 19:49 | 49.875
2025-04-19 | 19:49 | 49.875
2025-04-19 | 19:49 | 49.875
2025-04-19 | 19:49 | 49.876
2025-04-19 | 19:49 | 49.874
2025-04-19 | 19:49 | 49.876
2025-04-19 | 19:49 | 49.88
2025-04-19 | 19:49 | 49.883
2025-04-19 | 19:49 | 49.883
2025-04-19 | 19:49 | 49.878
2025-04-19 | 19:49 | 49.878
2025-04-19 | 19:49 | 49.877
2025-04-19 | 19:49 | 49.876
2025-04-19 | 19:49 | 49.876
2025-04-19 | 19:50 | 49.876
2025-04-19 | 19:50 | 49.876
2025-04-19 | 19:50 | 49.877
2025-04-19 | 19:50 | 49.878
2025-04-19 | 19:50 | 49.879
2025-04-19 | 19:50 | 49.877
2025-04-19 | 19:50 | 49.876
2025-04-19 | 19:50 | 49.878
2025-04-19 | 19:50 | 49.88
2025-04-19 | 19:50 | 49.879
2025-04-19 | 19:50 | 49.879
2025-04-19 | 19:50 | 49.88
2025-04-19 | 19:50 | 49.879
2025-04-19 | 19:50 | 49.878
2025-04-19 | 19:50 | 49.876
2025-04-19 | 19:50 | 49.876
2025-04-19 | 19:50 | 49.877
2025-04-19 | 19:50 | 49.876
2025-04-19 | 19:50 | 49.874
2025-04-19 | 19:50 | 49.873
2025-04-19 | 19:50 | 49.871
2025-04-19 | 19:50 | 49.868
2025-04-19 | 19:50 | 49.868
2025-04-19 | 19:50 | 49.869
2025-04-19 | 19:50 | 49.87
2025-04-19 | 19:50 | 49.871
2025-04-19 | 19:50 | 49.873
2025-04-19 | 19:50 | 49.875
2025-04-19 | 19:50 | 49.877
2025-04-19 | 19:50 | 49.879
2025-04-19 | 19:50 | 49.878
2025-04-19 | 19:50 | 49.875
2025-04-19 | 19:50 | 49.866
2025-04-19 | 19:50 | 49.858
2025-04-19 | 19:50 | 49.857
2025-04-19 | 19:50 | 49.858
2025-04-19 | 19:50 | 49.857
2025-04-19 | 19:50 | 49.857
2025-04-19 | 19:50 | 49.859
2025-04-19 | 19:50 | 49.862
2025-04-19 | 19:50 | 49.863
2025-04-19 | 19:50 | 49.864
2025-04-19 | 19:50 | 49.868
2025-04-19 | 19:50 | 49.87
2025-04-19 | 19:50 | 49.869
2025-04-19 | 19:50 | 49.867
2025-04-19 | 19:50 | 49.866
2025-04-19 | 19:50 | 49.865
2025-04-19 | 19:50 | 49.866
2025-04-19 | 19:50 | 49.865
2025-04-19 | 19:50 | 49.866
2025-04-19 | 19:50 | 49.866
2025-04-19 | 19:50 | 49.866
2025-04-19 | 19:50 | 49.863
2025-04-19 | 19:50 | 49.862
2025-04-19 | 19:50 | 49.862
2025-04-19 | 19:50 | 49.861
2025-04-19 | 19:50 | 49.861
2025-04-19 | 19:50 | 49.861
2025-04-19 | 19:50 | 49.859
2025-04-19 | 19:50 | 49.856
2025-04-19 | 19:51 | 49.856
2025-04-19 | 19:51 | 49.856
2025-04-19 | 19:51 | 49.856
2025-04-19 | 19:51 | 49.854
2025-04-19 | 19:51 | 49.856
2025-04-19 | 19:51 | 49.856
2025-04-19 | 19:51 | 49.854
2025-04-19 | 19:51 | 49.852
2025-04-19 | 19:51 | 49.855
2025-04-19 | 19:51 | 49.857
2025-04-19 | 19:51 | 49.86
2025-04-19 | 19:51 | 49.863
2025-04-19 | 19:51 | 49.863
2025-04-19 | 19:51 | 49.866
2025-04-19 | 19:51 | 49.864
2025-04-19 | 19:51 | 49.863
2025-04-19 | 19:51 | 49.865
2025-04-19 | 19:51 | 49.868
2025-04-19 | 19:51 | 49.868
2025-04-19 | 19:51 | 49.867
2025-04-19 | 19:51 | 49.869
2025-04-19 | 19:51 | 49.87
2025-04-19 | 19:51 | 49.868
2025-04-19 | 19:51 | 49.867
2025-04-19 | 19:51 | 49.867
2025-04-19 | 19:51 | 49.864
2025-04-19 | 19:51 | 49.861
2025-04-19 | 19:51 | 49.86
2025-04-19 | 19:51 | 49.861
2025-04-19 | 19:51 | 49.861
2025-04-19 | 19:51 | 49.86
2025-04-19 | 19:51 | 49.861
2025-04-19 | 19:51 | 49.864
2025-04-19 | 19:51 | 49.865
2025-04-19 | 19:51 | 49.864
2025-04-19 | 19:51 | 49.861
2025-04-19 | 19:51 | 49.861
2025-04-19 | 19:51 | 49.862
2025-04-19 | 19:51 | 49.863
2025-04-19 | 19:51 | 49.865
2025-04-19 | 19:51 | 49.866
2025-04-19 | 19:51 | 49.867
2025-04-19 | 19:51 | 49.869
2025-04-19 | 19:51 | 49.87
2025-04-19 | 19:51 | 49.871
2025-04-19 | 19:51 | 49.869
2025-04-19 | 19:51 | 49.869
2025-04-19 | 19:51 | 49.868
2025-04-19 | 19:51 | 49.871
2025-04-19 | 19:51 | 49.874
2025-04-19 | 19:51 | 49.874
2025-04-19 | 19:51 | 49.875
2025-04-19 | 19:51 | 49.875
2025-04-19 | 19:51 | 49.873
2025-04-19 | 19:51 | 49.873
2025-04-19 | 19:51 | 49.877
2025-04-19 | 19:51 | 49.877
2025-04-19 | 19:51 | 49.876
2025-04-19 | 19:51 | 49.875
2025-04-19 | 19:52 | 49.876
2025-04-19 | 19:52 | 49.877
2025-04-19 | 19:52 | 49.88
2025-04-19 | 19:52 | 49.879
2025-04-19 | 19:52 | 49.881
2025-04-19 | 19:52 | 49.883
2025-04-19 | 19:52 | 49.883
2025-04-19 | 19:52 | 49.886
2025-04-19 | 19:52 | 49.885
2025-04-19 | 19:52 | 49.887
2025-04-19 | 19:52 | 49.888
2025-04-19 | 19:52 | 49.889
2025-04-19 | 19:52 | 49.888
2025-04-19 | 19:52 | 49.886
2025-04-19 | 19:52 | 49.884
2025-04-19 | 19:52 | 49.886
2025-04-19 | 19:52 | 49.887
2025-04-19 | 19:52 | 49.885
2025-04-19 | 19:52 | 49.882
2025-04-19 | 19:52 | 49.883
2025-04-19 | 19:52 | 49.885
2025-04-19 | 19:52 | 49.883
2025-04-19 | 19:52 | 49.881
2025-04-19 | 19:52 | 49.882
2025-04-19 | 19:52 | 49.884
2025-04-19 | 19:52 | 49.885
2025-04-19 | 19:52 | 49.884
2025-04-19 | 19:52 | 49.883
2025-04-19 | 19:52 | 49.881
2025-04-19 | 19:52 | 49.879
2025-04-19 | 19:52 | 49.877
2025-04-19 | 19:52 | 49.877
2025-04-19 | 19:52 | 49.875
2025-04-19 | 19:52 | 49.875
2025-04-19 | 19:52 | 49.877
2025-04-19 | 19:52 | 49.879
2025-04-19 | 19:52 | 49.879
2025-04-19 | 19:52 | 49.877
2025-04-19 | 19:52 | 49.877
2025-04-19 | 19:52 | 49.877
2025-04-19 | 19:52 | 49.875
2025-04-19 | 19:52 | 49.872
2025-04-19 | 19:52 | 49.873
2025-04-19 | 19:52 | 49.875
2025-04-19 | 19:52 | 49.877
2025-04-19 | 19:52 | 49.876
2025-04-19 | 19:52 | 49.875
2025-04-19 | 19:52 | 49.874
2025-04-19 | 19:52 | 49.873
2025-04-19 | 19:52 | 49.871
2025-04-19 | 19:52 | 49.873
2025-04-19 | 19:52 | 49.874
2025-04-19 | 19:52 | 49.874
2025-04-19 | 19:52 | 49.874
2025-04-19 | 19:52 | 49.876
2025-04-19 | 19:52 | 49.875
2025-04-19 | 19:52 | 49.872
2025-04-19 | 19:52 | 49.871
2025-04-19 | 19:52 | 49.871
2025-04-19 | 19:52 | 49.871
2025-04-19 | 19:52 | 49.872
2025-04-19 | 19:53 | 49.874
2025-04-19 | 19:53 | 49.873
2025-04-19 | 19:53 | 49.871
2025-04-19 | 19:53 | 49.87
2025-04-19 | 19:53 | 49.869
2025-04-19 | 19:53 | 49.87
2025-04-19 | 19:53 | 49.872
2025-04-19 | 19:53 | 49.872
2025-04-19 | 19:53 | 49.872
2025-04-19 | 19:53 | 49.875
2025-04-19 | 19:53 | 49.876
2025-04-19 | 19:53 | 49.877
2025-04-19 | 19:53 | 49.877
2025-04-19 | 19:53 | 49.878
2025-04-19 | 19:53 | 49.88
2025-04-19 | 19:53 | 49.878
2025-04-19 | 19:53 | 49.877
2025-04-19 | 19:53 | 49.876
2025-04-19 | 19:53 | 49.876
2025-04-19 | 19:53 | 49.873
2025-04-19 | 19:53 | 49.872
2025-04-19 | 19:53 | 49.873
2025-04-19 | 19:53 | 49.872
2025-04-19 | 19:53 | 49.872
2025-04-19 | 19:53 | 49.874
2025-04-19 | 19:53 | 49.874
2025-04-19 | 19:53 | 49.872
2025-04-19 | 19:53 | 49.869
2025-04-19 | 19:53 | 49.866
2025-04-19 | 19:53 | 49.864
2025-04-19 | 19:53 | 49.86
2025-04-19 | 19:53 | 49.859
2025-04-19 | 19:53 | 49.859
2025-04-19 | 19:53 | 49.857
2025-04-19 | 19:53 | 49.856
2025-04-19 | 19:53 | 49.856
2025-04-19 | 19:53 | 49.859
2025-04-19 | 19:53 | 49.861
2025-04-19 | 19:53 | 49.86
2025-04-19 | 19:53 | 49.858
2025-04-19 | 19:53 | 49.857
2025-04-19 | 19:53 | 49.855
2025-04-19 | 19:53 | 49.854
2025-04-19 | 19:53 | 49.854
2025-04-19 | 19:53 | 49.855
2025-04-19 | 19:53 | 49.855
2025-04-19 | 19:53 | 49.852
2025-04-19 | 19:53 | 49.853
2025-04-19 | 19:53 | 49.853
2025-04-19 | 19:53 | 49.852
2025-04-19 | 19:53 | 49.852
2025-04-19 | 19:53 | 49.852
2025-04-19 | 19:53 | 49.851
2025-04-19 | 19:53 | 49.852
2025-04-19 | 19:53 | 49.851
2025-04-19 | 19:53 | 49.853
2025-04-19 | 19:53 | 49.852
2025-04-19 | 19:53 | 49.85
2025-04-19 | 19:53 | 49.851
2025-04-19 | 19:54 | 49.852
2025-04-19 | 19:54 | 49.851
2025-04-19 | 19:54 | 49.85
2025-04-19 | 19:54 | 49.85
2025-04-19 | 19:54 | 49.853
2025-04-19 | 19:54 | 49.852
2025-04-19 | 19:54 | 49.851
2025-04-19 | 19:54 | 49.852
2025-04-19 | 19:54 | 49.855
2025-04-19 | 19:54 | 49.855
2025-04-19 | 19:54 | 49.855
2025-04-19 | 19:54 | 49.855
2025-04-19 | 19:54 | 49.856
2025-04-19 | 19:54 | 49.859
2025-04-19 | 19:54 | 49.862
2025-04-19 | 19:54 | 49.865
2025-04-19 | 19:54 | 49.868
2025-04-19 | 19:54 | 49.868
2025-04-19 | 19:54 | 49.867
2025-04-19 | 19:54 | 49.868
2025-04-19 | 19:54 | 49.87
2025-04-19 | 19:54 | 49.871
2025-04-19 | 19:54 | 49.872
2025-04-19 | 19:54 | 49.874
2025-04-19 | 19:54 | 49.878
2025-04-19 | 19:54 | 49.877
2025-04-19 | 19:54 | 49.878
2025-04-19 | 19:54 | 49.879
2025-04-19 | 19:54 | 49.878
2025-04-19 | 19:54 | 49.877
2025-04-19 | 19:54 | 49.876
2025-04-19 | 19:54 | 49.874
2025-04-19 | 19:54 | 49.874
2025-04-19 | 19:54 | 49.872
2025-04-19 | 19:54 | 49.872
2025-04-19 | 19:54 | 49.872
2025-04-19 | 19:54 | 49.872
2025-04-19 | 19:54 | 49.869
2025-04-19 | 19:54 | 49.871
2025-04-19 | 19:54 | 49.872
2025-04-19 | 19:54 | 49.872
2025-04-19 | 19:54 | 49.871
2025-04-19 | 19:54 | 49.873
2025-04-19 | 19:54 | 49.875
2025-04-19 | 19:54 | 49.877
2025-04-19 | 19:54 | 49.877
2025-04-19 | 19:54 | 49.88
2025-04-19 | 19:54 | 49.88
2025-04-19 | 19:54 | 49.881
2025-04-19 | 19:54 | 49.878
2025-04-19 | 19:54 | 49.877
2025-04-19 | 19:54 | 49.879
2025-04-19 | 19:54 | 49.88
2025-04-19 | 19:54 | 49.878
2025-04-19 | 19:54 | 49.881
2025-04-19 | 19:54 | 49.884
2025-04-19 | 19:54 | 49.885
2025-04-19 | 19:54 | 49.886
2025-04-19 | 19:54 | 49.889
2025-04-19 | 19:54 | 49.891
2025-04-19 | 19:54 | 49.889
2025-04-19 | 19:55 | 49.888
2025-04-19 | 19:55 | 49.888
2025-04-19 | 19:55 | 49.886
2025-04-19 | 19:55 | 49.886
2025-04-19 | 19:55 | 49.886
2025-04-19 | 19:55 | 49.887
2025-04-19 | 19:55 | 49.887
2025-04-19 | 19:55 | 49.886
2025-04-19 | 19:55 | 49.886
2025-04-19 | 19:55 | 49.888
2025-04-19 | 19:55 | 49.887
2025-04-19 | 19:55 | 49.886
2025-04-19 | 19:55 | 49.89
2025-04-19 | 19:55 | 49.895
2025-04-19 | 19:55 | 49.896
2025-04-19 | 19:55 | 49.894
2025-04-19 | 19:55 | 49.892
2025-04-19 | 19:55 | 49.893
2025-04-19 | 19:55 | 49.892
2025-04-19 | 19:55 | 49.892
2025-04-19 | 19:55 | 49.892
2025-04-19 | 19:55 | 49.891
2025-04-19 | 19:55 | 49.89
2025-04-19 | 19:55 | 49.888
2025-04-19 | 19:55 | 49.888
2025-04-19 | 19:55 | 49.89
2025-04-19 | 19:55 | 49.891
2025-04-19 | 19:55 | 49.892
2025-04-19 | 19:55 | 49.893
2025-04-19 | 19:55 | 49.894
2025-04-19 | 19:55 | 49.897
2025-04-19 | 19:55 | 49.899
2025-04-19 | 19:55 | 49.898
2025-04-19 | 19:55 | 49.897
2025-04-19 | 19:55 | 49.895
2025-04-19 | 19:55 | 49.895
2025-04-19 | 19:55 | 49.897
2025-04-19 | 19:55 | 49.897
2025-04-19 | 19:55 | 49.897
2025-04-19 | 19:55 | 49.899
2025-04-19 | 19:55 | 49.903
2025-04-19 | 19:55 | 49.905
2025-04-19 | 19:55 | 49.904
2025-04-19 | 19:55 | 49.905
2025-04-19 | 19:55 | 49.908
2025-04-19 | 19:55 | 49.909
2025-04-19 | 19:55 | 49.913
2025-04-19 | 19:55 | 49.915
2025-04-19 | 19:55 | 49.917
2025-04-19 | 19:55 | 49.916
2025-04-19 | 19:55 | 49.913
2025-04-19 | 19:55 | 49.912
2025-04-19 | 19:55 | 49.913
2025-04-19 | 19:55 | 49.912
2025-04-19 | 19:55 | 49.91
2025-04-19 | 19:55 | 49.91
2025-04-19 | 19:55 | 49.911
2025-04-19 | 19:55 | 49.911
2025-04-19 | 19:55 | 49.914
2025-04-19 | 19:56 | 49.917
2025-04-19 | 19:56 | 49.918
2025-04-19 | 19:56 | 49.918
2025-04-19 | 19:56 | 49.919
2025-04-19 | 19:56 | 49.92
2025-04-19 | 19:56 | 49.92
2025-04-19 | 19:56 | 49.919
2025-04-19 | 19:56 | 49.918
2025-04-19 | 19:56 | 49.919
2025-04-19 | 19:56 | 49.92
2025-04-19 | 19:56 | 49.92
2025-04-19 | 19:56 | 49.921
2025-04-19 | 19:56 | 49.924
2025-04-19 | 19:56 | 49.926
2025-04-19 | 19:56 | 49.927
2025-04-19 | 19:56 | 49.929
2025-04-19 | 19:56 | 49.931
2025-04-19 | 19:56 | 49.933
2025-04-19 | 19:56 | 49.932
2025-04-19 | 19:56 | 49.935
2025-04-19 | 19:56 | 49.934
2025-04-19 | 19:56 | 49.932
2025-04-19 | 19:56 | 49.929
2025-04-19 | 19:56 | 49.929
2025-04-19 | 19:56 | 49.928
2025-04-19 | 19:56 | 49.931
2025-04-19 | 19:56 | 49.932
2025-04-19 | 19:56 | 49.933
2025-04-19 | 19:56 | 49.934
2025-04-19 | 19:56 | 49.932
2025-04-19 | 19:56 | 49.931
2025-04-19 | 19:56 | 49.93
2025-04-19 | 19:56 | 49.939
2025-04-19 | 19:56 | 49.947
2025-04-19 | 19:56 | 49.952
2025-04-19 | 19:56 | 49.954
2025-04-19 | 19:56 | 49.954
2025-04-19 | 19:56 | 49.953
2025-04-19 | 19:56 | 49.952
2025-04-19 | 19:56 | 49.951
2025-04-19 | 19:56 | 49.95
2025-04-19 | 19:56 | 49.948
2025-04-19 | 19:56 | 49.948
2025-04-19 | 19:56 | 49.951
2025-04-19 | 19:56 | 49.951
2025-04-19 | 19:56 | 49.954
2025-04-19 | 19:56 | 49.955
2025-04-19 | 19:56 | 49.959
2025-04-19 | 19:56 | 49.96
2025-04-19 | 19:56 | 49.963
2025-04-19 | 19:56 | 49.966
2025-04-19 | 19:56 | 49.968
2025-04-19 | 19:56 | 49.971
2025-04-19 | 19:56 | 49.973
2025-04-19 | 19:56 | 49.974
2025-04-19 | 19:56 | 49.978
2025-04-19 | 19:56 | 49.976
2025-04-19 | 19:56 | 49.972
2025-04-19 | 19:56 | 49.969
2025-04-19 | 19:56 | 49.969
2025-04-19 | 19:56 | 49.967
2025-04-19 | 19:57 | 49.966
2025-04-19 | 19:57 | 49.963
2025-04-19 | 19:57 | 49.962
2025-04-19 | 19:57 | 49.959
2025-04-19 | 19:57 | 49.959
2025-04-19 | 19:57 | 49.96
2025-04-19 | 19:57 | 49.96
2025-04-19 | 19:57 | 49.959
2025-04-19 | 19:57 | 49.956
2025-04-19 | 19:57 | 49.955
2025-04-19 | 19:57 | 49.956
2025-04-19 | 19:57 | 49.958
2025-04-19 | 19:57 | 49.959
2025-04-19 | 19:57 | 49.961
2025-04-19 | 19:57 | 49.962
2025-04-19 | 19:57 | 49.962
2025-04-19 | 19:57 | 49.961
2025-04-19 | 19:57 | 49.962
2025-04-19 | 19:57 | 49.965
2025-04-19 | 19:57 | 49.967
2025-04-19 | 19:57 | 49.967
2025-04-19 | 19:57 | 49.968
2025-04-19 | 19:57 | 49.967
2025-04-19 | 19:57 | 49.967
2025-04-19 | 19:57 | 49.966
2025-04-19 | 19:57 | 49.968
2025-04-19 | 19:57 | 49.968
2025-04-19 | 19:57 | 49.969
2025-04-19 | 19:57 | 49.968
2025-04-19 | 19:57 | 49.968
2025-04-19 | 19:57 | 49.966
2025-04-19 | 19:57 | 49.97
2025-04-19 | 19:57 | 49.976
2025-04-19 | 19:57 | 49.979
2025-04-19 | 19:57 | 49.981
2025-04-19 | 19:57 | 49.983
2025-04-19 | 19:57 | 49.984
2025-04-19 | 19:57 | 49.986
2025-04-19 | 19:57 | 49.985
2025-04-19 | 19:57 | 49.983
2025-04-19 | 19:57 | 49.981
2025-04-19 | 19:57 | 49.982
2025-04-19 | 19:57 | 49.98
2025-04-19 | 19:57 | 49.978
2025-04-19 | 19:57 | 49.976
2025-04-19 | 19:57 | 49.972
2025-04-19 | 19:57 | 49.971
2025-04-19 | 19:57 | 49.972
2025-04-19 | 19:57 | 49.975
2025-04-19 | 19:57 | 49.978
2025-04-19 | 19:57 | 49.98
2025-04-19 | 19:57 | 49.984
2025-04-19 | 19:57 | 49.988
2025-04-19 | 19:57 | 49.99
2025-04-19 | 19:57 | 49.99
2025-04-19 | 19:57 | 49.989
2025-04-19 | 19:57 | 49.99
2025-04-19 | 19:57 | 49.989
2025-04-19 | 19:57 | 49.988
2025-04-19 | 19:58 | 49.989
2025-04-19 | 19:58 | 49.991
2025-04-19 | 19:58 | 49.993
2025-04-19 | 19:58 | 49.995
2025-04-19 | 19:58 | 49.998
2025-04-19 | 19:58 | 50.002
2025-04-19 | 19:58 | 50.005
2025-04-19 | 19:58 | 50.008
2025-04-19 | 19:58 | 50.012
2025-04-19 | 19:58 | 50.015
2025-04-19 | 19:58 | 50.019
2025-04-19 | 19:58 | 50.025
2025-04-19 | 19:58 | 50.03
2025-04-19 | 19:58 | 50.033
2025-04-19 | 19:58 | 50.033
2025-04-19 | 19:58 | 50.035
2025-04-19 | 19:58 | 50.036
2025-04-19 | 19:58 | 50.038
2025-04-19 | 19:58 | 50.036
2025-04-19 | 19:58 | 50.034
2025-04-19 | 19:58 | 50.036
2025-04-19 | 19:58 | 50.037
2025-04-19 | 19:58 | 50.037
2025-04-19 | 19:58 | 50.038
2025-04-19 | 19:58 | 50.04
2025-04-19 | 19:58 | 50.043
2025-04-19 | 19:58 | 50.043
2025-04-19 | 19:58 | 50.044
2025-04-19 | 19:58 | 50.043
2025-04-19 | 19:58 | 50.043
2025-04-19 | 19:58 | 50.041
2025-04-19 | 19:58 | 50.041
2025-04-19 | 19:58 | 50.04
2025-04-19 | 19:58 | 50.04
2025-04-19 | 19:58 | 50.039
2025-04-19 | 19:58 | 50.04
2025-04-19 | 19:58 | 50.042
2025-04-19 | 19:58 | 50.042
2025-04-19 | 19:58 | 50.042
2025-04-19 | 19:58 | 50.045
2025-04-19 | 19:58 | 50.047
2025-04-19 | 19:58 | 50.049
2025-04-19 | 19:58 | 50.053
2025-04-19 | 19:58 | 50.056
2025-04-19 | 19:58 | 50.055
2025-04-19 | 19:58 | 50.053
2025-04-19 | 19:58 | 50.052
2025-04-19 | 19:58 | 50.052
2025-04-19 | 19:58 | 50.051
2025-04-19 | 19:58 | 50.048
2025-04-19 | 19:58 | 50.049
2025-04-19 | 19:58 | 50.054
2025-04-19 | 19:58 | 50.059
2025-04-19 | 19:58 | 50.061
2025-04-19 | 19:58 | 50.066
2025-04-19 | 19:58 | 50.071
2025-04-19 | 19:58 | 50.073
2025-04-19 | 19:58 | 50.072
2025-04-19 | 19:58 | 50.073
2025-04-19 | 19:58 | 50.076
2025-04-19 | 19:58 | 50.077
2025-04-19 | 19:59 | 50.076
2025-04-19 | 19:59 | 50.078
2025-04-19 | 19:59 | 50.08
2025-04-19 | 19:59 | 50.08
2025-04-19 | 19:59 | 50.081

## 20250419-2
In GMT
Date | Time | Freq
2025-04-19 | 20:13 | 49.943 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-04-19 | 20:13 | 49.939 | 222 | BRITNED | 676.211
2025-04-19 | 20:13 | 49.939 | 268 | WBURB-2 | 428.156
2025-04-19 | 20:13 | 49.941 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-04-19 | 20:13 | 49.945 |  | Viking Link | -648.9
2025-04-19 | 20:13 | 49.946 |  | Viking Link | 1398.96
2025-04-19 | 20:13 | 49.947 | 209 | DRAXX-3 | 626.95
2025-04-19 | 20:13 | 49.947 | 154 | CDCL-1 | 391.57
2025-04-19 | 20:13 | 49.949 | 268 | ROCK-1 | 468.495
2025-04-19 | 20:13 | 49.95 | 148 | IFA Bipole1 | 945.473
2025-04-19 | 20:13 | 49.952 | 132 | IFA Bipole1 | 999.1
2025-04-19 | 20:13 | 49.953 | 141 | IFA Bipole2 | 1000
2025-04-19 | 20:13 | 49.952 | 135 | IFA Bipole1 | 996.75
2025-04-19 | 20:13 | 49.951 |  | Viking Link | -780.3
2025-04-19 | 20:13 | 49.95
2025-04-19 | 20:13 | 49.95
2025-04-19 | 20:13 | 49.948
2025-04-19 | 20:13 | 49.947
2025-04-19 | 20:13 | 49.944
2025-04-19 | 20:13 | 49.942 | 130 | HEYM12 | 271.908
2025-04-19 | 20:13 | 49.939 | 228 | HUMR-1 | 303.75
2025-04-19 | 20:13 | 49.936
2025-04-19 | 20:13 | 49.936
2025-04-19 | 20:13 | 49.938
2025-04-19 | 20:13 | 49.938
2025-04-19 | 20:13 | 49.939
2025-04-19 | 20:13 | 49.942
2025-04-19 | 20:13 | 49.943
2025-04-19 | 20:13 | 49.943
2025-04-19 | 20:13 | 49.945
2025-04-19 | 20:13 | 49.944 | 211 | CDCL-1 | 291.5
2025-04-19 | 20:13 | 49.942 | 199 | STAY-2 | 413.125
2025-04-19 | 20:13 | 49.94 | 173 | CDCL-1 | 397.375
2025-04-19 | 20:13 | 49.937 | 248 | SEAB-2 | 361.25
2025-04-19 | 20:13 | 49.938 | 255 | FRANCE | 995.65
2025-04-19 | 20:13 | 49.936 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-04-19 | 20:14 | 49.933
2025-04-19 | 20:14 | 49.931
2025-04-19 | 20:14 | 49.929
2025-04-19 | 20:14 | 49.929
2025-04-19 | 20:14 | 49.925
2025-04-19 | 20:14 | 49.924
2025-04-19 | 20:14 | 49.924
2025-04-19 | 20:14 | 49.923
2025-04-19 | 20:14 | 49.923
2025-04-19 | 20:14 | 49.923
2025-04-19 | 20:14 | 49.926
2025-04-19 | 20:14 | 49.93
2025-04-19 | 20:14 | 49.932
2025-04-19 | 20:14 | 49.934
2025-04-19 | 20:14 | 49.937
2025-04-19 | 20:14 | 49.94
2025-04-19 | 20:14 | 49.94
2025-04-19 | 20:14 | 49.942
2025-04-19 | 20:14 | 49.945
2025-04-19 | 20:14 | 49.946
2025-04-19 | 20:14 | 49.944
2025-04-19 | 20:14 | 49.944
2025-04-19 | 20:14 | 49.943
2025-04-19 | 20:14 | 49.943
2025-04-19 | 20:14 | 49.942
2025-04-19 | 20:14 | 49.895
2025-04-19 | 20:14 | 49.845
2025-04-19 | 20:14 | 49.821
2025-04-19 | 20:14 | 49.795
2025-04-19 | 20:14 | 49.787
2025-04-19 | 20:14 | 49.788
2025-04-19 | 20:14 | 49.788
2025-04-19 | 20:14 | 49.79
2025-04-19 | 20:14 | 49.792
2025-04-19 | 20:14 | 49.792
2025-04-19 | 20:14 | 49.794
2025-04-19 | 20:14 | 49.794
2025-04-19 | 20:14 | 49.794
2025-04-19 | 20:14 | 49.793
2025-04-19 | 20:14 | 49.79
2025-04-19 | 20:14 | 49.786
2025-04-19 | 20:14 | 49.785
2025-04-19 | 20:14 | 49.785
2025-04-19 | 20:14 | 49.782
2025-04-19 | 20:14 | 49.782
2025-04-19 | 20:14 | 49.779
2025-04-19 | 20:14 | 49.777
2025-04-19 | 20:14 | 49.776
2025-04-19 | 20:14 | 49.779
2025-04-19 | 20:14 | 49.78
2025-04-19 | 20:14 | 49.781
2025-04-19 | 20:14 | 49.779
2025-04-19 | 20:14 | 49.781
2025-04-19 | 20:14 | 49.78
2025-04-19 | 20:14 | 49.781
2025-04-19 | 20:14 | 49.782
2025-04-19 | 20:14 | 49.786
2025-04-19 | 20:14 | 49.789
2025-04-19 | 20:14 | 49.789
2025-04-19 | 20:14 | 49.789
2025-04-19 | 20:14 | 49.788
2025-04-19 | 20:15 | 49.789
2025-04-19 | 20:15 | 49.79
2025-04-19 | 20:15 | 49.793
2025-04-19 | 20:15 | 49.796
2025-04-19 | 20:15 | 49.795
2025-04-19 | 20:15 | 49.793
2025-04-19 | 20:15 | 49.794
2025-04-19 | 20:15 | 49.798
2025-04-19 | 20:15 | 49.8
2025-04-19 | 20:15 | 49.8
2025-04-19 | 20:15 | 49.8
2025-04-19 | 20:15 | 49.803
2025-04-19 | 20:15 | 49.804
2025-04-19 | 20:15 | 49.804
2025-04-19 | 20:15 | 49.806
2025-04-19 | 20:15 | 49.808
2025-04-19 | 20:15 | 49.809
2025-04-19 | 20:15 | 49.811
2025-04-19 | 20:15 | 49.814
2025-04-19 | 20:15 | 49.815
2025-04-19 | 20:15 | 49.816
2025-04-19 | 20:15 | 49.818
2025-04-19 | 20:15 | 49.818
2025-04-19 | 20:15 | 49.82
2025-04-19 | 20:15 | 49.82
2025-04-19 | 20:15 | 49.819
2025-04-19 | 20:15 | 49.818
2025-04-19 | 20:15 | 49.816
2025-04-19 | 20:15 | 49.817
2025-04-19 | 20:15 | 49.819
2025-04-19 | 20:15 | 49.817
2025-04-19 | 20:15 | 49.814
2025-04-19 | 20:15 | 49.814
2025-04-19 | 20:15 | 49.816
2025-04-19 | 20:15 | 49.819
2025-04-19 | 20:15 | 49.822
2025-04-19 | 20:15 | 49.823
2025-04-19 | 20:15 | 49.824
2025-04-19 | 20:15 | 49.824
2025-04-19 | 20:15 | 49.823
2025-04-19 | 20:15 | 49.822
2025-04-19 | 20:15 | 49.822
2025-04-19 | 20:15 | 49.825
2025-04-19 | 20:15 | 49.825
2025-04-19 | 20:15 | 49.826
2025-04-19 | 20:15 | 49.826
2025-04-19 | 20:15 | 49.828
2025-04-19 | 20:15 | 49.829
2025-04-19 | 20:15 | 49.828
2025-04-19 | 20:15 | 49.829
2025-04-19 | 20:15 | 49.828
2025-04-19 | 20:15 | 49.828
2025-04-19 | 20:15 | 49.829
2025-04-19 | 20:15 | 49.832
2025-04-19 | 20:15 | 49.832
2025-04-19 | 20:15 | 49.832
2025-04-19 | 20:15 | 49.833
2025-04-19 | 20:15 | 49.835
2025-04-19 | 20:15 | 49.837
2025-04-19 | 20:16 | 49.836
2025-04-19 | 20:16 | 49.837
2025-04-19 | 20:16 | 49.838
2025-04-19 | 20:16 | 49.839
2025-04-19 | 20:16 | 49.84
2025-04-19 | 20:16 | 49.84
2025-04-19 | 20:16 | 49.841
2025-04-19 | 20:16 | 49.842
2025-04-19 | 20:16 | 49.842
2025-04-19 | 20:16 | 49.844
2025-04-19 | 20:16 | 49.848
2025-04-19 | 20:16 | 49.848
2025-04-19 | 20:16 | 49.848
2025-04-19 | 20:16 | 49.848
2025-04-19 | 20:16 | 49.847
2025-04-19 | 20:16 | 49.845
2025-04-19 | 20:16 | 49.843
2025-04-19 | 20:16 | 49.843
2025-04-19 | 20:16 | 49.843
2025-04-19 | 20:16 | 49.843
2025-04-19 | 20:16 | 49.842
2025-04-19 | 20:16 | 49.842
2025-04-19 | 20:16 | 49.842
2025-04-19 | 20:16 | 49.841
2025-04-19 | 20:16 | 49.84
2025-04-19 | 20:16 | 49.841
2025-04-19 | 20:16 | 49.84
2025-04-19 | 20:16 | 49.839
2025-04-19 | 20:16 | 49.838
2025-04-19 | 20:16 | 49.838
2025-04-19 | 20:16 | 49.837
2025-04-19 | 20:16 | 49.836
2025-04-19 | 20:16 | 49.836
2025-04-19 | 20:16 | 49.838
2025-04-19 | 20:16 | 49.838
2025-04-19 | 20:16 | 49.838
2025-04-19 | 20:16 | 49.84
2025-04-19 | 20:16 | 49.84
2025-04-19 | 20:16 | 49.842
2025-04-19 | 20:16 | 49.843
2025-04-19 | 20:16 | 49.846
2025-04-19 | 20:16 | 49.846
2025-04-19 | 20:16 | 49.846
2025-04-19 | 20:16 | 49.846
2025-04-19 | 20:16 | 49.845
2025-04-19 | 20:16 | 49.843
2025-04-19 | 20:16 | 49.84
2025-04-19 | 20:16 | 49.836
2025-04-19 | 20:16 | 49.837
2025-04-19 | 20:16 | 49.836
2025-04-19 | 20:16 | 49.833
2025-04-19 | 20:16 | 49.833
2025-04-19 | 20:16 | 49.835
2025-04-19 | 20:16 | 49.835
2025-04-19 | 20:16 | 49.835
2025-04-19 | 20:16 | 49.836
2025-04-19 | 20:16 | 49.838
2025-04-19 | 20:16 | 49.839
2025-04-19 | 20:16 | 49.84
2025-04-19 | 20:16 | 49.841
2025-04-19 | 20:16 | 49.844
2025-04-19 | 20:17 | 49.845
2025-04-19 | 20:17 | 49.842
2025-04-19 | 20:17 | 49.845
2025-04-19 | 20:17 | 49.846
2025-04-19 | 20:17 | 49.846
2025-04-19 | 20:17 | 49.846
2025-04-19 | 20:17 | 49.847
2025-04-19 | 20:17 | 49.846
2025-04-19 | 20:17 | 49.845
2025-04-19 | 20:17 | 49.84
2025-04-19 | 20:17 | 49.837
2025-04-19 | 20:17 | 49.837
2025-04-19 | 20:17 | 49.835
2025-04-19 | 20:17 | 49.833
2025-04-19 | 20:17 | 49.832
2025-04-19 | 20:17 | 49.831
2025-04-19 | 20:17 | 49.83
2025-04-19 | 20:17 | 49.828
2025-04-19 | 20:17 | 49.829
2025-04-19 | 20:17 | 49.829
2025-04-19 | 20:17 | 49.831
2025-04-19 | 20:17 | 49.832
2025-04-19 | 20:17 | 49.834
2025-04-19 | 20:17 | 49.833
2025-04-19 | 20:17 | 49.83
2025-04-19 | 20:17 | 49.827
2025-04-19 | 20:17 | 49.825
2025-04-19 | 20:17 | 49.825
2025-04-19 | 20:17 | 49.825
2025-04-19 | 20:17 | 49.825
2025-04-19 | 20:17 | 49.826
2025-04-19 | 20:17 | 49.825
2025-04-19 | 20:17 | 49.821
2025-04-19 | 20:17 | 49.822
2025-04-19 | 20:17 | 49.823
2025-04-19 | 20:17 | 49.824
2025-04-19 | 20:17 | 49.821
2025-04-19 | 20:17 | 49.818
2025-04-19 | 20:17 | 49.818
2025-04-19 | 20:17 | 49.818
2025-04-19 | 20:17 | 49.817
2025-04-19 | 20:17 | 49.816
2025-04-19 | 20:17 | 49.818
2025-04-19 | 20:17 | 49.818
2025-04-19 | 20:17 | 49.817
2025-04-19 | 20:17 | 49.82
2025-04-19 | 20:17 | 49.822
2025-04-19 | 20:17 | 49.822
2025-04-19 | 20:17 | 49.822
2025-04-19 | 20:17 | 49.824
2025-04-19 | 20:17 | 49.826
2025-04-19 | 20:17 | 49.824
2025-04-19 | 20:17 | 49.822
2025-04-19 | 20:17 | 49.822
2025-04-19 | 20:17 | 49.823
2025-04-19 | 20:17 | 49.822
2025-04-19 | 20:17 | 49.823
2025-04-19 | 20:17 | 49.824
2025-04-19 | 20:17 | 49.824
2025-04-19 | 20:18 | 49.823
2025-04-19 | 20:18 | 49.821
2025-04-19 | 20:18 | 49.824
2025-04-19 | 20:18 | 49.824
2025-04-19 | 20:18 | 49.826
2025-04-19 | 20:18 | 49.828
2025-04-19 | 20:18 | 49.832
2025-04-19 | 20:18 | 49.834
2025-04-19 | 20:18 | 49.833
2025-04-19 | 20:18 | 49.833
2025-04-19 | 20:18 | 49.834
2025-04-19 | 20:18 | 49.834
2025-04-19 | 20:18 | 49.834
2025-04-19 | 20:18 | 49.834
2025-04-19 | 20:18 | 49.835
2025-04-19 | 20:18 | 49.835
2025-04-19 | 20:18 | 49.834
2025-04-19 | 20:18 | 49.835
2025-04-19 | 20:18 | 49.837
2025-04-19 | 20:18 | 49.836
2025-04-19 | 20:18 | 49.836
2025-04-19 | 20:18 | 49.836
2025-04-19 | 20:18 | 49.835
2025-04-19 | 20:18 | 49.832
2025-04-19 | 20:18 | 49.83
2025-04-19 | 20:18 | 49.832
2025-04-19 | 20:18 | 49.833
2025-04-19 | 20:18 | 49.833
2025-04-19 | 20:18 | 49.828
2025-04-19 | 20:18 | 49.827
2025-04-19 | 20:18 | 49.828
2025-04-19 | 20:18 | 49.827
2025-04-19 | 20:18 | 49.83
2025-04-19 | 20:18 | 49.835
2025-04-19 | 20:18 | 49.836
2025-04-19 | 20:18 | 49.835
2025-04-19 | 20:18 | 49.837
2025-04-19 | 20:18 | 49.84
2025-04-19 | 20:18 | 49.84
2025-04-19 | 20:18 | 49.839
2025-04-19 | 20:18 | 49.837
2025-04-19 | 20:18 | 49.838
2025-04-19 | 20:18 | 49.839
2025-04-19 | 20:18 | 49.84
2025-04-19 | 20:18 | 49.84
2025-04-19 | 20:18 | 49.841
2025-04-19 | 20:18 | 49.841
2025-04-19 | 20:18 | 49.841
2025-04-19 | 20:18 | 49.844
2025-04-19 | 20:18 | 49.846
2025-04-19 | 20:18 | 49.848
2025-04-19 | 20:18 | 49.851
2025-04-19 | 20:18 | 49.853
2025-04-19 | 20:18 | 49.853
2025-04-19 | 20:18 | 49.854
2025-04-19 | 20:18 | 49.856
2025-04-19 | 20:18 | 49.859
2025-04-19 | 20:18 | 49.863
2025-04-19 | 20:18 | 49.864
2025-04-19 | 20:18 | 49.867
2025-04-19 | 20:18 | 49.872
2025-04-19 | 20:19 | 49.873
2025-04-19 | 20:19 | 49.872
2025-04-19 | 20:19 | 49.872
2025-04-19 | 20:19 | 49.875
2025-04-19 | 20:19 | 49.876
2025-04-19 | 20:19 | 49.875
2025-04-19 | 20:19 | 49.875
2025-04-19 | 20:19 | 49.878
2025-04-19 | 20:19 | 49.88
2025-04-19 | 20:19 | 49.88
2025-04-19 | 20:19 | 49.882
2025-04-19 | 20:19 | 49.883
2025-04-19 | 20:19 | 49.888
2025-04-19 | 20:19 | 49.89
2025-04-19 | 20:19 | 49.891
2025-04-19 | 20:19 | 49.893
2025-04-19 | 20:19 | 49.895
2025-04-19 | 20:19 | 49.897
2025-04-19 | 20:19 | 49.898
2025-04-19 | 20:19 | 49.901
2025-04-19 | 20:19 | 49.901
2025-04-19 | 20:19 | 49.901
2025-04-19 | 20:19 | 49.902
2025-04-19 | 20:19 | 49.906
2025-04-19 | 20:19 | 49.906
2025-04-19 | 20:19 | 49.907
2025-04-19 | 20:19 | 49.909
2025-04-19 | 20:19 | 49.911
2025-04-19 | 20:19 | 49.909
2025-04-19 | 20:19 | 49.906
2025-04-19 | 20:19 | 49.904
2025-04-19 | 20:19 | 49.901
2025-04-19 | 20:19 | 49.9
2025-04-19 | 20:19 | 49.899
2025-04-19 | 20:19 | 49.902
2025-04-19 | 20:19 | 49.903
2025-04-19 | 20:19 | 49.904
2025-04-19 | 20:19 | 49.905
2025-04-19 | 20:19 | 49.906
2025-04-19 | 20:19 | 49.905
2025-04-19 | 20:19 | 49.905
2025-04-19 | 20:19 | 49.904
2025-04-19 | 20:19 | 49.907
2025-04-19 | 20:19 | 49.906
2025-04-19 | 20:19 | 49.904
2025-04-19 | 20:19 | 49.904
2025-04-19 | 20:19 | 49.904
2025-04-19 | 20:19 | 49.904
2025-04-19 | 20:19 | 49.902
2025-04-19 | 20:19 | 49.903
2025-04-19 | 20:19 | 49.904
2025-04-19 | 20:19 | 49.905
2025-04-19 | 20:19 | 49.907
2025-04-19 | 20:19 | 49.908
2025-04-19 | 20:19 | 49.909
2025-04-19 | 20:19 | 49.908
2025-04-19 | 20:19 | 49.909
2025-04-19 | 20:19 | 49.912
2025-04-19 | 20:19 | 49.911
2025-04-19 | 20:20 | 49.908
2025-04-19 | 20:20 | 49.907
2025-04-19 | 20:20 | 49.908
2025-04-19 | 20:20 | 49.91
2025-04-19 | 20:20 | 49.909
2025-04-19 | 20:20 | 49.909
2025-04-19 | 20:20 | 49.91
2025-04-19 | 20:20 | 49.91
2025-04-19 | 20:20 | 49.91
2025-04-19 | 20:20 | 49.911
2025-04-19 | 20:20 | 49.91
2025-04-19 | 20:20 | 49.908
2025-04-19 | 20:20 | 49.904
2025-04-19 | 20:20 | 49.9
2025-04-19 | 20:20 | 49.896
2025-04-19 | 20:20 | 49.895
2025-04-19 | 20:20 | 49.895
2025-04-19 | 20:20 | 49.896
2025-04-19 | 20:20 | 49.898
2025-04-19 | 20:20 | 49.897
2025-04-19 | 20:20 | 49.894
2025-04-19 | 20:20 | 49.891
2025-04-19 | 20:20 | 49.891
2025-04-19 | 20:20 | 49.891
2025-04-19 | 20:20 | 49.889
2025-04-19 | 20:20 | 49.888
2025-04-19 | 20:20 | 49.889
2025-04-19 | 20:20 | 49.888
2025-04-19 | 20:20 | 49.887
2025-04-19 | 20:20 | 49.887
2025-04-19 | 20:20 | 49.887
2025-04-19 | 20:20 | 49.883
2025-04-19 | 20:20 | 49.88
2025-04-19 | 20:20 | 49.879
2025-04-19 | 20:20 | 49.881
2025-04-19 | 20:20 | 49.882
2025-04-19 | 20:20 | 49.884
2025-04-19 | 20:20 | 49.887
2025-04-19 | 20:20 | 49.889
2025-04-19 | 20:20 | 49.889
2025-04-19 | 20:20 | 49.888
2025-04-19 | 20:20 | 49.886
2025-04-19 | 20:20 | 49.886
2025-04-19 | 20:20 | 49.886
2025-04-19 | 20:20 | 49.888
2025-04-19 | 20:20 | 49.89
2025-04-19 | 20:20 | 49.89
2025-04-19 | 20:20 | 49.889
2025-04-19 | 20:20 | 49.888
2025-04-19 | 20:20 | 49.889
2025-04-19 | 20:20 | 49.89
2025-04-19 | 20:20 | 49.888
2025-04-19 | 20:20 | 49.889
2025-04-19 | 20:20 | 49.889
2025-04-19 | 20:20 | 49.89
2025-04-19 | 20:20 | 49.888
2025-04-19 | 20:20 | 49.888
2025-04-19 | 20:20 | 49.889
2025-04-19 | 20:20 | 49.89
2025-04-19 | 20:20 | 49.889
2025-04-19 | 20:20 | 49.891
2025-04-19 | 20:21 | 49.891
2025-04-19 | 20:21 | 49.889
2025-04-19 | 20:21 | 49.89
2025-04-19 | 20:21 | 49.893
2025-04-19 | 20:21 | 49.894
2025-04-19 | 20:21 | 49.891
2025-04-19 | 20:21 | 49.889
2025-04-19 | 20:21 | 49.891
2025-04-19 | 20:21 | 49.89
2025-04-19 | 20:21 | 49.89
2025-04-19 | 20:21 | 49.89
2025-04-19 | 20:21 | 49.893
2025-04-19 | 20:21 | 49.893
2025-04-19 | 20:21 | 49.893
2025-04-19 | 20:21 | 49.895
2025-04-19 | 20:21 | 49.895
2025-04-19 | 20:21 | 49.892
2025-04-19 | 20:21 | 49.89
2025-04-19 | 20:21 | 49.889
2025-04-19 | 20:21 | 49.888
2025-04-19 | 20:21 | 49.887
2025-04-19 | 20:21 | 49.885
2025-04-19 | 20:21 | 49.886
2025-04-19 | 20:21 | 49.886
2025-04-19 | 20:21 | 49.882
2025-04-19 | 20:21 | 49.88
2025-04-19 | 20:21 | 49.881
2025-04-19 | 20:21 | 49.882
2025-04-19 | 20:21 | 49.883
2025-04-19 | 20:21 | 49.882
2025-04-19 | 20:21 | 49.881
2025-04-19 | 20:21 | 49.882
2025-04-19 | 20:21 | 49.883
2025-04-19 | 20:21 | 49.884
2025-04-19 | 20:21 | 49.884
2025-04-19 | 20:21 | 49.885
2025-04-19 | 20:21 | 49.88
2025-04-19 | 20:21 | 49.88
2025-04-19 | 20:21 | 49.881
2025-04-19 | 20:21 | 49.883
2025-04-19 | 20:21 | 49.882
2025-04-19 | 20:21 | 49.882
2025-04-19 | 20:21 | 49.882
2025-04-19 | 20:21 | 49.881
2025-04-19 | 20:21 | 49.881
2025-04-19 | 20:21 | 49.881
2025-04-19 | 20:21 | 49.881
2025-04-19 | 20:21 | 49.881
2025-04-19 | 20:21 | 49.88
2025-04-19 | 20:21 | 49.883
2025-04-19 | 20:21 | 49.887
2025-04-19 | 20:21 | 49.888
2025-04-19 | 20:21 | 49.889
2025-04-19 | 20:21 | 49.89
2025-04-19 | 20:21 | 49.89
2025-04-19 | 20:21 | 49.89
2025-04-19 | 20:21 | 49.889
2025-04-19 | 20:21 | 49.889
2025-04-19 | 20:21 | 49.891
2025-04-19 | 20:22 | 49.89
2025-04-19 | 20:22 | 49.89
2025-04-19 | 20:22 | 49.89
2025-04-19 | 20:22 | 49.892
2025-04-19 | 20:22 | 49.893
2025-04-19 | 20:22 | 49.891
2025-04-19 | 20:22 | 49.891
2025-04-19 | 20:22 | 49.891
2025-04-19 | 20:22 | 49.89
2025-04-19 | 20:22 | 49.89
2025-04-19 | 20:22 | 49.892
2025-04-19 | 20:22 | 49.89
2025-04-19 | 20:22 | 49.888
2025-04-19 | 20:22 | 49.886
2025-04-19 | 20:22 | 49.887
2025-04-19 | 20:22 | 49.891
2025-04-19 | 20:22 | 49.893
2025-04-19 | 20:22 | 49.893
2025-04-19 | 20:22 | 49.897
2025-04-19 | 20:22 | 49.899
2025-04-19 | 20:22 | 49.901
2025-04-19 | 20:22 | 49.902
2025-04-19 | 20:22 | 49.906
2025-04-19 | 20:22 | 49.908
2025-04-19 | 20:22 | 49.911
2025-04-19 | 20:22 | 49.913
2025-04-19 | 20:22 | 49.914
2025-04-19 | 20:22 | 49.912
2025-04-19 | 20:22 | 49.905
2025-04-19 | 20:22 | 49.902
2025-04-19 | 20:22 | 49.9
2025-04-19 | 20:22 | 49.899
2025-04-19 | 20:22 | 49.899
2025-04-19 | 20:22 | 49.9
2025-04-19 | 20:22 | 49.898
2025-04-19 | 20:22 | 49.897
2025-04-19 | 20:22 | 49.896
2025-04-19 | 20:22 | 49.896
2025-04-19 | 20:22 | 49.896
2025-04-19 | 20:22 | 49.896
2025-04-19 | 20:22 | 49.897
2025-04-19 | 20:22 | 49.899
2025-04-19 | 20:22 | 49.901
2025-04-19 | 20:22 | 49.899
2025-04-19 | 20:22 | 49.9
2025-04-19 | 20:22 | 49.902
2025-04-19 | 20:22 | 49.899
2025-04-19 | 20:22 | 49.894
2025-04-19 | 20:22 | 49.891
2025-04-19 | 20:22 | 49.89
2025-04-19 | 20:22 | 49.891
2025-04-19 | 20:22 | 49.891
2025-04-19 | 20:22 | 49.891
2025-04-19 | 20:22 | 49.893
2025-04-19 | 20:22 | 49.894
2025-04-19 | 20:22 | 49.892
2025-04-19 | 20:22 | 49.892
2025-04-19 | 20:22 | 49.892
2025-04-19 | 20:22 | 49.891
2025-04-19 | 20:22 | 49.889
2025-04-19 | 20:22 | 49.889
2025-04-19 | 20:23 | 49.89
2025-04-19 | 20:23 | 49.888
2025-04-19 | 20:23 | 49.885
2025-04-19 | 20:23 | 49.884
2025-04-19 | 20:23 | 49.883
2025-04-19 | 20:23 | 49.882
2025-04-19 | 20:23 | 49.877
2025-04-19 | 20:23 | 49.878
2025-04-19 | 20:23 | 49.879
2025-04-19 | 20:23 | 49.881
2025-04-19 | 20:23 | 49.88
2025-04-19 | 20:23 | 49.881
2025-04-19 | 20:23 | 49.883
2025-04-19 | 20:23 | 49.882
2025-04-19 | 20:23 | 49.882
2025-04-19 | 20:23 | 49.883
2025-04-19 | 20:23 | 49.884
2025-04-19 | 20:23 | 49.885
2025-04-19 | 20:23 | 49.886
2025-04-19 | 20:23 | 49.887
2025-04-19 | 20:23 | 49.886
2025-04-19 | 20:23 | 49.885
2025-04-19 | 20:23 | 49.884
2025-04-19 | 20:23 | 49.883
2025-04-19 | 20:23 | 49.883
2025-04-19 | 20:23 | 49.882
2025-04-19 | 20:23 | 49.881
2025-04-19 | 20:23 | 49.881
2025-04-19 | 20:23 | 49.879
2025-04-19 | 20:23 | 49.879
2025-04-19 | 20:23 | 49.873
2025-04-19 | 20:23 | 49.867
2025-04-19 | 20:23 | 49.865
2025-04-19 | 20:23 | 49.866
2025-04-19 | 20:23 | 49.866
2025-04-19 | 20:23 | 49.864
2025-04-19 | 20:23 | 49.863
2025-04-19 | 20:23 | 49.864
2025-04-19 | 20:23 | 49.866
2025-04-19 | 20:23 | 49.866
2025-04-19 | 20:23 | 49.865
2025-04-19 | 20:23 | 49.863
2025-04-19 | 20:23 | 49.861
2025-04-19 | 20:23 | 49.859
2025-04-19 | 20:23 | 49.859
2025-04-19 | 20:23 | 49.862
2025-04-19 | 20:23 | 49.862
2025-04-19 | 20:23 | 49.862
2025-04-19 | 20:23 | 49.861
2025-04-19 | 20:23 | 49.86
2025-04-19 | 20:23 | 49.86
2025-04-19 | 20:23 | 49.859
2025-04-19 | 20:23 | 49.859
2025-04-19 | 20:23 | 49.859
2025-04-19 | 20:23 | 49.859
2025-04-19 | 20:23 | 49.858
2025-04-19 | 20:23 | 49.857
2025-04-19 | 20:23 | 49.861
2025-04-19 | 20:23 | 49.864
2025-04-19 | 20:24 | 49.863
2025-04-19 | 20:24 | 49.864
2025-04-19 | 20:24 | 49.863
2025-04-19 | 20:24 | 49.863
2025-04-19 | 20:24 | 49.861
2025-04-19 | 20:24 | 49.861
2025-04-19 | 20:24 | 49.863
2025-04-19 | 20:24 | 49.864
2025-04-19 | 20:24 | 49.863
2025-04-19 | 20:24 | 49.861
2025-04-19 | 20:24 | 49.862
2025-04-19 | 20:24 | 49.865
2025-04-19 | 20:24 | 49.867
2025-04-19 | 20:24 | 49.869
2025-04-19 | 20:24 | 49.87
2025-04-19 | 20:24 | 49.869
2025-04-19 | 20:24 | 49.867
2025-04-19 | 20:24 | 49.867
2025-04-19 | 20:24 | 49.869
2025-04-19 | 20:24 | 49.872
2025-04-19 | 20:24 | 49.873
2025-04-19 | 20:24 | 49.874
2025-04-19 | 20:24 | 49.875
2025-04-19 | 20:24 | 49.876
2025-04-19 | 20:24 | 49.877
2025-04-19 | 20:24 | 49.879
2025-04-19 | 20:24 | 49.879
2025-04-19 | 20:24 | 49.878
2025-04-19 | 20:24 | 49.876
2025-04-19 | 20:24 | 49.877
2025-04-19 | 20:24 | 49.876
2025-04-19 | 20:24 | 49.876
2025-04-19 | 20:24 | 49.875
2025-04-19 | 20:24 | 49.874
2025-04-19 | 20:24 | 49.873
2025-04-19 | 20:24 | 49.874
2025-04-19 | 20:24 | 49.873
2025-04-19 | 20:24 | 49.874
2025-04-19 | 20:24 | 49.873
2025-04-19 | 20:24 | 49.872
2025-04-19 | 20:24 | 49.87
2025-04-19 | 20:24 | 49.872
2025-04-19 | 20:24 | 49.873
2025-04-19 | 20:24 | 49.874
2025-04-19 | 20:24 | 49.875
2025-04-19 | 20:24 | 49.875
2025-04-19 | 20:24 | 49.875
2025-04-19 | 20:24 | 49.872
2025-04-19 | 20:24 | 49.871
2025-04-19 | 20:24 | 49.871
2025-04-19 | 20:24 | 49.869
2025-04-19 | 20:24 | 49.867
2025-04-19 | 20:24 | 49.867
2025-04-19 | 20:24 | 49.868
2025-04-19 | 20:24 | 49.867
2025-04-19 | 20:24 | 49.867
2025-04-19 | 20:24 | 49.868
2025-04-19 | 20:24 | 49.866
2025-04-19 | 20:24 | 49.864
2025-04-19 | 20:24 | 49.861
2025-04-19 | 20:24 | 49.861
2025-04-19 | 20:25 | 49.862
2025-04-19 | 20:25 | 49.862
2025-04-19 | 20:25 | 49.861
2025-04-19 | 20:25 | 49.86
2025-04-19 | 20:25 | 49.862
2025-04-19 | 20:25 | 49.861
2025-04-19 | 20:25 | 49.86
2025-04-19 | 20:25 | 49.859
2025-04-19 | 20:25 | 49.861
2025-04-19 | 20:25 | 49.863
2025-04-19 | 20:25 | 49.863
2025-04-19 | 20:25 | 49.864
2025-04-19 | 20:25 | 49.865
2025-04-19 | 20:25 | 49.864
2025-04-19 | 20:25 | 49.862
2025-04-19 | 20:25 | 49.863
2025-04-19 | 20:25 | 49.863
2025-04-19 | 20:25 | 49.862
2025-04-19 | 20:25 | 49.861
2025-04-19 | 20:25 | 49.864
2025-04-19 | 20:25 | 49.865
2025-04-19 | 20:25 | 49.862
2025-04-19 | 20:25 | 49.861
2025-04-19 | 20:25 | 49.861
2025-04-19 | 20:25 | 49.861
2025-04-19 | 20:25 | 49.859
2025-04-19 | 20:25 | 49.857
2025-04-19 | 20:25 | 49.855
2025-04-19 | 20:25 | 49.853
2025-04-19 | 20:25 | 49.851
2025-04-19 | 20:25 | 49.851
2025-04-19 | 20:25 | 49.854
2025-04-19 | 20:25 | 49.853
2025-04-19 | 20:25 | 49.851
2025-04-19 | 20:25 | 49.852
2025-04-19 | 20:25 | 49.855
2025-04-19 | 20:25 | 49.855
2025-04-19 | 20:25 | 49.854
2025-04-19 | 20:25 | 49.854
2025-04-19 | 20:25 | 49.853
2025-04-19 | 20:25 | 49.855
2025-04-19 | 20:25 | 49.858
2025-04-19 | 20:25 | 49.861
2025-04-19 | 20:25 | 49.861
2025-04-19 | 20:25 | 49.859
2025-04-19 | 20:25 | 49.859
2025-04-19 | 20:25 | 49.862
2025-04-19 | 20:25 | 49.863
2025-04-19 | 20:25 | 49.864
2025-04-19 | 20:25 | 49.862
2025-04-19 | 20:25 | 49.862
2025-04-19 | 20:25 | 49.864
2025-04-19 | 20:25 | 49.864
2025-04-19 | 20:25 | 49.865
2025-04-19 | 20:25 | 49.866
2025-04-19 | 20:25 | 49.866
2025-04-19 | 20:25 | 49.863
2025-04-19 | 20:25 | 49.861
2025-04-19 | 20:25 | 49.863
2025-04-19 | 20:26 | 49.863
2025-04-19 | 20:26 | 49.863
2025-04-19 | 20:26 | 49.864
2025-04-19 | 20:26 | 49.866
2025-04-19 | 20:26 | 49.865
2025-04-19 | 20:26 | 49.862
2025-04-19 | 20:26 | 49.864
2025-04-19 | 20:26 | 49.867
2025-04-19 | 20:26 | 49.868
2025-04-19 | 20:26 | 49.868
2025-04-19 | 20:26 | 49.868
2025-04-19 | 20:26 | 49.87
2025-04-19 | 20:26 | 49.872
2025-04-19 | 20:26 | 49.872
2025-04-19 | 20:26 | 49.872
2025-04-19 | 20:26 | 49.873
2025-04-19 | 20:26 | 49.873
2025-04-19 | 20:26 | 49.875
2025-04-19 | 20:26 | 49.877
2025-04-19 | 20:26 | 49.877
2025-04-19 | 20:26 | 49.875
2025-04-19 | 20:26 | 49.873
2025-04-19 | 20:26 | 49.873
2025-04-19 | 20:26 | 49.874
2025-04-19 | 20:26 | 49.874
2025-04-19 | 20:26 | 49.874
2025-04-19 | 20:26 | 49.876
2025-04-19 | 20:26 | 49.879
2025-04-19 | 20:26 | 49.878
2025-04-19 | 20:26 | 49.878
2025-04-19 | 20:26 | 49.876
2025-04-19 | 20:26 | 49.874
2025-04-19 | 20:26 | 49.871
2025-04-19 | 20:26 | 49.871
2025-04-19 | 20:26 | 49.871
2025-04-19 | 20:26 | 49.872
2025-04-19 | 20:26 | 49.869
2025-04-19 | 20:26 | 49.867
2025-04-19 | 20:26 | 49.867
2025-04-19 | 20:26 | 49.866
2025-04-19 | 20:26 | 49.865
2025-04-19 | 20:26 | 49.867
2025-04-19 | 20:26 | 49.869
2025-04-19 | 20:26 | 49.869
2025-04-19 | 20:26 | 49.866
2025-04-19 | 20:26 | 49.865
2025-04-19 | 20:26 | 49.864
2025-04-19 | 20:26 | 49.865
2025-04-19 | 20:26 | 49.864
2025-04-19 | 20:26 | 49.865
2025-04-19 | 20:26 | 49.865
2025-04-19 | 20:26 | 49.864
2025-04-19 | 20:26 | 49.864
2025-04-19 | 20:26 | 49.866
2025-04-19 | 20:26 | 49.865
2025-04-19 | 20:26 | 49.865
2025-04-19 | 20:26 | 49.866
2025-04-19 | 20:26 | 49.865
2025-04-19 | 20:26 | 49.863
2025-04-19 | 20:26 | 49.862
2025-04-19 | 20:26 | 49.863
2025-04-19 | 20:27 | 49.861
2025-04-19 | 20:27 | 49.858
2025-04-19 | 20:27 | 49.857
2025-04-19 | 20:27 | 49.857
2025-04-19 | 20:27 | 49.858
2025-04-19 | 20:27 | 49.858
2025-04-19 | 20:27 | 49.858
2025-04-19 | 20:27 | 49.857
2025-04-19 | 20:27 | 49.859
2025-04-19 | 20:27 | 49.86
2025-04-19 | 20:27 | 49.862
2025-04-19 | 20:27 | 49.863
2025-04-19 | 20:27 | 49.866
2025-04-19 | 20:27 | 49.867
2025-04-19 | 20:27 | 49.866
2025-04-19 | 20:27 | 49.866
2025-04-19 | 20:27 | 49.865
2025-04-19 | 20:27 | 49.863
2025-04-19 | 20:27 | 49.863
2025-04-19 | 20:27 | 49.865
2025-04-19 | 20:27 | 49.868
2025-04-19 | 20:27 | 49.868
2025-04-19 | 20:27 | 49.871
2025-04-19 | 20:27 | 49.873
2025-04-19 | 20:27 | 49.874
2025-04-19 | 20:27 | 49.874
2025-04-19 | 20:27 | 49.873
2025-04-19 | 20:27 | 49.873
2025-04-19 | 20:27 | 49.876
2025-04-19 | 20:27 | 49.874
2025-04-19 | 20:27 | 49.874
2025-04-19 | 20:27 | 49.88
2025-04-19 | 20:27 | 49.884
2025-04-19 | 20:27 | 49.884
2025-04-19 | 20:27 | 49.885
2025-04-19 | 20:27 | 49.889
2025-04-19 | 20:27 | 49.889
2025-04-19 | 20:27 | 49.889
2025-04-19 | 20:27 | 49.89
2025-04-19 | 20:27 | 49.891
2025-04-19 | 20:27 | 49.893
2025-04-19 | 20:27 | 49.894
2025-04-19 | 20:27 | 49.895
2025-04-19 | 20:27 | 49.895
2025-04-19 | 20:27 | 49.892
2025-04-19 | 20:27 | 49.889
2025-04-19 | 20:27 | 49.889
2025-04-19 | 20:27 | 49.889
2025-04-19 | 20:27 | 49.887
2025-04-19 | 20:27 | 49.887
2025-04-19 | 20:27 | 49.891
2025-04-19 | 20:27 | 49.892
2025-04-19 | 20:27 | 49.892
2025-04-19 | 20:27 | 49.891
2025-04-19 | 20:27 | 49.892
2025-04-19 | 20:27 | 49.892
2025-04-19 | 20:27 | 49.896
2025-04-19 | 20:27 | 49.899
2025-04-19 | 20:27 | 49.902
2025-04-19 | 20:28 | 49.903
2025-04-19 | 20:28 | 49.904
2025-04-19 | 20:28 | 49.904
2025-04-19 | 20:28 | 49.905
2025-04-19 | 20:28 | 49.904
2025-04-19 | 20:28 | 49.902
2025-04-19 | 20:28 | 49.902
2025-04-19 | 20:28 | 49.905
2025-04-19 | 20:28 | 49.906
2025-04-19 | 20:28 | 49.908
2025-04-19 | 20:28 | 49.91
2025-04-19 | 20:28 | 49.911
2025-04-19 | 20:28 | 49.913
2025-04-19 | 20:28 | 49.916
2025-04-19 | 20:28 | 49.918
2025-04-19 | 20:28 | 49.923
2025-04-19 | 20:28 | 49.925
2025-04-19 | 20:28 | 49.927
2025-04-19 | 20:28 | 49.928
2025-04-19 | 20:28 | 49.93
2025-04-19 | 20:28 | 49.928
2025-04-19 | 20:28 | 49.927
2025-04-19 | 20:28 | 49.928
2025-04-19 | 20:28 | 49.928
2025-04-19 | 20:28 | 49.928
2025-04-19 | 20:28 | 49.925
2025-04-19 | 20:28 | 49.924
2025-04-19 | 20:28 | 49.923
2025-04-19 | 20:28 | 49.921
2025-04-19 | 20:28 | 49.92
2025-04-19 | 20:28 | 49.919
2025-04-19 | 20:28 | 49.917
2025-04-19 | 20:28 | 49.915
2025-04-19 | 20:28 | 49.916
2025-04-19 | 20:28 | 49.917
2025-04-19 | 20:28 | 49.916
2025-04-19 | 20:28 | 49.912
2025-04-19 | 20:28 | 49.911
2025-04-19 | 20:28 | 49.911
2025-04-19 | 20:28 | 49.913
2025-04-19 | 20:28 | 49.913
2025-04-19 | 20:28 | 49.916
2025-04-19 | 20:28 | 49.919
2025-04-19 | 20:28 | 49.919
2025-04-19 | 20:28 | 49.918
2025-04-19 | 20:28 | 49.92
2025-04-19 | 20:28 | 49.922
2025-04-19 | 20:28 | 49.919
2025-04-19 | 20:28 | 49.918
2025-04-19 | 20:28 | 49.919
2025-04-19 | 20:28 | 49.921
2025-04-19 | 20:28 | 49.922
2025-04-19 | 20:28 | 49.922
2025-04-19 | 20:28 | 49.922
2025-04-19 | 20:28 | 49.92
2025-04-19 | 20:28 | 49.918
2025-04-19 | 20:28 | 49.919
2025-04-19 | 20:28 | 49.92
2025-04-19 | 20:28 | 49.919
2025-04-19 | 20:28 | 49.918
2025-04-19 | 20:28 | 49.918
2025-04-19 | 20:29 | 49.92
2025-04-19 | 20:29 | 49.919
2025-04-19 | 20:29 | 49.917
2025-04-19 | 20:29 | 49.919
2025-04-19 | 20:29 | 49.922
2025-04-19 | 20:29 | 49.925
2025-04-19 | 20:29 | 49.925
2025-04-19 | 20:29 | 49.928
2025-04-19 | 20:29 | 49.93
2025-04-19 | 20:29 | 49.93
2025-04-19 | 20:29 | 49.929
2025-04-19 | 20:29 | 49.932
2025-04-19 | 20:29 | 49.932
2025-04-19 | 20:29 | 49.932
2025-04-19 | 20:29 | 49.932
2025-04-19 | 20:29 | 49.935
2025-04-19 | 20:29 | 49.936
2025-04-19 | 20:29 | 49.936
2025-04-19 | 20:29 | 49.934
2025-04-19 | 20:29 | 49.935
2025-04-19 | 20:29 | 49.936
2025-04-19 | 20:29 | 49.938
2025-04-19 | 20:29 | 49.939
2025-04-19 | 20:29 | 49.942
2025-04-19 | 20:29 | 49.943
2025-04-19 | 20:29 | 49.942
2025-04-19 | 20:29 | 49.938
2025-04-19 | 20:29 | 49.937
2025-04-19 | 20:29 | 49.937
2025-04-19 | 20:29 | 49.934
2025-04-19 | 20:29 | 49.932
2025-04-19 | 20:29 | 49.937
2025-04-19 | 20:29 | 49.944
2025-04-19 | 20:29 | 49.949
2025-04-19 | 20:29 | 49.954
2025-04-19 | 20:29 | 49.958
2025-04-19 | 20:29 | 49.961
2025-04-19 | 20:29 | 49.96
2025-04-19 | 20:29 | 49.961
2025-04-19 | 20:29 | 49.962
2025-04-19 | 20:29 | 49.963
2025-04-19 | 20:29 | 49.962
2025-04-19 | 20:29 | 49.965
2025-04-19 | 20:29 | 49.968
2025-04-19 | 20:29 | 49.97
2025-04-19 | 20:29 | 49.971
2025-04-19 | 20:29 | 49.973
2025-04-19 | 20:29 | 49.975
2025-04-19 | 20:29 | 49.975
2025-04-19 | 20:29 | 49.974
2025-04-19 | 20:29 | 49.974
2025-04-19 | 20:29 | 49.972
2025-04-19 | 20:29 | 49.969
2025-04-19 | 20:29 | 49.966
2025-04-19 | 20:29 | 49.967
2025-04-19 | 20:29 | 49.969
2025-04-19 | 20:29 | 49.973
2025-04-19 | 20:29 | 49.977
2025-04-19 | 20:29 | 49.982
2025-04-19 | 20:30 | 49.988
2025-04-19 | 20:30 | 49.992
2025-04-19 | 20:30 | 49.996
2025-04-19 | 20:30 | 50.004
2025-04-19 | 20:30 | 50.011
2025-04-19 | 20:30 | 50.018
2025-04-19 | 20:30 | 50.022
2025-04-19 | 20:30 | 50.027
2025-04-19 | 20:30 | 50.028
2025-04-19 | 20:30 | 50.029
2025-04-19 | 20:30 | 50.028
2025-04-19 | 20:30 | 50.03
2025-04-19 | 20:30 | 50.03
2025-04-19 | 20:30 | 50.029
2025-04-19 | 20:30 | 50.029
2025-04-19 | 20:30 | 50.029
2025-04-19 | 20:30 | 50.028
2025-04-19 | 20:30 | 50.028
2025-04-19 | 20:30 | 50.031
2025-04-19 | 20:30 | 50.031
2025-04-19 | 20:30 | 50.03
2025-04-19 | 20:30 | 50.027
2025-04-19 | 20:30 | 50.024
2025-04-19 | 20:30 | 50.022
2025-04-19 | 20:30 | 50.021
2025-04-19 | 20:30 | 50.022
2025-04-19 | 20:30 | 50.019
2025-04-19 | 20:30 | 50.015
2025-04-19 | 20:30 | 50.014
2025-04-19 | 20:30 | 50.014
2025-04-19 | 20:30 | 50.012
2025-04-19 | 20:30 | 50.012
2025-04-19 | 20:30 | 50.02
2025-04-19 | 20:30 | 50.026
2025-04-19 | 20:30 | 50.032
2025-04-19 | 20:30 | 50.035
2025-04-19 | 20:30 | 50.039
2025-04-19 | 20:30 | 50.039
2025-04-19 | 20:30 | 50.037
2025-04-19 | 20:30 | 50.038
2025-04-19 | 20:30 | 50.043
2025-04-19 | 20:30 | 50.047
2025-04-19 | 20:30 | 50.05
2025-04-19 | 20:30 | 50.051
2025-04-19 | 20:30 | 50.052
2025-04-19 | 20:30 | 50.054
2025-04-19 | 20:30 | 50.052
2025-04-19 | 20:30 | 50.051
2025-04-19 | 20:30 | 50.048
2025-04-19 | 20:30 | 50.048
2025-04-19 | 20:30 | 50.048
2025-04-19 | 20:30 | 50.048
2025-04-19 | 20:30 | 50.049
2025-04-19 | 20:30 | 50.05
2025-04-19 | 20:30 | 50.052
2025-04-19 | 20:30 | 50.053
2025-04-19 | 20:30 | 50.054
2025-04-19 | 20:30 | 50.057
2025-04-19 | 20:30 | 50.059
2025-04-19 | 20:30 | 50.059
2025-04-19 | 20:30 | 50.061
2025-04-19 | 20:31 | 50.061
2025-04-19 | 20:31 | 50.062
2025-04-19 | 20:31 | 50.063

## 20250423-1
In GMT
Date | Time | Freq
2025-04-23 | 17:14 | 50.019 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-04-23 | 17:14 | 50.019 | 222 | BRITNED | 676.211
2025-04-23 | 17:14 | 50.019 | 268 | WBURB-2 | 428.156
2025-04-23 | 17:14 | 50.019 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-04-23 | 17:14 | 50.022 |  | Viking Link | -648.9
2025-04-23 | 17:14 | 50.021 |  | Viking Link | 1398.96
2025-04-23 | 17:14 | 50.022 | 209 | DRAXX-3 | 626.95
2025-04-23 | 17:14 | 50.023 | 154 | CDCL-1 | 391.57
2025-04-23 | 17:14 | 50.028 | 268 | ROCK-1 | 468.495
2025-04-23 | 17:14 | 50.033 | 148 | IFA Bipole1 | 945.473
2025-04-23 | 17:14 | 50.036 | 132 | IFA Bipole1 | 999.1
2025-04-23 | 17:14 | 50.035 | 141 | IFA Bipole2 | 1000
2025-04-23 | 17:14 | 50.032 | 135 | IFA Bipole1 | 996.75
2025-04-23 | 17:14 | 50.03 |  | Viking Link | -780.3
2025-04-23 | 17:14 | 50.028
2025-04-23 | 17:14 | 50.026
2025-04-23 | 17:14 | 50.025
2025-04-23 | 17:14 | 50.022
2025-04-23 | 17:14 | 50.019
2025-04-23 | 17:14 | 50.016 | 130 | HEYM12 | 271.908
2025-04-23 | 17:14 | 50.017 | 228 | HUMR-1 | 303.75
2025-04-23 | 17:14 | 50.016
2025-04-23 | 17:14 | 50.017
2025-04-23 | 17:14 | 50.019
2025-04-23 | 17:14 | 50.017
2025-04-23 | 17:14 | 50.017
2025-04-23 | 17:14 | 50.019
2025-04-23 | 17:14 | 50.018
2025-04-23 | 17:14 | 50.018
2025-04-23 | 17:14 | 50.018
2025-04-23 | 17:14 | 50.016 | 211 | CDCL-1 | 291.5
2025-04-23 | 17:14 | 50.014 | 199 | STAY-2 | 413.125
2025-04-23 | 17:14 | 50.011 | 173 | CDCL-1 | 397.375
2025-04-23 | 17:14 | 50.005 | 248 | SEAB-2 | 361.25
2025-04-23 | 17:14 | 50 | 255 | FRANCE | 995.65
2025-04-23 | 17:14 | 49.997 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-04-23 | 17:15 | 49.987
2025-04-23 | 17:15 | 49.98
2025-04-23 | 17:15 | 49.976
2025-04-23 | 17:15 | 49.971
2025-04-23 | 17:15 | 49.969
2025-04-23 | 17:15 | 49.968
2025-04-23 | 17:15 | 49.966
2025-04-23 | 17:15 | 49.967
2025-04-23 | 17:15 | 49.965
2025-04-23 | 17:15 | 49.966
2025-04-23 | 17:15 | 49.966
2025-04-23 | 17:15 | 49.969
2025-04-23 | 17:15 | 49.971
2025-04-23 | 17:15 | 49.973
2025-04-23 | 17:15 | 49.976
2025-04-23 | 17:15 | 49.98
2025-04-23 | 17:15 | 49.984
2025-04-23 | 17:15 | 49.988
2025-04-23 | 17:15 | 49.989
2025-04-23 | 17:15 | 49.988
2025-04-23 | 17:15 | 49.988
2025-04-23 | 17:15 | 49.988
2025-04-23 | 17:15 | 49.986
2025-04-23 | 17:15 | 49.986
2025-04-23 | 17:15 | 49.986
2025-04-23 | 17:15 | 49.942
2025-04-23 | 17:15 | 49.885
2025-04-23 | 17:15 | 49.848
2025-04-23 | 17:15 | 49.829
2025-04-23 | 17:15 | 49.82
2025-04-23 | 17:15 | 49.816
2025-04-23 | 17:15 | 49.821
2025-04-23 | 17:15 | 49.833
2025-04-23 | 17:15 | 49.842
2025-04-23 | 17:15 | 49.845
2025-04-23 | 17:15 | 49.847
2025-04-23 | 17:15 | 49.846
2025-04-23 | 17:15 | 49.845
2025-04-23 | 17:15 | 49.841
2025-04-23 | 17:15 | 49.841
2025-04-23 | 17:15 | 49.841
2025-04-23 | 17:15 | 49.84
2025-04-23 | 17:15 | 49.839
2025-04-23 | 17:15 | 49.838
2025-04-23 | 17:15 | 49.838
2025-04-23 | 17:15 | 49.839
2025-04-23 | 17:15 | 49.837
2025-04-23 | 17:15 | 49.836
2025-04-23 | 17:15 | 49.835
2025-04-23 | 17:15 | 49.837
2025-04-23 | 17:15 | 49.837
2025-04-23 | 17:15 | 49.838
2025-04-23 | 17:15 | 49.837
2025-04-23 | 17:15 | 49.837
2025-04-23 | 17:15 | 49.836
2025-04-23 | 17:15 | 49.837
2025-04-23 | 17:15 | 49.835
2025-04-23 | 17:15 | 49.835
2025-04-23 | 17:15 | 49.836
2025-04-23 | 17:16 | 49.836
2025-04-23 | 17:16 | 49.834
2025-04-23 | 17:16 | 49.833
2025-04-23 | 17:16 | 49.832
2025-04-23 | 17:16 | 49.832
2025-04-23 | 17:16 | 49.833
2025-04-23 | 17:16 | 49.832
2025-04-23 | 17:16 | 49.832
2025-04-23 | 17:16 | 49.832
2025-04-23 | 17:16 | 49.832
2025-04-23 | 17:16 | 49.834
2025-04-23 | 17:16 | 49.832
2025-04-23 | 17:16 | 49.834
2025-04-23 | 17:16 | 49.835
2025-04-23 | 17:16 | 49.838
2025-04-23 | 17:16 | 49.839
2025-04-23 | 17:16 | 49.841
2025-04-23 | 17:16 | 49.844
2025-04-23 | 17:16 | 49.846
2025-04-23 | 17:16 | 49.848
2025-04-23 | 17:16 | 49.849
2025-04-23 | 17:16 | 49.849
2025-04-23 | 17:16 | 49.849
2025-04-23 | 17:16 | 49.848
2025-04-23 | 17:16 | 49.849
2025-04-23 | 17:16 | 49.848
2025-04-23 | 17:16 | 49.847
2025-04-23 | 17:16 | 49.845
2025-04-23 | 17:16 | 49.843
2025-04-23 | 17:16 | 49.844
2025-04-23 | 17:16 | 49.841
2025-04-23 | 17:16 | 49.841
2025-04-23 | 17:16 | 49.844
2025-04-23 | 17:16 | 49.845
2025-04-23 | 17:16 | 49.846
2025-04-23 | 17:16 | 49.847
2025-04-23 | 17:16 | 49.847
2025-04-23 | 17:16 | 49.846
2025-04-23 | 17:16 | 49.847
2025-04-23 | 17:16 | 49.848
2025-04-23 | 17:16 | 49.85
2025-04-23 | 17:16 | 49.848
2025-04-23 | 17:16 | 49.848
2025-04-23 | 17:16 | 49.849
2025-04-23 | 17:16 | 49.85
2025-04-23 | 17:16 | 49.85
2025-04-23 | 17:16 | 49.852
2025-04-23 | 17:16 | 49.85
2025-04-23 | 17:16 | 49.848
2025-04-23 | 17:16 | 49.844
2025-04-23 | 17:16 | 49.842
2025-04-23 | 17:16 | 49.838
2025-04-23 | 17:16 | 49.836
2025-04-23 | 17:16 | 49.836
2025-04-23 | 17:16 | 49.835
2025-04-23 | 17:16 | 49.836
2025-04-23 | 17:16 | 49.835
2025-04-23 | 17:16 | 49.837
2025-04-23 | 17:16 | 49.836
2025-04-23 | 17:16 | 49.834
2025-04-23 | 17:16 | 49.836
2025-04-23 | 17:17 | 49.835
2025-04-23 | 17:17 | 49.837
2025-04-23 | 17:17 | 49.835
2025-04-23 | 17:17 | 49.838
2025-04-23 | 17:17 | 49.84
2025-04-23 | 17:17 | 49.842
2025-04-23 | 17:17 | 49.843
2025-04-23 | 17:17 | 49.845
2025-04-23 | 17:17 | 49.845
2025-04-23 | 17:17 | 49.846
2025-04-23 | 17:17 | 49.845
2025-04-23 | 17:17 | 49.846
2025-04-23 | 17:17 | 49.848
2025-04-23 | 17:17 | 49.85
2025-04-23 | 17:17 | 49.852
2025-04-23 | 17:17 | 49.855
2025-04-23 | 17:17 | 49.855
2025-04-23 | 17:17 | 49.858
2025-04-23 | 17:17 | 49.858
2025-04-23 | 17:17 | 49.859
2025-04-23 | 17:17 | 49.859
2025-04-23 | 17:17 | 49.86
2025-04-23 | 17:17 | 49.859
2025-04-23 | 17:17 | 49.859
2025-04-23 | 17:17 | 49.858
2025-04-23 | 17:17 | 49.859
2025-04-23 | 17:17 | 49.86
2025-04-23 | 17:17 | 49.86
2025-04-23 | 17:17 | 49.86
2025-04-23 | 17:17 | 49.858
2025-04-23 | 17:17 | 49.856
2025-04-23 | 17:17 | 49.853
2025-04-23 | 17:17 | 49.852
2025-04-23 | 17:17 | 49.849
2025-04-23 | 17:17 | 49.847
2025-04-23 | 17:17 | 49.847
2025-04-23 | 17:17 | 49.846
2025-04-23 | 17:17 | 49.846
2025-04-23 | 17:17 | 49.848
2025-04-23 | 17:17 | 49.851
2025-04-23 | 17:17 | 49.849
2025-04-23 | 17:17 | 49.849
2025-04-23 | 17:17 | 49.852
2025-04-23 | 17:17 | 49.854
2025-04-23 | 17:17 | 49.855
2025-04-23 | 17:17 | 49.853
2025-04-23 | 17:17 | 49.852
2025-04-23 | 17:17 | 49.85
2025-04-23 | 17:17 | 49.852
2025-04-23 | 17:17 | 49.853
2025-04-23 | 17:17 | 49.854
2025-04-23 | 17:17 | 49.852
2025-04-23 | 17:17 | 49.854
2025-04-23 | 17:17 | 49.855
2025-04-23 | 17:17 | 49.854
2025-04-23 | 17:17 | 49.855
2025-04-23 | 17:17 | 49.853
2025-04-23 | 17:17 | 49.854
2025-04-23 | 17:17 | 49.855
2025-04-23 | 17:18 | 49.856
2025-04-23 | 17:18 | 49.858
2025-04-23 | 17:18 | 49.859
2025-04-23 | 17:18 | 49.859
2025-04-23 | 17:18 | 49.86
2025-04-23 | 17:18 | 49.86
2025-04-23 | 17:18 | 49.861
2025-04-23 | 17:18 | 49.86
2025-04-23 | 17:18 | 49.862
2025-04-23 | 17:18 | 49.862
2025-04-23 | 17:18 | 49.862
2025-04-23 | 17:18 | 49.862
2025-04-23 | 17:18 | 49.862
2025-04-23 | 17:18 | 49.862
2025-04-23 | 17:18 | 49.86
2025-04-23 | 17:18 | 49.858
2025-04-23 | 17:18 | 49.859
2025-04-23 | 17:18 | 49.859
2025-04-23 | 17:18 | 49.859
2025-04-23 | 17:18 | 49.861
2025-04-23 | 17:18 | 49.862
2025-04-23 | 17:18 | 49.861
2025-04-23 | 17:18 | 49.862
2025-04-23 | 17:18 | 49.862
2025-04-23 | 17:18 | 49.861
2025-04-23 | 17:18 | 49.86
2025-04-23 | 17:18 | 49.861
2025-04-23 | 17:18 | 49.86
2025-04-23 | 17:18 | 49.861
2025-04-23 | 17:18 | 49.86
2025-04-23 | 17:18 | 49.86
2025-04-23 | 17:18 | 49.859
2025-04-23 | 17:18 | 49.858
2025-04-23 | 17:18 | 49.858
2025-04-23 | 17:18 | 49.859
2025-04-23 | 17:18 | 49.861
2025-04-23 | 17:18 | 49.862
2025-04-23 | 17:18 | 49.863
2025-04-23 | 17:18 | 49.864
2025-04-23 | 17:18 | 49.865
2025-04-23 | 17:18 | 49.866
2025-04-23 | 17:18 | 49.866
2025-04-23 | 17:18 | 49.865
2025-04-23 | 17:18 | 49.867
2025-04-23 | 17:18 | 49.868
2025-04-23 | 17:18 | 49.87
2025-04-23 | 17:18 | 49.871
2025-04-23 | 17:18 | 49.871
2025-04-23 | 17:18 | 49.871
2025-04-23 | 17:18 | 49.869
2025-04-23 | 17:18 | 49.867
2025-04-23 | 17:18 | 49.866
2025-04-23 | 17:18 | 49.867
2025-04-23 | 17:18 | 49.868
2025-04-23 | 17:18 | 49.869
2025-04-23 | 17:18 | 49.871
2025-04-23 | 17:18 | 49.872
2025-04-23 | 17:18 | 49.875
2025-04-23 | 17:18 | 49.877
2025-04-23 | 17:18 | 49.88
2025-04-23 | 17:18 | 49.881
2025-04-23 | 17:19 | 49.879
2025-04-23 | 17:19 | 49.876
2025-04-23 | 17:19 | 49.876
2025-04-23 | 17:19 | 49.876
2025-04-23 | 17:19 | 49.877
2025-04-23 | 17:19 | 49.878
2025-04-23 | 17:19 | 49.88
2025-04-23 | 17:19 | 49.881
2025-04-23 | 17:19 | 49.881
2025-04-23 | 17:19 | 49.881
2025-04-23 | 17:19 | 49.881
2025-04-23 | 17:19 | 49.88
2025-04-23 | 17:19 | 49.88
2025-04-23 | 17:19 | 49.88
2025-04-23 | 17:19 | 49.88
2025-04-23 | 17:19 | 49.88
2025-04-23 | 17:19 | 49.88
2025-04-23 | 17:19 | 49.881
2025-04-23 | 17:19 | 49.883
2025-04-23 | 17:19 | 49.885
2025-04-23 | 17:19 | 49.886
2025-04-23 | 17:19 | 49.89
2025-04-23 | 17:19 | 49.889
2025-04-23 | 17:19 | 49.893
2025-04-23 | 17:19 | 49.892
2025-04-23 | 17:19 | 49.892
2025-04-23 | 17:19 | 49.89
2025-04-23 | 17:19 | 49.889
2025-04-23 | 17:19 | 49.89
2025-04-23 | 17:19 | 49.889
2025-04-23 | 17:19 | 49.888
2025-04-23 | 17:19 | 49.891
2025-04-23 | 17:19 | 49.891
2025-04-23 | 17:19 | 49.894
2025-04-23 | 17:19 | 49.894
2025-04-23 | 17:19 | 49.895
2025-04-23 | 17:19 | 49.894
2025-04-23 | 17:19 | 49.892
2025-04-23 | 17:19 | 49.89
2025-04-23 | 17:19 | 49.888
2025-04-23 | 17:19 | 49.886
2025-04-23 | 17:19 | 49.887
2025-04-23 | 17:19 | 49.888
2025-04-23 | 17:19 | 49.89
2025-04-23 | 17:19 | 49.889
2025-04-23 | 17:19 | 49.888
2025-04-23 | 17:19 | 49.886
2025-04-23 | 17:19 | 49.886
2025-04-23 | 17:19 | 49.885
2025-04-23 | 17:19 | 49.886
2025-04-23 | 17:19 | 49.887
2025-04-23 | 17:19 | 49.887
2025-04-23 | 17:19 | 49.888
2025-04-23 | 17:19 | 49.888
2025-04-23 | 17:19 | 49.889
2025-04-23 | 17:19 | 49.89
2025-04-23 | 17:19 | 49.891
2025-04-23 | 17:19 | 49.889
2025-04-23 | 17:19 | 49.888
2025-04-23 | 17:20 | 49.887
2025-04-23 | 17:20 | 49.887
2025-04-23 | 17:20 | 49.888
2025-04-23 | 17:20 | 49.889
2025-04-23 | 17:20 | 49.891
2025-04-23 | 17:20 | 49.889
2025-04-23 | 17:20 | 49.887
2025-04-23 | 17:20 | 49.887
2025-04-23 | 17:20 | 49.886
2025-04-23 | 17:20 | 49.888
2025-04-23 | 17:20 | 49.889
2025-04-23 | 17:20 | 49.887
2025-04-23 | 17:20 | 49.885
2025-04-23 | 17:20 | 49.884
2025-04-23 | 17:20 | 49.885
2025-04-23 | 17:20 | 49.886
2025-04-23 | 17:20 | 49.885
2025-04-23 | 17:20 | 49.886
2025-04-23 | 17:20 | 49.887
2025-04-23 | 17:20 | 49.888
2025-04-23 | 17:20 | 49.892
2025-04-23 | 17:20 | 49.892
2025-04-23 | 17:20 | 49.895
2025-04-23 | 17:20 | 49.895
2025-04-23 | 17:20 | 49.897
2025-04-23 | 17:20 | 49.894
2025-04-23 | 17:20 | 49.895
2025-04-23 | 17:20 | 49.892
2025-04-23 | 17:20 | 49.893
2025-04-23 | 17:20 | 49.895
2025-04-23 | 17:20 | 49.895
2025-04-23 | 17:20 | 49.897
2025-04-23 | 17:20 | 49.895
2025-04-23 | 17:20 | 49.896
2025-04-23 | 17:20 | 49.896
2025-04-23 | 17:20 | 49.897
2025-04-23 | 17:20 | 49.896
2025-04-23 | 17:20 | 49.895
2025-04-23 | 17:20 | 49.893
2025-04-23 | 17:20 | 49.89
2025-04-23 | 17:20 | 49.889
2025-04-23 | 17:20 | 49.887
2025-04-23 | 17:20 | 49.886
2025-04-23 | 17:20 | 49.886
2025-04-23 | 17:20 | 49.886
2025-04-23 | 17:20 | 49.886
2025-04-23 | 17:20 | 49.888
2025-04-23 | 17:20 | 49.888
2025-04-23 | 17:20 | 49.89
2025-04-23 | 17:20 | 49.89
2025-04-23 | 17:20 | 49.89
2025-04-23 | 17:20 | 49.889
2025-04-23 | 17:20 | 49.888
2025-04-23 | 17:20 | 49.89
2025-04-23 | 17:20 | 49.889
2025-04-23 | 17:20 | 49.888
2025-04-23 | 17:20 | 49.885
2025-04-23 | 17:20 | 49.884
2025-04-23 | 17:20 | 49.881
2025-04-23 | 17:20 | 49.881
2025-04-23 | 17:20 | 49.881
2025-04-23 | 17:21 | 49.883
2025-04-23 | 17:21 | 49.881
2025-04-23 | 17:21 | 49.884
2025-04-23 | 17:21 | 49.886
2025-04-23 | 17:21 | 49.888
2025-04-23 | 17:21 | 49.889
2025-04-23 | 17:21 | 49.888
2025-04-23 | 17:21 | 49.888
2025-04-23 | 17:21 | 49.889
2025-04-23 | 17:21 | 49.889
2025-04-23 | 17:21 | 49.888
2025-04-23 | 17:21 | 49.887
2025-04-23 | 17:21 | 49.886
2025-04-23 | 17:21 | 49.887
2025-04-23 | 17:21 | 49.889
2025-04-23 | 17:21 | 49.889
2025-04-23 | 17:21 | 49.89
2025-04-23 | 17:21 | 49.89
2025-04-23 | 17:21 | 49.891
2025-04-23 | 17:21 | 49.892
2025-04-23 | 17:21 | 49.893
2025-04-23 | 17:21 | 49.893
2025-04-23 | 17:21 | 49.89
2025-04-23 | 17:21 | 49.891
2025-04-23 | 17:21 | 49.891
2025-04-23 | 17:21 | 49.891
2025-04-23 | 17:21 | 49.893
2025-04-23 | 17:21 | 49.896
2025-04-23 | 17:21 | 49.897
2025-04-23 | 17:21 | 49.897
2025-04-23 | 17:21 | 49.895
2025-04-23 | 17:21 | 49.892
2025-04-23 | 17:21 | 49.891
2025-04-23 | 17:21 | 49.892
2025-04-23 | 17:21 | 49.894
2025-04-23 | 17:21 | 49.897
2025-04-23 | 17:21 | 49.896
2025-04-23 | 17:21 | 49.895
2025-04-23 | 17:21 | 49.892
2025-04-23 | 17:21 | 49.89
2025-04-23 | 17:21 | 49.889
2025-04-23 | 17:21 | 49.889
2025-04-23 | 17:21 | 49.889
2025-04-23 | 17:21 | 49.889
2025-04-23 | 17:21 | 49.891
2025-04-23 | 17:21 | 49.892
2025-04-23 | 17:21 | 49.894
2025-04-23 | 17:21 | 49.897
2025-04-23 | 17:21 | 49.895
2025-04-23 | 17:21 | 49.895
2025-04-23 | 17:21 | 49.892
2025-04-23 | 17:21 | 49.891
2025-04-23 | 17:21 | 49.889
2025-04-23 | 17:21 | 49.89
2025-04-23 | 17:21 | 49.891
2025-04-23 | 17:21 | 49.89
2025-04-23 | 17:21 | 49.892
2025-04-23 | 17:21 | 49.89
2025-04-23 | 17:21 | 49.891
2025-04-23 | 17:22 | 49.891
2025-04-23 | 17:22 | 49.89
2025-04-23 | 17:22 | 49.889
2025-04-23 | 17:22 | 49.889
2025-04-23 | 17:22 | 49.887
2025-04-23 | 17:22 | 49.887
2025-04-23 | 17:22 | 49.888
2025-04-23 | 17:22 | 49.888
2025-04-23 | 17:22 | 49.893
2025-04-23 | 17:22 | 49.893
2025-04-23 | 17:22 | 49.892
2025-04-23 | 17:22 | 49.893
2025-04-23 | 17:22 | 49.895
2025-04-23 | 17:22 | 49.898
2025-04-23 | 17:22 | 49.897
2025-04-23 | 17:22 | 49.898
2025-04-23 | 17:22 | 49.896
2025-04-23 | 17:22 | 49.892
2025-04-23 | 17:22 | 49.891
2025-04-23 | 17:22 | 49.892
2025-04-23 | 17:22 | 49.891
2025-04-23 | 17:22 | 49.889
2025-04-23 | 17:22 | 49.889
2025-04-23 | 17:22 | 49.89
2025-04-23 | 17:22 | 49.892
2025-04-23 | 17:22 | 49.893
2025-04-23 | 17:22 | 49.891
2025-04-23 | 17:22 | 49.889
2025-04-23 | 17:22 | 49.888
2025-04-23 | 17:22 | 49.886
2025-04-23 | 17:22 | 49.885
2025-04-23 | 17:22 | 49.884
2025-04-23 | 17:22 | 49.885
2025-04-23 | 17:22 | 49.888
2025-04-23 | 17:22 | 49.887
2025-04-23 | 17:22 | 49.888
2025-04-23 | 17:22 | 49.888
2025-04-23 | 17:22 | 49.887
2025-04-23 | 17:22 | 49.883
2025-04-23 | 17:22 | 49.881
2025-04-23 | 17:22 | 49.881
2025-04-23 | 17:22 | 49.882
2025-04-23 | 17:22 | 49.882
2025-04-23 | 17:22 | 49.883
2025-04-23 | 17:22 | 49.882
2025-04-23 | 17:22 | 49.883
2025-04-23 | 17:22 | 49.882
2025-04-23 | 17:22 | 49.882
2025-04-23 | 17:22 | 49.882
2025-04-23 | 17:22 | 49.885
2025-04-23 | 17:22 | 49.886
2025-04-23 | 17:22 | 49.884
2025-04-23 | 17:22 | 49.887
2025-04-23 | 17:22 | 49.888
2025-04-23 | 17:22 | 49.892
2025-04-23 | 17:22 | 49.895
2025-04-23 | 17:22 | 49.897
2025-04-23 | 17:22 | 49.899
2025-04-23 | 17:22 | 49.899
2025-04-23 | 17:22 | 49.9
2025-04-23 | 17:22 | 49.902
2025-04-23 | 17:23 | 49.902
2025-04-23 | 17:23 | 49.904
2025-04-23 | 17:23 | 49.906
2025-04-23 | 17:23 | 49.906
2025-04-23 | 17:23 | 49.907
2025-04-23 | 17:23 | 49.909
2025-04-23 | 17:23 | 49.906
2025-04-23 | 17:23 | 49.904
2025-04-23 | 17:23 | 49.902
2025-04-23 | 17:23 | 49.9
2025-04-23 | 17:23 | 49.9
2025-04-23 | 17:23 | 49.899
2025-04-23 | 17:23 | 49.9
2025-04-23 | 17:23 | 49.9
2025-04-23 | 17:23 | 49.9
2025-04-23 | 17:23 | 49.899
2025-04-23 | 17:23 | 49.898
2025-04-23 | 17:23 | 49.898
2025-04-23 | 17:23 | 49.898
2025-04-23 | 17:23 | 49.897
2025-04-23 | 17:23 | 49.898
2025-04-23 | 17:23 | 49.897
2025-04-23 | 17:23 | 49.896
2025-04-23 | 17:23 | 49.894
2025-04-23 | 17:23 | 49.895
2025-04-23 | 17:23 | 49.897
2025-04-23 | 17:23 | 49.899
2025-04-23 | 17:23 | 49.899
2025-04-23 | 17:23 | 49.898
2025-04-23 | 17:23 | 49.9
2025-04-23 | 17:23 | 49.902
2025-04-23 | 17:23 | 49.904
2025-04-23 | 17:23 | 49.907
2025-04-23 | 17:23 | 49.909
2025-04-23 | 17:23 | 49.912
2025-04-23 | 17:23 | 49.913
2025-04-23 | 17:23 | 49.913
2025-04-23 | 17:23 | 49.914
2025-04-23 | 17:23 | 49.912
2025-04-23 | 17:23 | 49.91
2025-04-23 | 17:23 | 49.909
2025-04-23 | 17:23 | 49.907
2025-04-23 | 17:23 | 49.906
2025-04-23 | 17:23 | 49.906
2025-04-23 | 17:23 | 49.904
2025-04-23 | 17:23 | 49.903
2025-04-23 | 17:23 | 49.899
2025-04-23 | 17:23 | 49.895
2025-04-23 | 17:23 | 49.894
2025-04-23 | 17:23 | 49.891
2025-04-23 | 17:23 | 49.892
2025-04-23 | 17:23 | 49.894
2025-04-23 | 17:23 | 49.896
2025-04-23 | 17:23 | 49.899
2025-04-23 | 17:23 | 49.9
2025-04-23 | 17:23 | 49.9
2025-04-23 | 17:23 | 49.903
2025-04-23 | 17:23 | 49.904
2025-04-23 | 17:23 | 49.908
2025-04-23 | 17:24 | 49.908
2025-04-23 | 17:24 | 49.909
2025-04-23 | 17:24 | 49.909
2025-04-23 | 17:24 | 49.909
2025-04-23 | 17:24 | 49.91
2025-04-23 | 17:24 | 49.91
2025-04-23 | 17:24 | 49.91
2025-04-23 | 17:24 | 49.909
2025-04-23 | 17:24 | 49.907
2025-04-23 | 17:24 | 49.906
2025-04-23 | 17:24 | 49.905
2025-04-23 | 17:24 | 49.907
2025-04-23 | 17:24 | 49.906
2025-04-23 | 17:24 | 49.909
2025-04-23 | 17:24 | 49.91
2025-04-23 | 17:24 | 49.908
2025-04-23 | 17:24 | 49.907
2025-04-23 | 17:24 | 49.906
2025-04-23 | 17:24 | 49.903
2025-04-23 | 17:24 | 49.903
2025-04-23 | 17:24 | 49.901
2025-04-23 | 17:24 | 49.901
2025-04-23 | 17:24 | 49.9
2025-04-23 | 17:24 | 49.902
2025-04-23 | 17:24 | 49.904
2025-04-23 | 17:24 | 49.903
2025-04-23 | 17:24 | 49.902
2025-04-23 | 17:24 | 49.902
2025-04-23 | 17:24 | 49.899
2025-04-23 | 17:24 | 49.896
2025-04-23 | 17:24 | 49.895
2025-04-23 | 17:24 | 49.894
2025-04-23 | 17:24 | 49.895
2025-04-23 | 17:24 | 49.897
2025-04-23 | 17:24 | 49.898
2025-04-23 | 17:24 | 49.896
2025-04-23 | 17:24 | 49.893
2025-04-23 | 17:24 | 49.893
2025-04-23 | 17:24 | 49.893
2025-04-23 | 17:24 | 49.892
2025-04-23 | 17:24 | 49.892
2025-04-23 | 17:24 | 49.891
2025-04-23 | 17:24 | 49.892
2025-04-23 | 17:24 | 49.89
2025-04-23 | 17:24 | 49.892
2025-04-23 | 17:24 | 49.89
2025-04-23 | 17:24 | 49.891
2025-04-23 | 17:24 | 49.89
2025-04-23 | 17:24 | 49.891
2025-04-23 | 17:24 | 49.892
2025-04-23 | 17:24 | 49.894
2025-04-23 | 17:24 | 49.891
2025-04-23 | 17:24 | 49.89
2025-04-23 | 17:24 | 49.888
2025-04-23 | 17:24 | 49.888
2025-04-23 | 17:24 | 49.886
2025-04-23 | 17:24 | 49.886
2025-04-23 | 17:24 | 49.886
2025-04-23 | 17:24 | 49.887
2025-04-23 | 17:24 | 49.888
2025-04-23 | 17:24 | 49.888
2025-04-23 | 17:25 | 49.887
2025-04-23 | 17:25 | 49.886
2025-04-23 | 17:25 | 49.887
2025-04-23 | 17:25 | 49.886
2025-04-23 | 17:25 | 49.888
2025-04-23 | 17:25 | 49.888
2025-04-23 | 17:25 | 49.888
2025-04-23 | 17:25 | 49.888
2025-04-23 | 17:25 | 49.891
2025-04-23 | 17:25 | 49.891
2025-04-23 | 17:25 | 49.892
2025-04-23 | 17:25 | 49.89
2025-04-23 | 17:25 | 49.89
2025-04-23 | 17:25 | 49.889
2025-04-23 | 17:25 | 49.891
2025-04-23 | 17:25 | 49.89
2025-04-23 | 17:25 | 49.891
2025-04-23 | 17:25 | 49.89
2025-04-23 | 17:25 | 49.89
2025-04-23 | 17:25 | 49.89
2025-04-23 | 17:25 | 49.891
2025-04-23 | 17:25 | 49.893
2025-04-23 | 17:25 | 49.893
2025-04-23 | 17:25 | 49.894
2025-04-23 | 17:25 | 49.897
2025-04-23 | 17:25 | 49.897
2025-04-23 | 17:25 | 49.898
2025-04-23 | 17:25 | 49.9
2025-04-23 | 17:25 | 49.901
2025-04-23 | 17:25 | 49.903
2025-04-23 | 17:25 | 49.902
2025-04-23 | 17:25 | 49.902
2025-04-23 | 17:25 | 49.902
2025-04-23 | 17:25 | 49.902
2025-04-23 | 17:25 | 49.899
2025-04-23 | 17:25 | 49.895
2025-04-23 | 17:25 | 49.893
2025-04-23 | 17:25 | 49.89
2025-04-23 | 17:25 | 49.89
2025-04-23 | 17:25 | 49.886
2025-04-23 | 17:25 | 49.883
2025-04-23 | 17:25 | 49.881
2025-04-23 | 17:25 | 49.879
2025-04-23 | 17:25 | 49.881
2025-04-23 | 17:25 | 49.881
2025-04-23 | 17:25 | 49.883
2025-04-23 | 17:25 | 49.883
2025-04-23 | 17:25 | 49.883
2025-04-23 | 17:25 | 49.885
2025-04-23 | 17:25 | 49.885
2025-04-23 | 17:25 | 49.888
2025-04-23 | 17:25 | 49.888
2025-04-23 | 17:25 | 49.888
2025-04-23 | 17:25 | 49.887
2025-04-23 | 17:25 | 49.888
2025-04-23 | 17:25 | 49.887
2025-04-23 | 17:25 | 49.888
2025-04-23 | 17:25 | 49.89
2025-04-23 | 17:25 | 49.892
2025-04-23 | 17:26 | 49.891
2025-04-23 | 17:26 | 49.888
2025-04-23 | 17:26 | 49.889
2025-04-23 | 17:26 | 49.888
2025-04-23 | 17:26 | 49.889
2025-04-23 | 17:26 | 49.888
2025-04-23 | 17:26 | 49.89
2025-04-23 | 17:26 | 49.891
2025-04-23 | 17:26 | 49.894
2025-04-23 | 17:26 | 49.897
2025-04-23 | 17:26 | 49.9
2025-04-23 | 17:26 | 49.9
2025-04-23 | 17:26 | 49.899
2025-04-23 | 17:26 | 49.899
2025-04-23 | 17:26 | 49.898
2025-04-23 | 17:26 | 49.897
2025-04-23 | 17:26 | 49.896
2025-04-23 | 17:26 | 49.895
2025-04-23 | 17:26 | 49.892
2025-04-23 | 17:26 | 49.893
2025-04-23 | 17:26 | 49.894
2025-04-23 | 17:26 | 49.894
2025-04-23 | 17:26 | 49.893
2025-04-23 | 17:26 | 49.895
2025-04-23 | 17:26 | 49.894
2025-04-23 | 17:26 | 49.895
2025-04-23 | 17:26 | 49.893
2025-04-23 | 17:26 | 49.895
2025-04-23 | 17:26 | 49.894
2025-04-23 | 17:26 | 49.893
2025-04-23 | 17:26 | 49.893
2025-04-23 | 17:26 | 49.89
2025-04-23 | 17:26 | 49.887
2025-04-23 | 17:26 | 49.883
2025-04-23 | 17:26 | 49.881
2025-04-23 | 17:26 | 49.883
2025-04-23 | 17:26 | 49.883
2025-04-23 | 17:26 | 49.886
2025-04-23 | 17:26 | 49.884
2025-04-23 | 17:26 | 49.885
2025-04-23 | 17:26 | 49.887
2025-04-23 | 17:26 | 49.886
2025-04-23 | 17:26 | 49.886
2025-04-23 | 17:26 | 49.887
2025-04-23 | 17:26 | 49.889
2025-04-23 | 17:26 | 49.889
2025-04-23 | 17:26 | 49.891
2025-04-23 | 17:26 | 49.89
2025-04-23 | 17:26 | 49.888
2025-04-23 | 17:26 | 49.889
2025-04-23 | 17:26 | 49.888
2025-04-23 | 17:26 | 49.889
2025-04-23 | 17:26 | 49.889
2025-04-23 | 17:26 | 49.888
2025-04-23 | 17:26 | 49.887
2025-04-23 | 17:26 | 49.886
2025-04-23 | 17:26 | 49.889
2025-04-23 | 17:26 | 49.89
2025-04-23 | 17:26 | 49.891
2025-04-23 | 17:26 | 49.892
2025-04-23 | 17:26 | 49.892
2025-04-23 | 17:27 | 49.892
2025-04-23 | 17:27 | 49.893
2025-04-23 | 17:27 | 49.893
2025-04-23 | 17:27 | 49.893
2025-04-23 | 17:27 | 49.892
2025-04-23 | 17:27 | 49.893
2025-04-23 | 17:27 | 49.893
2025-04-23 | 17:27 | 49.894
2025-04-23 | 17:27 | 49.894
2025-04-23 | 17:27 | 49.892
2025-04-23 | 17:27 | 49.89
2025-04-23 | 17:27 | 49.889
2025-04-23 | 17:27 | 49.889
2025-04-23 | 17:27 | 49.889
2025-04-23 | 17:27 | 49.889
2025-04-23 | 17:27 | 49.893
2025-04-23 | 17:27 | 49.894
2025-04-23 | 17:27 | 49.893
2025-04-23 | 17:27 | 49.891
2025-04-23 | 17:27 | 49.888
2025-04-23 | 17:27 | 49.886
2025-04-23 | 17:27 | 49.884
2025-04-23 | 17:27 | 49.882
2025-04-23 | 17:27 | 49.883
2025-04-23 | 17:27 | 49.883
2025-04-23 | 17:27 | 49.884
2025-04-23 | 17:27 | 49.883
2025-04-23 | 17:27 | 49.883
2025-04-23 | 17:27 | 49.884
2025-04-23 | 17:27 | 49.884
2025-04-23 | 17:27 | 49.883
2025-04-23 | 17:27 | 49.884
2025-04-23 | 17:27 | 49.885
2025-04-23 | 17:27 | 49.885
2025-04-23 | 17:27 | 49.884
2025-04-23 | 17:27 | 49.883
2025-04-23 | 17:27 | 49.882
2025-04-23 | 17:27 | 49.884
2025-04-23 | 17:27 | 49.884
2025-04-23 | 17:27 | 49.885
2025-04-23 | 17:27 | 49.882
2025-04-23 | 17:27 | 49.879
2025-04-23 | 17:27 | 49.879
2025-04-23 | 17:27 | 49.879
2025-04-23 | 17:27 | 49.88
2025-04-23 | 17:27 | 49.879
2025-04-23 | 17:27 | 49.879
2025-04-23 | 17:27 | 49.879
2025-04-23 | 17:27 | 49.881
2025-04-23 | 17:27 | 49.882
2025-04-23 | 17:27 | 49.881
2025-04-23 | 17:27 | 49.881
2025-04-23 | 17:27 | 49.882
2025-04-23 | 17:27 | 49.884
2025-04-23 | 17:27 | 49.886
2025-04-23 | 17:27 | 49.888
2025-04-23 | 17:27 | 49.89
2025-04-23 | 17:27 | 49.888
2025-04-23 | 17:27 | 49.888
2025-04-23 | 17:28 | 49.885
2025-04-23 | 17:28 | 49.886
2025-04-23 | 17:28 | 49.888
2025-04-23 | 17:28 | 49.888
2025-04-23 | 17:28 | 49.889
2025-04-23 | 17:28 | 49.891
2025-04-23 | 17:28 | 49.892
2025-04-23 | 17:28 | 49.893
2025-04-23 | 17:28 | 49.892
2025-04-23 | 17:28 | 49.892
2025-04-23 | 17:28 | 49.892
2025-04-23 | 17:28 | 49.89
2025-04-23 | 17:28 | 49.89
2025-04-23 | 17:28 | 49.891
2025-04-23 | 17:28 | 49.892
2025-04-23 | 17:28 | 49.894
2025-04-23 | 17:28 | 49.894
2025-04-23 | 17:28 | 49.895
2025-04-23 | 17:28 | 49.893
2025-04-23 | 17:28 | 49.889
2025-04-23 | 17:28 | 49.888
2025-04-23 | 17:28 | 49.883
2025-04-23 | 17:28 | 49.882
2025-04-23 | 17:28 | 49.882
2025-04-23 | 17:28 | 49.878
2025-04-23 | 17:28 | 49.876
2025-04-23 | 17:28 | 49.873
2025-04-23 | 17:28 | 49.872
2025-04-23 | 17:28 | 49.871
2025-04-23 | 17:28 | 49.872
2025-04-23 | 17:28 | 49.87
2025-04-23 | 17:28 | 49.868
2025-04-23 | 17:28 | 49.868
2025-04-23 | 17:28 | 49.868
2025-04-23 | 17:28 | 49.868
2025-04-23 | 17:28 | 49.868
2025-04-23 | 17:28 | 49.869
2025-04-23 | 17:28 | 49.868
2025-04-23 | 17:28 | 49.869
2025-04-23 | 17:28 | 49.87
2025-04-23 | 17:28 | 49.872
2025-04-23 | 17:28 | 49.873
2025-04-23 | 17:28 | 49.873
2025-04-23 | 17:28 | 49.87
2025-04-23 | 17:28 | 49.87
2025-04-23 | 17:28 | 49.869
2025-04-23 | 17:28 | 49.869
2025-04-23 | 17:28 | 49.868
2025-04-23 | 17:28 | 49.867
2025-04-23 | 17:28 | 49.867
2025-04-23 | 17:28 | 49.866
2025-04-23 | 17:28 | 49.866
2025-04-23 | 17:28 | 49.866
2025-04-23 | 17:28 | 49.865
2025-04-23 | 17:28 | 49.867
2025-04-23 | 17:28 | 49.866
2025-04-23 | 17:28 | 49.869
2025-04-23 | 17:28 | 49.87
2025-04-23 | 17:28 | 49.871
2025-04-23 | 17:28 | 49.869
2025-04-23 | 17:28 | 49.868
2025-04-23 | 17:29 | 49.867
2025-04-23 | 17:29 | 49.866
2025-04-23 | 17:29 | 49.865
2025-04-23 | 17:29 | 49.865
2025-04-23 | 17:29 | 49.867
2025-04-23 | 17:29 | 49.87
2025-04-23 | 17:29 | 49.872
2025-04-23 | 17:29 | 49.874
2025-04-23 | 17:29 | 49.875
2025-04-23 | 17:29 | 49.876
2025-04-23 | 17:29 | 49.875
2025-04-23 | 17:29 | 49.877
2025-04-23 | 17:29 | 49.876
2025-04-23 | 17:29 | 49.878
2025-04-23 | 17:29 | 49.878
2025-04-23 | 17:29 | 49.877
2025-04-23 | 17:29 | 49.876
2025-04-23 | 17:29 | 49.875
2025-04-23 | 17:29 | 49.874
2025-04-23 | 17:29 | 49.872
2025-04-23 | 17:29 | 49.872
2025-04-23 | 17:29 | 49.869
2025-04-23 | 17:29 | 49.867
2025-04-23 | 17:29 | 49.864
2025-04-23 | 17:29 | 49.863
2025-04-23 | 17:29 | 49.863
2025-04-23 | 17:29 | 49.862
2025-04-23 | 17:29 | 49.865
2025-04-23 | 17:29 | 49.864
2025-04-23 | 17:29 | 49.863
2025-04-23 | 17:29 | 49.86
2025-04-23 | 17:29 | 49.857
2025-04-23 | 17:29 | 49.852
2025-04-23 | 17:29 | 49.853
2025-04-23 | 17:29 | 49.851
2025-04-23 | 17:29 | 49.851
2025-04-23 | 17:29 | 49.851
2025-04-23 | 17:29 | 49.85
2025-04-23 | 17:29 | 49.85
2025-04-23 | 17:29 | 49.849
2025-04-23 | 17:29 | 49.851
2025-04-23 | 17:29 | 49.852
2025-04-23 | 17:29 | 49.852
2025-04-23 | 17:29 | 49.851
2025-04-23 | 17:29 | 49.849
2025-04-23 | 17:29 | 49.848
2025-04-23 | 17:29 | 49.848
2025-04-23 | 17:29 | 49.852
2025-04-23 | 17:29 | 49.853
2025-04-23 | 17:29 | 49.854
2025-04-23 | 17:29 | 49.855
2025-04-23 | 17:29 | 49.856
2025-04-23 | 17:29 | 49.855
2025-04-23 | 17:29 | 49.854
2025-04-23 | 17:29 | 49.856
2025-04-23 | 17:29 | 49.853
2025-04-23 | 17:29 | 49.853
2025-04-23 | 17:29 | 49.853
2025-04-23 | 17:29 | 49.852
2025-04-23 | 17:30 | 49.853
2025-04-23 | 17:30 | 49.851
2025-04-23 | 17:30 | 49.851
2025-04-23 | 17:30 | 49.848
2025-04-23 | 17:30 | 49.847
2025-04-23 | 17:30 | 49.848
2025-04-23 | 17:30 | 49.846
2025-04-23 | 17:30 | 49.848
2025-04-23 | 17:30 | 49.848
2025-04-23 | 17:30 | 49.851
2025-04-23 | 17:30 | 49.851
2025-04-23 | 17:30 | 49.851
2025-04-23 | 17:30 | 49.85
2025-04-23 | 17:30 | 49.849
2025-04-23 | 17:30 | 49.851
2025-04-23 | 17:30 | 49.85
2025-04-23 | 17:30 | 49.848
2025-04-23 | 17:30 | 49.845
2025-04-23 | 17:30 | 49.843
2025-04-23 | 17:30 | 49.844
2025-04-23 | 17:30 | 49.845
2025-04-23 | 17:30 | 49.847
2025-04-23 | 17:30 | 49.847
2025-04-23 | 17:30 | 49.85
2025-04-23 | 17:30 | 49.85
2025-04-23 | 17:30 | 49.851
2025-04-23 | 17:30 | 49.85
2025-04-23 | 17:30 | 49.847
2025-04-23 | 17:30 | 49.844
2025-04-23 | 17:30 | 49.839
2025-04-23 | 17:30 | 49.835
2025-04-23 | 17:30 | 49.839
2025-04-23 | 17:30 | 49.848
2025-04-23 | 17:30 | 49.854
2025-04-23 | 17:30 | 49.856
2025-04-23 | 17:30 | 49.858
2025-04-23 | 17:30 | 49.859
2025-04-23 | 17:30 | 49.861
2025-04-23 | 17:30 | 49.862
2025-04-23 | 17:30 | 49.862
2025-04-23 | 17:30 | 49.863
2025-04-23 | 17:30 | 49.864
2025-04-23 | 17:30 | 49.867
2025-04-23 | 17:30 | 49.867
2025-04-23 | 17:30 | 49.87
2025-04-23 | 17:30 | 49.87
2025-04-23 | 17:30 | 49.871
2025-04-23 | 17:30 | 49.87
2025-04-23 | 17:30 | 49.871
2025-04-23 | 17:30 | 49.872
2025-04-23 | 17:30 | 49.871
2025-04-23 | 17:30 | 49.87
2025-04-23 | 17:30 | 49.873
2025-04-23 | 17:30 | 49.875
2025-04-23 | 17:30 | 49.877
2025-04-23 | 17:30 | 49.878
2025-04-23 | 17:30 | 49.879
2025-04-23 | 17:30 | 49.882
2025-04-23 | 17:30 | 49.882
2025-04-23 | 17:30 | 49.886
2025-04-23 | 17:30 | 49.887
2025-04-23 | 17:31 | 49.889
2025-04-23 | 17:31 | 49.892
2025-04-23 | 17:31 | 49.894
2025-04-23 | 17:31 | 49.895
2025-04-23 | 17:31 | 49.894
2025-04-23 | 17:31 | 49.893
2025-04-23 | 17:31 | 49.893
2025-04-23 | 17:31 | 49.893
2025-04-23 | 17:31 | 49.892
2025-04-23 | 17:31 | 49.888
2025-04-23 | 17:31 | 49.888
2025-04-23 | 17:31 | 49.888
2025-04-23 | 17:31 | 49.888
2025-04-23 | 17:31 | 49.888
2025-04-23 | 17:31 | 49.889
2025-04-23 | 17:31 | 49.891
2025-04-23 | 17:31 | 49.893
2025-04-23 | 17:31 | 49.895
2025-04-23 | 17:31 | 49.898
2025-04-23 | 17:31 | 49.898
2025-04-23 | 17:31 | 49.901
2025-04-23 | 17:31 | 49.901
2025-04-23 | 17:31 | 49.899
2025-04-23 | 17:31 | 49.899
2025-04-23 | 17:31 | 49.898
2025-04-23 | 17:31 | 49.899
2025-04-23 | 17:31 | 49.899
2025-04-23 | 17:31 | 49.902
2025-04-23 | 17:31 | 49.904
2025-04-23 | 17:31 | 49.907
2025-04-23 | 17:31 | 49.908
2025-04-23 | 17:31 | 49.912
2025-04-23 | 17:31 | 49.913
2025-04-23 | 17:31 | 49.919
2025-04-23 | 17:31 | 49.92
2025-04-23 | 17:31 | 49.923
2025-04-23 | 17:31 | 49.926
2025-04-23 | 17:31 | 49.927
2025-04-23 | 17:31 | 49.925
2025-04-23 | 17:31 | 49.927
2025-04-23 | 17:31 | 49.928
2025-04-23 | 17:31 | 49.93
2025-04-23 | 17:31 | 49.933
2025-04-23 | 17:31 | 49.935
2025-04-23 | 17:31 | 49.937
2025-04-23 | 17:31 | 49.939
2025-04-23 | 17:31 | 49.939
2025-04-23 | 17:31 | 49.942
2025-04-23 | 17:31 | 49.94
2025-04-23 | 17:31 | 49.936
2025-04-23 | 17:31 | 49.933
2025-04-23 | 17:31 | 49.93
2025-04-23 | 17:31 | 49.928
2025-04-23 | 17:31 | 49.93
2025-04-23 | 17:31 | 49.93
2025-04-23 | 17:31 | 49.932
2025-04-23 | 17:31 | 49.931
2025-04-23 | 17:31 | 49.931
2025-04-23 | 17:31 | 49.929
2025-04-23 | 17:32 | 49.93
2025-04-23 | 17:32 | 49.93
2025-04-23 | 17:32 | 49.93
2025-04-23 | 17:32 | 49.934
2025-04-23 | 17:32 | 49.935
2025-04-23 | 17:32 | 49.938
2025-04-23 | 17:32 | 49.942
2025-04-23 | 17:32 | 49.943
2025-04-23 | 17:32 | 49.946
2025-04-23 | 17:32 | 49.947
2025-04-23 | 17:32 | 49.949
2025-04-23 | 17:32 | 49.951
2025-04-23 | 17:32 | 49.955
2025-04-23 | 17:32 | 49.959
2025-04-23 | 17:32 | 49.961
2025-04-23 | 17:32 | 49.965
2025-04-23 | 17:32 | 49.968
2025-04-23 | 17:32 | 49.968
2025-04-23 | 17:32 | 49.969
2025-04-23 | 17:32 | 49.971
2025-04-23 | 17:32 | 49.972
2025-04-23 | 17:32 | 49.974
2025-04-23 | 17:32 | 49.974
2025-04-23 | 17:32 | 49.975
2025-04-23 | 17:32 | 49.979
2025-04-23 | 17:32 | 49.981
2025-04-23 | 17:32 | 49.982
2025-04-23 | 17:32 | 49.979
2025-04-23 | 17:32 | 49.979
2025-04-23 | 17:32 | 49.976
2025-04-23 | 17:32 | 49.973
2025-04-23 | 17:32 | 49.974
2025-04-23 | 17:32 | 49.976
2025-04-23 | 17:32 | 49.978
2025-04-23 | 17:32 | 49.98
2025-04-23 | 17:32 | 49.981
2025-04-23 | 17:32 | 49.982
2025-04-23 | 17:32 | 49.983
2025-04-23 | 17:32 | 49.987
2025-04-23 | 17:32 | 49.988
2025-04-23 | 17:32 | 49.988
2025-04-23 | 17:32 | 49.988
2025-04-23 | 17:32 | 49.988
2025-04-23 | 17:32 | 49.986
2025-04-23 | 17:32 | 49.985
2025-04-23 | 17:32 | 49.984
2025-04-23 | 17:32 | 49.983
2025-04-23 | 17:32 | 49.98
2025-04-23 | 17:32 | 49.979
2025-04-23 | 17:32 | 49.978
2025-04-23 | 17:32 | 49.976
2025-04-23 | 17:32 | 49.975
2025-04-23 | 17:32 | 49.974
2025-04-23 | 17:32 | 49.974
2025-04-23 | 17:32 | 49.975
2025-04-23 | 17:32 | 49.977
2025-04-23 | 17:32 | 49.98
2025-04-23 | 17:32 | 49.984
2025-04-23 | 17:32 | 49.991
2025-04-23 | 17:32 | 49.996
2025-04-23 | 17:32 | 50.001
2025-04-23 | 17:33 | 50.004
2025-04-23 | 17:33 | 50.005
2025-04-23 | 17:33 | 50.007
2025-04-23 | 17:33 | 50.005
2025-04-23 | 17:33 | 50.003
2025-04-23 | 17:33 | 50
2025-04-23 | 17:33 | 49.999
2025-04-23 | 17:33 | 49.996
2025-04-23 | 17:33 | 49.994
2025-04-23 | 17:33 | 49.995
2025-04-23 | 17:33 | 49.993
2025-04-23 | 17:33 | 49.995
2025-04-23 | 17:33 | 49.998
2025-04-23 | 17:33 | 50
2025-04-23 | 17:33 | 50.001
2025-04-23 | 17:33 | 50.005
2025-04-23 | 17:33 | 50.01
2025-04-23 | 17:33 | 50.015
2025-04-23 | 17:33 | 50.02
2025-04-23 | 17:33 | 50.026
2025-04-23 | 17:33 | 50.031
2025-04-23 | 17:33 | 50.029
2025-04-23 | 17:33 | 50.03
2025-04-23 | 17:33 | 50.032
2025-04-23 | 17:33 | 50.032
2025-04-23 | 17:33 | 50.032
2025-04-23 | 17:33 | 50.029
2025-04-23 | 17:33 | 50.03
2025-04-23 | 17:33 | 50.03
2025-04-23 | 17:33 | 50.03
2025-04-23 | 17:33 | 50.028
2025-04-23 | 17:33 | 50.028
2025-04-23 | 17:33 | 50.029
2025-04-23 | 17:33 | 50.03
2025-04-23 | 17:33 | 50.03
2025-04-23 | 17:33 | 50.028
2025-04-23 | 17:33 | 50.029
2025-04-23 | 17:33 | 50.032
2025-04-23 | 17:33 | 50.034
2025-04-23 | 17:33 | 50.036
2025-04-23 | 17:33 | 50.037
2025-04-23 | 17:33 | 50.037
2025-04-23 | 17:33 | 50.035
2025-04-23 | 17:33 | 50.032
2025-04-23 | 17:33 | 50.03
2025-04-23 | 17:33 | 50.029
2025-04-23 | 17:33 | 50.029
2025-04-23 | 17:33 | 50.032
2025-04-23 | 17:33 | 50.035
2025-04-23 | 17:33 | 50.037
2025-04-23 | 17:33 | 50.041
2025-04-23 | 17:33 | 50.043
2025-04-23 | 17:33 | 50.045
2025-04-23 | 17:33 | 50.045
2025-04-23 | 17:33 | 50.044
2025-04-23 | 17:33 | 50.042
2025-04-23 | 17:33 | 50.042
2025-04-23 | 17:33 | 50.044
2025-04-23 | 17:33 | 50.046
2025-04-23 | 17:34 | 50.044

## 20250426-1
In GMT
Date | Time | Freq
2025-04-26 | 23:32 | 50.065 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-04-26 | 23:32 | 50.065 | 222 | BRITNED | 676.211
2025-04-26 | 23:32 | 50.063 | 268 | WBURB-2 | 428.156
2025-04-26 | 23:32 | 50.063 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-04-26 | 23:32 | 50.063 |  | Viking Link | -648.9
2025-04-26 | 23:32 | 50.066 |  | Viking Link | 1398.96
2025-04-26 | 23:32 | 50.064 | 209 | DRAXX-3 | 626.95
2025-04-26 | 23:32 | 50.063 | 154 | CDCL-1 | 391.57
2025-04-26 | 23:32 | 50.063 | 268 | ROCK-1 | 468.495
2025-04-26 | 23:32 | 50.063 | 148 | IFA Bipole1 | 945.473
2025-04-26 | 23:32 | 50.064 | 132 | IFA Bipole1 | 999.1
2025-04-26 | 23:32 | 50.059 | 141 | IFA Bipole2 | 1000
2025-04-26 | 23:32 | 50.056 | 135 | IFA Bipole1 | 996.75
2025-04-26 | 23:32 | 50.053 |  | Viking Link | -780.3
2025-04-26 | 23:32 | 50.051
2025-04-26 | 23:32 | 50.051
2025-04-26 | 23:32 | 50.051
2025-04-26 | 23:32 | 50.051
2025-04-26 | 23:32 | 50.049
2025-04-26 | 23:32 | 50.046 | 130 | HEYM12 | 271.908
2025-04-26 | 23:32 | 50.047 | 228 | HUMR-1 | 303.75
2025-04-26 | 23:32 | 50.048
2025-04-26 | 23:32 | 50.045
2025-04-26 | 23:32 | 50.042
2025-04-26 | 23:32 | 50.042
2025-04-26 | 23:32 | 50.039
2025-04-26 | 23:32 | 50.04
2025-04-26 | 23:32 | 50.043
2025-04-26 | 23:32 | 50.046
2025-04-26 | 23:32 | 50.05
2025-04-26 | 23:32 | 50.049 | 211 | CDCL-1 | 291.5
2025-04-26 | 23:32 | 50.047 | 199 | STAY-2 | 413.125
2025-04-26 | 23:32 | 50.044 | 173 | CDCL-1 | 397.375
2025-04-26 | 23:32 | 50.04 | 248 | SEAB-2 | 361.25
2025-04-26 | 23:32 | 50.038 | 255 | FRANCE | 995.65
2025-04-26 | 23:32 | 50.037 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-04-26 | 23:32 | 50.037
2025-04-26 | 23:32 | 50.035
2025-04-26 | 23:32 | 50.033
2025-04-26 | 23:32 | 50.03
2025-04-26 | 23:32 | 50.027
2025-04-26 | 23:33 | 50.024
2025-04-26 | 23:33 | 50.023
2025-04-26 | 23:33 | 50.027
2025-04-26 | 23:33 | 50.029
2025-04-26 | 23:33 | 50.029
2025-04-26 | 23:33 | 50.028
2025-04-26 | 23:33 | 50.028
2025-04-26 | 23:33 | 50.03
2025-04-26 | 23:33 | 50.031
2025-04-26 | 23:33 | 50.032
2025-04-26 | 23:33 | 50.033
2025-04-26 | 23:33 | 50.037
2025-04-26 | 23:33 | 50.039
2025-04-26 | 23:33 | 50.041
2025-04-26 | 23:33 | 50.041
2025-04-26 | 23:33 | 50.041
2025-04-26 | 23:33 | 50.04
2025-04-26 | 23:33 | 50.04
2025-04-26 | 23:33 | 50.038
2025-04-26 | 23:33 | 50.037
2025-04-26 | 23:33 | 50.031
2025-04-26 | 23:33 | 50.001
2025-04-26 | 23:33 | 49.979
2025-04-26 | 23:33 | 49.97
2025-04-26 | 23:33 | 49.942
2025-04-26 | 23:33 | 49.927
2025-04-26 | 23:33 | 49.923
2025-04-26 | 23:33 | 49.922
2025-04-26 | 23:33 | 49.923
2025-04-26 | 23:33 | 49.924
2025-04-26 | 23:33 | 49.922
2025-04-26 | 23:33 | 49.921
2025-04-26 | 23:33 | 49.919
2025-04-26 | 23:33 | 49.917
2025-04-26 | 23:33 | 49.916
2025-04-26 | 23:33 | 49.912
2025-04-26 | 23:33 | 49.91
2025-04-26 | 23:33 | 49.909
2025-04-26 | 23:33 | 49.905
2025-04-26 | 23:33 | 49.902
2025-04-26 | 23:33 | 49.899
2025-04-26 | 23:33 | 49.9
2025-04-26 | 23:33 | 49.899
2025-04-26 | 23:33 | 49.898
2025-04-26 | 23:33 | 49.898
2025-04-26 | 23:33 | 49.898
2025-04-26 | 23:33 | 49.896
2025-04-26 | 23:33 | 49.895
2025-04-26 | 23:33 | 49.896
2025-04-26 | 23:33 | 49.895
2025-04-26 | 23:33 | 49.896
2025-04-26 | 23:33 | 49.898
2025-04-26 | 23:33 | 49.9
2025-04-26 | 23:33 | 49.901
2025-04-26 | 23:33 | 49.902
2025-04-26 | 23:33 | 49.904
2025-04-26 | 23:33 | 49.904
2025-04-26 | 23:33 | 49.904
2025-04-26 | 23:33 | 49.904
2025-04-26 | 23:34 | 49.904
2025-04-26 | 23:34 | 49.902
2025-04-26 | 23:34 | 49.904
2025-04-26 | 23:34 | 49.907
2025-04-26 | 23:34 | 49.905
2025-04-26 | 23:34 | 49.905
2025-04-26 | 23:34 | 49.903
2025-04-26 | 23:34 | 49.901
2025-04-26 | 23:34 | 49.901
2025-04-26 | 23:34 | 49.903
2025-04-26 | 23:34 | 49.904
2025-04-26 | 23:34 | 49.906
2025-04-26 | 23:34 | 49.908
2025-04-26 | 23:34 | 49.909
2025-04-26 | 23:34 | 49.907
2025-04-26 | 23:34 | 49.909
2025-04-26 | 23:34 | 49.91
2025-04-26 | 23:34 | 49.909
2025-04-26 | 23:34 | 49.91
2025-04-26 | 23:34 | 49.911
2025-04-26 | 23:34 | 49.91
2025-04-26 | 23:34 | 49.91
2025-04-26 | 23:34 | 49.908
2025-04-26 | 23:34 | 49.91
2025-04-26 | 23:34 | 49.909
2025-04-26 | 23:34 | 49.909
2025-04-26 | 23:34 | 49.909
2025-04-26 | 23:34 | 49.909
2025-04-26 | 23:34 | 49.91
2025-04-26 | 23:34 | 49.91
2025-04-26 | 23:34 | 49.908
2025-04-26 | 23:34 | 49.908
2025-04-26 | 23:34 | 49.908
2025-04-26 | 23:34 | 49.909
2025-04-26 | 23:34 | 49.911
2025-04-26 | 23:34 | 49.912
2025-04-26 | 23:34 | 49.913
2025-04-26 | 23:34 | 49.914
2025-04-26 | 23:34 | 49.913
2025-04-26 | 23:34 | 49.912
2025-04-26 | 23:34 | 49.911
2025-04-26 | 23:34 | 49.91
2025-04-26 | 23:34 | 49.907
2025-04-26 | 23:34 | 49.905
2025-04-26 | 23:34 | 49.902
2025-04-26 | 23:34 | 49.902
2025-04-26 | 23:34 | 49.902
2025-04-26 | 23:34 | 49.902
2025-04-26 | 23:34 | 49.901
2025-04-26 | 23:34 | 49.9
2025-04-26 | 23:34 | 49.899
2025-04-26 | 23:34 | 49.896
2025-04-26 | 23:34 | 49.896
2025-04-26 | 23:34 | 49.895
2025-04-26 | 23:34 | 49.896
2025-04-26 | 23:34 | 49.898
2025-04-26 | 23:34 | 49.899
2025-04-26 | 23:34 | 49.9
2025-04-26 | 23:34 | 49.9
2025-04-26 | 23:34 | 49.898
2025-04-26 | 23:34 | 49.899
2025-04-26 | 23:35 | 49.899
2025-04-26 | 23:35 | 49.9
2025-04-26 | 23:35 | 49.9
2025-04-26 | 23:35 | 49.9
2025-04-26 | 23:35 | 49.9
2025-04-26 | 23:35 | 49.902
2025-04-26 | 23:35 | 49.904
2025-04-26 | 23:35 | 49.903
2025-04-26 | 23:35 | 49.903
2025-04-26 | 23:35 | 49.9
2025-04-26 | 23:35 | 49.897
2025-04-26 | 23:35 | 49.895
2025-04-26 | 23:35 | 49.897
2025-04-26 | 23:35 | 49.898
2025-04-26 | 23:35 | 49.899
2025-04-26 | 23:35 | 49.9
2025-04-26 | 23:35 | 49.899
2025-04-26 | 23:35 | 49.897
2025-04-26 | 23:35 | 49.897
2025-04-26 | 23:35 | 49.899
2025-04-26 | 23:35 | 49.899
2025-04-26 | 23:35 | 49.896
2025-04-26 | 23:35 | 49.893
2025-04-26 | 23:35 | 49.893
2025-04-26 | 23:35 | 49.894
2025-04-26 | 23:35 | 49.893
2025-04-26 | 23:35 | 49.893
2025-04-26 | 23:35 | 49.891
2025-04-26 | 23:35 | 49.888
2025-04-26 | 23:35 | 49.888
2025-04-26 | 23:35 | 49.887
2025-04-26 | 23:35 | 49.888
2025-04-26 | 23:35 | 49.89
2025-04-26 | 23:35 | 49.889
2025-04-26 | 23:35 | 49.889
2025-04-26 | 23:35 | 49.89
2025-04-26 | 23:35 | 49.891
2025-04-26 | 23:35 | 49.89
2025-04-26 | 23:35 | 49.89
2025-04-26 | 23:35 | 49.891
2025-04-26 | 23:35 | 49.891
2025-04-26 | 23:35 | 49.891
2025-04-26 | 23:35 | 49.892
2025-04-26 | 23:35 | 49.892
2025-04-26 | 23:35 | 49.892
2025-04-26 | 23:35 | 49.894
2025-04-26 | 23:35 | 49.894
2025-04-26 | 23:35 | 49.893
2025-04-26 | 23:35 | 49.892
2025-04-26 | 23:35 | 49.892
2025-04-26 | 23:35 | 49.892
2025-04-26 | 23:35 | 49.891
2025-04-26 | 23:35 | 49.889
2025-04-26 | 23:35 | 49.888
2025-04-26 | 23:35 | 49.886
2025-04-26 | 23:35 | 49.886
2025-04-26 | 23:35 | 49.887
2025-04-26 | 23:35 | 49.89
2025-04-26 | 23:35 | 49.892
2025-04-26 | 23:36 | 49.894
2025-04-26 | 23:36 | 49.894
2025-04-26 | 23:36 | 49.895
2025-04-26 | 23:36 | 49.895
2025-04-26 | 23:36 | 49.894
2025-04-26 | 23:36 | 49.893
2025-04-26 | 23:36 | 49.894
2025-04-26 | 23:36 | 49.895
2025-04-26 | 23:36 | 49.895
2025-04-26 | 23:36 | 49.895
2025-04-26 | 23:36 | 49.894
2025-04-26 | 23:36 | 49.894
2025-04-26 | 23:36 | 49.893
2025-04-26 | 23:36 | 49.894
2025-04-26 | 23:36 | 49.895
2025-04-26 | 23:36 | 49.896
2025-04-26 | 23:36 | 49.898
2025-04-26 | 23:36 | 49.898
2025-04-26 | 23:36 | 49.9
2025-04-26 | 23:36 | 49.901
2025-04-26 | 23:36 | 49.903
2025-04-26 | 23:36 | 49.902
2025-04-26 | 23:36 | 49.901
2025-04-26 | 23:36 | 49.898
2025-04-26 | 23:36 | 49.898
2025-04-26 | 23:36 | 49.897
2025-04-26 | 23:36 | 49.897
2025-04-26 | 23:36 | 49.896
2025-04-26 | 23:36 | 49.894
2025-04-26 | 23:36 | 49.895
2025-04-26 | 23:36 | 49.898
2025-04-26 | 23:36 | 49.897
2025-04-26 | 23:36 | 49.896
2025-04-26 | 23:36 | 49.895
2025-04-26 | 23:36 | 49.897
2025-04-26 | 23:36 | 49.9
2025-04-26 | 23:36 | 49.901
2025-04-26 | 23:36 | 49.899
2025-04-26 | 23:36 | 49.901
2025-04-26 | 23:36 | 49.903
2025-04-26 | 23:36 | 49.904
2025-04-26 | 23:36 | 49.903
2025-04-26 | 23:36 | 49.903
2025-04-26 | 23:36 | 49.904
2025-04-26 | 23:36 | 49.903
2025-04-26 | 23:36 | 49.902
2025-04-26 | 23:36 | 49.902
2025-04-26 | 23:36 | 49.902
2025-04-26 | 23:36 | 49.901
2025-04-26 | 23:36 | 49.9
2025-04-26 | 23:36 | 49.899
2025-04-26 | 23:36 | 49.898
2025-04-26 | 23:36 | 49.9
2025-04-26 | 23:36 | 49.901
2025-04-26 | 23:36 | 49.903
2025-04-26 | 23:36 | 49.904
2025-04-26 | 23:36 | 49.905
2025-04-26 | 23:36 | 49.905
2025-04-26 | 23:36 | 49.904
2025-04-26 | 23:36 | 49.903
2025-04-26 | 23:36 | 49.904
2025-04-26 | 23:37 | 49.904
2025-04-26 | 23:37 | 49.902
2025-04-26 | 23:37 | 49.9
2025-04-26 | 23:37 | 49.9
2025-04-26 | 23:37 | 49.903
2025-04-26 | 23:37 | 49.904
2025-04-26 | 23:37 | 49.904
2025-04-26 | 23:37 | 49.902
2025-04-26 | 23:37 | 49.902
2025-04-26 | 23:37 | 49.902
2025-04-26 | 23:37 | 49.904
2025-04-26 | 23:37 | 49.908
2025-04-26 | 23:37 | 49.908
2025-04-26 | 23:37 | 49.906
2025-04-26 | 23:37 | 49.905
2025-04-26 | 23:37 | 49.906
2025-04-26 | 23:37 | 49.905
2025-04-26 | 23:37 | 49.905
2025-04-26 | 23:37 | 49.904
2025-04-26 | 23:37 | 49.903
2025-04-26 | 23:37 | 49.901
2025-04-26 | 23:37 | 49.9
2025-04-26 | 23:37 | 49.899
2025-04-26 | 23:37 | 49.9
2025-04-26 | 23:37 | 49.899
2025-04-26 | 23:37 | 49.898
2025-04-26 | 23:37 | 49.897
2025-04-26 | 23:37 | 49.896
2025-04-26 | 23:37 | 49.898
2025-04-26 | 23:37 | 49.899
2025-04-26 | 23:37 | 49.898
2025-04-26 | 23:37 | 49.9
2025-04-26 | 23:37 | 49.904
2025-04-26 | 23:37 | 49.907
2025-04-26 | 23:37 | 49.909
2025-04-26 | 23:37 | 49.909
2025-04-26 | 23:37 | 49.909
2025-04-26 | 23:37 | 49.911
2025-04-26 | 23:37 | 49.91
2025-04-26 | 23:37 | 49.912
2025-04-26 | 23:37 | 49.915
2025-04-26 | 23:37 | 49.915
2025-04-26 | 23:37 | 49.914
2025-04-26 | 23:37 | 49.917
2025-04-26 | 23:37 | 49.917
2025-04-26 | 23:37 | 49.916
2025-04-26 | 23:37 | 49.917
2025-04-26 | 23:37 | 49.919
2025-04-26 | 23:37 | 49.924
2025-04-26 | 23:37 | 49.926
2025-04-26 | 23:37 | 49.927
2025-04-26 | 23:37 | 49.926
2025-04-26 | 23:37 | 49.925
2025-04-26 | 23:37 | 49.923
2025-04-26 | 23:37 | 49.922
2025-04-26 | 23:37 | 49.922
2025-04-26 | 23:37 | 49.925
2025-04-26 | 23:37 | 49.929
2025-04-26 | 23:37 | 49.929
2025-04-26 | 23:38 | 49.93
2025-04-26 | 23:38 | 49.931
2025-04-26 | 23:38 | 49.932
2025-04-26 | 23:38 | 49.932
2025-04-26 | 23:38 | 49.933
2025-04-26 | 23:38 | 49.934
2025-04-26 | 23:38 | 49.933
2025-04-26 | 23:38 | 49.932
2025-04-26 | 23:38 | 49.932
2025-04-26 | 23:38 | 49.933
2025-04-26 | 23:38 | 49.934
2025-04-26 | 23:38 | 49.936
2025-04-26 | 23:38 | 49.937
2025-04-26 | 23:38 | 49.935
2025-04-26 | 23:38 | 49.933
2025-04-26 | 23:38 | 49.935
2025-04-26 | 23:38 | 49.935
2025-04-26 | 23:38 | 49.934
2025-04-26 | 23:38 | 49.932
2025-04-26 | 23:38 | 49.932
2025-04-26 | 23:38 | 49.935
2025-04-26 | 23:38 | 49.937
2025-04-26 | 23:38 | 49.936
2025-04-26 | 23:38 | 49.932
2025-04-26 | 23:38 | 49.93
2025-04-26 | 23:38 | 49.927
2025-04-26 | 23:38 | 49.926
2025-04-26 | 23:38 | 49.927
2025-04-26 | 23:38 | 49.928
2025-04-26 | 23:38 | 49.929
2025-04-26 | 23:38 | 49.93
2025-04-26 | 23:38 | 49.929
2025-04-26 | 23:38 | 49.927
2025-04-26 | 23:38 | 49.928
2025-04-26 | 23:38 | 49.928
2025-04-26 | 23:38 | 49.928
2025-04-26 | 23:38 | 49.927
2025-04-26 | 23:38 | 49.928
2025-04-26 | 23:38 | 49.929
2025-04-26 | 23:38 | 49.931
2025-04-26 | 23:38 | 49.931
2025-04-26 | 23:38 | 49.932
2025-04-26 | 23:38 | 49.932
2025-04-26 | 23:38 | 49.934
2025-04-26 | 23:38 | 49.934
2025-04-26 | 23:38 | 49.935
2025-04-26 | 23:38 | 49.937
2025-04-26 | 23:38 | 49.94
2025-04-26 | 23:38 | 49.945
2025-04-26 | 23:38 | 49.947
2025-04-26 | 23:38 | 49.947
2025-04-26 | 23:38 | 49.947
2025-04-26 | 23:38 | 49.947
2025-04-26 | 23:38 | 49.945
2025-04-26 | 23:38 | 49.944
2025-04-26 | 23:38 | 49.943
2025-04-26 | 23:38 | 49.941
2025-04-26 | 23:38 | 49.937
2025-04-26 | 23:38 | 49.934
2025-04-26 | 23:38 | 49.93
2025-04-26 | 23:38 | 49.93
2025-04-26 | 23:39 | 49.932
2025-04-26 | 23:39 | 49.936
2025-04-26 | 23:39 | 49.939
2025-04-26 | 23:39 | 49.939
2025-04-26 | 23:39 | 49.94
2025-04-26 | 23:39 | 49.941
2025-04-26 | 23:39 | 49.944
2025-04-26 | 23:39 | 49.943
2025-04-26 | 23:39 | 49.944
2025-04-26 | 23:39 | 49.942
2025-04-26 | 23:39 | 49.944
2025-04-26 | 23:39 | 49.946
2025-04-26 | 23:39 | 49.945
2025-04-26 | 23:39 | 49.943
2025-04-26 | 23:39 | 49.943
2025-04-26 | 23:39 | 49.944
2025-04-26 | 23:39 | 49.945
2025-04-26 | 23:39 | 49.947
2025-04-26 | 23:39 | 49.949
2025-04-26 | 23:39 | 49.951
2025-04-26 | 23:39 | 49.954
2025-04-26 | 23:39 | 49.956
2025-04-26 | 23:39 | 49.958
2025-04-26 | 23:39 | 49.96
2025-04-26 | 23:39 | 49.963
2025-04-26 | 23:39 | 49.965
2025-04-26 | 23:39 | 49.966
2025-04-26 | 23:39 | 49.966
2025-04-26 | 23:39 | 49.967
2025-04-26 | 23:39 | 49.968
2025-04-26 | 23:39 | 49.966
2025-04-26 | 23:39 | 49.964
2025-04-26 | 23:39 | 49.963
2025-04-26 | 23:39 | 49.963
2025-04-26 | 23:39 | 49.963
2025-04-26 | 23:39 | 49.963
2025-04-26 | 23:39 | 49.964
2025-04-26 | 23:39 | 49.965
2025-04-26 | 23:39 | 49.965
2025-04-26 | 23:39 | 49.963
2025-04-26 | 23:39 | 49.962
2025-04-26 | 23:39 | 49.963
2025-04-26 | 23:39 | 49.963
2025-04-26 | 23:39 | 49.962
2025-04-26 | 23:39 | 49.961
2025-04-26 | 23:39 | 49.958
2025-04-26 | 23:39 | 49.957
2025-04-26 | 23:39 | 49.958
2025-04-26 | 23:39 | 49.958
2025-04-26 | 23:39 | 49.956
2025-04-26 | 23:39 | 49.954
2025-04-26 | 23:39 | 49.953
2025-04-26 | 23:39 | 49.95
2025-04-26 | 23:39 | 49.947
2025-04-26 | 23:39 | 49.945
2025-04-26 | 23:39 | 49.944
2025-04-26 | 23:39 | 49.944
2025-04-26 | 23:39 | 49.943
2025-04-26 | 23:39 | 49.945
2025-04-26 | 23:40 | 49.948
2025-04-26 | 23:40 | 49.95
2025-04-26 | 23:40 | 49.954
2025-04-26 | 23:40 | 49.954
2025-04-26 | 23:40 | 49.953
2025-04-26 | 23:40 | 49.953
2025-04-26 | 23:40 | 49.957
2025-04-26 | 23:40 | 49.962
2025-04-26 | 23:40 | 49.965
2025-04-26 | 23:40 | 49.966
2025-04-26 | 23:40 | 49.968
2025-04-26 | 23:40 | 49.971
2025-04-26 | 23:40 | 49.974
2025-04-26 | 23:40 | 49.977
2025-04-26 | 23:40 | 49.976
2025-04-26 | 23:40 | 49.977
2025-04-26 | 23:40 | 49.976
2025-04-26 | 23:40 | 49.976
2025-04-26 | 23:40 | 49.975
2025-04-26 | 23:40 | 49.976
2025-04-26 | 23:40 | 49.976
2025-04-26 | 23:40 | 49.978
2025-04-26 | 23:40 | 49.977
2025-04-26 | 23:40 | 49.98
2025-04-26 | 23:40 | 49.981
2025-04-26 | 23:40 | 49.98
2025-04-26 | 23:40 | 49.977
2025-04-26 | 23:40 | 49.974
2025-04-26 | 23:40 | 49.97
2025-04-26 | 23:40 | 49.968
2025-04-26 | 23:40 | 49.967
2025-04-26 | 23:40 | 49.966
2025-04-26 | 23:40 | 49.965
2025-04-26 | 23:40 | 49.965
2025-04-26 | 23:40 | 49.965
2025-04-26 | 23:40 | 49.967
2025-04-26 | 23:40 | 49.967
2025-04-26 | 23:40 | 49.967
2025-04-26 | 23:40 | 49.967
2025-04-26 | 23:40 | 49.967
2025-04-26 | 23:40 | 49.968
2025-04-26 | 23:40 | 49.966
2025-04-26 | 23:40 | 49.964
2025-04-26 | 23:40 | 49.962
2025-04-26 | 23:40 | 49.962
2025-04-26 | 23:40 | 49.962
2025-04-26 | 23:40 | 49.961
2025-04-26 | 23:40 | 49.961
2025-04-26 | 23:40 | 49.959
2025-04-26 | 23:40 | 49.958
2025-04-26 | 23:40 | 49.956
2025-04-26 | 23:40 | 49.959
2025-04-26 | 23:40 | 49.964
2025-04-26 | 23:40 | 49.968
2025-04-26 | 23:40 | 49.97
2025-04-26 | 23:40 | 49.974
2025-04-26 | 23:40 | 49.977
2025-04-26 | 23:40 | 49.981
2025-04-26 | 23:40 | 49.984
2025-04-26 | 23:40 | 49.987
2025-04-26 | 23:40 | 49.988
2025-04-26 | 23:41 | 49.988
2025-04-26 | 23:41 | 49.988
2025-04-26 | 23:41 | 49.986
2025-04-26 | 23:41 | 49.984
2025-04-26 | 23:41 | 49.982
2025-04-26 | 23:41 | 49.982
2025-04-26 | 23:41 | 49.983
2025-04-26 | 23:41 | 49.984
2025-04-26 | 23:41 | 49.983
2025-04-26 | 23:41 | 49.981
2025-04-26 | 23:41 | 49.979
2025-04-26 | 23:41 | 49.977
2025-04-26 | 23:41 | 49.973
2025-04-26 | 23:41 | 49.971
2025-04-26 | 23:41 | 49.971
2025-04-26 | 23:41 | 49.972
2025-04-26 | 23:41 | 49.974
2025-04-26 | 23:41 | 49.973
2025-04-26 | 23:41 | 49.975
2025-04-26 | 23:41 | 49.975
2025-04-26 | 23:41 | 49.976
2025-04-26 | 23:41 | 49.974
2025-04-26 | 23:41 | 49.973
2025-04-26 | 23:41 | 49.972
2025-04-26 | 23:41 | 49.97
2025-04-26 | 23:41 | 49.969
2025-04-26 | 23:41 | 49.967
2025-04-26 | 23:41 | 49.968
2025-04-26 | 23:41 | 49.969
2025-04-26 | 23:41 | 49.97
2025-04-26 | 23:41 | 49.967
2025-04-26 | 23:41 | 49.965
2025-04-26 | 23:41 | 49.965
2025-04-26 | 23:41 | 49.967
2025-04-26 | 23:41 | 49.97
2025-04-26 | 23:41 | 49.971
2025-04-26 | 23:41 | 49.973
2025-04-26 | 23:41 | 49.972
2025-04-26 | 23:41 | 49.971
2025-04-26 | 23:41 | 49.97
2025-04-26 | 23:41 | 49.969
2025-04-26 | 23:41 | 49.969
2025-04-26 | 23:41 | 49.969
2025-04-26 | 23:41 | 49.971
2025-04-26 | 23:41 | 49.971
2025-04-26 | 23:41 | 49.972
2025-04-26 | 23:41 | 49.972
2025-04-26 | 23:41 | 49.972
2025-04-26 | 23:41 | 49.972
2025-04-26 | 23:41 | 49.969
2025-04-26 | 23:41 | 49.967
2025-04-26 | 23:41 | 49.965
2025-04-26 | 23:41 | 49.965
2025-04-26 | 23:41 | 49.965
2025-04-26 | 23:41 | 49.966
2025-04-26 | 23:41 | 49.966
2025-04-26 | 23:41 | 49.967
2025-04-26 | 23:41 | 49.969
2025-04-26 | 23:41 | 49.972
2025-04-26 | 23:42 | 49.973
2025-04-26 | 23:42 | 49.972
2025-04-26 | 23:42 | 49.972
2025-04-26 | 23:42 | 49.973
2025-04-26 | 23:42 | 49.974
2025-04-26 | 23:42 | 49.975
2025-04-26 | 23:42 | 49.973
2025-04-26 | 23:42 | 49.972
2025-04-26 | 23:42 | 49.97
2025-04-26 | 23:42 | 49.97
2025-04-26 | 23:42 | 49.972
2025-04-26 | 23:42 | 49.974
2025-04-26 | 23:42 | 49.975
2025-04-26 | 23:42 | 49.975
2025-04-26 | 23:42 | 49.973
2025-04-26 | 23:42 | 49.973
2025-04-26 | 23:42 | 49.975
2025-04-26 | 23:42 | 49.976
2025-04-26 | 23:42 | 49.976
2025-04-26 | 23:42 | 49.975
2025-04-26 | 23:42 | 49.975
2025-04-26 | 23:42 | 49.976
2025-04-26 | 23:42 | 49.977
2025-04-26 | 23:42 | 49.978
2025-04-26 | 23:42 | 49.978
2025-04-26 | 23:42 | 49.978
2025-04-26 | 23:42 | 49.978
2025-04-26 | 23:42 | 49.982
2025-04-26 | 23:42 | 49.983
2025-04-26 | 23:42 | 49.982
2025-04-26 | 23:42 | 49.982
2025-04-26 | 23:42 | 49.982
2025-04-26 | 23:42 | 49.982
2025-04-26 | 23:42 | 49.982
2025-04-26 | 23:42 | 49.984
2025-04-26 | 23:42 | 49.986
2025-04-26 | 23:42 | 49.989
2025-04-26 | 23:42 | 49.991
2025-04-26 | 23:42 | 49.994
2025-04-26 | 23:42 | 49.996
2025-04-26 | 23:42 | 49.996
2025-04-26 | 23:42 | 50.001
2025-04-26 | 23:42 | 50.004
2025-04-26 | 23:42 | 50.007
2025-04-26 | 23:42 | 50.008
2025-04-26 | 23:42 | 50.008
2025-04-26 | 23:42 | 50.01
2025-04-26 | 23:42 | 50.015
2025-04-26 | 23:42 | 50.015
2025-04-26 | 23:42 | 50.016
2025-04-26 | 23:42 | 50.018
2025-04-26 | 23:42 | 50.02
2025-04-26 | 23:42 | 50.021
2025-04-26 | 23:42 | 50.022
2025-04-26 | 23:42 | 50.019
2025-04-26 | 23:42 | 50.019
2025-04-26 | 23:42 | 50.014
2025-04-26 | 23:42 | 50.014
2025-04-26 | 23:42 | 50.012
2025-04-26 | 23:42 | 50.011
2025-04-26 | 23:42 | 50.009
2025-04-26 | 23:43 | 50.007
2025-04-26 | 23:43 | 50.006
2025-04-26 | 23:43 | 50.007
2025-04-26 | 23:43 | 50.008
2025-04-26 | 23:43 | 50.008
2025-04-26 | 23:43 | 50.01
2025-04-26 | 23:43 | 50.014
2025-04-26 | 23:43 | 50.017
2025-04-26 | 23:43 | 50.02
2025-04-26 | 23:43 | 50.018
2025-04-26 | 23:43 | 50.016
2025-04-26 | 23:43 | 50.016
2025-04-26 | 23:43 | 50.017
2025-04-26 | 23:43 | 50.018
2025-04-26 | 23:43 | 50.019
2025-04-26 | 23:43 | 50.016
2025-04-26 | 23:43 | 50.018
2025-04-26 | 23:43 | 50.018
2025-04-26 | 23:43 | 50.02
2025-04-26 | 23:43 | 50.021
2025-04-26 | 23:43 | 50.022
2025-04-26 | 23:43 | 50.025
2025-04-26 | 23:43 | 50.025
2025-04-26 | 23:43 | 50.022
2025-04-26 | 23:43 | 50.023
2025-04-26 | 23:43 | 50.024
2025-04-26 | 23:43 | 50.027
2025-04-26 | 23:43 | 50.025
2025-04-26 | 23:43 | 50.024
2025-04-26 | 23:43 | 50.023
2025-04-26 | 23:43 | 50.021
2025-04-26 | 23:43 | 50.021
2025-04-26 | 23:43 | 50.023
2025-04-26 | 23:43 | 50.027
2025-04-26 | 23:43 | 50.03
2025-04-26 | 23:43 | 50.031
2025-04-26 | 23:43 | 50.031
2025-04-26 | 23:43 | 50.029
2025-04-26 | 23:43 | 50.027
2025-04-26 | 23:43 | 50.027
2025-04-26 | 23:43 | 50.027

## 20250427-1
In GMT
Date | Time | Freq
2025-04-27 | 3:04 | 49.941 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-04-27 | 3:04 | 49.943 | 222 | BRITNED | 676.211
2025-04-27 | 3:04 | 49.944 | 268 | WBURB-2 | 428.156
2025-04-27 | 3:04 | 49.945 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-04-27 | 3:04 | 49.945 |  | Viking Link | -648.9
2025-04-27 | 3:04 | 49.945 |  | Viking Link | 1398.96
2025-04-27 | 3:04 | 49.945 | 209 | DRAXX-3 | 626.95
2025-04-27 | 3:04 | 49.946 | 154 | CDCL-1 | 391.57
2025-04-27 | 3:04 | 49.946 | 268 | ROCK-1 | 468.495
2025-04-27 | 3:04 | 49.946 | 148 | IFA Bipole1 | 945.473
2025-04-27 | 3:04 | 49.947 | 132 | IFA Bipole1 | 999.1
2025-04-27 | 3:04 | 49.948 | 141 | IFA Bipole2 | 1000
2025-04-27 | 3:04 | 49.948 | 135 | IFA Bipole1 | 996.75
2025-04-27 | 3:04 | 49.948 |  | Viking Link | -780.3
2025-04-27 | 3:05 | 49.946
2025-04-27 | 3:05 | 49.944
2025-04-27 | 3:05 | 49.945
2025-04-27 | 3:05 | 49.945
2025-04-27 | 3:05 | 49.946
2025-04-27 | 3:05 | 49.946 | 130 | HEYM12 | 271.908
2025-04-27 | 3:05 | 49.946 | 228 | HUMR-1 | 303.75
2025-04-27 | 3:05 | 49.948
2025-04-27 | 3:05 | 49.948
2025-04-27 | 3:05 | 49.948
2025-04-27 | 3:05 | 49.947
2025-04-27 | 3:05 | 49.947
2025-04-27 | 3:05 | 49.949
2025-04-27 | 3:05 | 49.951
2025-04-27 | 3:05 | 49.952
2025-04-27 | 3:05 | 49.953
2025-04-27 | 3:05 | 49.954 | 211 | CDCL-1 | 291.5
2025-04-27 | 3:05 | 49.954 | 199 | STAY-2 | 413.125
2025-04-27 | 3:05 | 49.954 | 173 | CDCL-1 | 397.375
2025-04-27 | 3:05 | 49.955 | 248 | SEAB-2 | 361.25
2025-04-27 | 3:05 | 49.955 | 255 | FRANCE | 995.65
2025-04-27 | 3:05 | 49.956 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-04-27 | 3:05 | 49.959
2025-04-27 | 3:05 | 49.962
2025-04-27 | 3:05 | 49.962
2025-04-27 | 3:05 | 49.962
2025-04-27 | 3:05 | 49.962
2025-04-27 | 3:05 | 49.962
2025-04-27 | 3:05 | 49.963
2025-04-27 | 3:05 | 49.963
2025-04-27 | 3:05 | 49.961
2025-04-27 | 3:05 | 49.96
2025-04-27 | 3:05 | 49.958
2025-04-27 | 3:05 | 49.958
2025-04-27 | 3:05 | 49.957
2025-04-27 | 3:05 | 49.957
2025-04-27 | 3:05 | 49.958
2025-04-27 | 3:05 | 49.96
2025-04-27 | 3:05 | 49.96
2025-04-27 | 3:05 | 49.961
2025-04-27 | 3:05 | 49.961
2025-04-27 | 3:05 | 49.96
2025-04-27 | 3:05 | 49.959
2025-04-27 | 3:05 | 49.959
2025-04-27 | 3:05 | 49.961
2025-04-27 | 3:05 | 49.96
2025-04-27 | 3:05 | 49.961
2025-04-27 | 3:05 | 49.943
2025-04-27 | 3:05 | 49.809
2025-04-27 | 3:05 | 49.774
2025-04-27 | 3:05 | 49.784
2025-04-27 | 3:05 | 49.794
2025-04-27 | 3:05 | 49.797
2025-04-27 | 3:05 | 49.799
2025-04-27 | 3:05 | 49.803
2025-04-27 | 3:05 | 49.796
2025-04-27 | 3:05 | 49.786
2025-04-27 | 3:05 | 49.782
2025-04-27 | 3:05 | 49.782
2025-04-27 | 3:05 | 49.782
2025-04-27 | 3:06 | 49.782
2025-04-27 | 3:06 | 49.781
2025-04-27 | 3:06 | 49.782
2025-04-27 | 3:06 | 49.783
2025-04-27 | 3:06 | 49.783
2025-04-27 | 3:06 | 49.781
2025-04-27 | 3:06 | 49.781
2025-04-27 | 3:06 | 49.78
2025-04-27 | 3:06 | 49.781
2025-04-27 | 3:06 | 49.781
2025-04-27 | 3:06 | 49.78
2025-04-27 | 3:06 | 49.779
2025-04-27 | 3:06 | 49.778
2025-04-27 | 3:06 | 49.777
2025-04-27 | 3:06 | 49.775
2025-04-27 | 3:06 | 49.773
2025-04-27 | 3:06 | 49.772
2025-04-27 | 3:06 | 49.772
2025-04-27 | 3:06 | 49.771
2025-04-27 | 3:06 | 49.77
2025-04-27 | 3:06 | 49.769
2025-04-27 | 3:06 | 49.77
2025-04-27 | 3:06 | 49.769
2025-04-27 | 3:06 | 49.77
2025-04-27 | 3:06 | 49.772
2025-04-27 | 3:06 | 49.771
2025-04-27 | 3:06 | 49.772
2025-04-27 | 3:06 | 49.773
2025-04-27 | 3:06 | 49.772
2025-04-27 | 3:06 | 49.772
2025-04-27 | 3:06 | 49.772
2025-04-27 | 3:06 | 49.773
2025-04-27 | 3:06 | 49.773
2025-04-27 | 3:06 | 49.775
2025-04-27 | 3:06 | 49.776
2025-04-27 | 3:06 | 49.777
2025-04-27 | 3:06 | 49.777
2025-04-27 | 3:06 | 49.779
2025-04-27 | 3:06 | 49.779
2025-04-27 | 3:06 | 49.781
2025-04-27 | 3:06 | 49.782
2025-04-27 | 3:06 | 49.782
2025-04-27 | 3:06 | 49.783
2025-04-27 | 3:06 | 49.784
2025-04-27 | 3:06 | 49.783
2025-04-27 | 3:06 | 49.783
2025-04-27 | 3:06 | 49.784
2025-04-27 | 3:06 | 49.787
2025-04-27 | 3:06 | 49.787
2025-04-27 | 3:06 | 49.789
2025-04-27 | 3:06 | 49.789
2025-04-27 | 3:06 | 49.791
2025-04-27 | 3:06 | 49.792
2025-04-27 | 3:06 | 49.793
2025-04-27 | 3:06 | 49.793
2025-04-27 | 3:06 | 49.793
2025-04-27 | 3:06 | 49.794
2025-04-27 | 3:06 | 49.793
2025-04-27 | 3:06 | 49.794
2025-04-27 | 3:07 | 49.794
2025-04-27 | 3:07 | 49.793
2025-04-27 | 3:07 | 49.794
2025-04-27 | 3:07 | 49.794
2025-04-27 | 3:07 | 49.794
2025-04-27 | 3:07 | 49.796
2025-04-27 | 3:07 | 49.796
2025-04-27 | 3:07 | 49.797
2025-04-27 | 3:07 | 49.797
2025-04-27 | 3:07 | 49.798
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.8
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.8
2025-04-27 | 3:07 | 49.8
2025-04-27 | 3:07 | 49.803
2025-04-27 | 3:07 | 49.804
2025-04-27 | 3:07 | 49.804
2025-04-27 | 3:07 | 49.804
2025-04-27 | 3:07 | 49.805
2025-04-27 | 3:07 | 49.805
2025-04-27 | 3:07 | 49.805
2025-04-27 | 3:07 | 49.805
2025-04-27 | 3:07 | 49.804
2025-04-27 | 3:07 | 49.803
2025-04-27 | 3:07 | 49.804
2025-04-27 | 3:07 | 49.804
2025-04-27 | 3:07 | 49.804
2025-04-27 | 3:07 | 49.802
2025-04-27 | 3:07 | 49.801
2025-04-27 | 3:07 | 49.801
2025-04-27 | 3:07 | 49.798
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.798
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.797
2025-04-27 | 3:07 | 49.797
2025-04-27 | 3:07 | 49.798
2025-04-27 | 3:07 | 49.798
2025-04-27 | 3:07 | 49.798
2025-04-27 | 3:07 | 49.797
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.798
2025-04-27 | 3:07 | 49.798
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.8
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.798
2025-04-27 | 3:07 | 49.8
2025-04-27 | 3:07 | 49.8
2025-04-27 | 3:07 | 49.8
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.8
2025-04-27 | 3:07 | 49.799
2025-04-27 | 3:07 | 49.798
2025-04-27 | 3:07 | 49.797
2025-04-27 | 3:08 | 49.797
2025-04-27 | 3:08 | 49.796
2025-04-27 | 3:08 | 49.795
2025-04-27 | 3:08 | 49.794
2025-04-27 | 3:08 | 49.794
2025-04-27 | 3:08 | 49.795
2025-04-27 | 3:08 | 49.796
2025-04-27 | 3:08 | 49.799
2025-04-27 | 3:08 | 49.8
2025-04-27 | 3:08 | 49.8
2025-04-27 | 3:08 | 49.801
2025-04-27 | 3:08 | 49.8
2025-04-27 | 3:08 | 49.802
2025-04-27 | 3:08 | 49.8
2025-04-27 | 3:08 | 49.799
2025-04-27 | 3:08 | 49.799
2025-04-27 | 3:08 | 49.799
2025-04-27 | 3:08 | 49.798
2025-04-27 | 3:08 | 49.8
2025-04-27 | 3:08 | 49.799
2025-04-27 | 3:08 | 49.8
2025-04-27 | 3:08 | 49.801
2025-04-27 | 3:08 | 49.801
2025-04-27 | 3:08 | 49.801
2025-04-27 | 3:08 | 49.803
2025-04-27 | 3:08 | 49.803
2025-04-27 | 3:08 | 49.804
2025-04-27 | 3:08 | 49.804
2025-04-27 | 3:08 | 49.804
2025-04-27 | 3:08 | 49.804
2025-04-27 | 3:08 | 49.805
2025-04-27 | 3:08 | 49.803
2025-04-27 | 3:08 | 49.804
2025-04-27 | 3:08 | 49.805
2025-04-27 | 3:08 | 49.806
2025-04-27 | 3:08 | 49.805
2025-04-27 | 3:08 | 49.806
2025-04-27 | 3:08 | 49.806
2025-04-27 | 3:08 | 49.806
2025-04-27 | 3:08 | 49.806
2025-04-27 | 3:08 | 49.807
2025-04-27 | 3:08 | 49.809
2025-04-27 | 3:08 | 49.811
2025-04-27 | 3:08 | 49.813
2025-04-27 | 3:08 | 49.812
2025-04-27 | 3:08 | 49.813
2025-04-27 | 3:08 | 49.814
2025-04-27 | 3:08 | 49.813
2025-04-27 | 3:08 | 49.814
2025-04-27 | 3:08 | 49.814
2025-04-27 | 3:08 | 49.815
2025-04-27 | 3:08 | 49.815
2025-04-27 | 3:08 | 49.817
2025-04-27 | 3:08 | 49.815
2025-04-27 | 3:08 | 49.816
2025-04-27 | 3:08 | 49.816
2025-04-27 | 3:08 | 49.815
2025-04-27 | 3:08 | 49.817
2025-04-27 | 3:08 | 49.818
2025-04-27 | 3:08 | 49.819
2025-04-27 | 3:08 | 49.818
2025-04-27 | 3:09 | 49.819
2025-04-27 | 3:09 | 49.821
2025-04-27 | 3:09 | 49.821
2025-04-27 | 3:09 | 49.822
2025-04-27 | 3:09 | 49.822
2025-04-27 | 3:09 | 49.823
2025-04-27 | 3:09 | 49.825
2025-04-27 | 3:09 | 49.826
2025-04-27 | 3:09 | 49.826
2025-04-27 | 3:09 | 49.825
2025-04-27 | 3:09 | 49.825
2025-04-27 | 3:09 | 49.825
2025-04-27 | 3:09 | 49.825
2025-04-27 | 3:09 | 49.826
2025-04-27 | 3:09 | 49.825
2025-04-27 | 3:09 | 49.826
2025-04-27 | 3:09 | 49.827
2025-04-27 | 3:09 | 49.827
2025-04-27 | 3:09 | 49.827
2025-04-27 | 3:09 | 49.827
2025-04-27 | 3:09 | 49.829
2025-04-27 | 3:09 | 49.829
2025-04-27 | 3:09 | 49.83
2025-04-27 | 3:09 | 49.831
2025-04-27 | 3:09 | 49.832
2025-04-27 | 3:09 | 49.832
2025-04-27 | 3:09 | 49.834
2025-04-27 | 3:09 | 49.834
2025-04-27 | 3:09 | 49.836
2025-04-27 | 3:09 | 49.835
2025-04-27 | 3:09 | 49.834
2025-04-27 | 3:09 | 49.834
2025-04-27 | 3:09 | 49.836
2025-04-27 | 3:09 | 49.838
2025-04-27 | 3:09 | 49.838
2025-04-27 | 3:09 | 49.837
2025-04-27 | 3:09 | 49.839
2025-04-27 | 3:09 | 49.839
2025-04-27 | 3:09 | 49.839
2025-04-27 | 3:09 | 49.839
2025-04-27 | 3:09 | 49.84
2025-04-27 | 3:09 | 49.843
2025-04-27 | 3:09 | 49.844
2025-04-27 | 3:09 | 49.844
2025-04-27 | 3:09 | 49.845
2025-04-27 | 3:09 | 49.845
2025-04-27 | 3:09 | 49.846
2025-04-27 | 3:09 | 49.847
2025-04-27 | 3:09 | 49.847
2025-04-27 | 3:09 | 49.847
2025-04-27 | 3:09 | 49.847
2025-04-27 | 3:09 | 49.847
2025-04-27 | 3:09 | 49.847
2025-04-27 | 3:09 | 49.847
2025-04-27 | 3:09 | 49.848
2025-04-27 | 3:09 | 49.85
2025-04-27 | 3:09 | 49.85
2025-04-27 | 3:09 | 49.853
2025-04-27 | 3:09 | 49.854
2025-04-27 | 3:10 | 49.853
2025-04-27 | 3:10 | 49.854
2025-04-27 | 3:10 | 49.855
2025-04-27 | 3:10 | 49.855
2025-04-27 | 3:10 | 49.855
2025-04-27 | 3:10 | 49.855
2025-04-27 | 3:10 | 49.854
2025-04-27 | 3:10 | 49.855
2025-04-27 | 3:10 | 49.857
2025-04-27 | 3:10 | 49.859
2025-04-27 | 3:10 | 49.86
2025-04-27 | 3:10 | 49.86
2025-04-27 | 3:10 | 49.86
2025-04-27 | 3:10 | 49.86
2025-04-27 | 3:10 | 49.859
2025-04-27 | 3:10 | 49.861
2025-04-27 | 3:10 | 49.862
2025-04-27 | 3:10 | 49.863
2025-04-27 | 3:10 | 49.864
2025-04-27 | 3:10 | 49.866
2025-04-27 | 3:10 | 49.865
2025-04-27 | 3:10 | 49.865
2025-04-27 | 3:10 | 49.865
2025-04-27 | 3:10 | 49.865
2025-04-27 | 3:10 | 49.866
2025-04-27 | 3:10 | 49.867
2025-04-27 | 3:10 | 49.867
2025-04-27 | 3:10 | 49.869
2025-04-27 | 3:10 | 49.869
2025-04-27 | 3:10 | 49.87
2025-04-27 | 3:10 | 49.871
2025-04-27 | 3:10 | 49.87
2025-04-27 | 3:10 | 49.869
2025-04-27 | 3:10 | 49.869
2025-04-27 | 3:10 | 49.87
2025-04-27 | 3:10 | 49.871
2025-04-27 | 3:10 | 49.871
2025-04-27 | 3:10 | 49.871
2025-04-27 | 3:10 | 49.872
2025-04-27 | 3:10 | 49.871
2025-04-27 | 3:10 | 49.871
2025-04-27 | 3:10 | 49.872
2025-04-27 | 3:10 | 49.872
2025-04-27 | 3:10 | 49.872
2025-04-27 | 3:10 | 49.873
2025-04-27 | 3:10 | 49.873
2025-04-27 | 3:10 | 49.874
2025-04-27 | 3:10 | 49.875
2025-04-27 | 3:10 | 49.875
2025-04-27 | 3:10 | 49.876
2025-04-27 | 3:10 | 49.876
2025-04-27 | 3:10 | 49.877
2025-04-27 | 3:10 | 49.878
2025-04-27 | 3:10 | 49.879
2025-04-27 | 3:10 | 49.879
2025-04-27 | 3:10 | 49.879
2025-04-27 | 3:10 | 49.879
2025-04-27 | 3:10 | 49.878
2025-04-27 | 3:10 | 49.878
2025-04-27 | 3:10 | 49.879
2025-04-27 | 3:10 | 49.88
2025-04-27 | 3:11 | 49.881
2025-04-27 | 3:11 | 49.881
2025-04-27 | 3:11 | 49.881
2025-04-27 | 3:11 | 49.882
2025-04-27 | 3:11 | 49.882
2025-04-27 | 3:11 | 49.883
2025-04-27 | 3:11 | 49.884
2025-04-27 | 3:11 | 49.885
2025-04-27 | 3:11 | 49.885
2025-04-27 | 3:11 | 49.886
2025-04-27 | 3:11 | 49.886
2025-04-27 | 3:11 | 49.887
2025-04-27 | 3:11 | 49.887
2025-04-27 | 3:11 | 49.887
2025-04-27 | 3:11 | 49.888
2025-04-27 | 3:11 | 49.887
2025-04-27 | 3:11 | 49.887
2025-04-27 | 3:11 | 49.888
2025-04-27 | 3:11 | 49.888
2025-04-27 | 3:11 | 49.888
2025-04-27 | 3:11 | 49.888
2025-04-27 | 3:11 | 49.888
2025-04-27 | 3:11 | 49.889
2025-04-27 | 3:11 | 49.89
2025-04-27 | 3:11 | 49.89
2025-04-27 | 3:11 | 49.891
2025-04-27 | 3:11 | 49.891
2025-04-27 | 3:11 | 49.891
2025-04-27 | 3:11 | 49.891
2025-04-27 | 3:11 | 49.891
2025-04-27 | 3:11 | 49.891
2025-04-27 | 3:11 | 49.891
2025-04-27 | 3:11 | 49.893
2025-04-27 | 3:11 | 49.894
2025-04-27 | 3:11 | 49.894
2025-04-27 | 3:11 | 49.894
2025-04-27 | 3:11 | 49.895
2025-04-27 | 3:11 | 49.895
2025-04-27 | 3:11 | 49.895
2025-04-27 | 3:11 | 49.896
2025-04-27 | 3:11 | 49.895
2025-04-27 | 3:11 | 49.895
2025-04-27 | 3:11 | 49.893
2025-04-27 | 3:11 | 49.893
2025-04-27 | 3:11 | 49.893
2025-04-27 | 3:11 | 49.893
2025-04-27 | 3:11 | 49.892
2025-04-27 | 3:11 | 49.893
2025-04-27 | 3:11 | 49.895
2025-04-27 | 3:11 | 49.894
2025-04-27 | 3:11 | 49.894
2025-04-27 | 3:11 | 49.895
2025-04-27 | 3:11 | 49.895
2025-04-27 | 3:11 | 49.894
2025-04-27 | 3:11 | 49.894
2025-04-27 | 3:11 | 49.894
2025-04-27 | 3:11 | 49.895
2025-04-27 | 3:11 | 49.896
2025-04-27 | 3:11 | 49.896
2025-04-27 | 3:12 | 49.897
2025-04-27 | 3:12 | 49.898
2025-04-27 | 3:12 | 49.898
2025-04-27 | 3:12 | 49.899
2025-04-27 | 3:12 | 49.899
2025-04-27 | 3:12 | 49.9
2025-04-27 | 3:12 | 49.9
2025-04-27 | 3:12 | 49.9
2025-04-27 | 3:12 | 49.9
2025-04-27 | 3:12 | 49.9
2025-04-27 | 3:12 | 49.901
2025-04-27 | 3:12 | 49.899
2025-04-27 | 3:12 | 49.899
2025-04-27 | 3:12 | 49.9
2025-04-27 | 3:12 | 49.9
2025-04-27 | 3:12 | 49.901
2025-04-27 | 3:12 | 49.902
2025-04-27 | 3:12 | 49.904
2025-04-27 | 3:12 | 49.906
2025-04-27 | 3:12 | 49.907
2025-04-27 | 3:12 | 49.907
2025-04-27 | 3:12 | 49.908
2025-04-27 | 3:12 | 49.908
2025-04-27 | 3:12 | 49.909
2025-04-27 | 3:12 | 49.914
2025-04-27 | 3:12 | 49.92
2025-04-27 | 3:12 | 49.923
2025-04-27 | 3:12 | 49.924
2025-04-27 | 3:12 | 49.924
2025-04-27 | 3:12 | 49.926
2025-04-27 | 3:12 | 49.928
2025-04-27 | 3:12 | 49.934
2025-04-27 | 3:12 | 49.94
2025-04-27 | 3:12 | 49.943
2025-04-27 | 3:12 | 49.945
2025-04-27 | 3:12 | 49.945
2025-04-27 | 3:12 | 49.945
2025-04-27 | 3:12 | 49.945
2025-04-27 | 3:12 | 49.945
2025-04-27 | 3:12 | 49.945
2025-04-27 | 3:12 | 49.943
2025-04-27 | 3:12 | 49.943
2025-04-27 | 3:12 | 49.942
2025-04-27 | 3:12 | 49.942
2025-04-27 | 3:12 | 49.941
2025-04-27 | 3:12 | 49.941
2025-04-27 | 3:12 | 49.94
2025-04-27 | 3:12 | 49.94
2025-04-27 | 3:12 | 49.943
2025-04-27 | 3:12 | 49.945
2025-04-27 | 3:12 | 49.944
2025-04-27 | 3:12 | 49.944
2025-04-27 | 3:12 | 49.944
2025-04-27 | 3:12 | 49.944
2025-04-27 | 3:12 | 49.946
2025-04-27 | 3:12 | 49.947
2025-04-27 | 3:12 | 49.948
2025-04-27 | 3:12 | 49.948
2025-04-27 | 3:12 | 49.95
2025-04-27 | 3:12 | 49.949
2025-04-27 | 3:12 | 49.95
2025-04-27 | 3:13 | 49.949
2025-04-27 | 3:13 | 49.951
2025-04-27 | 3:13 | 49.951
2025-04-27 | 3:13 | 49.952
2025-04-27 | 3:13 | 49.952
2025-04-27 | 3:13 | 49.95
2025-04-27 | 3:13 | 49.949
2025-04-27 | 3:13 | 49.948
2025-04-27 | 3:13 | 49.948
2025-04-27 | 3:13 | 49.948
2025-04-27 | 3:13 | 49.949
2025-04-27 | 3:13 | 49.951
2025-04-27 | 3:13 | 49.951
2025-04-27 | 3:13 | 49.953
2025-04-27 | 3:13 | 49.952
2025-04-27 | 3:13 | 49.951
2025-04-27 | 3:13 | 49.95
2025-04-27 | 3:13 | 49.951
2025-04-27 | 3:13 | 49.951
2025-04-27 | 3:13 | 49.952
2025-04-27 | 3:13 | 49.952
2025-04-27 | 3:13 | 49.95
2025-04-27 | 3:13 | 49.95
2025-04-27 | 3:13 | 49.95
2025-04-27 | 3:13 | 49.949
2025-04-27 | 3:13 | 49.948
2025-04-27 | 3:13 | 49.948
2025-04-27 | 3:13 | 49.947
2025-04-27 | 3:13 | 49.946
2025-04-27 | 3:13 | 49.945
2025-04-27 | 3:13 | 49.946
2025-04-27 | 3:13 | 49.956
2025-04-27 | 3:13 | 49.962
2025-04-27 | 3:13 | 49.965
2025-04-27 | 3:13 | 49.964
2025-04-27 | 3:13 | 49.964
2025-04-27 | 3:13 | 49.965
2025-04-27 | 3:13 | 49.968
2025-04-27 | 3:13 | 49.969
2025-04-27 | 3:13 | 49.97
2025-04-27 | 3:13 | 49.97
2025-04-27 | 3:13 | 49.971
2025-04-27 | 3:13 | 49.973
2025-04-27 | 3:13 | 49.974
2025-04-27 | 3:13 | 49.975
2025-04-27 | 3:13 | 49.976
2025-04-27 | 3:13 | 49.975
2025-04-27 | 3:13 | 49.977
2025-04-27 | 3:13 | 49.981
2025-04-27 | 3:13 | 49.983
2025-04-27 | 3:13 | 49.983
2025-04-27 | 3:13 | 49.983
2025-04-27 | 3:13 | 49.983
2025-04-27 | 3:13 | 49.984
2025-04-27 | 3:13 | 49.984
2025-04-27 | 3:13 | 49.984
2025-04-27 | 3:13 | 49.984
2025-04-27 | 3:13 | 49.982
2025-04-27 | 3:13 | 49.98
2025-04-27 | 3:14 | 49.981
2025-04-27 | 3:14 | 49.979
2025-04-27 | 3:14 | 49.979
2025-04-27 | 3:14 | 49.98
2025-04-27 | 3:14 | 49.981
2025-04-27 | 3:14 | 49.977
2025-04-27 | 3:14 | 49.973
2025-04-27 | 3:14 | 49.969
2025-04-27 | 3:14 | 49.967
2025-04-27 | 3:14 | 49.965
2025-04-27 | 3:14 | 49.963
2025-04-27 | 3:14 | 49.961
2025-04-27 | 3:14 | 49.962
2025-04-27 | 3:14 | 49.963
2025-04-27 | 3:14 | 49.965
2025-04-27 | 3:14 | 49.967
2025-04-27 | 3:14 | 49.968
2025-04-27 | 3:14 | 49.968
2025-04-27 | 3:14 | 49.969
2025-04-27 | 3:14 | 49.97
2025-04-27 | 3:14 | 49.97
2025-04-27 | 3:14 | 49.97
2025-04-27 | 3:14 | 49.97
2025-04-27 | 3:14 | 49.971
2025-04-27 | 3:14 | 49.97
2025-04-27 | 3:14 | 49.969
2025-04-27 | 3:14 | 49.967
2025-04-27 | 3:14 | 49.965
2025-04-27 | 3:14 | 49.966
2025-04-27 | 3:14 | 49.968
2025-04-27 | 3:14 | 49.97
2025-04-27 | 3:14 | 49.97
2025-04-27 | 3:14 | 49.974
2025-04-27 | 3:14 | 49.977
2025-04-27 | 3:14 | 49.979
2025-04-27 | 3:14 | 49.979
2025-04-27 | 3:14 | 49.981
2025-04-27 | 3:14 | 49.981
2025-04-27 | 3:14 | 49.981
2025-04-27 | 3:14 | 49.981
2025-04-27 | 3:14 | 49.98
2025-04-27 | 3:14 | 49.98
2025-04-27 | 3:14 | 49.979
2025-04-27 | 3:14 | 49.978
2025-04-27 | 3:14 | 49.977
2025-04-27 | 3:14 | 49.976
2025-04-27 | 3:14 | 49.974
2025-04-27 | 3:14 | 49.974
2025-04-27 | 3:14 | 49.973
2025-04-27 | 3:14 | 49.973
2025-04-27 | 3:14 | 49.972
2025-04-27 | 3:14 | 49.97
2025-04-27 | 3:14 | 49.969
2025-04-27 | 3:14 | 49.969
2025-04-27 | 3:14 | 49.97
2025-04-27 | 3:14 | 49.969
2025-04-27 | 3:14 | 49.968
2025-04-27 | 3:14 | 49.967
2025-04-27 | 3:14 | 49.967
2025-04-27 | 3:14 | 49.967
2025-04-27 | 3:14 | 49.967
2025-04-27 | 3:15 | 49.965
2025-04-27 | 3:15 | 49.965
2025-04-27 | 3:15 | 49.963
2025-04-27 | 3:15 | 49.961
2025-04-27 | 3:15 | 49.959
2025-04-27 | 3:15 | 49.958
2025-04-27 | 3:15 | 49.956
2025-04-27 | 3:15 | 49.956
2025-04-27 | 3:15 | 49.955
2025-04-27 | 3:15 | 49.955
2025-04-27 | 3:15 | 49.954
2025-04-27 | 3:15 | 49.955
2025-04-27 | 3:15 | 49.956
2025-04-27 | 3:15 | 49.958
2025-04-27 | 3:15 | 49.96
2025-04-27 | 3:15 | 49.96
2025-04-27 | 3:15 | 49.959
2025-04-27 | 3:15 | 49.959
2025-04-27 | 3:15 | 49.96
2025-04-27 | 3:15 | 49.96
2025-04-27 | 3:15 | 49.959
2025-04-27 | 3:15 | 49.959
2025-04-27 | 3:15 | 49.958
2025-04-27 | 3:15 | 49.958
2025-04-27 | 3:15 | 49.957
2025-04-27 | 3:15 | 49.957
2025-04-27 | 3:15 | 49.956
2025-04-27 | 3:15 | 49.955
2025-04-27 | 3:15 | 49.955
2025-04-27 | 3:15 | 49.955
2025-04-27 | 3:15 | 49.949
2025-04-27 | 3:15 | 49.939
2025-04-27 | 3:15 | 49.933
2025-04-27 | 3:15 | 49.933
2025-04-27 | 3:15 | 49.934
2025-04-27 | 3:15 | 49.935
2025-04-27 | 3:15 | 49.934
2025-04-27 | 3:15 | 49.935
2025-04-27 | 3:15 | 49.935
2025-04-27 | 3:15 | 49.936
2025-04-27 | 3:15 | 49.937
2025-04-27 | 3:15 | 49.938
2025-04-27 | 3:15 | 49.938
2025-04-27 | 3:15 | 49.939
2025-04-27 | 3:15 | 49.938
2025-04-27 | 3:15 | 49.939
2025-04-27 | 3:15 | 49.939
2025-04-27 | 3:15 | 49.938
2025-04-27 | 3:15 | 49.939
2025-04-27 | 3:15 | 49.939
2025-04-27 | 3:15 | 49.938
2025-04-27 | 3:15 | 49.94
2025-04-27 | 3:15 | 49.938
2025-04-27 | 3:15 | 49.94
2025-04-27 | 3:15 | 49.94
2025-04-27 | 3:15 | 49.94
2025-04-27 | 3:15 | 49.939
2025-04-27 | 3:15 | 49.94
2025-04-27 | 3:15 | 49.941
2025-04-27 | 3:15 | 49.941
2025-04-27 | 3:16 | 49.94
2025-04-27 | 3:16 | 49.941
2025-04-27 | 3:16 | 49.942
2025-04-27 | 3:16 | 49.943
2025-04-27 | 3:16 | 49.943
2025-04-27 | 3:16 | 49.943
2025-04-27 | 3:16 | 49.943
2025-04-27 | 3:16 | 49.943
2025-04-27 | 3:16 | 49.944
2025-04-27 | 3:16 | 49.942
2025-04-27 | 3:16 | 49.941
2025-04-27 | 3:16 | 49.942
2025-04-27 | 3:16 | 49.942
2025-04-27 | 3:16 | 49.942
2025-04-27 | 3:16 | 49.941
2025-04-27 | 3:16 | 49.939
2025-04-27 | 3:16 | 49.94
2025-04-27 | 3:16 | 49.94
2025-04-27 | 3:16 | 49.941
2025-04-27 | 3:16 | 49.941
2025-04-27 | 3:16 | 49.941
2025-04-27 | 3:16 | 49.942
2025-04-27 | 3:16 | 49.942
2025-04-27 | 3:16 | 49.943
2025-04-27 | 3:16 | 49.944
2025-04-27 | 3:16 | 49.946
2025-04-27 | 3:16 | 49.946
2025-04-27 | 3:16 | 49.948
2025-04-27 | 3:16 | 49.95
2025-04-27 | 3:16 | 49.949
2025-04-27 | 3:16 | 49.943
2025-04-27 | 3:16 | 49.936
2025-04-27 | 3:16 | 49.93
2025-04-27 | 3:16 | 49.93
2025-04-27 | 3:16 | 49.931
2025-04-27 | 3:16 | 49.932
2025-04-27 | 3:16 | 49.933
2025-04-27 | 3:16 | 49.934
2025-04-27 | 3:16 | 49.935
2025-04-27 | 3:16 | 49.938
2025-04-27 | 3:16 | 49.939
2025-04-27 | 3:16 | 49.94
2025-04-27 | 3:16 | 49.94
2025-04-27 | 3:16 | 49.94
2025-04-27 | 3:16 | 49.94
2025-04-27 | 3:16 | 49.939
2025-04-27 | 3:16 | 49.939
2025-04-27 | 3:16 | 49.938
2025-04-27 | 3:16 | 49.938
2025-04-27 | 3:16 | 49.939
2025-04-27 | 3:16 | 49.938
2025-04-27 | 3:16 | 49.938
2025-04-27 | 3:16 | 49.938
2025-04-27 | 3:16 | 49.938
2025-04-27 | 3:16 | 49.94
2025-04-27 | 3:16 | 49.936
2025-04-27 | 3:16 | 49.935
2025-04-27 | 3:16 | 49.935
2025-04-27 | 3:16 | 49.935
2025-04-27 | 3:16 | 49.935
2025-04-27 | 3:17 | 49.935
2025-04-27 | 3:17 | 49.935
2025-04-27 | 3:17 | 49.937
2025-04-27 | 3:17 | 49.937
2025-04-27 | 3:17 | 49.938
2025-04-27 | 3:17 | 49.937
2025-04-27 | 3:17 | 49.934
2025-04-27 | 3:17 | 49.935
2025-04-27 | 3:17 | 49.935
2025-04-27 | 3:17 | 49.935
2025-04-27 | 3:17 | 49.934
2025-04-27 | 3:17 | 49.933
2025-04-27 | 3:17 | 49.932
2025-04-27 | 3:17 | 49.932
2025-04-27 | 3:17 | 49.931
2025-04-27 | 3:17 | 49.93
2025-04-27 | 3:17 | 49.93
2025-04-27 | 3:17 | 49.93
2025-04-27 | 3:17 | 49.93
2025-04-27 | 3:17 | 49.928
2025-04-27 | 3:17 | 49.926
2025-04-27 | 3:17 | 49.924
2025-04-27 | 3:17 | 49.922
2025-04-27 | 3:17 | 49.922
2025-04-27 | 3:17 | 49.923
2025-04-27 | 3:17 | 49.923
2025-04-27 | 3:17 | 49.923
2025-04-27 | 3:17 | 49.923
2025-04-27 | 3:17 | 49.922
2025-04-27 | 3:17 | 49.921
2025-04-27 | 3:17 | 49.92
2025-04-27 | 3:17 | 49.92
2025-04-27 | 3:17 | 49.921
2025-04-27 | 3:17 | 49.923
2025-04-27 | 3:17 | 49.923
2025-04-27 | 3:17 | 49.924
2025-04-27 | 3:17 | 49.925
2025-04-27 | 3:17 | 49.926
2025-04-27 | 3:17 | 49.926
2025-04-27 | 3:17 | 49.926
2025-04-27 | 3:17 | 49.925
2025-04-27 | 3:17 | 49.923
2025-04-27 | 3:17 | 49.922
2025-04-27 | 3:17 | 49.922
2025-04-27 | 3:17 | 49.921
2025-04-27 | 3:17 | 49.919
2025-04-27 | 3:17 | 49.918
2025-04-27 | 3:17 | 49.919
2025-04-27 | 3:17 | 49.919
2025-04-27 | 3:17 | 49.921
2025-04-27 | 3:17 | 49.922
2025-04-27 | 3:17 | 49.923
2025-04-27 | 3:17 | 49.925
2025-04-27 | 3:17 | 49.928
2025-04-27 | 3:17 | 49.928
2025-04-27 | 3:17 | 49.929
2025-04-27 | 3:17 | 49.93
2025-04-27 | 3:17 | 49.931
2025-04-27 | 3:17 | 49.931
2025-04-27 | 3:18 | 49.932
2025-04-27 | 3:18 | 49.931
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.928
2025-04-27 | 3:18 | 49.93
2025-04-27 | 3:18 | 49.931
2025-04-27 | 3:18 | 49.931
2025-04-27 | 3:18 | 49.932
2025-04-27 | 3:18 | 49.933
2025-04-27 | 3:18 | 49.932
2025-04-27 | 3:18 | 49.931
2025-04-27 | 3:18 | 49.932
2025-04-27 | 3:18 | 49.932
2025-04-27 | 3:18 | 49.931
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.931
2025-04-27 | 3:18 | 49.93
2025-04-27 | 3:18 | 49.93
2025-04-27 | 3:18 | 49.93
2025-04-27 | 3:18 | 49.93
2025-04-27 | 3:18 | 49.931
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.928
2025-04-27 | 3:18 | 49.927
2025-04-27 | 3:18 | 49.926
2025-04-27 | 3:18 | 49.927
2025-04-27 | 3:18 | 49.927
2025-04-27 | 3:18 | 49.928
2025-04-27 | 3:18 | 49.927
2025-04-27 | 3:18 | 49.928
2025-04-27 | 3:18 | 49.929
2025-04-27 | 3:18 | 49.931
2025-04-27 | 3:18 | 49.931
2025-04-27 | 3:18 | 49.931
2025-04-27 | 3:18 | 49.93
2025-04-27 | 3:18 | 49.932
2025-04-27 | 3:18 | 49.933
2025-04-27 | 3:18 | 49.934
2025-04-27 | 3:18 | 49.933
2025-04-27 | 3:18 | 49.936
2025-04-27 | 3:18 | 49.936
2025-04-27 | 3:18 | 49.936
2025-04-27 | 3:18 | 49.936
2025-04-27 | 3:18 | 49.935
2025-04-27 | 3:18 | 49.934
2025-04-27 | 3:18 | 49.934
2025-04-27 | 3:18 | 49.936
2025-04-27 | 3:18 | 49.936
2025-04-27 | 3:18 | 49.936
2025-04-27 | 3:18 | 49.935
2025-04-27 | 3:18 | 49.936
2025-04-27 | 3:18 | 49.936
2025-04-27 | 3:18 | 49.937
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.935
2025-04-27 | 3:19 | 49.935
2025-04-27 | 3:19 | 49.935
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.938
2025-04-27 | 3:19 | 49.938
2025-04-27 | 3:19 | 49.938
2025-04-27 | 3:19 | 49.937
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.937
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.939
2025-04-27 | 3:19 | 49.937
2025-04-27 | 3:19 | 49.937
2025-04-27 | 3:19 | 49.935
2025-04-27 | 3:19 | 49.934
2025-04-27 | 3:19 | 49.933
2025-04-27 | 3:19 | 49.931
2025-04-27 | 3:19 | 49.93
2025-04-27 | 3:19 | 49.93
2025-04-27 | 3:19 | 49.931
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.939
2025-04-27 | 3:19 | 49.94
2025-04-27 | 3:19 | 49.939
2025-04-27 | 3:19 | 49.939
2025-04-27 | 3:19 | 49.938
2025-04-27 | 3:19 | 49.938
2025-04-27 | 3:19 | 49.935
2025-04-27 | 3:19 | 49.934
2025-04-27 | 3:19 | 49.934
2025-04-27 | 3:19 | 49.935
2025-04-27 | 3:19 | 49.935
2025-04-27 | 3:19 | 49.934
2025-04-27 | 3:19 | 49.935
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.934
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.937
2025-04-27 | 3:19 | 49.936
2025-04-27 | 3:19 | 49.935
2025-04-27 | 3:19 | 49.933
2025-04-27 | 3:19 | 49.934
2025-04-27 | 3:19 | 49.933
2025-04-27 | 3:19 | 49.932
2025-04-27 | 3:19 | 49.93
2025-04-27 | 3:19 | 49.929
2025-04-27 | 3:19 | 49.929
2025-04-27 | 3:19 | 49.928
2025-04-27 | 3:19 | 49.929
2025-04-27 | 3:19 | 49.928
2025-04-27 | 3:19 | 49.927
2025-04-27 | 3:19 | 49.928
2025-04-27 | 3:19 | 49.927
2025-04-27 | 3:20 | 49.928
2025-04-27 | 3:20 | 49.928
2025-04-27 | 3:20 | 49.929
2025-04-27 | 3:20 | 49.929
2025-04-27 | 3:20 | 49.93
2025-04-27 | 3:20 | 49.93
2025-04-27 | 3:20 | 49.929
2025-04-27 | 3:20 | 49.928
2025-04-27 | 3:20 | 49.928
2025-04-27 | 3:20 | 49.929
2025-04-27 | 3:20 | 49.93
2025-04-27 | 3:20 | 49.933
2025-04-27 | 3:20 | 49.934
2025-04-27 | 3:20 | 49.936
2025-04-27 | 3:20 | 49.936
2025-04-27 | 3:20 | 49.936
2025-04-27 | 3:20 | 49.936
2025-04-27 | 3:20 | 49.935
2025-04-27 | 3:20 | 49.934
2025-04-27 | 3:20 | 49.933
2025-04-27 | 3:20 | 49.933
2025-04-27 | 3:20 | 49.932
2025-04-27 | 3:20 | 49.932
2025-04-27 | 3:20 | 49.932
2025-04-27 | 3:20 | 49.931
2025-04-27 | 3:20 | 49.93
2025-04-27 | 3:20 | 49.929
2025-04-27 | 3:20 | 49.93
2025-04-27 | 3:20 | 49.929
2025-04-27 | 3:20 | 49.93
2025-04-27 | 3:20 | 49.93
2025-04-27 | 3:20 | 49.928
2025-04-27 | 3:20 | 49.926
2025-04-27 | 3:20 | 49.926
2025-04-27 | 3:20 | 49.925
2025-04-27 | 3:20 | 49.924
2025-04-27 | 3:20 | 49.925
2025-04-27 | 3:20 | 49.925
2025-04-27 | 3:20 | 49.927
2025-04-27 | 3:20 | 49.927
2025-04-27 | 3:20 | 49.926
2025-04-27 | 3:20 | 49.925
2025-04-27 | 3:20 | 49.924
2025-04-27 | 3:20 | 49.923
2025-04-27 | 3:20 | 49.922
2025-04-27 | 3:20 | 49.922
2025-04-27 | 3:20 | 49.922
2025-04-27 | 3:20 | 49.923
2025-04-27 | 3:20 | 49.922
2025-04-27 | 3:20 | 49.923
2025-04-27 | 3:20 | 49.923
2025-04-27 | 3:20 | 49.922
2025-04-27 | 3:20 | 49.922
2025-04-27 | 3:20 | 49.92
2025-04-27 | 3:20 | 49.92
2025-04-27 | 3:20 | 49.919
2025-04-27 | 3:20 | 49.919
2025-04-27 | 3:20 | 49.918
2025-04-27 | 3:20 | 49.919
2025-04-27 | 3:20 | 49.918
2025-04-27 | 3:20 | 49.917
2025-04-27 | 3:21 | 49.916
2025-04-27 | 3:21 | 49.915
2025-04-27 | 3:21 | 49.915
2025-04-27 | 3:21 | 49.915
2025-04-27 | 3:21 | 49.916
2025-04-27 | 3:21 | 49.916
2025-04-27 | 3:21 | 49.917
2025-04-27 | 3:21 | 49.917
2025-04-27 | 3:21 | 49.917
2025-04-27 | 3:21 | 49.918
2025-04-27 | 3:21 | 49.917
2025-04-27 | 3:21 | 49.919
2025-04-27 | 3:21 | 49.919
2025-04-27 | 3:21 | 49.92
2025-04-27 | 3:21 | 49.92
2025-04-27 | 3:21 | 49.921
2025-04-27 | 3:21 | 49.921
2025-04-27 | 3:21 | 49.921
2025-04-27 | 3:21 | 49.922
2025-04-27 | 3:21 | 49.923
2025-04-27 | 3:21 | 49.923
2025-04-27 | 3:21 | 49.923
2025-04-27 | 3:21 | 49.923
2025-04-27 | 3:21 | 49.922
2025-04-27 | 3:21 | 49.923
2025-04-27 | 3:21 | 49.923
2025-04-27 | 3:21 | 49.922
2025-04-27 | 3:21 | 49.923
2025-04-27 | 3:21 | 49.924
2025-04-27 | 3:21 | 49.923
2025-04-27 | 3:21 | 49.926
2025-04-27 | 3:21 | 49.928
2025-04-27 | 3:21 | 49.93
2025-04-27 | 3:21 | 49.932
2025-04-27 | 3:21 | 49.934
2025-04-27 | 3:21 | 49.934
2025-04-27 | 3:21 | 49.934
2025-04-27 | 3:21 | 49.934
2025-04-27 | 3:21 | 49.932
2025-04-27 | 3:21 | 49.932
2025-04-27 | 3:21 | 49.932
2025-04-27 | 3:21 | 49.932
2025-04-27 | 3:21 | 49.933
2025-04-27 | 3:21 | 49.932
2025-04-27 | 3:21 | 49.933
2025-04-27 | 3:21 | 49.931
2025-04-27 | 3:21 | 49.931
2025-04-27 | 3:21 | 49.931
2025-04-27 | 3:21 | 49.932
2025-04-27 | 3:21 | 49.933
2025-04-27 | 3:21 | 49.934
2025-04-27 | 3:21 | 49.933
2025-04-27 | 3:21 | 49.932
2025-04-27 | 3:21 | 49.933
2025-04-27 | 3:21 | 49.932
2025-04-27 | 3:21 | 49.931
2025-04-27 | 3:21 | 49.931
2025-04-27 | 3:21 | 49.932
2025-04-27 | 3:21 | 49.93
2025-04-27 | 3:22 | 49.93
2025-04-27 | 3:22 | 49.929
2025-04-27 | 3:22 | 49.929
2025-04-27 | 3:22 | 49.929
2025-04-27 | 3:22 | 49.93
2025-04-27 | 3:22 | 49.93
2025-04-27 | 3:22 | 49.93
2025-04-27 | 3:22 | 49.931
2025-04-27 | 3:22 | 49.933
2025-04-27 | 3:22 | 49.934
2025-04-27 | 3:22 | 49.934
2025-04-27 | 3:22 | 49.934
2025-04-27 | 3:22 | 49.935
2025-04-27 | 3:22 | 49.934
2025-04-27 | 3:22 | 49.934
2025-04-27 | 3:22 | 49.934
2025-04-27 | 3:22 | 49.934
2025-04-27 | 3:22 | 49.934
2025-04-27 | 3:22 | 49.936
2025-04-27 | 3:22 | 49.935
2025-04-27 | 3:22 | 49.935
2025-04-27 | 3:22 | 49.935
2025-04-27 | 3:22 | 49.935
2025-04-27 | 3:22 | 49.936
2025-04-27 | 3:22 | 49.935
2025-04-27 | 3:22 | 49.935
2025-04-27 | 3:22 | 49.934
2025-04-27 | 3:22 | 49.935
2025-04-27 | 3:22 | 49.934
2025-04-27 | 3:22 | 49.936
2025-04-27 | 3:22 | 49.936
2025-04-27 | 3:22 | 49.936
2025-04-27 | 3:22 | 49.936
2025-04-27 | 3:22 | 49.937
2025-04-27 | 3:22 | 49.938
2025-04-27 | 3:22 | 49.94
2025-04-27 | 3:22 | 49.942
2025-04-27 | 3:22 | 49.943
2025-04-27 | 3:22 | 49.943
2025-04-27 | 3:22 | 49.944
2025-04-27 | 3:22 | 49.943
2025-04-27 | 3:22 | 49.944
2025-04-27 | 3:22 | 49.944
2025-04-27 | 3:22 | 49.943
2025-04-27 | 3:22 | 49.943
2025-04-27 | 3:22 | 49.942
2025-04-27 | 3:22 | 49.942
2025-04-27 | 3:22 | 49.941
2025-04-27 | 3:22 | 49.942
2025-04-27 | 3:22 | 49.943
2025-04-27 | 3:22 | 49.945
2025-04-27 | 3:22 | 49.945
2025-04-27 | 3:22 | 49.946
2025-04-27 | 3:22 | 49.945
2025-04-27 | 3:22 | 49.945
2025-04-27 | 3:22 | 49.945
2025-04-27 | 3:22 | 49.946
2025-04-27 | 3:22 | 49.946
2025-04-27 | 3:22 | 49.945
2025-04-27 | 3:22 | 49.944
2025-04-27 | 3:22 | 49.944
2025-04-27 | 3:23 | 49.944
2025-04-27 | 3:23 | 49.944
2025-04-27 | 3:23 | 49.944
2025-04-27 | 3:23 | 49.944
2025-04-27 | 3:23 | 49.946
2025-04-27 | 3:23 | 49.948
2025-04-27 | 3:23 | 49.949
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.952
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.949
2025-04-27 | 3:23 | 49.949
2025-04-27 | 3:23 | 49.948
2025-04-27 | 3:23 | 49.949
2025-04-27 | 3:23 | 49.95
2025-04-27 | 3:23 | 49.95
2025-04-27 | 3:23 | 49.95
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.952
2025-04-27 | 3:23 | 49.952
2025-04-27 | 3:23 | 49.953
2025-04-27 | 3:23 | 49.953
2025-04-27 | 3:23 | 49.952
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.952
2025-04-27 | 3:23 | 49.953
2025-04-27 | 3:23 | 49.953
2025-04-27 | 3:23 | 49.952
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.95
2025-04-27 | 3:23 | 49.95
2025-04-27 | 3:23 | 49.949
2025-04-27 | 3:23 | 49.948
2025-04-27 | 3:23 | 49.948
2025-04-27 | 3:23 | 49.948
2025-04-27 | 3:23 | 49.948
2025-04-27 | 3:23 | 49.946
2025-04-27 | 3:23 | 49.947
2025-04-27 | 3:23 | 49.947
2025-04-27 | 3:23 | 49.948
2025-04-27 | 3:23 | 49.949
2025-04-27 | 3:23 | 49.949
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.951
2025-04-27 | 3:23 | 49.95
2025-04-27 | 3:23 | 49.95
2025-04-27 | 3:23 | 49.949
2025-04-27 | 3:23 | 49.95
2025-04-27 | 3:23 | 49.95
2025-04-27 | 3:23 | 49.95
2025-04-27 | 3:24 | 49.949
2025-04-27 | 3:24 | 49.946
2025-04-27 | 3:24 | 49.945
2025-04-27 | 3:24 | 49.945
2025-04-27 | 3:24 | 49.945
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.943
2025-04-27 | 3:24 | 49.943
2025-04-27 | 3:24 | 49.942
2025-04-27 | 3:24 | 49.943
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.943
2025-04-27 | 3:24 | 49.943
2025-04-27 | 3:24 | 49.942
2025-04-27 | 3:24 | 49.943
2025-04-27 | 3:24 | 49.942
2025-04-27 | 3:24 | 49.942
2025-04-27 | 3:24 | 49.943
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.945
2025-04-27 | 3:24 | 49.944
2025-04-27 | 3:24 | 49.946
2025-04-27 | 3:24 | 49.948
2025-04-27 | 3:24 | 49.95
2025-04-27 | 3:24 | 49.952
2025-04-27 | 3:24 | 49.953
2025-04-27 | 3:24 | 49.954
2025-04-27 | 3:24 | 49.956
2025-04-27 | 3:24 | 49.956
2025-04-27 | 3:24 | 49.958
2025-04-27 | 3:24 | 49.958
2025-04-27 | 3:24 | 49.957
2025-04-27 | 3:24 | 49.957
2025-04-27 | 3:24 | 49.956
2025-04-27 | 3:24 | 49.955
2025-04-27 | 3:24 | 49.953
2025-04-27 | 3:24 | 49.954
2025-04-27 | 3:24 | 49.955
2025-04-27 | 3:24 | 49.956
2025-04-27 | 3:24 | 49.956
2025-04-27 | 3:24 | 49.957
2025-04-27 | 3:24 | 49.956
2025-04-27 | 3:24 | 49.956
2025-04-27 | 3:24 | 49.957
2025-04-27 | 3:24 | 49.956
2025-04-27 | 3:24 | 49.958
2025-04-27 | 3:24 | 49.958
2025-04-27 | 3:24 | 49.96
2025-04-27 | 3:24 | 49.961
2025-04-27 | 3:24 | 49.962
2025-04-27 | 3:25 | 49.964
2025-04-27 | 3:25 | 49.965
2025-04-27 | 3:25 | 49.966
2025-04-27 | 3:25 | 49.967
2025-04-27 | 3:25 | 49.968
2025-04-27 | 3:25 | 49.967
2025-04-27 | 3:25 | 49.967
2025-04-27 | 3:25 | 49.967
2025-04-27 | 3:25 | 49.965
2025-04-27 | 3:25 | 49.964
2025-04-27 | 3:25 | 49.961
2025-04-27 | 3:25 | 49.961
2025-04-27 | 3:25 | 49.959
2025-04-27 | 3:25 | 49.959
2025-04-27 | 3:25 | 49.959
2025-04-27 | 3:25 | 49.957
2025-04-27 | 3:25 | 49.956
2025-04-27 | 3:25 | 49.957
2025-04-27 | 3:25 | 49.956
2025-04-27 | 3:25 | 49.956
2025-04-27 | 3:25 | 49.956
2025-04-27 | 3:25 | 49.956
2025-04-27 | 3:25 | 49.957
2025-04-27 | 3:25 | 49.958
2025-04-27 | 3:25 | 49.959
2025-04-27 | 3:25 | 49.958
2025-04-27 | 3:25 | 49.957
2025-04-27 | 3:25 | 49.957
2025-04-27 | 3:25 | 49.956
2025-04-27 | 3:25 | 49.955
2025-04-27 | 3:25 | 49.954
2025-04-27 | 3:25 | 49.956
2025-04-27 | 3:25 | 49.956
2025-04-27 | 3:25 | 49.958
2025-04-27 | 3:25 | 49.96
2025-04-27 | 3:25 | 49.961
2025-04-27 | 3:25 | 49.961
2025-04-27 | 3:25 | 49.961
2025-04-27 | 3:25 | 49.962
2025-04-27 | 3:25 | 49.961
2025-04-27 | 3:25 | 49.963
2025-04-27 | 3:25 | 49.963
2025-04-27 | 3:25 | 49.964
2025-04-27 | 3:25 | 49.966
2025-04-27 | 3:25 | 49.966
2025-04-27 | 3:25 | 49.966
2025-04-27 | 3:25 | 49.967
2025-04-27 | 3:25 | 49.968
2025-04-27 | 3:25 | 49.969
2025-04-27 | 3:25 | 49.969
2025-04-27 | 3:25 | 49.969
2025-04-27 | 3:25 | 49.97
2025-04-27 | 3:25 | 49.972
2025-04-27 | 3:25 | 49.972
2025-04-27 | 3:25 | 49.972
2025-04-27 | 3:25 | 49.971
2025-04-27 | 3:25 | 49.972
2025-04-27 | 3:25 | 49.971
2025-04-27 | 3:25 | 49.97
2025-04-27 | 3:26 | 49.97
2025-04-27 | 3:26 | 49.97
2025-04-27 | 3:26 | 49.971
2025-04-27 | 3:26 | 49.973
2025-04-27 | 3:26 | 49.973
2025-04-27 | 3:26 | 49.972
2025-04-27 | 3:26 | 49.972
2025-04-27 | 3:26 | 49.972
2025-04-27 | 3:26 | 49.972
2025-04-27 | 3:26 | 49.972
2025-04-27 | 3:26 | 49.974
2025-04-27 | 3:26 | 49.975
2025-04-27 | 3:26 | 49.976
2025-04-27 | 3:26 | 49.976
2025-04-27 | 3:26 | 49.976
2025-04-27 | 3:26 | 49.978
2025-04-27 | 3:26 | 49.978
2025-04-27 | 3:26 | 49.979
2025-04-27 | 3:26 | 49.979
2025-04-27 | 3:26 | 49.981
2025-04-27 | 3:26 | 49.982
2025-04-27 | 3:26 | 49.981
2025-04-27 | 3:26 | 49.982
2025-04-27 | 3:26 | 49.983
2025-04-27 | 3:26 | 49.984
2025-04-27 | 3:26 | 49.986
2025-04-27 | 3:26 | 49.986
2025-04-27 | 3:26 | 49.986
2025-04-27 | 3:26 | 49.985
2025-04-27 | 3:26 | 49.985
2025-04-27 | 3:26 | 49.985
2025-04-27 | 3:26 | 49.985
2025-04-27 | 3:26 | 49.987
2025-04-27 | 3:26 | 49.99
2025-04-27 | 3:26 | 49.994
2025-04-27 | 3:26 | 49.996
2025-04-27 | 3:26 | 49.999
2025-04-27 | 3:26 | 50.001
2025-04-27 | 3:26 | 50.005
2025-04-27 | 3:26 | 50.005
2025-04-27 | 3:26 | 50.005
2025-04-27 | 3:26 | 50.002
2025-04-27 | 3:26 | 50.001
2025-04-27 | 3:26 | 49.997
2025-04-27 | 3:26 | 49.994
2025-04-27 | 3:26 | 49.993
2025-04-27 | 3:26 | 49.99
2025-04-27 | 3:26 | 49.988
2025-04-27 | 3:26 | 49.986
2025-04-27 | 3:26 | 49.986
2025-04-27 | 3:26 | 49.987
2025-04-27 | 3:26 | 49.986
2025-04-27 | 3:26 | 49.985
2025-04-27 | 3:26 | 49.984
2025-04-27 | 3:26 | 49.984
2025-04-27 | 3:26 | 49.984
2025-04-27 | 3:26 | 49.985
2025-04-27 | 3:26 | 49.987
2025-04-27 | 3:26 | 49.99
2025-04-27 | 3:26 | 49.993
2025-04-27 | 3:26 | 49.994
2025-04-27 | 3:27 | 49.994
2025-04-27 | 3:27 | 49.995
2025-04-27 | 3:27 | 49.996
2025-04-27 | 3:27 | 49.996
2025-04-27 | 3:27 | 49.997
2025-04-27 | 3:27 | 49.999
2025-04-27 | 3:27 | 50
2025-04-27 | 3:27 | 50.002
2025-04-27 | 3:27 | 50.004
2025-04-27 | 3:27 | 50.006
2025-04-27 | 3:27 | 50.006
2025-04-27 | 3:27 | 50.007
2025-04-27 | 3:27 | 50.007
2025-04-27 | 3:27 | 50.01
2025-04-27 | 3:27 | 50.011
2025-04-27 | 3:27 | 50.011
2025-04-27 | 3:27 | 50.012
2025-04-27 | 3:27 | 50.011
2025-04-27 | 3:27 | 50.011
2025-04-27 | 3:27 | 50.01
2025-04-27 | 3:27 | 50.009
2025-04-27 | 3:27 | 50.01
2025-04-27 | 3:27 | 50.01
2025-04-27 | 3:27 | 50.012
2025-04-27 | 3:27 | 50.012
2025-04-27 | 3:27 | 50.013
2025-04-27 | 3:27 | 50.014
2025-04-27 | 3:27 | 50.014
2025-04-27 | 3:27 | 50.013
2025-04-27 | 3:27 | 50.012
2025-04-27 | 3:27 | 50.004
2025-04-27 | 3:27 | 49.997
2025-04-27 | 3:27 | 49.993
2025-04-27 | 3:27 | 49.988
2025-04-27 | 3:27 | 49.986
2025-04-27 | 3:27 | 49.983
2025-04-27 | 3:27 | 49.985
2025-04-27 | 3:27 | 49.987
2025-04-27 | 3:27 | 49.991
2025-04-27 | 3:27 | 49.997
2025-04-27 | 3:27 | 50.002
2025-04-27 | 3:27 | 50.007
2025-04-27 | 3:27 | 50.011
2025-04-27 | 3:27 | 50.014
2025-04-27 | 3:27 | 50.015
2025-04-27 | 3:27 | 50.015
2025-04-27 | 3:27 | 50.014
2025-04-27 | 3:27 | 50.015
2025-04-27 | 3:27 | 50.014
2025-04-27 | 3:27 | 50.014
2025-04-27 | 3:27 | 50.012
2025-04-27 | 3:27 | 50.01
2025-04-27 | 3:27 | 50.008
2025-04-27 | 3:27 | 50.002
2025-04-27 | 3:27 | 49.998
2025-04-27 | 3:27 | 49.995
2025-04-27 | 3:27 | 49.991
2025-04-27 | 3:27 | 49.986
2025-04-27 | 3:27 | 49.983
2025-04-27 | 3:27 | 49.981
2025-04-27 | 3:28 | 49.981
2025-04-27 | 3:28 | 49.981
2025-04-27 | 3:28 | 49.982
2025-04-27 | 3:28 | 49.982
2025-04-27 | 3:28 | 49.982
2025-04-27 | 3:28 | 49.981
2025-04-27 | 3:28 | 49.982
2025-04-27 | 3:28 | 49.982
2025-04-27 | 3:28 | 49.983
2025-04-27 | 3:28 | 49.984
2025-04-27 | 3:28 | 49.984
2025-04-27 | 3:28 | 49.985
2025-04-27 | 3:28 | 49.984
2025-04-27 | 3:28 | 49.985
2025-04-27 | 3:28 | 49.984
2025-04-27 | 3:28 | 49.984
2025-04-27 | 3:28 | 49.983
2025-04-27 | 3:28 | 49.983
2025-04-27 | 3:28 | 49.983
2025-04-27 | 3:28 | 49.982
2025-04-27 | 3:28 | 49.983
2025-04-27 | 3:28 | 49.984
2025-04-27 | 3:28 | 49.986
2025-04-27 | 3:28 | 49.988
2025-04-27 | 3:28 | 49.989
2025-04-27 | 3:28 | 49.992
2025-04-27 | 3:28 | 49.993
2025-04-27 | 3:28 | 49.995
2025-04-27 | 3:28 | 49.997
2025-04-27 | 3:28 | 49.998
2025-04-27 | 3:28 | 49.997
2025-04-27 | 3:28 | 49.997
2025-04-27 | 3:28 | 49.995
2025-04-27 | 3:28 | 49.994
2025-04-27 | 3:28 | 49.995
2025-04-27 | 3:28 | 49.995
2025-04-27 | 3:28 | 49.996
2025-04-27 | 3:28 | 49.996
2025-04-27 | 3:28 | 49.996
2025-04-27 | 3:28 | 49.994
2025-04-27 | 3:28 | 49.994

## 20250427-2
In GMT
Date | Time | Freq
2025-04-27 | 10:31 | 49.936 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-04-27 | 10:31 | 49.933 | 222 | BRITNED | 676.211
2025-04-27 | 10:31 | 49.928 | 268 | WBURB-2 | 428.156
2025-04-27 | 10:31 | 49.928 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-04-27 | 10:31 | 49.929 |  | Viking Link | -648.9
2025-04-27 | 10:31 | 49.928 |  | Viking Link | 1398.96
2025-04-27 | 10:31 | 49.925 | 209 | DRAXX-3 | 626.95
2025-04-27 | 10:31 | 49.926 | 154 | CDCL-1 | 391.57
2025-04-27 | 10:31 | 49.928 | 268 | ROCK-1 | 468.495
2025-04-27 | 10:31 | 49.926 | 148 | IFA Bipole1 | 945.473
2025-04-27 | 10:31 | 49.929 | 132 | IFA Bipole1 | 999.1
2025-04-27 | 10:31 | 49.933 | 141 | IFA Bipole2 | 1000
2025-04-27 | 10:31 | 49.935 | 135 | IFA Bipole1 | 996.75
2025-04-27 | 10:31 | 49.936 |  | Viking Link | -780.3
2025-04-27 | 10:31 | 49.936
2025-04-27 | 10:31 | 49.933
2025-04-27 | 10:31 | 49.935
2025-04-27 | 10:31 | 49.936
2025-04-27 | 10:31 | 49.938
2025-04-27 | 10:31 | 49.94 | 130 | HEYM12 | 271.908
2025-04-27 | 10:31 | 49.936 | 228 | HUMR-1 | 303.75
2025-04-27 | 10:31 | 49.937
2025-04-27 | 10:31 | 49.941
2025-04-27 | 10:32 | 49.944
2025-04-27 | 10:32 | 49.944
2025-04-27 | 10:32 | 49.946
2025-04-27 | 10:32 | 49.947
2025-04-27 | 10:32 | 49.945
2025-04-27 | 10:32 | 49.944
2025-04-27 | 10:32 | 49.942
2025-04-27 | 10:32 | 49.94 | 211 | CDCL-1 | 291.5
2025-04-27 | 10:32 | 49.939 | 199 | STAY-2 | 413.125
2025-04-27 | 10:32 | 49.938 | 173 | CDCL-1 | 397.375
2025-04-27 | 10:32 | 49.94 | 248 | SEAB-2 | 361.25
2025-04-27 | 10:32 | 49.938 | 255 | FRANCE | 995.65
2025-04-27 | 10:32 | 49.94 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-04-27 | 10:32 | 49.939
2025-04-27 | 10:32 | 49.938
2025-04-27 | 10:32 | 49.935
2025-04-27 | 10:32 | 49.935
2025-04-27 | 10:32 | 49.936
2025-04-27 | 10:32 | 49.936
2025-04-27 | 10:32 | 49.939
2025-04-27 | 10:32 | 49.938
2025-04-27 | 10:32 | 49.937
2025-04-27 | 10:32 | 49.936
2025-04-27 | 10:32 | 49.937
2025-04-27 | 10:32 | 49.937
2025-04-27 | 10:32 | 49.941
2025-04-27 | 10:32 | 49.943
2025-04-27 | 10:32 | 49.94
2025-04-27 | 10:32 | 49.937
2025-04-27 | 10:32 | 49.933
2025-04-27 | 10:32 | 49.929
2025-04-27 | 10:32 | 49.928
2025-04-27 | 10:32 | 49.926
2025-04-27 | 10:32 | 49.926
2025-04-27 | 10:32 | 49.93
2025-04-27 | 10:32 | 49.932
2025-04-27 | 10:32 | 49.935
2025-04-27 | 10:32 | 49.937
2025-04-27 | 10:32 | 49.896
2025-04-27 | 10:32 | 49.843
2025-04-27 | 10:32 | 49.837
2025-04-27 | 10:32 | 49.846
2025-04-27 | 10:32 | 49.854
2025-04-27 | 10:32 | 49.854
2025-04-27 | 10:32 | 49.85
2025-04-27 | 10:32 | 49.853
2025-04-27 | 10:32 | 49.85
2025-04-27 | 10:32 | 49.848
2025-04-27 | 10:32 | 49.847
2025-04-27 | 10:32 | 49.845
2025-04-27 | 10:32 | 49.844
2025-04-27 | 10:32 | 49.842
2025-04-27 | 10:32 | 49.841
2025-04-27 | 10:32 | 49.843
2025-04-27 | 10:32 | 49.845
2025-04-27 | 10:32 | 49.845
2025-04-27 | 10:32 | 49.844
2025-04-27 | 10:32 | 49.841
2025-04-27 | 10:32 | 49.843
2025-04-27 | 10:32 | 49.851
2025-04-27 | 10:32 | 49.849
2025-04-27 | 10:33 | 49.843
2025-04-27 | 10:33 | 49.844
2025-04-27 | 10:33 | 49.844
2025-04-27 | 10:33 | 49.841
2025-04-27 | 10:33 | 49.841
2025-04-27 | 10:33 | 49.838
2025-04-27 | 10:33 | 49.838
2025-04-27 | 10:33 | 49.838
2025-04-27 | 10:33 | 49.838
2025-04-27 | 10:33 | 49.838
2025-04-27 | 10:33 | 49.84
2025-04-27 | 10:33 | 49.841
2025-04-27 | 10:33 | 49.845
2025-04-27 | 10:33 | 49.844
2025-04-27 | 10:33 | 49.844
2025-04-27 | 10:33 | 49.845
2025-04-27 | 10:33 | 49.845
2025-04-27 | 10:33 | 49.845
2025-04-27 | 10:33 | 49.849
2025-04-27 | 10:33 | 49.85
2025-04-27 | 10:33 | 49.853
2025-04-27 | 10:33 | 49.856
2025-04-27 | 10:33 | 49.858
2025-04-27 | 10:33 | 49.86
2025-04-27 | 10:33 | 49.862
2025-04-27 | 10:33 | 49.859
2025-04-27 | 10:33 | 49.857
2025-04-27 | 10:33 | 49.858
2025-04-27 | 10:33 | 49.857
2025-04-27 | 10:33 | 49.859
2025-04-27 | 10:33 | 49.859
2025-04-27 | 10:33 | 49.866
2025-04-27 | 10:33 | 49.864
2025-04-27 | 10:33 | 49.861
2025-04-27 | 10:33 | 49.86
2025-04-27 | 10:33 | 49.859
2025-04-27 | 10:33 | 49.864
2025-04-27 | 10:33 | 49.865
2025-04-27 | 10:33 | 49.863
2025-04-27 | 10:33 | 49.862
2025-04-27 | 10:33 | 49.859
2025-04-27 | 10:33 | 49.86
2025-04-27 | 10:33 | 49.864
2025-04-27 | 10:33 | 49.864
2025-04-27 | 10:33 | 49.864
2025-04-27 | 10:33 | 49.869
2025-04-27 | 10:33 | 49.871
2025-04-27 | 10:33 | 49.873
2025-04-27 | 10:33 | 49.875
2025-04-27 | 10:33 | 49.878
2025-04-27 | 10:33 | 49.88
2025-04-27 | 10:33 | 49.88
2025-04-27 | 10:33 | 49.879
2025-04-27 | 10:33 | 49.883
2025-04-27 | 10:33 | 49.884
2025-04-27 | 10:33 | 49.882
2025-04-27 | 10:33 | 49.885
2025-04-27 | 10:33 | 49.889
2025-04-27 | 10:33 | 49.887
2025-04-27 | 10:34 | 49.889
2025-04-27 | 10:34 | 49.888
2025-04-27 | 10:34 | 49.886
2025-04-27 | 10:34 | 49.886
2025-04-27 | 10:34 | 49.882
2025-04-27 | 10:34 | 49.881
2025-04-27 | 10:34 | 49.884
2025-04-27 | 10:34 | 49.885
2025-04-27 | 10:34 | 49.887
2025-04-27 | 10:34 | 49.892
2025-04-27 | 10:34 | 49.899
2025-04-27 | 10:34 | 49.9
2025-04-27 | 10:34 | 49.897
2025-04-27 | 10:34 | 49.897
2025-04-27 | 10:34 | 49.897
2025-04-27 | 10:34 | 49.895
2025-04-27 | 10:34 | 49.894
2025-04-27 | 10:34 | 49.892
2025-04-27 | 10:34 | 49.89
2025-04-27 | 10:34 | 49.89
2025-04-27 | 10:34 | 49.89
2025-04-27 | 10:34 | 49.89
2025-04-27 | 10:34 | 49.888
2025-04-27 | 10:34 | 49.886
2025-04-27 | 10:34 | 49.887
2025-04-27 | 10:34 | 49.886
2025-04-27 | 10:34 | 49.888
2025-04-27 | 10:34 | 49.891
2025-04-27 | 10:34 | 49.891
2025-04-27 | 10:34 | 49.893
2025-04-27 | 10:34 | 49.893
2025-04-27 | 10:34 | 49.895
2025-04-27 | 10:34 | 49.896
2025-04-27 | 10:34 | 49.894
2025-04-27 | 10:34 | 49.895
2025-04-27 | 10:34 | 49.897
2025-04-27 | 10:34 | 49.895
2025-04-27 | 10:34 | 49.895
2025-04-27 | 10:34 | 49.895
2025-04-27 | 10:34 | 49.895
2025-04-27 | 10:34 | 49.897
2025-04-27 | 10:34 | 49.898
2025-04-27 | 10:34 | 49.899
2025-04-27 | 10:34 | 49.9
2025-04-27 | 10:34 | 49.9
2025-04-27 | 10:34 | 49.902
2025-04-27 | 10:34 | 49.901
2025-04-27 | 10:34 | 49.898
2025-04-27 | 10:34 | 49.898
2025-04-27 | 10:34 | 49.896
2025-04-27 | 10:34 | 49.895
2025-04-27 | 10:34 | 49.894
2025-04-27 | 10:34 | 49.894
2025-04-27 | 10:34 | 49.894
2025-04-27 | 10:34 | 49.894
2025-04-27 | 10:34 | 49.892
2025-04-27 | 10:34 | 49.892
2025-04-27 | 10:34 | 49.893
2025-04-27 | 10:34 | 49.892
2025-04-27 | 10:34 | 49.894
2025-04-27 | 10:34 | 49.895
2025-04-27 | 10:35 | 49.897
2025-04-27 | 10:35 | 49.898
2025-04-27 | 10:35 | 49.898
2025-04-27 | 10:35 | 49.9
2025-04-27 | 10:35 | 49.9
2025-04-27 | 10:35 | 49.899
2025-04-27 | 10:35 | 49.898
2025-04-27 | 10:35 | 49.898
2025-04-27 | 10:35 | 49.895
2025-04-27 | 10:35 | 49.894
2025-04-27 | 10:35 | 49.893
2025-04-27 | 10:35 | 49.894
2025-04-27 | 10:35 | 49.896
2025-04-27 | 10:35 | 49.893
2025-04-27 | 10:35 | 49.895
2025-04-27 | 10:35 | 49.892
2025-04-27 | 10:35 | 49.892
2025-04-27 | 10:35 | 49.894
2025-04-27 | 10:35 | 49.896
2025-04-27 | 10:35 | 49.897
2025-04-27 | 10:35 | 49.899
2025-04-27 | 10:35 | 49.897
2025-04-27 | 10:35 | 49.896
2025-04-27 | 10:35 | 49.894
2025-04-27 | 10:35 | 49.895
2025-04-27 | 10:35 | 49.895
2025-04-27 | 10:35 | 49.892
2025-04-27 | 10:35 | 49.89
2025-04-27 | 10:35 | 49.893
2025-04-27 | 10:35 | 49.893
2025-04-27 | 10:35 | 49.893
2025-04-27 | 10:35 | 49.893
2025-04-27 | 10:35 | 49.894
2025-04-27 | 10:35 | 49.894
2025-04-27 | 10:35 | 49.897
2025-04-27 | 10:35 | 49.897
2025-04-27 | 10:35 | 49.894
2025-04-27 | 10:35 | 49.895
2025-04-27 | 10:35 | 49.894
2025-04-27 | 10:35 | 49.895
2025-04-27 | 10:35 | 49.898
2025-04-27 | 10:35 | 49.9
2025-04-27 | 10:35 | 49.901
2025-04-27 | 10:35 | 49.9
2025-04-27 | 10:35 | 49.901
2025-04-27 | 10:35 | 49.902
2025-04-27 | 10:35 | 49.902
2025-04-27 | 10:35 | 49.903
2025-04-27 | 10:35 | 49.904
2025-04-27 | 10:35 | 49.904
2025-04-27 | 10:35 | 49.898
2025-04-27 | 10:35 | 49.895
2025-04-27 | 10:35 | 49.89
2025-04-27 | 10:35 | 49.885
2025-04-27 | 10:35 | 49.888
2025-04-27 | 10:35 | 49.89
2025-04-27 | 10:35 | 49.894
2025-04-27 | 10:35 | 49.894
2025-04-27 | 10:35 | 49.892
2025-04-27 | 10:36 | 49.892
2025-04-27 | 10:36 | 49.891
2025-04-27 | 10:36 | 49.892
2025-04-27 | 10:36 | 49.894
2025-04-27 | 10:36 | 49.894
2025-04-27 | 10:36 | 49.893
2025-04-27 | 10:36 | 49.891
2025-04-27 | 10:36 | 49.89
2025-04-27 | 10:36 | 49.888
2025-04-27 | 10:36 | 49.886
2025-04-27 | 10:36 | 49.89
2025-04-27 | 10:36 | 49.891
2025-04-27 | 10:36 | 49.894
2025-04-27 | 10:36 | 49.896
2025-04-27 | 10:36 | 49.893
2025-04-27 | 10:36 | 49.891
2025-04-27 | 10:36 | 49.892
2025-04-27 | 10:36 | 49.895
2025-04-27 | 10:36 | 49.894
2025-04-27 | 10:36 | 49.892
2025-04-27 | 10:36 | 49.893
2025-04-27 | 10:36 | 49.894
2025-04-27 | 10:36 | 49.893
2025-04-27 | 10:36 | 49.896
2025-04-27 | 10:36 | 49.899
2025-04-27 | 10:36 | 49.898
2025-04-27 | 10:36 | 49.9
2025-04-27 | 10:36 | 49.898
2025-04-27 | 10:36 | 49.902
2025-04-27 | 10:36 | 49.906
2025-04-27 | 10:36 | 49.908
2025-04-27 | 10:36 | 49.908
2025-04-27 | 10:36 | 49.908
2025-04-27 | 10:36 | 49.907
2025-04-27 | 10:36 | 49.906
2025-04-27 | 10:36 | 49.905
2025-04-27 | 10:36 | 49.902
2025-04-27 | 10:36 | 49.901
2025-04-27 | 10:36 | 49.902
2025-04-27 | 10:36 | 49.906
2025-04-27 | 10:36 | 49.908
2025-04-27 | 10:36 | 49.911
2025-04-27 | 10:36 | 49.91
2025-04-27 | 10:36 | 49.91
2025-04-27 | 10:36 | 49.906
2025-04-27 | 10:36 | 49.908
2025-04-27 | 10:36 | 49.911
2025-04-27 | 10:36 | 49.915
2025-04-27 | 10:36 | 49.915
2025-04-27 | 10:36 | 49.911
2025-04-27 | 10:36 | 49.907
2025-04-27 | 10:36 | 49.907
2025-04-27 | 10:36 | 49.909
2025-04-27 | 10:36 | 49.91
2025-04-27 | 10:36 | 49.911
2025-04-27 | 10:36 | 49.911
2025-04-27 | 10:36 | 49.911
2025-04-27 | 10:36 | 49.914
2025-04-27 | 10:36 | 49.917
2025-04-27 | 10:36 | 49.917
2025-04-27 | 10:36 | 49.918
2025-04-27 | 10:37 | 49.92
2025-04-27 | 10:37 | 49.922
2025-04-27 | 10:37 | 49.923
2025-04-27 | 10:37 | 49.924
2025-04-27 | 10:37 | 49.924
2025-04-27 | 10:37 | 49.923
2025-04-27 | 10:37 | 49.921
2025-04-27 | 10:37 | 49.92
2025-04-27 | 10:37 | 49.917
2025-04-27 | 10:37 | 49.916
2025-04-27 | 10:37 | 49.914
2025-04-27 | 10:37 | 49.912
2025-04-27 | 10:37 | 49.911
2025-04-27 | 10:37 | 49.909
2025-04-27 | 10:37 | 49.913
2025-04-27 | 10:37 | 49.915
2025-04-27 | 10:37 | 49.918
2025-04-27 | 10:37 | 49.918
2025-04-27 | 10:37 | 49.919
2025-04-27 | 10:37 | 49.919
2025-04-27 | 10:37 | 49.918
2025-04-27 | 10:37 | 49.916
2025-04-27 | 10:37 | 49.915
2025-04-27 | 10:37 | 49.916
2025-04-27 | 10:37 | 49.914
2025-04-27 | 10:37 | 49.91
2025-04-27 | 10:37 | 49.915
2025-04-27 | 10:37 | 49.916
2025-04-27 | 10:37 | 49.918
2025-04-27 | 10:37 | 49.916
2025-04-27 | 10:37 | 49.917
2025-04-27 | 10:37 | 49.917
2025-04-27 | 10:37 | 49.918
2025-04-27 | 10:37 | 49.917
2025-04-27 | 10:37 | 49.917
2025-04-27 | 10:37 | 49.915
2025-04-27 | 10:37 | 49.917
2025-04-27 | 10:37 | 49.916
2025-04-27 | 10:37 | 49.918
2025-04-27 | 10:37 | 49.919
2025-04-27 | 10:37 | 49.921
2025-04-27 | 10:37 | 49.919
2025-04-27 | 10:37 | 49.919
2025-04-27 | 10:37 | 49.921
2025-04-27 | 10:37 | 49.921
2025-04-27 | 10:37 | 49.921
2025-04-27 | 10:37 | 49.925
2025-04-27 | 10:37 | 49.926
2025-04-27 | 10:37 | 49.924
2025-04-27 | 10:37 | 49.922
2025-04-27 | 10:37 | 49.92
2025-04-27 | 10:37 | 49.919
2025-04-27 | 10:37 | 49.921
2025-04-27 | 10:37 | 49.921
2025-04-27 | 10:37 | 49.92
2025-04-27 | 10:37 | 49.918
2025-04-27 | 10:37 | 49.917
2025-04-27 | 10:37 | 49.917
2025-04-27 | 10:37 | 49.918
2025-04-27 | 10:38 | 49.915
2025-04-27 | 10:38 | 49.913
2025-04-27 | 10:38 | 49.913
2025-04-27 | 10:38 | 49.912
2025-04-27 | 10:38 | 49.914
2025-04-27 | 10:38 | 49.918
2025-04-27 | 10:38 | 49.919
2025-04-27 | 10:38 | 49.918
2025-04-27 | 10:38 | 49.914
2025-04-27 | 10:38 | 49.911
2025-04-27 | 10:38 | 49.911
2025-04-27 | 10:38 | 49.913
2025-04-27 | 10:38 | 49.917
2025-04-27 | 10:38 | 49.924
2025-04-27 | 10:38 | 49.926
2025-04-27 | 10:38 | 49.928
2025-04-27 | 10:38 | 49.926
2025-04-27 | 10:38 | 49.93
2025-04-27 | 10:38 | 49.932
2025-04-27 | 10:38 | 49.926
2025-04-27 | 10:38 | 49.925
2025-04-27 | 10:38 | 49.925
2025-04-27 | 10:38 | 49.92
2025-04-27 | 10:38 | 49.914
2025-04-27 | 10:38 | 49.911
2025-04-27 | 10:38 | 49.909
2025-04-27 | 10:38 | 49.911
2025-04-27 | 10:38 | 49.915
2025-04-27 | 10:38 | 49.916
2025-04-27 | 10:38 | 49.919
2025-04-27 | 10:38 | 49.915
2025-04-27 | 10:38 | 49.924
2025-04-27 | 10:38 | 49.931
2025-04-27 | 10:38 | 49.933
2025-04-27 | 10:38 | 49.936
2025-04-27 | 10:38 | 49.939
2025-04-27 | 10:38 | 49.938
2025-04-27 | 10:38 | 49.936
2025-04-27 | 10:38 | 49.94
2025-04-27 | 10:38 | 49.94
2025-04-27 | 10:38 | 49.943
2025-04-27 | 10:38 | 49.945
2025-04-27 | 10:38 | 49.942
2025-04-27 | 10:38 | 49.942
2025-04-27 | 10:38 | 49.941
2025-04-27 | 10:38 | 49.941
2025-04-27 | 10:38 | 49.943
2025-04-27 | 10:38 | 49.947
2025-04-27 | 10:38 | 49.947
2025-04-27 | 10:38 | 49.946
2025-04-27 | 10:38 | 49.943
2025-04-27 | 10:38 | 49.941
2025-04-27 | 10:38 | 49.943
2025-04-27 | 10:38 | 49.944
2025-04-27 | 10:38 | 49.945
2025-04-27 | 10:38 | 49.946
2025-04-27 | 10:38 | 49.95
2025-04-27 | 10:38 | 49.953
2025-04-27 | 10:38 | 49.961
2025-04-27 | 10:38 | 49.961
2025-04-27 | 10:38 | 49.958
2025-04-27 | 10:39 | 49.956
2025-04-27 | 10:39 | 49.955
2025-04-27 | 10:39 | 49.953
2025-04-27 | 10:39 | 49.951
2025-04-27 | 10:39 | 49.948
2025-04-27 | 10:39 | 49.946
2025-04-27 | 10:39 | 49.949
2025-04-27 | 10:39 | 49.95
2025-04-27 | 10:39 | 49.952
2025-04-27 | 10:39 | 49.958
2025-04-27 | 10:39 | 49.961
2025-04-27 | 10:39 | 49.964
2025-04-27 | 10:39 | 49.964
2025-04-27 | 10:39 | 49.96
2025-04-27 | 10:39 | 49.961
2025-04-27 | 10:39 | 49.96
2025-04-27 | 10:39 | 49.96
2025-04-27 | 10:39 | 49.963
2025-04-27 | 10:39 | 49.966
2025-04-27 | 10:39 | 49.968
2025-04-27 | 10:39 | 49.969
2025-04-27 | 10:39 | 49.97
2025-04-27 | 10:39 | 49.97
2025-04-27 | 10:39 | 49.971
2025-04-27 | 10:39 | 49.974
2025-04-27 | 10:39 | 49.977
2025-04-27 | 10:39 | 49.98
2025-04-27 | 10:39 | 49.98
2025-04-27 | 10:39 | 49.977
2025-04-27 | 10:39 | 49.978
2025-04-27 | 10:39 | 49.976
2025-04-27 | 10:39 | 49.977
2025-04-27 | 10:39 | 49.976
2025-04-27 | 10:39 | 49.979
2025-04-27 | 10:39 | 49.981
2025-04-27 | 10:39 | 49.98
2025-04-27 | 10:39 | 49.977
2025-04-27 | 10:39 | 49.976
2025-04-27 | 10:39 | 49.978
2025-04-27 | 10:39 | 49.98
2025-04-27 | 10:39 | 49.983
2025-04-27 | 10:39 | 49.979
2025-04-27 | 10:39 | 49.977
2025-04-27 | 10:39 | 49.972
2025-04-27 | 10:39 | 49.969
2025-04-27 | 10:39 | 49.967
2025-04-27 | 10:39 | 49.968
2025-04-27 | 10:39 | 49.968
2025-04-27 | 10:39 | 49.964
2025-04-27 | 10:39 | 49.966
2025-04-27 | 10:39 | 49.966
2025-04-27 | 10:39 | 49.964
2025-04-27 | 10:39 | 49.963
2025-04-27 | 10:39 | 49.966
2025-04-27 | 10:39 | 49.968
2025-04-27 | 10:39 | 49.971
2025-04-27 | 10:39 | 49.971
2025-04-27 | 10:39 | 49.971
2025-04-27 | 10:39 | 49.976
2025-04-27 | 10:40 | 49.975
2025-04-27 | 10:40 | 49.976
2025-04-27 | 10:40 | 49.971
2025-04-27 | 10:40 | 49.97
2025-04-27 | 10:40 | 49.968
2025-04-27 | 10:40 | 49.969
2025-04-27 | 10:40 | 49.973
2025-04-27 | 10:40 | 49.972
2025-04-27 | 10:40 | 49.973
2025-04-27 | 10:40 | 49.975
2025-04-27 | 10:40 | 49.975
2025-04-27 | 10:40 | 49.974
2025-04-27 | 10:40 | 49.971
2025-04-27 | 10:40 | 49.971
2025-04-27 | 10:40 | 49.971
2025-04-27 | 10:40 | 49.973
2025-04-27 | 10:40 | 49.977
2025-04-27 | 10:40 | 49.98
2025-04-27 | 10:40 | 49.98
2025-04-27 | 10:40 | 49.979
2025-04-27 | 10:40 | 49.975
2025-04-27 | 10:40 | 49.979
2025-04-27 | 10:40 | 49.982
2025-04-27 | 10:40 | 49.984
2025-04-27 | 10:40 | 49.982
2025-04-27 | 10:40 | 49.975
2025-04-27 | 10:40 | 49.968
2025-04-27 | 10:40 | 49.966
2025-04-27 | 10:40 | 49.967
2025-04-27 | 10:40 | 49.975
2025-04-27 | 10:40 | 49.98
2025-04-27 | 10:40 | 49.966
2025-04-27 | 10:40 | 49.954
2025-04-27 | 10:40 | 49.954
2025-04-27 | 10:40 | 49.957
2025-04-27 | 10:40 | 49.958
2025-04-27 | 10:40 | 49.957
2025-04-27 | 10:40 | 49.953
2025-04-27 | 10:40 | 49.957
2025-04-27 | 10:40 | 49.959
2025-04-27 | 10:40 | 49.955
2025-04-27 | 10:40 | 49.953
2025-04-27 | 10:40 | 49.959
2025-04-27 | 10:40 | 49.959
2025-04-27 | 10:40 | 49.961
2025-04-27 | 10:40 | 49.966
2025-04-27 | 10:40 | 49.975
2025-04-27 | 10:40 | 49.978
2025-04-27 | 10:40 | 49.98
2025-04-27 | 10:40 | 49.977
2025-04-27 | 10:40 | 49.977
2025-04-27 | 10:40 | 49.974
2025-04-27 | 10:40 | 49.974
2025-04-27 | 10:40 | 49.977
2025-04-27 | 10:40 | 49.972
2025-04-27 | 10:40 | 49.964
2025-04-27 | 10:40 | 49.959
2025-04-27 | 10:40 | 49.96
2025-04-27 | 10:40 | 49.964
2025-04-27 | 10:40 | 49.964
2025-04-27 | 10:40 | 49.963
2025-04-27 | 10:41 | 49.972
2025-04-27 | 10:41 | 49.977
2025-04-27 | 10:41 | 49.98
2025-04-27 | 10:41 | 49.984
2025-04-27 | 10:41 | 49.983
2025-04-27 | 10:41 | 49.979
2025-04-27 | 10:41 | 49.977
2025-04-27 | 10:41 | 49.975
2025-04-27 | 10:41 | 49.981
2025-04-27 | 10:41 | 49.983
2025-04-27 | 10:41 | 49.983
2025-04-27 | 10:41 | 49.982
2025-04-27 | 10:41 | 49.977
2025-04-27 | 10:41 | 49.974
2025-04-27 | 10:41 | 49.969
2025-04-27 | 10:41 | 49.965
2025-04-27 | 10:41 | 49.969
2025-04-27 | 10:41 | 49.973
2025-04-27 | 10:41 | 49.971
2025-04-27 | 10:41 | 49.965
2025-04-27 | 10:41 | 49.963
2025-04-27 | 10:41 | 49.966
2025-04-27 | 10:41 | 49.967
2025-04-27 | 10:41 | 49.972
2025-04-27 | 10:41 | 49.975
2025-04-27 | 10:41 | 49.976
2025-04-27 | 10:41 | 49.98
2025-04-27 | 10:41 | 49.984
2025-04-27 | 10:41 | 49.991
2025-04-27 | 10:41 | 49.996
2025-04-27 | 10:41 | 49.993
2025-04-27 | 10:41 | 49.987
2025-04-27 | 10:41 | 49.981
2025-04-27 | 10:41 | 49.977
2025-04-27 | 10:41 | 49.978
2025-04-27 | 10:41 | 49.979
2025-04-27 | 10:41 | 49.981
2025-04-27 | 10:41 | 49.978
2025-04-27 | 10:41 | 49.978
2025-04-27 | 10:41 | 49.976
2025-04-27 | 10:41 | 49.974
2025-04-27 | 10:41 | 49.972
2025-04-27 | 10:41 | 49.975
2025-04-27 | 10:41 | 49.977
2025-04-27 | 10:41 | 49.981
2025-04-27 | 10:41 | 49.985
2025-04-27 | 10:41 | 49.983
2025-04-27 | 10:41 | 49.98
2025-04-27 | 10:41 | 49.979
2025-04-27 | 10:41 | 49.978
2025-04-27 | 10:41 | 49.973
2025-04-27 | 10:41 | 49.971
2025-04-27 | 10:41 | 49.971
2025-04-27 | 10:41 | 49.972
2025-04-27 | 10:41 | 49.974
2025-04-27 | 10:41 | 49.979
2025-04-27 | 10:41 | 49.984
2025-04-27 | 10:41 | 49.982
2025-04-27 | 10:41 | 49.976
2025-04-27 | 10:42 | 49.969
2025-04-27 | 10:42 | 49.965
2025-04-27 | 10:42 | 49.963
2025-04-27 | 10:42 | 49.962
2025-04-27 | 10:42 | 49.961
2025-04-27 | 10:42 | 49.962
2025-04-27 | 10:42 | 49.962
2025-04-27 | 10:42 | 49.962
2025-04-27 | 10:42 | 49.963
2025-04-27 | 10:42 | 49.962
2025-04-27 | 10:42 | 49.958
2025-04-27 | 10:42 | 49.958
2025-04-27 | 10:42 | 49.959
2025-04-27 | 10:42 | 49.961
2025-04-27 | 10:42 | 49.967
2025-04-27 | 10:42 | 49.966
2025-04-27 | 10:42 | 49.97
2025-04-27 | 10:42 | 49.969
2025-04-27 | 10:42 | 49.969
2025-04-27 | 10:42 | 49.965
2025-04-27 | 10:42 | 49.965
2025-04-27 | 10:42 | 49.964
2025-04-27 | 10:42 | 49.965
2025-04-27 | 10:42 | 49.967
2025-04-27 | 10:42 | 49.968
2025-04-27 | 10:42 | 49.97
2025-04-27 | 10:42 | 49.975
2025-04-27 | 10:42 | 49.977
2025-04-27 | 10:42 | 49.976
2025-04-27 | 10:42 | 49.975
2025-04-27 | 10:42 | 49.975
2025-04-27 | 10:42 | 49.973
2025-04-27 | 10:42 | 49.973
2025-04-27 | 10:42 | 49.973
2025-04-27 | 10:42 | 49.975
2025-04-27 | 10:42 | 49.977
2025-04-27 | 10:42 | 49.971
2025-04-27 | 10:42 | 49.966
2025-04-27 | 10:42 | 49.963
2025-04-27 | 10:42 | 49.959
2025-04-27 | 10:42 | 49.959
2025-04-27 | 10:42 | 49.957
2025-04-27 | 10:42 | 49.955
2025-04-27 | 10:42 | 49.951
2025-04-27 | 10:42 | 49.95
2025-04-27 | 10:42 | 49.952
2025-04-27 | 10:42 | 49.953
2025-04-27 | 10:42 | 49.953
2025-04-27 | 10:42 | 49.952
2025-04-27 | 10:42 | 49.956
2025-04-27 | 10:42 | 49.96
2025-04-27 | 10:42 | 49.96
2025-04-27 | 10:42 | 49.956
2025-04-27 | 10:42 | 49.953
2025-04-27 | 10:42 | 49.948
2025-04-27 | 10:42 | 49.945
2025-04-27 | 10:42 | 49.945
2025-04-27 | 10:42 | 49.948
2025-04-27 | 10:42 | 49.948
2025-04-27 | 10:42 | 49.948
2025-04-27 | 10:42 | 49.952
2025-04-27 | 10:43 | 49.958
2025-04-27 | 10:43 | 49.96
2025-04-27 | 10:43 | 49.96
2025-04-27 | 10:43 | 49.959
2025-04-27 | 10:43 | 49.96
2025-04-27 | 10:43 | 49.958
2025-04-27 | 10:43 | 49.96
2025-04-27 | 10:43 | 49.964
2025-04-27 | 10:43 | 49.966
2025-04-27 | 10:43 | 49.966
2025-04-27 | 10:43 | 49.969
2025-04-27 | 10:43 | 49.973
2025-04-27 | 10:43 | 49.973
2025-04-27 | 10:43 | 49.968
2025-04-27 | 10:43 | 49.96
2025-04-27 | 10:43 | 49.957
2025-04-27 | 10:43 | 49.958
2025-04-27 | 10:43 | 49.965
2025-04-27 | 10:43 | 49.966
2025-04-27 | 10:43 | 49.963
2025-04-27 | 10:43 | 49.961
2025-04-27 | 10:43 | 49.956
2025-04-27 | 10:43 | 49.951
2025-04-27 | 10:43 | 49.952
2025-04-27 | 10:43 | 49.948
2025-04-27 | 10:43 | 49.946
2025-04-27 | 10:43 | 49.945
2025-04-27 | 10:43 | 49.947
2025-04-27 | 10:43 | 49.953
2025-04-27 | 10:43 | 49.955
2025-04-27 | 10:43 | 49.952
2025-04-27 | 10:43 | 49.946
2025-04-27 | 10:43 | 49.943
2025-04-27 | 10:43 | 49.942
2025-04-27 | 10:43 | 49.943
2025-04-27 | 10:43 | 49.944
2025-04-27 | 10:43 | 49.946
2025-04-27 | 10:43 | 49.946
2025-04-27 | 10:43 | 49.944
2025-04-27 | 10:43 | 49.942
2025-04-27 | 10:43 | 49.94
2025-04-27 | 10:43 | 49.941
2025-04-27 | 10:43 | 49.94
2025-04-27 | 10:43 | 49.941
2025-04-27 | 10:43 | 49.94
2025-04-27 | 10:43 | 49.94
2025-04-27 | 10:43 | 49.94
2025-04-27 | 10:43 | 49.942
2025-04-27 | 10:43 | 49.943
2025-04-27 | 10:43 | 49.946
2025-04-27 | 10:43 | 49.946
2025-04-27 | 10:43 | 49.951
2025-04-27 | 10:43 | 49.955
2025-04-27 | 10:43 | 49.958
2025-04-27 | 10:43 | 49.959
2025-04-27 | 10:43 | 49.958
2025-04-27 | 10:43 | 49.958
2025-04-27 | 10:43 | 49.956
2025-04-27 | 10:43 | 49.957
2025-04-27 | 10:44 | 49.962
2025-04-27 | 10:44 | 49.96
2025-04-27 | 10:44 | 49.958
2025-04-27 | 10:44 | 49.957
2025-04-27 | 10:44 | 49.955
2025-04-27 | 10:44 | 49.958
2025-04-27 | 10:44 | 49.963
2025-04-27 | 10:44 | 49.962
2025-04-27 | 10:44 | 49.959
2025-04-27 | 10:44 | 49.958
2025-04-27 | 10:44 | 49.955
2025-04-27 | 10:44 | 49.95
2025-04-27 | 10:44 | 49.946
2025-04-27 | 10:44 | 49.948
2025-04-27 | 10:44 | 49.949
2025-04-27 | 10:44 | 49.952
2025-04-27 | 10:44 | 49.952
2025-04-27 | 10:44 | 49.951
2025-04-27 | 10:44 | 49.951
2025-04-27 | 10:44 | 49.949
2025-04-27 | 10:44 | 49.946
2025-04-27 | 10:44 | 49.943
2025-04-27 | 10:44 | 49.94
2025-04-27 | 10:44 | 49.94
2025-04-27 | 10:44 | 49.941
2025-04-27 | 10:44 | 49.945
2025-04-27 | 10:44 | 49.947
2025-04-27 | 10:44 | 49.948
2025-04-27 | 10:44 | 49.947
2025-04-27 | 10:44 | 49.95
2025-04-27 | 10:44 | 49.951
2025-04-27 | 10:44 | 49.954
2025-04-27 | 10:44 | 49.954
2025-04-27 | 10:44 | 49.951
2025-04-27 | 10:44 | 49.953
2025-04-27 | 10:44 | 49.953
2025-04-27 | 10:44 | 49.954
2025-04-27 | 10:44 | 49.956
2025-04-27 | 10:44 | 49.954
2025-04-27 | 10:44 | 49.949
2025-04-27 | 10:44 | 49.945
2025-04-27 | 10:44 | 49.94
2025-04-27 | 10:44 | 49.938
2025-04-27 | 10:44 | 49.94
2025-04-27 | 10:44 | 49.944
2025-04-27 | 10:44 | 49.945
2025-04-27 | 10:44 | 49.944
2025-04-27 | 10:44 | 49.945
2025-04-27 | 10:44 | 49.947
2025-04-27 | 10:44 | 49.949
2025-04-27 | 10:44 | 49.945
2025-04-27 | 10:44 | 49.941
2025-04-27 | 10:44 | 49.937
2025-04-27 | 10:44 | 49.934
2025-04-27 | 10:44 | 49.934
2025-04-27 | 10:44 | 49.934
2025-04-27 | 10:44 | 49.932
2025-04-27 | 10:44 | 49.933
2025-04-27 | 10:44 | 49.936
2025-04-27 | 10:44 | 49.937
2025-04-27 | 10:44 | 49.936
2025-04-27 | 10:45 | 49.936
2025-04-27 | 10:45 | 49.94
2025-04-27 | 10:45 | 49.945
2025-04-27 | 10:45 | 49.944
2025-04-27 | 10:45 | 49.944
2025-04-27 | 10:45 | 49.942
2025-04-27 | 10:45 | 49.937
2025-04-27 | 10:45 | 49.933
2025-04-27 | 10:45 | 49.93
2025-04-27 | 10:45 | 49.929
2025-04-27 | 10:45 | 49.93
2025-04-27 | 10:45 | 49.928
2025-04-27 | 10:45 | 49.925
2025-04-27 | 10:45 | 49.923
2025-04-27 | 10:45 | 49.921
2025-04-27 | 10:45 | 49.92
2025-04-27 | 10:45 | 49.919
2025-04-27 | 10:45 | 49.922
2025-04-27 | 10:45 | 49.923
2025-04-27 | 10:45 | 49.923
2025-04-27 | 10:45 | 49.92
2025-04-27 | 10:45 | 49.916
2025-04-27 | 10:45 | 49.914
2025-04-27 | 10:45 | 49.914
2025-04-27 | 10:45 | 49.912
2025-04-27 | 10:45 | 49.91
2025-04-27 | 10:45 | 49.911
2025-04-27 | 10:45 | 49.913
2025-04-27 | 10:45 | 49.911
2025-04-27 | 10:45 | 49.909
2025-04-27 | 10:45 | 49.909
2025-04-27 | 10:45 | 49.914
2025-04-27 | 10:45 | 49.917
2025-04-27 | 10:45 | 49.922
2025-04-27 | 10:45 | 49.924
2025-04-27 | 10:45 | 49.927
2025-04-27 | 10:45 | 49.926
2025-04-27 | 10:45 | 49.924
2025-04-27 | 10:45 | 49.923
2025-04-27 | 10:45 | 49.924
2025-04-27 | 10:45 | 49.923
2025-04-27 | 10:45 | 49.922
2025-04-27 | 10:45 | 49.923
2025-04-27 | 10:45 | 49.928
2025-04-27 | 10:45 | 49.928
2025-04-27 | 10:45 | 49.927
2025-04-27 | 10:45 | 49.926
2025-04-27 | 10:45 | 49.928
2025-04-27 | 10:45 | 49.927
2025-04-27 | 10:45 | 49.927
2025-04-27 | 10:45 | 49.925
2025-04-27 | 10:45 | 49.927
2025-04-27 | 10:45 | 49.929
2025-04-27 | 10:45 | 49.93
2025-04-27 | 10:45 | 49.932
2025-04-27 | 10:45 | 49.934
2025-04-27 | 10:45 | 49.936
2025-04-27 | 10:45 | 49.935
2025-04-27 | 10:45 | 49.935
2025-04-27 | 10:46 | 49.934
2025-04-27 | 10:46 | 49.933
2025-04-27 | 10:46 | 49.933
2025-04-27 | 10:46 | 49.933
2025-04-27 | 10:46 | 49.933
2025-04-27 | 10:46 | 49.933
2025-04-27 | 10:46 | 49.936
2025-04-27 | 10:46 | 49.938
2025-04-27 | 10:46 | 49.94
2025-04-27 | 10:46 | 49.939
2025-04-27 | 10:46 | 49.94
2025-04-27 | 10:46 | 49.938
2025-04-27 | 10:46 | 49.935
2025-04-27 | 10:46 | 49.933
2025-04-27 | 10:46 | 49.934
2025-04-27 | 10:46 | 49.936
2025-04-27 | 10:46 | 49.938
2025-04-27 | 10:46 | 49.94
2025-04-27 | 10:46 | 49.943
2025-04-27 | 10:46 | 49.946
2025-04-27 | 10:46 | 49.948
2025-04-27 | 10:46 | 49.952
2025-04-27 | 10:46 | 49.949
2025-04-27 | 10:46 | 49.948
2025-04-27 | 10:46 | 49.946
2025-04-27 | 10:46 | 49.947
2025-04-27 | 10:46 | 49.947
2025-04-27 | 10:46 | 49.945
2025-04-27 | 10:46 | 49.944
2025-04-27 | 10:46 | 49.942
2025-04-27 | 10:46 | 49.94
2025-04-27 | 10:46 | 49.937
2025-04-27 | 10:46 | 49.939
2025-04-27 | 10:46 | 49.938
2025-04-27 | 10:46 | 49.937
2025-04-27 | 10:46 | 49.937
2025-04-27 | 10:46 | 49.936
2025-04-27 | 10:46 | 49.933
2025-04-27 | 10:46 | 49.931
2025-04-27 | 10:46 | 49.933
2025-04-27 | 10:46 | 49.933
2025-04-27 | 10:46 | 49.936
2025-04-27 | 10:46 | 49.939
2025-04-27 | 10:46 | 49.941
2025-04-27 | 10:46 | 49.94
2025-04-27 | 10:46 | 49.94
2025-04-27 | 10:46 | 49.939
2025-04-27 | 10:46 | 49.94
2025-04-27 | 10:46 | 49.942
2025-04-27 | 10:46 | 49.944
2025-04-27 | 10:46 | 49.946
2025-04-27 | 10:46 | 49.948
2025-04-27 | 10:46 | 49.946
2025-04-27 | 10:46 | 49.945
2025-04-27 | 10:46 | 49.943
2025-04-27 | 10:46 | 49.943
2025-04-27 | 10:46 | 49.943
2025-04-27 | 10:46 | 49.947
2025-04-27 | 10:46 | 49.948
2025-04-27 | 10:46 | 49.95
2025-04-27 | 10:46 | 49.95
2025-04-27 | 10:47 | 49.951
2025-04-27 | 10:47 | 49.95
2025-04-27 | 10:47 | 49.948
2025-04-27 | 10:47 | 49.946
2025-04-27 | 10:47 | 49.946
2025-04-27 | 10:47 | 49.943
2025-04-27 | 10:47 | 49.945
2025-04-27 | 10:47 | 49.946
2025-04-27 | 10:47 | 49.945
2025-04-27 | 10:47 | 49.949
2025-04-27 | 10:47 | 49.951
2025-04-27 | 10:47 | 49.953
2025-04-27 | 10:47 | 49.952
2025-04-27 | 10:47 | 49.953
2025-04-27 | 10:47 | 49.952
2025-04-27 | 10:47 | 49.952
2025-04-27 | 10:47 | 49.953
2025-04-27 | 10:47 | 49.954
2025-04-27 | 10:47 | 49.951
2025-04-27 | 10:47 | 49.951
2025-04-27 | 10:47 | 49.949
2025-04-27 | 10:47 | 49.947
2025-04-27 | 10:47 | 49.949
2025-04-27 | 10:47 | 49.954
2025-04-27 | 10:47 | 49.955
2025-04-27 | 10:47 | 49.956
2025-04-27 | 10:47 | 49.958
2025-04-27 | 10:47 | 49.958
2025-04-27 | 10:47 | 49.958
2025-04-27 | 10:47 | 49.958
2025-04-27 | 10:47 | 49.957
2025-04-27 | 10:47 | 49.956
2025-04-27 | 10:47 | 49.955
2025-04-27 | 10:47 | 49.957
2025-04-27 | 10:47 | 49.959
2025-04-27 | 10:47 | 49.96
2025-04-27 | 10:47 | 49.963
2025-04-27 | 10:47 | 49.964
2025-04-27 | 10:47 | 49.967
2025-04-27 | 10:47 | 49.97
2025-04-27 | 10:47 | 49.97
2025-04-27 | 10:47 | 49.973
2025-04-27 | 10:47 | 49.974
2025-04-27 | 10:47 | 49.971
2025-04-27 | 10:47 | 49.969
2025-04-27 | 10:47 | 49.967
2025-04-27 | 10:47 | 49.966
2025-04-27 | 10:47 | 49.964
2025-04-27 | 10:47 | 49.962
2025-04-27 | 10:47 | 49.962
2025-04-27 | 10:47 | 49.965
2025-04-27 | 10:47 | 49.967
2025-04-27 | 10:47 | 49.968
2025-04-27 | 10:47 | 49.969
2025-04-27 | 10:47 | 49.968
2025-04-27 | 10:47 | 49.967
2025-04-27 | 10:47 | 49.967
2025-04-27 | 10:47 | 49.966
2025-04-27 | 10:47 | 49.964
2025-04-27 | 10:48 | 49.963
2025-04-27 | 10:48 | 49.962
2025-04-27 | 10:48 | 49.961
2025-04-27 | 10:48 | 49.962
2025-04-27 | 10:48 | 49.961
2025-04-27 | 10:48 | 49.964
2025-04-27 | 10:48 | 49.964
2025-04-27 | 10:48 | 49.965
2025-04-27 | 10:48 | 49.963
2025-04-27 | 10:48 | 49.963
2025-04-27 | 10:48 | 49.962
2025-04-27 | 10:48 | 49.965
2025-04-27 | 10:48 | 49.963
2025-04-27 | 10:48 | 49.965
2025-04-27 | 10:48 | 49.969
2025-04-27 | 10:48 | 49.971
2025-04-27 | 10:48 | 49.973
2025-04-27 | 10:48 | 49.973
2025-04-27 | 10:48 | 49.974
2025-04-27 | 10:48 | 49.975
2025-04-27 | 10:48 | 49.974
2025-04-27 | 10:48 | 49.975
2025-04-27 | 10:48 | 49.976
2025-04-27 | 10:48 | 49.977
2025-04-27 | 10:48 | 49.974
2025-04-27 | 10:48 | 49.975
2025-04-27 | 10:48 | 49.977
2025-04-27 | 10:48 | 49.975
2025-04-27 | 10:48 | 49.97
2025-04-27 | 10:48 | 49.968
2025-04-27 | 10:48 | 49.965
2025-04-27 | 10:48 | 49.959
2025-04-27 | 10:48 | 49.956
2025-04-27 | 10:48 | 49.955
2025-04-27 | 10:48 | 49.956
2025-04-27 | 10:48 | 49.959
2025-04-27 | 10:48 | 49.96
2025-04-27 | 10:48 | 49.964
2025-04-27 | 10:48 | 49.965
2025-04-27 | 10:48 | 49.966
2025-04-27 | 10:48 | 49.965
2025-04-27 | 10:48 | 49.964
2025-04-27 | 10:48 | 49.964
2025-04-27 | 10:48 | 49.965
2025-04-27 | 10:48 | 49.966
2025-04-27 | 10:48 | 49.964
2025-04-27 | 10:48 | 49.961
2025-04-27 | 10:48 | 49.957
2025-04-27 | 10:48 | 49.956
2025-04-27 | 10:48 | 49.956
2025-04-27 | 10:48 | 49.958
2025-04-27 | 10:48 | 49.96
2025-04-27 | 10:48 | 49.962
2025-04-27 | 10:48 | 49.963
2025-04-27 | 10:48 | 49.963
2025-04-27 | 10:48 | 49.964
2025-04-27 | 10:48 | 49.964
2025-04-27 | 10:48 | 49.966
2025-04-27 | 10:48 | 49.966
2025-04-27 | 10:48 | 49.965
2025-04-27 | 10:48 | 49.967
2025-04-27 | 10:49 | 49.967
2025-04-27 | 10:49 | 49.967
2025-04-27 | 10:49 | 49.968
2025-04-27 | 10:49 | 49.968
2025-04-27 | 10:49 | 49.969
2025-04-27 | 10:49 | 49.969
2025-04-27 | 10:49 | 49.967
2025-04-27 | 10:49 | 49.965
2025-04-27 | 10:49 | 49.968
2025-04-27 | 10:49 | 49.969
2025-04-27 | 10:49 | 49.971
2025-04-27 | 10:49 | 49.972
2025-04-27 | 10:49 | 49.975
2025-04-27 | 10:49 | 49.977
2025-04-27 | 10:49 | 49.98
2025-04-27 | 10:49 | 49.98
2025-04-27 | 10:49 | 49.982
2025-04-27 | 10:49 | 49.983
2025-04-27 | 10:49 | 49.982
2025-04-27 | 10:49 | 49.981
2025-04-27 | 10:49 | 49.977
2025-04-27 | 10:49 | 49.972
2025-04-27 | 10:49 | 49.968
2025-04-27 | 10:49 | 49.966
2025-04-27 | 10:49 | 49.963
2025-04-27 | 10:49 | 49.96
2025-04-27 | 10:49 | 49.958
2025-04-27 | 10:49 | 49.959
2025-04-27 | 10:49 | 49.965
2025-04-27 | 10:49 | 49.97
2025-04-27 | 10:49 | 49.971
2025-04-27 | 10:49 | 49.976
2025-04-27 | 10:49 | 49.978
2025-04-27 | 10:49 | 49.98
2025-04-27 | 10:49 | 49.981
2025-04-27 | 10:49 | 49.982
2025-04-27 | 10:49 | 49.981
2025-04-27 | 10:49 | 49.979
2025-04-27 | 10:49 | 49.979
2025-04-27 | 10:49 | 49.979
2025-04-27 | 10:49 | 49.979
2025-04-27 | 10:49 | 49.978
2025-04-27 | 10:49 | 49.978
2025-04-27 | 10:49 | 49.978
2025-04-27 | 10:49 | 49.979
2025-04-27 | 10:49 | 49.978
2025-04-27 | 10:49 | 49.976
2025-04-27 | 10:49 | 49.977
2025-04-27 | 10:49 | 49.977
2025-04-27 | 10:49 | 49.975
2025-04-27 | 10:49 | 49.972
2025-04-27 | 10:49 | 49.968
2025-04-27 | 10:49 | 49.969
2025-04-27 | 10:49 | 49.969
2025-04-27 | 10:49 | 49.97
2025-04-27 | 10:49 | 49.969
2025-04-27 | 10:49 | 49.967
2025-04-27 | 10:49 | 49.965
2025-04-27 | 10:49 | 49.966
2025-04-27 | 10:50 | 49.965
2025-04-27 | 10:50 | 49.965
2025-04-27 | 10:50 | 49.968
2025-04-27 | 10:50 | 49.968
2025-04-27 | 10:50 | 49.969
2025-04-27 | 10:50 | 49.969
2025-04-27 | 10:50 | 49.971
2025-04-27 | 10:50 | 49.973
2025-04-27 | 10:50 | 49.975
2025-04-27 | 10:50 | 49.975
2025-04-27 | 10:50 | 49.972
2025-04-27 | 10:50 | 49.968
2025-04-27 | 10:50 | 49.967
2025-04-27 | 10:50 | 49.966
2025-04-27 | 10:50 | 49.963
2025-04-27 | 10:50 | 49.965
2025-04-27 | 10:50 | 49.969
2025-04-27 | 10:50 | 49.971
2025-04-27 | 10:50 | 49.97
2025-04-27 | 10:50 | 49.968
2025-04-27 | 10:50 | 49.967
2025-04-27 | 10:50 | 49.964
2025-04-27 | 10:50 | 49.964
2025-04-27 | 10:50 | 49.962
2025-04-27 | 10:50 | 49.964
2025-04-27 | 10:50 | 49.969
2025-04-27 | 10:50 | 49.972
2025-04-27 | 10:50 | 49.972
2025-04-27 | 10:50 | 49.972
2025-04-27 | 10:50 | 49.971
2025-04-27 | 10:50 | 49.972
2025-04-27 | 10:50 | 49.972
2025-04-27 | 10:50 | 49.969
2025-04-27 | 10:50 | 49.961
2025-04-27 | 10:50 | 49.958
2025-04-27 | 10:50 | 49.96
2025-04-27 | 10:50 | 49.962
2025-04-27 | 10:50 | 49.965
2025-04-27 | 10:50 | 49.965
2025-04-27 | 10:50 | 49.964
2025-04-27 | 10:50 | 49.963
2025-04-27 | 10:50 | 49.961
2025-04-27 | 10:50 | 49.957
2025-04-27 | 10:50 | 49.958
2025-04-27 | 10:50 | 49.956
2025-04-27 | 10:50 | 49.955
2025-04-27 | 10:50 | 49.954
2025-04-27 | 10:50 | 49.955
2025-04-27 | 10:50 | 49.961
2025-04-27 | 10:50 | 49.973
2025-04-27 | 10:50 | 49.975
2025-04-27 | 10:50 | 49.976
2025-04-27 | 10:50 | 49.976
2025-04-27 | 10:50 | 49.973
2025-04-27 | 10:50 | 49.972
2025-04-27 | 10:50 | 49.973
2025-04-27 | 10:50 | 49.972
2025-04-27 | 10:50 | 49.973
2025-04-27 | 10:50 | 49.977
2025-04-27 | 10:50 | 49.978
2025-04-27 | 10:50 | 49.979
2025-04-27 | 10:51 | 49.979
2025-04-27 | 10:51 | 49.979
2025-04-27 | 10:51 | 49.98
2025-04-27 | 10:51 | 49.981
2025-04-27 | 10:51 | 49.98
2025-04-27 | 10:51 | 49.979
2025-04-27 | 10:51 | 49.979
2025-04-27 | 10:51 | 49.976
2025-04-27 | 10:51 | 49.976
2025-04-27 | 10:51 | 49.974
2025-04-27 | 10:51 | 49.976
2025-04-27 | 10:51 | 49.979
2025-04-27 | 10:51 | 49.98
2025-04-27 | 10:51 | 49.978
2025-04-27 | 10:51 | 49.98
2025-04-27 | 10:51 | 49.982
2025-04-27 | 10:51 | 49.981
2025-04-27 | 10:51 | 49.984
2025-04-27 | 10:51 | 49.992
2025-04-27 | 10:51 | 49.996
2025-04-27 | 10:51 | 49.998
2025-04-27 | 10:51 | 49.998
2025-04-27 | 10:51 | 49.998
2025-04-27 | 10:51 | 50
2025-04-27 | 10:51 | 50.001
2025-04-27 | 10:51 | 49.999
2025-04-27 | 10:51 | 49.995
2025-04-27 | 10:51 | 49.993
2025-04-27 | 10:51 | 49.991
2025-04-27 | 10:51 | 49.989
2025-04-27 | 10:51 | 49.984
2025-04-27 | 10:51 | 49.978
2025-04-27 | 10:51 | 49.975
2025-04-27 | 10:51 | 49.973
2025-04-27 | 10:51 | 49.973
2025-04-27 | 10:51 | 49.973
2025-04-27 | 10:51 | 49.975
2025-04-27 | 10:51 | 49.974
2025-04-27 | 10:51 | 49.976
2025-04-27 | 10:51 | 49.978
2025-04-27 | 10:51 | 49.978
2025-04-27 | 10:51 | 49.981
2025-04-27 | 10:51 | 49.985
2025-04-27 | 10:51 | 49.986
2025-04-27 | 10:51 | 49.984
2025-04-27 | 10:51 | 49.978
2025-04-27 | 10:51 | 49.973
2025-04-27 | 10:51 | 49.974
2025-04-27 | 10:51 | 49.973
2025-04-27 | 10:51 | 49.97
2025-04-27 | 10:51 | 49.967
2025-04-27 | 10:51 | 49.969
2025-04-27 | 10:51 | 49.971
2025-04-27 | 10:51 | 49.972
2025-04-27 | 10:51 | 49.972
2025-04-27 | 10:51 | 49.971
2025-04-27 | 10:51 | 49.97
2025-04-27 | 10:51 | 49.971
2025-04-27 | 10:51 | 49.969
2025-04-27 | 10:52 | 49.968
2025-04-27 | 10:52 | 49.969
2025-04-27 | 10:52 | 49.97
2025-04-27 | 10:52 | 49.97
2025-04-27 | 10:52 | 49.972
2025-04-27 | 10:52 | 49.974
2025-04-27 | 10:52 | 49.976
2025-04-27 | 10:52 | 49.976
2025-04-27 | 10:52 | 49.977
2025-04-27 | 10:52 | 49.976
2025-04-27 | 10:52 | 49.975
2025-04-27 | 10:52 | 49.971
2025-04-27 | 10:52 | 49.969
2025-04-27 | 10:52 | 49.971
2025-04-27 | 10:52 | 49.973
2025-04-27 | 10:52 | 49.975
2025-04-27 | 10:52 | 49.978
2025-04-27 | 10:52 | 49.978
2025-04-27 | 10:52 | 49.976
2025-04-27 | 10:52 | 49.975
2025-04-27 | 10:52 | 49.973
2025-04-27 | 10:52 | 49.971
2025-04-27 | 10:52 | 49.969
2025-04-27 | 10:52 | 49.976
2025-04-27 | 10:52 | 49.978

## 20250427-3
In GMT
Date | Time | Freq
2025-04-27 | 18:12 | 50.054 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-04-27 | 18:12 | 50.051 | 222 | BRITNED | 676.211
2025-04-27 | 18:12 | 50.05 | 268 | WBURB-2 | 428.156
2025-04-27 | 18:12 | 50.049 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-04-27 | 18:12 | 50.049 |  | Viking Link | -648.9
2025-04-27 | 18:12 | 50.049 |  | Viking Link | 1398.96
2025-04-27 | 18:12 | 50.05 | 209 | DRAXX-3 | 626.95
2025-04-27 | 18:12 | 50.051 | 154 | CDCL-1 | 391.57
2025-04-27 | 18:12 | 50.046 | 268 | ROCK-1 | 468.495
2025-04-27 | 18:12 | 50.034 | 148 | IFA Bipole1 | 945.473
2025-04-27 | 18:12 | 50.026 | 132 | IFA Bipole1 | 999.1
2025-04-27 | 18:12 | 50.022 | 141 | IFA Bipole2 | 1000
2025-04-27 | 18:12 | 50.022 | 135 | IFA Bipole1 | 996.75
2025-04-27 | 18:12 | 50.024 |  | Viking Link | -780.3
2025-04-27 | 18:12 | 50.027
2025-04-27 | 18:12 | 50.029
2025-04-27 | 18:12 | 50.033
2025-04-27 | 18:12 | 50.035
2025-04-27 | 18:12 | 50.035
2025-04-27 | 18:12 | 50.036 | 130 | HEYM12 | 271.908
2025-04-27 | 18:12 | 50.035 | 228 | HUMR-1 | 303.75
2025-04-27 | 18:12 | 50.032
2025-04-27 | 18:12 | 50.029
2025-04-27 | 18:12 | 50.027
2025-04-27 | 18:12 | 50.025
2025-04-27 | 18:12 | 50.023
2025-04-27 | 18:12 | 50.021
2025-04-27 | 18:12 | 50.019
2025-04-27 | 18:12 | 50.02
2025-04-27 | 18:12 | 50.018
2025-04-27 | 18:12 | 50.017 | 211 | CDCL-1 | 291.5
2025-04-27 | 18:12 | 50.016 | 199 | STAY-2 | 413.125
2025-04-27 | 18:12 | 50.014 | 173 | CDCL-1 | 397.375
2025-04-27 | 18:12 | 50.015 | 248 | SEAB-2 | 361.25
2025-04-27 | 18:12 | 50.017 | 255 | FRANCE | 995.65
2025-04-27 | 18:12 | 50.018 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-04-27 | 18:12 | 50.017
2025-04-27 | 18:12 | 50.019
2025-04-27 | 18:13 | 50.02
2025-04-27 | 18:13 | 50.02
2025-04-27 | 18:13 | 50.022
2025-04-27 | 18:13 | 50.023
2025-04-27 | 18:13 | 50.023
2025-04-27 | 18:13 | 50.023
2025-04-27 | 18:13 | 50.022
2025-04-27 | 18:13 | 50.024
2025-04-27 | 18:13 | 50.025
2025-04-27 | 18:13 | 50.027
2025-04-27 | 18:13 | 50.029
2025-04-27 | 18:13 | 50.029
2025-04-27 | 18:13 | 50.028
2025-04-27 | 18:13 | 50.026
2025-04-27 | 18:13 | 50.023
2025-04-27 | 18:13 | 50.019
2025-04-27 | 18:13 | 50.015
2025-04-27 | 18:13 | 50.012
2025-04-27 | 18:13 | 50.01
2025-04-27 | 18:13 | 50.007
2025-04-27 | 18:13 | 50.004
2025-04-27 | 18:13 | 50.003
2025-04-27 | 18:13 | 50.002
2025-04-27 | 18:13 | 49.96
2025-04-27 | 18:13 | 49.931
2025-04-27 | 18:13 | 49.917
2025-04-27 | 18:13 | 49.907
2025-04-27 | 18:13 | 49.904
2025-04-27 | 18:13 | 49.903
2025-04-27 | 18:13 | 49.907
2025-04-27 | 18:13 | 49.909
2025-04-27 | 18:13 | 49.91
2025-04-27 | 18:13 | 49.911
2025-04-27 | 18:13 | 49.911
2025-04-27 | 18:13 | 49.913
2025-04-27 | 18:13 | 49.914
2025-04-27 | 18:13 | 49.914
2025-04-27 | 18:13 | 49.914
2025-04-27 | 18:13 | 49.917
2025-04-27 | 18:13 | 49.915
2025-04-27 | 18:13 | 49.915
2025-04-27 | 18:13 | 49.915
2025-04-27 | 18:13 | 49.916
2025-04-27 | 18:13 | 49.918
2025-04-27 | 18:13 | 49.918
2025-04-27 | 18:13 | 49.918
2025-04-27 | 18:13 | 49.92
2025-04-27 | 18:13 | 49.918
2025-04-27 | 18:13 | 49.915
2025-04-27 | 18:13 | 49.911
2025-04-27 | 18:13 | 49.909
2025-04-27 | 18:13 | 49.909
2025-04-27 | 18:13 | 49.906
2025-04-27 | 18:13 | 49.904
2025-04-27 | 18:13 | 49.9
2025-04-27 | 18:13 | 49.9
2025-04-27 | 18:13 | 49.899
2025-04-27 | 18:13 | 49.901
2025-04-27 | 18:13 | 49.903
2025-04-27 | 18:14 | 49.906
2025-04-27 | 18:14 | 49.906
2025-04-27 | 18:14 | 49.906
2025-04-27 | 18:14 | 49.908
2025-04-27 | 18:14 | 49.908
2025-04-27 | 18:14 | 49.908
2025-04-27 | 18:14 | 49.907
2025-04-27 | 18:14 | 49.907
2025-04-27 | 18:14 | 49.907
2025-04-27 | 18:14 | 49.906
2025-04-27 | 18:14 | 49.908
2025-04-27 | 18:14 | 49.909
2025-04-27 | 18:14 | 49.91
2025-04-27 | 18:14 | 49.912
2025-04-27 | 18:14 | 49.91
2025-04-27 | 18:14 | 49.911
2025-04-27 | 18:14 | 49.911
2025-04-27 | 18:14 | 49.91
2025-04-27 | 18:14 | 49.912
2025-04-27 | 18:14 | 49.914
2025-04-27 | 18:14 | 49.914
2025-04-27 | 18:14 | 49.913
2025-04-27 | 18:14 | 49.913
2025-04-27 | 18:14 | 49.912
2025-04-27 | 18:14 | 49.909
2025-04-27 | 18:14 | 49.906
2025-04-27 | 18:14 | 49.906
2025-04-27 | 18:14 | 49.907
2025-04-27 | 18:14 | 49.907
2025-04-27 | 18:14 | 49.911
2025-04-27 | 18:14 | 49.91
2025-04-27 | 18:14 | 49.91
2025-04-27 | 18:14 | 49.909
2025-04-27 | 18:14 | 49.91
2025-04-27 | 18:14 | 49.909
2025-04-27 | 18:14 | 49.91
2025-04-27 | 18:14 | 49.911
2025-04-27 | 18:14 | 49.911
2025-04-27 | 18:14 | 49.913
2025-04-27 | 18:14 | 49.915
2025-04-27 | 18:14 | 49.913
2025-04-27 | 18:14 | 49.912
2025-04-27 | 18:14 | 49.907
2025-04-27 | 18:14 | 49.907
2025-04-27 | 18:14 | 49.904
2025-04-27 | 18:14 | 49.904
2025-04-27 | 18:14 | 49.902
2025-04-27 | 18:14 | 49.903
2025-04-27 | 18:14 | 49.902
2025-04-27 | 18:14 | 49.904
2025-04-27 | 18:14 | 49.908
2025-04-27 | 18:14 | 49.913
2025-04-27 | 18:14 | 49.916
2025-04-27 | 18:14 | 49.916
2025-04-27 | 18:14 | 49.917
2025-04-27 | 18:14 | 49.917
2025-04-27 | 18:14 | 49.917
2025-04-27 | 18:14 | 49.916
2025-04-27 | 18:14 | 49.916
2025-04-27 | 18:14 | 49.917
2025-04-27 | 18:14 | 49.916
2025-04-27 | 18:15 | 49.916
2025-04-27 | 18:15 | 49.915
2025-04-27 | 18:15 | 49.915
2025-04-27 | 18:15 | 49.916
2025-04-27 | 18:15 | 49.918
2025-04-27 | 18:15 | 49.921
2025-04-27 | 18:15 | 49.925
2025-04-27 | 18:15 | 49.924
2025-04-27 | 18:15 | 49.923
2025-04-27 | 18:15 | 49.92
2025-04-27 | 18:15 | 49.919
2025-04-27 | 18:15 | 49.92
2025-04-27 | 18:15 | 49.922
2025-04-27 | 18:15 | 49.923
2025-04-27 | 18:15 | 49.923
2025-04-27 | 18:15 | 49.923
2025-04-27 | 18:15 | 49.923
2025-04-27 | 18:15 | 49.925
2025-04-27 | 18:15 | 49.926
2025-04-27 | 18:15 | 49.924
2025-04-27 | 18:15 | 49.926
2025-04-27 | 18:15 | 49.924
2025-04-27 | 18:15 | 49.924
2025-04-27 | 18:15 | 49.926
2025-04-27 | 18:15 | 49.928
2025-04-27 | 18:15 | 49.929
2025-04-27 | 18:15 | 49.929
2025-04-27 | 18:15 | 49.931
2025-04-27 | 18:15 | 49.934
2025-04-27 | 18:15 | 49.938
2025-04-27 | 18:15 | 49.937
2025-04-27 | 18:15 | 49.936
2025-04-27 | 18:15 | 49.936
2025-04-27 | 18:15 | 49.938
2025-04-27 | 18:15 | 49.939
2025-04-27 | 18:15 | 49.939
2025-04-27 | 18:15 | 49.937
2025-04-27 | 18:15 | 49.935
2025-04-27 | 18:15 | 49.932
2025-04-27 | 18:15 | 49.932
2025-04-27 | 18:15 | 49.933
2025-04-27 | 18:15 | 49.932
2025-04-27 | 18:15 | 49.934
2025-04-27 | 18:15 | 49.937
2025-04-27 | 18:15 | 49.938
2025-04-27 | 18:15 | 49.938
2025-04-27 | 18:15 | 49.939
2025-04-27 | 18:15 | 49.939
2025-04-27 | 18:15 | 49.938
2025-04-27 | 18:15 | 49.939
2025-04-27 | 18:15 | 49.941
2025-04-27 | 18:15 | 49.94
2025-04-27 | 18:15 | 49.942
2025-04-27 | 18:15 | 49.942
2025-04-27 | 18:15 | 49.941
2025-04-27 | 18:15 | 49.938
2025-04-27 | 18:15 | 49.936
2025-04-27 | 18:15 | 49.934
2025-04-27 | 18:15 | 49.933
2025-04-27 | 18:16 | 49.931
2025-04-27 | 18:16 | 49.928
2025-04-27 | 18:16 | 49.928
2025-04-27 | 18:16 | 49.929
2025-04-27 | 18:16 | 49.931
2025-04-27 | 18:16 | 49.932
2025-04-27 | 18:16 | 49.933
2025-04-27 | 18:16 | 49.933
2025-04-27 | 18:16 | 49.935
2025-04-27 | 18:16 | 49.936
2025-04-27 | 18:16 | 49.934
2025-04-27 | 18:16 | 49.933
2025-04-27 | 18:16 | 49.931
2025-04-27 | 18:16 | 49.929
2025-04-27 | 18:16 | 49.93
2025-04-27 | 18:16 | 49.93
2025-04-27 | 18:16 | 49.932
2025-04-27 | 18:16 | 49.93
2025-04-27 | 18:16 | 49.929
2025-04-27 | 18:16 | 49.93
2025-04-27 | 18:16 | 49.931
2025-04-27 | 18:16 | 49.931
2025-04-27 | 18:16 | 49.932
2025-04-27 | 18:16 | 49.932
2025-04-27 | 18:16 | 49.935
2025-04-27 | 18:16 | 49.936
2025-04-27 | 18:16 | 49.939
2025-04-27 | 18:16 | 49.941
2025-04-27 | 18:16 | 49.938
2025-04-27 | 18:16 | 49.94
2025-04-27 | 18:16 | 49.941
2025-04-27 | 18:16 | 49.937
2025-04-27 | 18:16 | 49.936
2025-04-27 | 18:16 | 49.936
2025-04-27 | 18:16 | 49.935
2025-04-27 | 18:16 | 49.935
2025-04-27 | 18:16 | 49.932
2025-04-27 | 18:16 | 49.93
2025-04-27 | 18:16 | 49.926
2025-04-27 | 18:16 | 49.924
2025-04-27 | 18:16 | 49.925
2025-04-27 | 18:16 | 49.924
2025-04-27 | 18:16 | 49.924
2025-04-27 | 18:16 | 49.925
2025-04-27 | 18:16 | 49.927
2025-04-27 | 18:16 | 49.928
2025-04-27 | 18:16 | 49.928
2025-04-27 | 18:16 | 49.925
2025-04-27 | 18:16 | 49.922
2025-04-27 | 18:16 | 49.92
2025-04-27 | 18:16 | 49.919
2025-04-27 | 18:16 | 49.916
2025-04-27 | 18:16 | 49.913
2025-04-27 | 18:16 | 49.912
2025-04-27 | 18:16 | 49.911
2025-04-27 | 18:16 | 49.909
2025-04-27 | 18:16 | 49.908
2025-04-27 | 18:16 | 49.908
2025-04-27 | 18:16 | 49.908
2025-04-27 | 18:16 | 49.906
2025-04-27 | 18:16 | 49.906
2025-04-27 | 18:17 | 49.906
2025-04-27 | 18:17 | 49.905
2025-04-27 | 18:17 | 49.903
2025-04-27 | 18:17 | 49.903
2025-04-27 | 18:17 | 49.902
2025-04-27 | 18:17 | 49.902
2025-04-27 | 18:17 | 49.905
2025-04-27 | 18:17 | 49.907
2025-04-27 | 18:17 | 49.909
2025-04-27 | 18:17 | 49.91
2025-04-27 | 18:17 | 49.913
2025-04-27 | 18:17 | 49.916
2025-04-27 | 18:17 | 49.917
2025-04-27 | 18:17 | 49.916
2025-04-27 | 18:17 | 49.914
2025-04-27 | 18:17 | 49.912
2025-04-27 | 18:17 | 49.907
2025-04-27 | 18:17 | 49.906
2025-04-27 | 18:17 | 49.906
2025-04-27 | 18:17 | 49.906
2025-04-27 | 18:17 | 49.907
2025-04-27 | 18:17 | 49.907
2025-04-27 | 18:17 | 49.908
2025-04-27 | 18:17 | 49.907
2025-04-27 | 18:17 | 49.905
2025-04-27 | 18:17 | 49.905
2025-04-27 | 18:17 | 49.902
2025-04-27 | 18:17 | 49.901
2025-04-27 | 18:17 | 49.902
2025-04-27 | 18:17 | 49.902
2025-04-27 | 18:17 | 49.898
2025-04-27 | 18:17 | 49.898
2025-04-27 | 18:17 | 49.898
2025-04-27 | 18:17 | 49.898
2025-04-27 | 18:17 | 49.897
2025-04-27 | 18:17 | 49.896
2025-04-27 | 18:17 | 49.896
2025-04-27 | 18:17 | 49.895
2025-04-27 | 18:17 | 49.896
2025-04-27 | 18:17 | 49.896
2025-04-27 | 18:17 | 49.896
2025-04-27 | 18:17 | 49.896
2025-04-27 | 18:17 | 49.894
2025-04-27 | 18:17 | 49.893
2025-04-27 | 18:17 | 49.893
2025-04-27 | 18:17 | 49.894
2025-04-27 | 18:17 | 49.895
2025-04-27 | 18:17 | 49.9
2025-04-27 | 18:17 | 49.902
2025-04-27 | 18:17 | 49.903
2025-04-27 | 18:17 | 49.902
2025-04-27 | 18:17 | 49.9
2025-04-27 | 18:17 | 49.899
2025-04-27 | 18:17 | 49.9
2025-04-27 | 18:17 | 49.899
2025-04-27 | 18:17 | 49.897
2025-04-27 | 18:17 | 49.897
2025-04-27 | 18:17 | 49.894
2025-04-27 | 18:17 | 49.893
2025-04-27 | 18:18 | 49.891
2025-04-27 | 18:18 | 49.892
2025-04-27 | 18:18 | 49.895
2025-04-27 | 18:18 | 49.898
2025-04-27 | 18:18 | 49.9
2025-04-27 | 18:18 | 49.897
2025-04-27 | 18:18 | 49.898
2025-04-27 | 18:18 | 49.897
2025-04-27 | 18:18 | 49.896
2025-04-27 | 18:18 | 49.895
2025-04-27 | 18:18 | 49.896
2025-04-27 | 18:18 | 49.895
2025-04-27 | 18:18 | 49.896
2025-04-27 | 18:18 | 49.896
2025-04-27 | 18:18 | 49.895
2025-04-27 | 18:18 | 49.895
2025-04-27 | 18:18 | 49.896
2025-04-27 | 18:18 | 49.898
2025-04-27 | 18:18 | 49.898
2025-04-27 | 18:18 | 49.898
2025-04-27 | 18:18 | 49.898
2025-04-27 | 18:18 | 49.898
2025-04-27 | 18:18 | 49.899
2025-04-27 | 18:18 | 49.899
2025-04-27 | 18:18 | 49.897
2025-04-27 | 18:18 | 49.895
2025-04-27 | 18:18 | 49.894
2025-04-27 | 18:18 | 49.896
2025-04-27 | 18:18 | 49.898
2025-04-27 | 18:18 | 49.898
2025-04-27 | 18:18 | 49.899
2025-04-27 | 18:18 | 49.899
2025-04-27 | 18:18 | 49.899
2025-04-27 | 18:18 | 49.901
2025-04-27 | 18:18 | 49.901
2025-04-27 | 18:18 | 49.9
2025-04-27 | 18:18 | 49.896
2025-04-27 | 18:18 | 49.894
2025-04-27 | 18:18 | 49.894
2025-04-27 | 18:18 | 49.894
2025-04-27 | 18:18 | 49.892
2025-04-27 | 18:18 | 49.889
2025-04-27 | 18:18 | 49.886
2025-04-27 | 18:18 | 49.883
2025-04-27 | 18:18 | 49.884
2025-04-27 | 18:18 | 49.883
2025-04-27 | 18:18 | 49.881
2025-04-27 | 18:18 | 49.878
2025-04-27 | 18:18 | 49.877
2025-04-27 | 18:18 | 49.876
2025-04-27 | 18:18 | 49.875
2025-04-27 | 18:18 | 49.874
2025-04-27 | 18:18 | 49.872
2025-04-27 | 18:18 | 49.876
2025-04-27 | 18:18 | 49.881
2025-04-27 | 18:18 | 49.884
2025-04-27 | 18:18 | 49.886
2025-04-27 | 18:18 | 49.888
2025-04-27 | 18:18 | 49.893
2025-04-27 | 18:18 | 49.894
2025-04-27 | 18:18 | 49.894
2025-04-27 | 18:19 | 49.894
2025-04-27 | 18:19 | 49.894
2025-04-27 | 18:19 | 49.895
2025-04-27 | 18:19 | 49.894
2025-04-27 | 18:19 | 49.891
2025-04-27 | 18:19 | 49.89
2025-04-27 | 18:19 | 49.89
2025-04-27 | 18:19 | 49.887
2025-04-27 | 18:19 | 49.888
2025-04-27 | 18:19 | 49.886
2025-04-27 | 18:19 | 49.885
2025-04-27 | 18:19 | 49.883
2025-04-27 | 18:19 | 49.882
2025-04-27 | 18:19 | 49.883
2025-04-27 | 18:19 | 49.885
2025-04-27 | 18:19 | 49.885
2025-04-27 | 18:19 | 49.888
2025-04-27 | 18:19 | 49.889
2025-04-27 | 18:19 | 49.888
2025-04-27 | 18:19 | 49.89
2025-04-27 | 18:19 | 49.893
2025-04-27 | 18:19 | 49.895
2025-04-27 | 18:19 | 49.894
2025-04-27 | 18:19 | 49.894
2025-04-27 | 18:19 | 49.895
2025-04-27 | 18:19 | 49.895
2025-04-27 | 18:19 | 49.895
2025-04-27 | 18:19 | 49.894
2025-04-27 | 18:19 | 49.892
2025-04-27 | 18:19 | 49.891
2025-04-27 | 18:19 | 49.888
2025-04-27 | 18:19 | 49.885
2025-04-27 | 18:19 | 49.884
2025-04-27 | 18:19 | 49.883
2025-04-27 | 18:19 | 49.885
2025-04-27 | 18:19 | 49.886
2025-04-27 | 18:19 | 49.886
2025-04-27 | 18:19 | 49.886
2025-04-27 | 18:19 | 49.884
2025-04-27 | 18:19 | 49.884
2025-04-27 | 18:19 | 49.883
2025-04-27 | 18:19 | 49.882
2025-04-27 | 18:19 | 49.883
2025-04-27 | 18:19 | 49.883
2025-04-27 | 18:19 | 49.885
2025-04-27 | 18:19 | 49.886
2025-04-27 | 18:19 | 49.89
2025-04-27 | 18:19 | 49.893
2025-04-27 | 18:19 | 49.894
2025-04-27 | 18:19 | 49.893
2025-04-27 | 18:19 | 49.893
2025-04-27 | 18:19 | 49.897
2025-04-27 | 18:19 | 49.897
2025-04-27 | 18:19 | 49.896
2025-04-27 | 18:19 | 49.896
2025-04-27 | 18:19 | 49.893
2025-04-27 | 18:19 | 49.892
2025-04-27 | 18:19 | 49.893
2025-04-27 | 18:19 | 49.892
2025-04-27 | 18:20 | 49.89
2025-04-27 | 18:20 | 49.891
2025-04-27 | 18:20 | 49.89
2025-04-27 | 18:20 | 49.891
2025-04-27 | 18:20 | 49.892
2025-04-27 | 18:20 | 49.89
2025-04-27 | 18:20 | 49.889
2025-04-27 | 18:20 | 49.888
2025-04-27 | 18:20 | 49.885
2025-04-27 | 18:20 | 49.883
2025-04-27 | 18:20 | 49.883
2025-04-27 | 18:20 | 49.884
2025-04-27 | 18:20 | 49.885
2025-04-27 | 18:20 | 49.885
2025-04-27 | 18:20 | 49.885
2025-04-27 | 18:20 | 49.884
2025-04-27 | 18:20 | 49.884
2025-04-27 | 18:20 | 49.882
2025-04-27 | 18:20 | 49.881
2025-04-27 | 18:20 | 49.881
2025-04-27 | 18:20 | 49.879
2025-04-27 | 18:20 | 49.88
2025-04-27 | 18:20 | 49.881
2025-04-27 | 18:20 | 49.883
2025-04-27 | 18:20 | 49.883
2025-04-27 | 18:20 | 49.884
2025-04-27 | 18:20 | 49.883
2025-04-27 | 18:20 | 49.884
2025-04-27 | 18:20 | 49.885
2025-04-27 | 18:20 | 49.885
2025-04-27 | 18:20 | 49.885
2025-04-27 | 18:20 | 49.882
2025-04-27 | 18:20 | 49.882
2025-04-27 | 18:20 | 49.882
2025-04-27 | 18:20 | 49.884
2025-04-27 | 18:20 | 49.884
2025-04-27 | 18:20 | 49.884
2025-04-27 | 18:20 | 49.887
2025-04-27 | 18:20 | 49.888
2025-04-27 | 18:20 | 49.892
2025-04-27 | 18:20 | 49.894
2025-04-27 | 18:20 | 49.894
2025-04-27 | 18:20 | 49.894
2025-04-27 | 18:20 | 49.894
2025-04-27 | 18:20 | 49.896
2025-04-27 | 18:20 | 49.898
2025-04-27 | 18:20 | 49.898
2025-04-27 | 18:20 | 49.9
2025-04-27 | 18:20 | 49.899
2025-04-27 | 18:20 | 49.896
2025-04-27 | 18:20 | 49.894
2025-04-27 | 18:20 | 49.893
2025-04-27 | 18:20 | 49.893
2025-04-27 | 18:20 | 49.894
2025-04-27 | 18:20 | 49.894
2025-04-27 | 18:20 | 49.895
2025-04-27 | 18:20 | 49.896
2025-04-27 | 18:20 | 49.894
2025-04-27 | 18:20 | 49.891
2025-04-27 | 18:20 | 49.892
2025-04-27 | 18:20 | 49.894
2025-04-27 | 18:21 | 49.894
2025-04-27 | 18:21 | 49.896
2025-04-27 | 18:21 | 49.895
2025-04-27 | 18:21 | 49.894
2025-04-27 | 18:21 | 49.892
2025-04-27 | 18:21 | 49.892
2025-04-27 | 18:21 | 49.893
2025-04-27 | 18:21 | 49.893
2025-04-27 | 18:21 | 49.893
2025-04-27 | 18:21 | 49.893
2025-04-27 | 18:21 | 49.892
2025-04-27 | 18:21 | 49.891
2025-04-27 | 18:21 | 49.892
2025-04-27 | 18:21 | 49.893
2025-04-27 | 18:21 | 49.891
2025-04-27 | 18:21 | 49.893
2025-04-27 | 18:21 | 49.894
2025-04-27 | 18:21 | 49.895
2025-04-27 | 18:21 | 49.896
2025-04-27 | 18:21 | 49.898
2025-04-27 | 18:21 | 49.898
2025-04-27 | 18:21 | 49.899
2025-04-27 | 18:21 | 49.9
2025-04-27 | 18:21 | 49.898
2025-04-27 | 18:21 | 49.897
2025-04-27 | 18:21 | 49.896
2025-04-27 | 18:21 | 49.894
2025-04-27 | 18:21 | 49.892
2025-04-27 | 18:21 | 49.891
2025-04-27 | 18:21 | 49.892
2025-04-27 | 18:21 | 49.891
2025-04-27 | 18:21 | 49.895
2025-04-27 | 18:21 | 49.899
2025-04-27 | 18:21 | 49.901
2025-04-27 | 18:21 | 49.901
2025-04-27 | 18:21 | 49.901
2025-04-27 | 18:21 | 49.9
2025-04-27 | 18:21 | 49.9
2025-04-27 | 18:21 | 49.903
2025-04-27 | 18:21 | 49.906
2025-04-27 | 18:21 | 49.908
2025-04-27 | 18:21 | 49.91
2025-04-27 | 18:21 | 49.911
2025-04-27 | 18:21 | 49.91
2025-04-27 | 18:21 | 49.911
2025-04-27 | 18:21 | 49.912
2025-04-27 | 18:21 | 49.912
2025-04-27 | 18:21 | 49.914
2025-04-27 | 18:21 | 49.913
2025-04-27 | 18:21 | 49.911
2025-04-27 | 18:21 | 49.909
2025-04-27 | 18:21 | 49.907
2025-04-27 | 18:21 | 49.905
2025-04-27 | 18:21 | 49.903
2025-04-27 | 18:21 | 49.902
2025-04-27 | 18:21 | 49.901
2025-04-27 | 18:21 | 49.9
2025-04-27 | 18:21 | 49.901
2025-04-27 | 18:21 | 49.901
2025-04-27 | 18:22 | 49.9
2025-04-27 | 18:22 | 49.899
2025-04-27 | 18:22 | 49.9
2025-04-27 | 18:22 | 49.899
2025-04-27 | 18:22 | 49.899
2025-04-27 | 18:22 | 49.899
2025-04-27 | 18:22 | 49.898
2025-04-27 | 18:22 | 49.898
2025-04-27 | 18:22 | 49.902
2025-04-27 | 18:22 | 49.903
2025-04-27 | 18:22 | 49.903
2025-04-27 | 18:22 | 49.902
2025-04-27 | 18:22 | 49.901
2025-04-27 | 18:22 | 49.9
2025-04-27 | 18:22 | 49.901
2025-04-27 | 18:22 | 49.901
2025-04-27 | 18:22 | 49.903
2025-04-27 | 18:22 | 49.902
2025-04-27 | 18:22 | 49.901
2025-04-27 | 18:22 | 49.898
2025-04-27 | 18:22 | 49.897
2025-04-27 | 18:22 | 49.896
2025-04-27 | 18:22 | 49.898
2025-04-27 | 18:22 | 49.901
2025-04-27 | 18:22 | 49.905
2025-04-27 | 18:22 | 49.904
2025-04-27 | 18:22 | 49.904
2025-04-27 | 18:22 | 49.904
2025-04-27 | 18:22 | 49.903
2025-04-27 | 18:22 | 49.9
2025-04-27 | 18:22 | 49.899
2025-04-27 | 18:22 | 49.896
2025-04-27 | 18:22 | 49.894
2025-04-27 | 18:22 | 49.893
2025-04-27 | 18:22 | 49.893
2025-04-27 | 18:22 | 49.892
2025-04-27 | 18:22 | 49.892
2025-04-27 | 18:22 | 49.893
2025-04-27 | 18:22 | 49.893
2025-04-27 | 18:22 | 49.893
2025-04-27 | 18:22 | 49.896
2025-04-27 | 18:22 | 49.897
2025-04-27 | 18:22 | 49.899
2025-04-27 | 18:22 | 49.899
2025-04-27 | 18:22 | 49.899
2025-04-27 | 18:22 | 49.898
2025-04-27 | 18:22 | 49.899
2025-04-27 | 18:22 | 49.899
2025-04-27 | 18:22 | 49.9
2025-04-27 | 18:22 | 49.898
2025-04-27 | 18:22 | 49.895
2025-04-27 | 18:22 | 49.894
2025-04-27 | 18:22 | 49.895
2025-04-27 | 18:22 | 49.894
2025-04-27 | 18:22 | 49.894
2025-04-27 | 18:22 | 49.896
2025-04-27 | 18:22 | 49.898
2025-04-27 | 18:22 | 49.898
2025-04-27 | 18:22 | 49.901
2025-04-27 | 18:22 | 49.904
2025-04-27 | 18:22 | 49.908
2025-04-27 | 18:23 | 49.909
2025-04-27 | 18:23 | 49.909
2025-04-27 | 18:23 | 49.912
2025-04-27 | 18:23 | 49.914
2025-04-27 | 18:23 | 49.915
2025-04-27 | 18:23 | 49.915
2025-04-27 | 18:23 | 49.915
2025-04-27 | 18:23 | 49.916
2025-04-27 | 18:23 | 49.914
2025-04-27 | 18:23 | 49.914
2025-04-27 | 18:23 | 49.914
2025-04-27 | 18:23 | 49.915
2025-04-27 | 18:23 | 49.912
2025-04-27 | 18:23 | 49.913
2025-04-27 | 18:23 | 49.914
2025-04-27 | 18:23 | 49.913
2025-04-27 | 18:23 | 49.911
2025-04-27 | 18:23 | 49.911
2025-04-27 | 18:23 | 49.912
2025-04-27 | 18:23 | 49.911
2025-04-27 | 18:23 | 49.912
2025-04-27 | 18:23 | 49.913
2025-04-27 | 18:23 | 49.913
2025-04-27 | 18:23 | 49.912
2025-04-27 | 18:23 | 49.912
2025-04-27 | 18:23 | 49.917
2025-04-27 | 18:23 | 49.921
2025-04-27 | 18:23 | 49.923
2025-04-27 | 18:23 | 49.924
2025-04-27 | 18:23 | 49.925
2025-04-27 | 18:23 | 49.924
2025-04-27 | 18:23 | 49.925
2025-04-27 | 18:23 | 49.925
2025-04-27 | 18:23 | 49.928
2025-04-27 | 18:23 | 49.927
2025-04-27 | 18:23 | 49.927
2025-04-27 | 18:23 | 49.927
2025-04-27 | 18:23 | 49.929
2025-04-27 | 18:23 | 49.929
2025-04-27 | 18:23 | 49.931
2025-04-27 | 18:23 | 49.931
2025-04-27 | 18:23 | 49.931
2025-04-27 | 18:23 | 49.931
2025-04-27 | 18:23 | 49.932
2025-04-27 | 18:23 | 49.931
2025-04-27 | 18:23 | 49.933
2025-04-27 | 18:23 | 49.933
2025-04-27 | 18:23 | 49.932
2025-04-27 | 18:23 | 49.932
2025-04-27 | 18:23 | 49.932
2025-04-27 | 18:23 | 49.931
2025-04-27 | 18:23 | 49.931
2025-04-27 | 18:23 | 49.93
2025-04-27 | 18:23 | 49.928
2025-04-27 | 18:23 | 49.927
2025-04-27 | 18:23 | 49.924
2025-04-27 | 18:23 | 49.924
2025-04-27 | 18:23 | 49.923
2025-04-27 | 18:23 | 49.925
2025-04-27 | 18:24 | 49.926
2025-04-27 | 18:24 | 49.927
2025-04-27 | 18:24 | 49.928
2025-04-27 | 18:24 | 49.929
2025-04-27 | 18:24 | 49.929
2025-04-27 | 18:24 | 49.928
2025-04-27 | 18:24 | 49.928
2025-04-27 | 18:24 | 49.927
2025-04-27 | 18:24 | 49.926
2025-04-27 | 18:24 | 49.925
2025-04-27 | 18:24 | 49.924
2025-04-27 | 18:24 | 49.923
2025-04-27 | 18:24 | 49.923
2025-04-27 | 18:24 | 49.923
2025-04-27 | 18:24 | 49.923
2025-04-27 | 18:24 | 49.921
2025-04-27 | 18:24 | 49.919
2025-04-27 | 18:24 | 49.917
2025-04-27 | 18:24 | 49.916
2025-04-27 | 18:24 | 49.916
2025-04-27 | 18:24 | 49.915
2025-04-27 | 18:24 | 49.916
2025-04-27 | 18:24 | 49.919
2025-04-27 | 18:24 | 49.921
2025-04-27 | 18:24 | 49.923
2025-04-27 | 18:24 | 49.923
2025-04-27 | 18:24 | 49.923
2025-04-27 | 18:24 | 49.923
2025-04-27 | 18:24 | 49.922
2025-04-27 | 18:24 | 49.922
2025-04-27 | 18:24 | 49.924
2025-04-27 | 18:24 | 49.924
2025-04-27 | 18:24 | 49.924
2025-04-27 | 18:24 | 49.923
2025-04-27 | 18:24 | 49.924
2025-04-27 | 18:24 | 49.924
2025-04-27 | 18:24 | 49.925
2025-04-27 | 18:24 | 49.927
2025-04-27 | 18:24 | 49.931
2025-04-27 | 18:24 | 49.934
2025-04-27 | 18:24 | 49.938
2025-04-27 | 18:24 | 49.94
2025-04-27 | 18:24 | 49.939
2025-04-27 | 18:24 | 49.938
2025-04-27 | 18:24 | 49.938
2025-04-27 | 18:24 | 49.939
2025-04-27 | 18:24 | 49.938
2025-04-27 | 18:24 | 49.937
2025-04-27 | 18:24 | 49.933
2025-04-27 | 18:24 | 49.933
2025-04-27 | 18:24 | 49.934
2025-04-27 | 18:24 | 49.934
2025-04-27 | 18:24 | 49.934
2025-04-27 | 18:24 | 49.935
2025-04-27 | 18:24 | 49.936
2025-04-27 | 18:24 | 49.935
2025-04-27 | 18:24 | 49.933
2025-04-27 | 18:24 | 49.932
2025-04-27 | 18:24 | 49.929
2025-04-27 | 18:24 | 49.925
2025-04-27 | 18:24 | 49.923
2025-04-27 | 18:25 | 49.921
2025-04-27 | 18:25 | 49.92
2025-04-27 | 18:25 | 49.917
2025-04-27 | 18:25 | 49.917
2025-04-27 | 18:25 | 49.918
2025-04-27 | 18:25 | 49.919
2025-04-27 | 18:25 | 49.92
2025-04-27 | 18:25 | 49.923
2025-04-27 | 18:25 | 49.926
2025-04-27 | 18:25 | 49.926
2025-04-27 | 18:25 | 49.929
2025-04-27 | 18:25 | 49.93
2025-04-27 | 18:25 | 49.93
2025-04-27 | 18:25 | 49.931
2025-04-27 | 18:25 | 49.93
2025-04-27 | 18:25 | 49.93
2025-04-27 | 18:25 | 49.93
2025-04-27 | 18:25 | 49.929
2025-04-27 | 18:25 | 49.927
2025-04-27 | 18:25 | 49.929
2025-04-27 | 18:25 | 49.93
2025-04-27 | 18:25 | 49.932
2025-04-27 | 18:25 | 49.934
2025-04-27 | 18:25 | 49.936
2025-04-27 | 18:25 | 49.938
2025-04-27 | 18:25 | 49.942
2025-04-27 | 18:25 | 49.946
2025-04-27 | 18:25 | 49.948
2025-04-27 | 18:25 | 49.949
2025-04-27 | 18:25 | 49.951
2025-04-27 | 18:25 | 49.956
2025-04-27 | 18:25 | 49.962
2025-04-27 | 18:25 | 49.962
2025-04-27 | 18:25 | 49.963
2025-04-27 | 18:25 | 49.963
2025-04-27 | 18:25 | 49.964
2025-04-27 | 18:25 | 49.963
2025-04-27 | 18:25 | 49.963
2025-04-27 | 18:25 | 49.961
2025-04-27 | 18:25 | 49.957
2025-04-27 | 18:25 | 49.952
2025-04-27 | 18:25 | 49.951
2025-04-27 | 18:25 | 49.949
2025-04-27 | 18:25 | 49.947
2025-04-27 | 18:25 | 49.947
2025-04-27 | 18:25 | 49.949
2025-04-27 | 18:25 | 49.95
2025-04-27 | 18:25 | 49.95
2025-04-27 | 18:25 | 49.952
2025-04-27 | 18:25 | 49.952
2025-04-27 | 18:25 | 49.955
2025-04-27 | 18:25 | 49.957
2025-04-27 | 18:25 | 49.96
2025-04-27 | 18:25 | 49.96
2025-04-27 | 18:25 | 49.96
2025-04-27 | 18:25 | 49.959
2025-04-27 | 18:25 | 49.959
2025-04-27 | 18:25 | 49.962
2025-04-27 | 18:25 | 49.964
2025-04-27 | 18:26 | 49.965
2025-04-27 | 18:26 | 49.965
2025-04-27 | 18:26 | 49.965
2025-04-27 | 18:26 | 49.965
2025-04-27 | 18:26 | 49.966
2025-04-27 | 18:26 | 49.965
2025-04-27 | 18:26 | 49.965
2025-04-27 | 18:26 | 49.962
2025-04-27 | 18:26 | 49.96
2025-04-27 | 18:26 | 49.959
2025-04-27 | 18:26 | 49.961
2025-04-27 | 18:26 | 49.962
2025-04-27 | 18:26 | 49.965
2025-04-27 | 18:26 | 49.97
2025-04-27 | 18:26 | 49.975
2025-04-27 | 18:26 | 49.978
2025-04-27 | 18:26 | 49.983
2025-04-27 | 18:26 | 49.989
2025-04-27 | 18:26 | 49.993
2025-04-27 | 18:26 | 49.996
2025-04-27 | 18:26 | 49.999
2025-04-27 | 18:26 | 49.999
2025-04-27 | 18:26 | 49.996
2025-04-27 | 18:26 | 49.992
2025-04-27 | 18:26 | 49.987
2025-04-27 | 18:26 | 49.981
2025-04-27 | 18:26 | 49.978
2025-04-27 | 18:26 | 49.977
2025-04-27 | 18:26 | 49.975
2025-04-27 | 18:26 | 49.975
2025-04-27 | 18:26 | 49.976
2025-04-27 | 18:26 | 49.977
2025-04-27 | 18:26 | 49.975
2025-04-27 | 18:26 | 49.974
2025-04-27 | 18:26 | 49.973
2025-04-27 | 18:26 | 49.972
2025-04-27 | 18:26 | 49.971
2025-04-27 | 18:26 | 49.97
2025-04-27 | 18:26 | 49.969
2025-04-27 | 18:26 | 49.969
2025-04-27 | 18:26 | 49.97
2025-04-27 | 18:26 | 49.973
2025-04-27 | 18:26 | 49.977
2025-04-27 | 18:26 | 49.979
2025-04-27 | 18:26 | 49.979
2025-04-27 | 18:26 | 49.978
2025-04-27 | 18:26 | 49.979
2025-04-27 | 18:26 | 49.98
2025-04-27 | 18:26 | 49.981
2025-04-27 | 18:26 | 49.982
2025-04-27 | 18:26 | 49.981
2025-04-27 | 18:26 | 49.979
2025-04-27 | 18:26 | 49.979
2025-04-27 | 18:26 | 49.978
2025-04-27 | 18:26 | 49.978
2025-04-27 | 18:26 | 49.98
2025-04-27 | 18:26 | 49.981
2025-04-27 | 18:26 | 49.981
2025-04-27 | 18:26 | 49.981
2025-04-27 | 18:26 | 49.984
2025-04-27 | 18:26 | 49.987
2025-04-27 | 18:27 | 49.988
2025-04-27 | 18:27 | 49.993
2025-04-27 | 18:27 | 50
2025-04-27 | 18:27 | 50.004
2025-04-27 | 18:27 | 50.009
2025-04-27 | 18:27 | 50.013
2025-04-27 | 18:27 | 50.017
2025-04-27 | 18:27 | 50.02
2025-04-27 | 18:27 | 50.023
2025-04-27 | 18:27 | 50.025
2025-04-27 | 18:27 | 50.026
2025-04-27 | 18:27 | 50.027
2025-04-27 | 18:27 | 50.024
2025-04-27 | 18:27 | 50.022
2025-04-27 | 18:27 | 50.019
2025-04-27 | 18:27 | 50.015
2025-04-27 | 18:27 | 50.013
2025-04-27 | 18:27 | 50.015
2025-04-27 | 18:27 | 50.017
2025-04-27 | 18:27 | 50.018
2025-04-27 | 18:27 | 50.02
2025-04-27 | 18:27 | 50.02
2025-04-27 | 18:27 | 50.021
2025-04-27 | 18:27 | 50.024
2025-04-27 | 18:27 | 50.026
2025-04-27 | 18:27 | 50.024
2025-04-27 | 18:27 | 50.025
2025-04-27 | 18:27 | 50.025
2025-04-27 | 18:27 | 50.026
2025-04-27 | 18:27 | 50.024
2025-04-27 | 18:27 | 50.022
2025-04-27 | 18:27 | 50.022
2025-04-27 | 18:27 | 50.023
2025-04-27 | 18:27 | 50.023
2025-04-27 | 18:27 | 50.024
2025-04-27 | 18:27 | 50.025
2025-04-27 | 18:27 | 50.026
2025-04-27 | 18:27 | 50.028
2025-04-27 | 18:27 | 50.028
2025-04-27 | 18:27 | 50.029
2025-04-27 | 18:27 | 50.03
2025-04-27 | 18:27 | 50.031
2025-04-27 | 18:27 | 50.033
2025-04-27 | 18:27 | 50.032
2025-04-27 | 18:27 | 50.031
2025-04-27 | 18:27 | 50.029
2025-04-27 | 18:27 | 50.029
2025-04-27 | 18:27 | 50.028
2025-04-27 | 18:27 | 50.027
2025-04-27 | 18:27 | 50.025
2025-04-27 | 18:27 | 50.023
2025-04-27 | 18:27 | 50.023
2025-04-27 | 18:27 | 50.024
2025-04-27 | 18:27 | 50.027
2025-04-27 | 18:27 | 50.027
2025-04-27 | 18:27 | 50.028
2025-04-27 | 18:27 | 50.029
2025-04-27 | 18:27 | 50.029
2025-04-27 | 18:27 | 50.031
2025-04-27 | 18:28 | 50.033
2025-04-27 | 18:28 | 50.035
2025-04-27 | 18:28 | 50.035
2025-04-27 | 18:28 | 50.036

## 20250429-1
In GMT
Date | Time | Freq
2025-04-29 | 16:24 | 49.962 | 193 | IFA2 | 847.99 |  |  |  | Interconnector total swing was 1600MW gain
2025-04-29 | 16:24 | 49.959 | 222 | BRITNED | 676.211
2025-04-29 | 16:24 | 49.96 | 268 | WBURB-2 | 428.156
2025-04-29 | 16:24 | 49.96 |  |  |  | Arbroath | 14 | Arbroath GT2 tripped
2025-04-29 | 16:24 | 49.958 |  | Viking Link | -648.9
2025-04-29 | 16:24 | 49.958 |  | Viking Link | 1398.96
2025-04-29 | 16:24 | 49.958 | 209 | DRAXX-3 | 626.95
2025-04-29 | 16:24 | 49.961 | 154 | CDCL-1 | 391.57
2025-04-29 | 16:24 | 49.963 | 268 | ROCK-1 | 468.495
2025-04-29 | 16:24 | 49.963 | 148 | IFA Bipole1 | 945.473
2025-04-29 | 16:24 | 49.968 | 132 | IFA Bipole1 | 999.1
2025-04-29 | 16:24 | 49.968 | 141 | IFA Bipole2 | 1000
2025-04-29 | 16:24 | 49.97 | 135 | IFA Bipole1 | 996.75
2025-04-29 | 16:24 | 49.97 |  | Viking Link | -780.3
2025-04-29 | 16:24 | 49.968
2025-04-29 | 16:24 | 49.966
2025-04-29 | 16:24 | 49.966
2025-04-29 | 16:24 | 49.968
2025-04-29 | 16:24 | 49.969
2025-04-29 | 16:24 | 49.972 | 130 | HEYM12 | 271.908
2025-04-29 | 16:24 | 49.973 | 228 | HUMR-1 | 303.75
2025-04-29 | 16:24 | 49.974
2025-04-29 | 16:24 | 49.971
2025-04-29 | 16:24 | 49.971
2025-04-29 | 16:24 | 49.969
2025-04-29 | 16:24 | 49.969
2025-04-29 | 16:24 | 49.971
2025-04-29 | 16:24 | 49.975
2025-04-29 | 16:25 | 49.979
2025-04-29 | 16:25 | 49.984
2025-04-29 | 16:25 | 49.987 | 211 | CDCL-1 | 291.5
2025-04-29 | 16:25 | 49.99 | 199 | STAY-2 | 413.125
2025-04-29 | 16:25 | 49.991 | 173 | CDCL-1 | 397.375
2025-04-29 | 16:25 | 49.989 | 248 | SEAB-2 | 361.25
2025-04-29 | 16:25 | 49.985 | 255 | FRANCE | 995.65
2025-04-29 | 16:25 | 49.983 |  |  |  | Barking | 21 | Barking 132kV circuit breaker Grid 410B tripped
2025-04-29 | 16:25 | 49.981
2025-04-29 | 16:25 | 49.981
2025-04-29 | 16:25 | 49.98
2025-04-29 | 16:25 | 49.98
2025-04-29 | 16:25 | 49.982
2025-04-29 | 16:25 | 49.984
2025-04-29 | 16:25 | 49.986
2025-04-29 | 16:25 | 49.988
2025-04-29 | 16:25 | 49.989
2025-04-29 | 16:25 | 49.989
2025-04-29 | 16:25 | 49.991
2025-04-29 | 16:25 | 49.992
2025-04-29 | 16:25 | 49.994
2025-04-29 | 16:25 | 49.996
2025-04-29 | 16:25 | 49.997
2025-04-29 | 16:25 | 49.999
2025-04-29 | 16:25 | 49.998
2025-04-29 | 16:25 | 50.001
2025-04-29 | 16:25 | 50.001
2025-04-29 | 16:25 | 50
2025-04-29 | 16:25 | 49.996
2025-04-29 | 16:25 | 49.993
2025-04-29 | 16:25 | 49.986
2025-04-29 | 16:25 | 49.978
2025-04-29 | 16:25 | 49.971
2025-04-29 | 16:25 | 49.92
2025-04-29 | 16:25 | 49.823
2025-04-29 | 16:25 | 49.785
2025-04-29 | 16:25 | 49.778
2025-04-29 | 16:25 | 49.781
2025-04-29 | 16:25 | 49.785
2025-04-29 | 16:25 | 49.789
2025-04-29 | 16:25 | 49.792
2025-04-29 | 16:25 | 49.796
2025-04-29 | 16:25 | 49.796
2025-04-29 | 16:25 | 49.793
2025-04-29 | 16:25 | 49.789
2025-04-29 | 16:25 | 49.788
2025-04-29 | 16:25 | 49.788
2025-04-29 | 16:25 | 49.789
2025-04-29 | 16:25 | 49.789
2025-04-29 | 16:25 | 49.789
2025-04-29 | 16:25 | 49.788
2025-04-29 | 16:25 | 49.788
2025-04-29 | 16:25 | 49.792
2025-04-29 | 16:25 | 49.795
2025-04-29 | 16:25 | 49.796
2025-04-29 | 16:25 | 49.798
2025-04-29 | 16:25 | 49.796
2025-04-29 | 16:25 | 49.795
2025-04-29 | 16:25 | 49.794
2025-04-29 | 16:25 | 49.796
2025-04-29 | 16:26 | 49.796
2025-04-29 | 16:26 | 49.797
2025-04-29 | 16:26 | 49.797
2025-04-29 | 16:26 | 49.801
2025-04-29 | 16:26 | 49.802
2025-04-29 | 16:26 | 49.803
2025-04-29 | 16:26 | 49.803
2025-04-29 | 16:26 | 49.804
2025-04-29 | 16:26 | 49.803
2025-04-29 | 16:26 | 49.8
2025-04-29 | 16:26 | 49.801
2025-04-29 | 16:26 | 49.802
2025-04-29 | 16:26 | 49.804
2025-04-29 | 16:26 | 49.805
2025-04-29 | 16:26 | 49.805
2025-04-29 | 16:26 | 49.804
2025-04-29 | 16:26 | 49.805
2025-04-29 | 16:26 | 49.803
2025-04-29 | 16:26 | 49.806
2025-04-29 | 16:26 | 49.806
2025-04-29 | 16:26 | 49.807
2025-04-29 | 16:26 | 49.807
2025-04-29 | 16:26 | 49.807
2025-04-29 | 16:26 | 49.808
2025-04-29 | 16:26 | 49.808
2025-04-29 | 16:26 | 49.809
2025-04-29 | 16:26 | 49.812
2025-04-29 | 16:26 | 49.813
2025-04-29 | 16:26 | 49.814
2025-04-29 | 16:26 | 49.815
2025-04-29 | 16:26 | 49.814
2025-04-29 | 16:26 | 49.813
2025-04-29 | 16:26 | 49.813
2025-04-29 | 16:26 | 49.814
2025-04-29 | 16:26 | 49.818
2025-04-29 | 16:26 | 49.822
2025-04-29 | 16:26 | 49.825
2025-04-29 | 16:26 | 49.827
2025-04-29 | 16:26 | 49.828
2025-04-29 | 16:26 | 49.832
2025-04-29 | 16:26 | 49.832
2025-04-29 | 16:26 | 49.832
2025-04-29 | 16:26 | 49.834
2025-04-29 | 16:26 | 49.832
2025-04-29 | 16:26 | 49.827
2025-04-29 | 16:26 | 49.824
2025-04-29 | 16:26 | 49.824
2025-04-29 | 16:26 | 49.825
2025-04-29 | 16:26 | 49.824
2025-04-29 | 16:26 | 49.823
2025-04-29 | 16:26 | 49.824
2025-04-29 | 16:26 | 49.823
2025-04-29 | 16:26 | 49.822
2025-04-29 | 16:26 | 49.826
2025-04-29 | 16:26 | 49.829
2025-04-29 | 16:26 | 49.829
2025-04-29 | 16:26 | 49.829
2025-04-29 | 16:26 | 49.829
2025-04-29 | 16:26 | 49.83
2025-04-29 | 16:26 | 49.826
2025-04-29 | 16:27 | 49.823
2025-04-29 | 16:27 | 49.823
2025-04-29 | 16:27 | 49.824
2025-04-29 | 16:27 | 49.826
2025-04-29 | 16:27 | 49.83
2025-04-29 | 16:27 | 49.834
2025-04-29 | 16:27 | 49.833
2025-04-29 | 16:27 | 49.835
2025-04-29 | 16:27 | 49.836
2025-04-29 | 16:27 | 49.837
2025-04-29 | 16:27 | 49.839
2025-04-29 | 16:27 | 49.84
2025-04-29 | 16:27 | 49.844
2025-04-29 | 16:27 | 49.846
2025-04-29 | 16:27 | 49.85
2025-04-29 | 16:27 | 49.852
2025-04-29 | 16:27 | 49.855
2025-04-29 | 16:27 | 49.854
2025-04-29 | 16:27 | 49.854
2025-04-29 | 16:27 | 49.856
2025-04-29 | 16:27 | 49.856
2025-04-29 | 16:27 | 49.856
2025-04-29 | 16:27 | 49.854
2025-04-29 | 16:27 | 49.856
2025-04-29 | 16:27 | 49.858
2025-04-29 | 16:27 | 49.859
2025-04-29 | 16:27 | 49.86
2025-04-29 | 16:27 | 49.859
2025-04-29 | 16:27 | 49.859
2025-04-29 | 16:27 | 49.856
2025-04-29 | 16:27 | 49.851
2025-04-29 | 16:27 | 49.849
2025-04-29 | 16:27 | 49.851
2025-04-29 | 16:27 | 49.853
2025-04-29 | 16:27 | 49.853
2025-04-29 | 16:27 | 49.852
2025-04-29 | 16:27 | 49.852
2025-04-29 | 16:27 | 49.851
2025-04-29 | 16:27 | 49.85
2025-04-29 | 16:27 | 49.852
2025-04-29 | 16:27 | 49.853
2025-04-29 | 16:27 | 49.855
2025-04-29 | 16:27 | 49.856
2025-04-29 | 16:27 | 49.859
2025-04-29 | 16:27 | 49.861
2025-04-29 | 16:27 | 49.864
2025-04-29 | 16:27 | 49.863
2025-04-29 | 16:27 | 49.864
2025-04-29 | 16:27 | 49.865
2025-04-29 | 16:27 | 49.863
2025-04-29 | 16:27 | 49.863
2025-04-29 | 16:27 | 49.865
2025-04-29 | 16:27 | 49.865
2025-04-29 | 16:27 | 49.866
2025-04-29 | 16:27 | 49.866
2025-04-29 | 16:27 | 49.864
2025-04-29 | 16:27 | 49.864
2025-04-29 | 16:27 | 49.863
2025-04-29 | 16:27 | 49.862
2025-04-29 | 16:27 | 49.863
2025-04-29 | 16:28 | 49.862
2025-04-29 | 16:28 | 49.861
2025-04-29 | 16:28 | 49.862
2025-04-29 | 16:28 | 49.862
2025-04-29 | 16:28 | 49.863
2025-04-29 | 16:28 | 49.864
2025-04-29 | 16:28 | 49.862
2025-04-29 | 16:28 | 49.861
2025-04-29 | 16:28 | 49.86
2025-04-29 | 16:28 | 49.859
2025-04-29 | 16:28 | 49.858
2025-04-29 | 16:28 | 49.86
2025-04-29 | 16:28 | 49.861
2025-04-29 | 16:28 | 49.861
2025-04-29 | 16:28 | 49.859
2025-04-29 | 16:28 | 49.857
2025-04-29 | 16:28 | 49.858
2025-04-29 | 16:28 | 49.858
2025-04-29 | 16:28 | 49.86
2025-04-29 | 16:28 | 49.859
2025-04-29 | 16:28 | 49.855
2025-04-29 | 16:28 | 49.853
2025-04-29 | 16:28 | 49.852
2025-04-29 | 16:28 | 49.852
2025-04-29 | 16:28 | 49.851
2025-04-29 | 16:28 | 49.853
2025-04-29 | 16:28 | 49.853
2025-04-29 | 16:28 | 49.851
2025-04-29 | 16:28 | 49.851
2025-04-29 | 16:28 | 49.851
2025-04-29 | 16:28 | 49.847
2025-04-29 | 16:28 | 49.843
2025-04-29 | 16:28 | 49.842
2025-04-29 | 16:28 | 49.842
2025-04-29 | 16:28 | 49.845
2025-04-29 | 16:28 | 49.847
2025-04-29 | 16:28 | 49.848
2025-04-29 | 16:28 | 49.849
2025-04-29 | 16:28 | 49.848
2025-04-29 | 16:28 | 49.848
2025-04-29 | 16:28 | 49.848
2025-04-29 | 16:28 | 49.848
2025-04-29 | 16:28 | 49.851
2025-04-29 | 16:28 | 49.851
2025-04-29 | 16:28 | 49.849
2025-04-29 | 16:28 | 49.847
2025-04-29 | 16:28 | 49.849
2025-04-29 | 16:28 | 49.849
2025-04-29 | 16:28 | 49.849
2025-04-29 | 16:28 | 49.853
2025-04-29 | 16:28 | 49.85
2025-04-29 | 16:28 | 49.851
2025-04-29 | 16:28 | 49.852
2025-04-29 | 16:28 | 49.852
2025-04-29 | 16:28 | 49.852
2025-04-29 | 16:28 | 49.856
2025-04-29 | 16:28 | 49.859
2025-04-29 | 16:28 | 49.862
2025-04-29 | 16:28 | 49.864
2025-04-29 | 16:28 | 49.866
2025-04-29 | 16:29 | 49.867
2025-04-29 | 16:29 | 49.864
2025-04-29 | 16:29 | 49.865
2025-04-29 | 16:29 | 49.865
2025-04-29 | 16:29 | 49.867
2025-04-29 | 16:29 | 49.865
2025-04-29 | 16:29 | 49.866
2025-04-29 | 16:29 | 49.864
2025-04-29 | 16:29 | 49.863
2025-04-29 | 16:29 | 49.864
2025-04-29 | 16:29 | 49.865
2025-04-29 | 16:29 | 49.864
2025-04-29 | 16:29 | 49.865
2025-04-29 | 16:29 | 49.867
2025-04-29 | 16:29 | 49.867
2025-04-29 | 16:29 | 49.867
2025-04-29 | 16:29 | 49.867
2025-04-29 | 16:29 | 49.869
2025-04-29 | 16:29 | 49.87
2025-04-29 | 16:29 | 49.872
2025-04-29 | 16:29 | 49.872
2025-04-29 | 16:29 | 49.873
2025-04-29 | 16:29 | 49.875
2025-04-29 | 16:29 | 49.875
2025-04-29 | 16:29 | 49.878
2025-04-29 | 16:29 | 49.878
2025-04-29 | 16:29 | 49.877
2025-04-29 | 16:29 | 49.875
2025-04-29 | 16:29 | 49.871
2025-04-29 | 16:29 | 49.87
2025-04-29 | 16:29 | 49.869
2025-04-29 | 16:29 | 49.877
2025-04-29 | 16:29 | 49.883
2025-04-29 | 16:29 | 49.884
2025-04-29 | 16:29 | 49.884
2025-04-29 | 16:29 | 49.883
2025-04-29 | 16:29 | 49.883
2025-04-29 | 16:29 | 49.883
2025-04-29 | 16:29 | 49.882
2025-04-29 | 16:29 | 49.883
2025-04-29 | 16:29 | 49.882
2025-04-29 | 16:29 | 49.884
2025-04-29 | 16:29 | 49.884
2025-04-29 | 16:29 | 49.884
2025-04-29 | 16:29 | 49.884
2025-04-29 | 16:29 | 49.88
2025-04-29 | 16:29 | 49.882
2025-04-29 | 16:29 | 49.882
2025-04-29 | 16:29 | 49.882
2025-04-29 | 16:29 | 49.882
2025-04-29 | 16:29 | 49.88
2025-04-29 | 16:29 | 49.879
2025-04-29 | 16:29 | 49.881
2025-04-29 | 16:29 | 49.879
2025-04-29 | 16:29 | 49.878
2025-04-29 | 16:29 | 49.88
2025-04-29 | 16:29 | 49.88
2025-04-29 | 16:29 | 49.882
2025-04-29 | 16:29 | 49.883
2025-04-29 | 16:29 | 49.886
2025-04-29 | 16:30 | 49.887
2025-04-29 | 16:30 | 49.887
2025-04-29 | 16:30 | 49.889
2025-04-29 | 16:30 | 49.891
2025-04-29 | 16:30 | 49.892
2025-04-29 | 16:30 | 49.89
2025-04-29 | 16:30 | 49.89
2025-04-29 | 16:30 | 49.889
2025-04-29 | 16:30 | 49.891
2025-04-29 | 16:30 | 49.894
2025-04-29 | 16:30 | 49.897
2025-04-29 | 16:30 | 49.902
2025-04-29 | 16:30 | 49.904
2025-04-29 | 16:30 | 49.907
2025-04-29 | 16:30 | 49.908
2025-04-29 | 16:30 | 49.907
2025-04-29 | 16:30 | 49.908
2025-04-29 | 16:30 | 49.908
2025-04-29 | 16:30 | 49.913
2025-04-29 | 16:30 | 49.913
2025-04-29 | 16:30 | 49.908
2025-04-29 | 16:30 | 49.909
2025-04-29 | 16:30 | 49.917
2025-04-29 | 16:30 | 49.923
2025-04-29 | 16:30 | 49.924
2025-04-29 | 16:30 | 49.927
2025-04-29 | 16:30 | 49.927
2025-04-29 | 16:30 | 49.93
2025-04-29 | 16:30 | 49.933
2025-04-29 | 16:30 | 49.937
2025-04-29 | 16:30 | 49.938
2025-04-29 | 16:30 | 49.941
2025-04-29 | 16:30 | 49.937
2025-04-29 | 16:30 | 49.937
2025-04-29 | 16:30 | 49.935
2025-04-29 | 16:30 | 49.931
2025-04-29 | 16:30 | 49.926
2025-04-29 | 16:30 | 49.922
2025-04-29 | 16:30 | 49.92
2025-04-29 | 16:30 | 49.916
2025-04-29 | 16:30 | 49.916
2025-04-29 | 16:30 | 49.918
2025-04-29 | 16:30 | 49.92
2025-04-29 | 16:30 | 49.92
2025-04-29 | 16:30 | 49.926
2025-04-29 | 16:30 | 49.927
2025-04-29 | 16:30 | 49.925
2025-04-29 | 16:30 | 49.925
2025-04-29 | 16:30 | 49.92
2025-04-29 | 16:30 | 49.916
2025-04-29 | 16:30 | 49.914
2025-04-29 | 16:30 | 49.908
2025-04-29 | 16:30 | 49.908
2025-04-29 | 16:30 | 49.907
2025-04-29 | 16:30 | 49.903
2025-04-29 | 16:30 | 49.9
2025-04-29 | 16:30 | 49.899
2025-04-29 | 16:30 | 49.902
2025-04-29 | 16:30 | 49.9
2025-04-29 | 16:31 | 49.898
2025-04-29 | 16:31 | 49.9
2025-04-29 | 16:31 | 49.903
2025-04-29 | 16:31 | 49.902
2025-04-29 | 16:31 | 49.903
2025-04-29 | 16:31 | 49.907
2025-04-29 | 16:31 | 49.907
2025-04-29 | 16:31 | 49.907
2025-04-29 | 16:31 | 49.905
2025-04-29 | 16:31 | 49.905
2025-04-29 | 16:31 | 49.904
2025-04-29 | 16:31 | 49.905
2025-04-29 | 16:31 | 49.906
2025-04-29 | 16:31 | 49.901
2025-04-29 | 16:31 | 49.902
2025-04-29 | 16:31 | 49.905
2025-04-29 | 16:31 | 49.909
2025-04-29 | 16:31 | 49.914
2025-04-29 | 16:31 | 49.917
2025-04-29 | 16:31 | 49.92
2025-04-29 | 16:31 | 49.921
2025-04-29 | 16:31 | 49.922
2025-04-29 | 16:31 | 49.923
2025-04-29 | 16:31 | 49.92
2025-04-29 | 16:31 | 49.919
2025-04-29 | 16:31 | 49.917
2025-04-29 | 16:31 | 49.916
2025-04-29 | 16:31 | 49.916
2025-04-29 | 16:31 | 49.915
2025-04-29 | 16:31 | 49.91
2025-04-29 | 16:31 | 49.909
2025-04-29 | 16:31 | 49.916
2025-04-29 | 16:31 | 49.922
2025-04-29 | 16:31 | 49.926
2025-04-29 | 16:31 | 49.927
2025-04-29 | 16:31 | 49.926
2025-04-29 | 16:31 | 49.925
2025-04-29 | 16:31 | 49.922
2025-04-29 | 16:31 | 49.922
2025-04-29 | 16:31 | 49.923
2025-04-29 | 16:31 | 49.923
2025-04-29 | 16:31 | 49.921
2025-04-29 | 16:31 | 49.917
2025-04-29 | 16:31 | 49.918
2025-04-29 | 16:31 | 49.92
2025-04-29 | 16:31 | 49.921
2025-04-29 | 16:31 | 49.919
2025-04-29 | 16:31 | 49.915
2025-04-29 | 16:31 | 49.914
2025-04-29 | 16:31 | 49.914
2025-04-29 | 16:31 | 49.913
2025-04-29 | 16:31 | 49.91
2025-04-29 | 16:31 | 49.905
2025-04-29 | 16:31 | 49.904
2025-04-29 | 16:31 | 49.905
2025-04-29 | 16:31 | 49.91
2025-04-29 | 16:31 | 49.913
2025-04-29 | 16:31 | 49.916
2025-04-29 | 16:31 | 49.916
2025-04-29 | 16:31 | 49.916
2025-04-29 | 16:32 | 49.916
2025-04-29 | 16:32 | 49.916
2025-04-29 | 16:32 | 49.916
2025-04-29 | 16:32 | 49.916
2025-04-29 | 16:32 | 49.917
2025-04-29 | 16:32 | 49.916
2025-04-29 | 16:32 | 49.919
2025-04-29 | 16:32 | 49.924
2025-04-29 | 16:32 | 49.931
2025-04-29 | 16:32 | 49.932
2025-04-29 | 16:32 | 49.93
2025-04-29 | 16:32 | 49.931
2025-04-29 | 16:32 | 49.929
2025-04-29 | 16:32 | 49.93
2025-04-29 | 16:32 | 49.931
2025-04-29 | 16:32 | 49.93
2025-04-29 | 16:32 | 49.929
2025-04-29 | 16:32 | 49.928
2025-04-29 | 16:32 | 49.93
2025-04-29 | 16:32 | 49.93
2025-04-29 | 16:32 | 49.932
2025-04-29 | 16:32 | 49.933
2025-04-29 | 16:32 | 49.932
2025-04-29 | 16:32 | 49.931
2025-04-29 | 16:32 | 49.932
2025-04-29 | 16:32 | 49.934
2025-04-29 | 16:32 | 49.934
2025-04-29 | 16:32 | 49.932
2025-04-29 | 16:32 | 49.932
2025-04-29 | 16:32 | 49.928
2025-04-29 | 16:32 | 49.926
2025-04-29 | 16:32 | 49.924
2025-04-29 | 16:32 | 49.926
2025-04-29 | 16:32 | 49.926
2025-04-29 | 16:32 | 49.931
2025-04-29 | 16:32 | 49.93
2025-04-29 | 16:32 | 49.929
2025-04-29 | 16:32 | 49.93
2025-04-29 | 16:32 | 49.934
2025-04-29 | 16:32 | 49.936
2025-04-29 | 16:32 | 49.939
2025-04-29 | 16:32 | 49.941
2025-04-29 | 16:32 | 49.942
2025-04-29 | 16:32 | 49.941
2025-04-29 | 16:32 | 49.944
2025-04-29 | 16:32 | 49.943
2025-04-29 | 16:32 | 49.943
2025-04-29 | 16:32 | 49.939
2025-04-29 | 16:32 | 49.936
2025-04-29 | 16:32 | 49.932
2025-04-29 | 16:32 | 49.929
2025-04-29 | 16:32 | 49.927
2025-04-29 | 16:32 | 49.925
2025-04-29 | 16:32 | 49.926
2025-04-29 | 16:32 | 49.925
2025-04-29 | 16:32 | 49.926
2025-04-29 | 16:32 | 49.929
2025-04-29 | 16:32 | 49.93
2025-04-29 | 16:32 | 49.932
2025-04-29 | 16:32 | 49.935
2025-04-29 | 16:33 | 49.938
2025-04-29 | 16:33 | 49.939
2025-04-29 | 16:33 | 49.938
2025-04-29 | 16:33 | 49.937
2025-04-29 | 16:33 | 49.939
2025-04-29 | 16:33 | 49.939
2025-04-29 | 16:33 | 49.941
2025-04-29 | 16:33 | 49.944
2025-04-29 | 16:33 | 49.948
2025-04-29 | 16:33 | 49.954
2025-04-29 | 16:33 | 49.955
2025-04-29 | 16:33 | 49.956
2025-04-29 | 16:33 | 49.956
2025-04-29 | 16:33 | 49.956
2025-04-29 | 16:33 | 49.957
2025-04-29 | 16:33 | 49.957
2025-04-29 | 16:33 | 49.959
2025-04-29 | 16:33 | 49.959
2025-04-29 | 16:33 | 49.962
2025-04-29 | 16:33 | 49.963
2025-04-29 | 16:33 | 49.96
2025-04-29 | 16:33 | 49.959
2025-04-29 | 16:33 | 49.96
2025-04-29 | 16:33 | 49.96
2025-04-29 | 16:33 | 49.959
2025-04-29 | 16:33 | 49.961
2025-04-29 | 16:33 | 49.96
2025-04-29 | 16:33 | 49.958
2025-04-29 | 16:33 | 49.961
2025-04-29 | 16:33 | 49.96
2025-04-29 | 16:33 | 49.963
2025-04-29 | 16:33 | 49.962
2025-04-29 | 16:33 | 49.965
2025-04-29 | 16:33 | 49.969
2025-04-29 | 16:33 | 49.967
2025-04-29 | 16:33 | 49.968
2025-04-29 | 16:33 | 49.968
2025-04-29 | 16:33 | 49.965
2025-04-29 | 16:33 | 49.965
2025-04-29 | 16:33 | 49.966
2025-04-29 | 16:33 | 49.965
2025-04-29 | 16:33 | 49.965
2025-04-29 | 16:33 | 49.964
2025-04-29 | 16:33 | 49.962
2025-04-29 | 16:33 | 49.959
2025-04-29 | 16:33 | 49.959
2025-04-29 | 16:33 | 49.959
2025-04-29 | 16:33 | 49.963
2025-04-29 | 16:33 | 49.966
2025-04-29 | 16:33 | 49.969
2025-04-29 | 16:33 | 49.973
2025-04-29 | 16:33 | 49.973
2025-04-29 | 16:33 | 49.974
2025-04-29 | 16:33 | 49.974
2025-04-29 | 16:33 | 49.975
2025-04-29 | 16:33 | 49.977
2025-04-29 | 16:33 | 49.978
2025-04-29 | 16:33 | 49.976
2025-04-29 | 16:33 | 49.978
2025-04-29 | 16:33 | 49.983
2025-04-29 | 16:34 | 49.99
2025-04-29 | 16:34 | 49.992
2025-04-29 | 16:34 | 49.998
2025-04-29 | 16:34 | 50.001
2025-04-29 | 16:34 | 50.009
2025-04-29 | 16:34 | 50.01
2025-04-29 | 16:34 | 50.01
2025-04-29 | 16:34 | 50.011
2025-04-29 | 16:34 | 50.014
2025-04-29 | 16:34 | 50.015
2025-04-29 | 16:34 | 50.014
2025-04-29 | 16:34 | 50.014
2025-04-29 | 16:34 | 50.018
2025-04-29 | 16:34 | 50.019
2025-04-29 | 16:34 | 50.019
2025-04-29 | 16:34 | 50.018
2025-04-29 | 16:34 | 50.017
2025-04-29 | 16:34 | 50.017
2025-04-29 | 16:34 | 50.018
2025-04-29 | 16:34 | 50.019
2025-04-29 | 16:34 | 50.016
2025-04-29 | 16:34 | 50.017
2025-04-29 | 16:34 | 50.016
2025-04-29 | 16:34 | 50.015
2025-04-29 | 16:34 | 50.012
2025-04-29 | 16:34 | 50.008
2025-04-29 | 16:34 | 50.007
2025-04-29 | 16:34 | 50.007
2025-04-29 | 16:34 | 50.004
2025-04-29 | 16:34 | 50.003
2025-04-29 | 16:34 | 50.002
2025-04-29 | 16:34 | 49.997
2025-04-29 | 16:34 | 49.988
2025-04-29 | 16:34 | 49.981
2025-04-29 | 16:34 | 49.977
2025-04-29 | 16:34 | 49.978
2025-04-29 | 16:34 | 49.979
2025-04-29 | 16:34 | 49.982
2025-04-29 | 16:34 | 49.985
2025-04-29 | 16:34 | 49.985
2025-04-29 | 16:34 | 49.984
2025-04-29 | 16:34 | 49.989
2025-04-29 | 16:34 | 49.993
2025-04-29 | 16:34 | 49.995
2025-04-29 | 16:34 | 49.997
2025-04-29 | 16:34 | 49.99
2025-04-29 | 16:34 | 49.987
2025-04-29 | 16:34 | 49.985
2025-04-29 | 16:34 | 49.983
2025-04-29 | 16:34 | 49.983
2025-04-29 | 16:34 | 49.984
2025-04-29 | 16:34 | 49.989
2025-04-29 | 16:34 | 49.993
2025-04-29 | 16:34 | 49.995
2025-04-29 | 16:34 | 49.999
2025-04-29 | 16:34 | 50.006
2025-04-29 | 16:34 | 50.012
2025-04-29 | 16:34 | 50.014
2025-04-29 | 16:34 | 50.017
2025-04-29 | 16:34 | 50.014
2025-04-29 | 16:35 | 50.009
2025-04-29 | 16:35 | 50
2025-04-29 | 16:35 | 49.992
2025-04-29 | 16:35 | 49.984

## V20250408-1
Date | Time | Va PU | Vb PU | Vc PU
2025-04-08 | 3:50 | 1.0029 | 1.0067 | 1.0056
2025-04-08 | 3:50 | 1.0029 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.0029 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.0029 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.0029 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.0029 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.0029 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.0029 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.0029 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.0029 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.003 | 1.0068 | 1.0056
2025-04-08 | 3:50 | 1.0002 | 1.0071 | 1.0059
2025-04-08 | 3:50 | 0.98964 | 1.0076 | 1.0069
2025-04-08 | 3:50 | 0.97441 | 1.0079 | 1.0084
2025-04-08 | 3:50 | 0.95949 | 1.0079 | 1.0092
2025-04-08 | 3:50 | 0.94658 | 1.008 | 1.0088
2025-04-08 | 3:50 | 0.93612 | 1.0083 | 1.0078
2025-04-08 | 3:50 | 0.92837 | 1.0089 | 1.0064
2025-04-08 | 3:50 | 0.92315 | 1.0098 | 1.0046
2025-04-08 | 3:50 | 0.92006 | 1.0108 | 1.0031
2025-04-08 | 3:50 | 0.9187 | 1.0118 | 1.0024
2025-04-08 | 3:50 | 0.91837 | 1.0127 | 1.0018
2025-04-08 | 3:50 | 0.91837 | 1.0138 | 1.0011
2025-04-08 | 3:50 | 0.91807 | 1.0151 | 1.0005
2025-04-08 | 3:50 | 0.91687 | 1.0162 | 0.99942
2025-04-08 | 3:50 | 0.91425 | 1.0173 | 0.99837
2025-04-08 | 3:50 | 0.90963 | 1.0176 | 0.99768
2025-04-08 | 3:50 | 0.90255 | 1.0174 | 0.99725
2025-04-08 | 3:50 | 0.89257 | 1.017 | 0.99708
2025-04-08 | 3:50 | 0.87945 | 1.0165 | 0.99706
2025-04-08 | 3:50 | 0.86319 | 1.016 | 0.99706
2025-04-08 | 3:50 | 0.84397 | 1.0157 | 0.99703
2025-04-08 | 3:50 | 0.82225 | 1.0152 | 0.99689
2025-04-08 | 3:50 | 0.79859 | 1.0145 | 0.99657
2025-04-08 | 3:50 | 0.77381 | 1.0139 | 0.99602
2025-04-08 | 3:50 | 0.74877 | 1.0134 | 0.99525
2025-04-08 | 3:50 | 0.72437 | 1.013 | 0.99431
2025-04-08 | 3:50 | 0.70143 | 1.0129 | 0.99326
2025-04-08 | 3:50 | 0.68072 | 1.0129 | 0.99212
2025-04-08 | 3:50 | 0.66284 | 1.0131 | 0.99077
2025-04-08 | 3:50 | 0.64823 | 1.0135 | 0.98912
2025-04-08 | 3:50 | 0.63715 | 1.0141 | 0.98722
2025-04-08 | 3:50 | 0.6296 | 1.015 | 0.98522
2025-04-08 | 3:50 | 0.62526 | 1.016 | 0.98335
2025-04-08 | 3:50 | 0.62341 | 1.0168 | 0.98179
2025-04-08 | 3:50 | 0.62306 | 1.0176 | 0.98047
2025-04-08 | 3:50 | 0.62315 | 1.0182 | 0.97927
2025-04-08 | 3:50 | 0.62269 | 1.0186 | 0.97814
2025-04-08 | 3:50 | 0.62083 | 1.0188 | 0.97707
2025-04-08 | 3:50 | 0.61678 | 1.0186 | 0.97615
2025-04-08 | 3:50 | 0.60966 | 1.0178 | 0.97551
2025-04-08 | 3:50 | 0.59859 | 1.0169 | 0.97516
2025-04-08 | 3:50 | 0.5828 | 1.0158 | 0.97507
2025-04-08 | 3:50 | 0.56164 | 1.0147 | 0.9751
2025-04-08 | 3:50 | 0.53469 | 1.0138 | 0.97511
2025-04-08 | 3:50 | 0.50171 | 1.0129 | 0.97499
2025-04-08 | 3:50 | 0.46246 | 1.012 | 0.97467
2025-04-08 | 3:50 | 0.41676 | 1.0112 | 0.9741
2025-04-08 | 3:50 | 0.36434 | 1.0105 | 0.97327
2025-04-08 | 3:50 | 0.3131 | 1.0098 | 0.97196
2025-04-08 | 3:50 | 0.28492 | 1.0089 | 0.96961
2025-04-08 | 3:50 | 0.27662 | 1.0085 | 0.96664
2025-04-08 | 3:50 | 0.27397 | 1.0085 | 0.96426
2025-04-08 | 3:50 | 0.2722 | 1.0086 | 0.96288
2025-04-08 | 3:50 | 0.27062 | 1.0086 | 0.96206
2025-04-08 | 3:50 | 0.26864 | 1.0084 | 0.96153
2025-04-08 | 3:50 | 0.2669 | 1.0081 | 0.96155
2025-04-08 | 3:50 | 0.26578 | 1.0077 | 0.96144
2025-04-08 | 3:50 | 0.26505 | 1.0073 | 0.96086
2025-04-08 | 3:50 | 0.26477 | 1.0068 | 0.96044
2025-04-08 | 3:50 | 0.26481 | 1.0058 | 0.96019
2025-04-08 | 3:50 | 0.26503 | 1.0045 | 0.96011
2025-04-08 | 3:50 | 0.26535 | 1.0029 | 0.96052
2025-04-08 | 3:50 | 0.26575 | 1.0011 | 0.96105
2025-04-08 | 3:50 | 0.26621 | 0.99966 | 0.96141
2025-04-08 | 3:50 | 0.26661 | 0.99865 | 0.9617
2025-04-08 | 3:50 | 0.26696 | 0.99771 | 0.96192
2025-04-08 | 3:50 | 0.26725 | 0.99706 | 0.96203
2025-04-08 | 3:50 | 0.26741 | 0.99662 | 0.96206
2025-04-08 | 3:50 | 0.26749 | 0.99608 | 0.96194
2025-04-08 | 3:50 | 0.26737 | 0.99579 | 0.96168
2025-04-08 | 3:50 | 0.26696 | 0.99592 | 0.96135
2025-04-08 | 3:50 | 0.26633 | 0.99611 | 0.96101
2025-04-08 | 3:50 | 0.26552 | 0.99631 | 0.96068
2025-04-08 | 3:50 | 0.26472 | 0.99653 | 0.96037
2025-04-08 | 3:50 | 0.26403 | 0.99661 | 0.96006
2025-04-08 | 3:50 | 0.26339 | 0.9966 | 0.95977
2025-04-08 | 3:50 | 0.2628 | 0.99647 | 0.95966
2025-04-08 | 3:50 | 0.26216 | 0.99619 | 0.95986
2025-04-08 | 3:50 | 0.26153 | 0.99579 | 0.9604
2025-04-08 | 3:50 | 0.26093 | 0.99517 | 0.96123
2025-04-08 | 3:50 | 0.26038 | 0.99449 | 0.96217
2025-04-08 | 3:50 | 0.25992 | 0.99398 | 0.96305
2025-04-08 | 3:50 | 0.25958 | 0.99344 | 0.96395
2025-04-08 | 3:50 | 0.25939 | 0.99288 | 0.96486
2025-04-08 | 3:50 | 0.25939 | 0.99243 | 0.96575
2025-04-08 | 3:50 | 0.25959 | 0.99201 | 0.96662
2025-04-08 | 3:50 | 0.26001 | 0.99173 | 0.96742
2025-04-08 | 3:50 | 0.26065 | 0.99175 | 0.96808
2025-04-08 | 3:50 | 0.26151 | 0.992 | 0.96857
2025-04-08 | 3:50 | 0.26263 | 0.99239 | 0.96889
2025-04-08 | 3:50 | 0.26401 | 0.99295 | 0.96905
2025-04-08 | 3:50 | 0.26565 | 0.99354 | 0.96909
2025-04-08 | 3:50 | 0.26754 | 0.99424 | 0.96902
2025-04-08 | 3:50 | 0.26964 | 0.99507 | 0.96888
2025-04-08 | 3:50 | 0.27189 | 0.99591 | 0.9687
2025-04-08 | 3:50 | 0.27429 | 0.99665 | 0.96849
2025-04-08 | 3:50 | 0.27678 | 0.99722 | 0.96828
2025-04-08 | 3:50 | 0.27931 | 0.99757 | 0.96813
2025-04-08 | 3:50 | 0.28179 | 0.99772 | 0.96808
2025-04-08 | 3:50 | 0.28415 | 0.99771 | 0.9682
2025-04-08 | 3:50 | 0.28632 | 0.99758 | 0.96853
2025-04-08 | 3:50 | 0.28823 | 0.99736 | 0.96913
2025-04-08 | 3:50 | 0.28987 | 0.99708 | 0.96994
2025-04-08 | 3:50 | 0.29118 | 0.9968 | 0.97087
2025-04-08 | 3:50 | 0.29217 | 0.99658 | 0.9718
2025-04-08 | 3:50 | 0.29281 | 0.99649 | 0.97271
2025-04-08 | 3:50 | 0.29312 | 0.9966 | 0.97361
2025-04-08 | 3:50 | 0.29313 | 0.99689 | 0.97453
2025-04-08 | 3:50 | 0.2929 | 0.99737 | 0.97545
2025-04-08 | 3:50 | 0.29245 | 0.99809 | 0.97633
2025-04-08 | 3:50 | 0.2918 | 0.99905 | 0.97713
2025-04-08 | 3:50 | 0.29095 | 1.0002 | 0.97778
2025-04-08 | 3:50 | 0.28993 | 1.0014 | 0.97827
2025-04-08 | 3:50 | 0.28878 | 1.0027 | 0.97858
2025-04-08 | 3:50 | 0.28755 | 1.0039 | 0.97873
2025-04-08 | 3:50 | 0.28628 | 1.0049 | 0.97876
2025-04-08 | 3:50 | 0.28496 | 1.0059 | 0.97872
2025-04-08 | 3:50 | 0.28364 | 1.0068 | 0.97864
2025-04-08 | 3:50 | 0.28232 | 1.0076 | 0.97853
2025-04-08 | 3:50 | 0.28108 | 1.0082 | 0.97839
2025-04-08 | 3:50 | 0.27992 | 1.0086 | 0.97825
2025-04-08 | 3:50 | 0.27886 | 1.0088 | 0.97815
2025-04-08 | 3:50 | 0.27789 | 1.0089 | 0.97818
2025-04-08 | 3:50 | 0.27701 | 1.0089 | 0.97837
2025-04-08 | 3:50 | 0.27623 | 1.0089 | 0.97876
2025-04-08 | 3:50 | 0.27558 | 1.0089 | 0.97934
2025-04-08 | 3:50 | 0.27504 | 1.009 | 0.97995
2025-04-08 | 3:50 | 0.2746 | 1.0091 | 0.98026
2025-04-08 | 3:50 | 0.27427 | 1.0094 | 0.97997
2025-04-08 | 3:50 | 0.27403 | 1.0098 | 0.97934
2025-04-08 | 3:50 | 0.27391 | 1.0103 | 0.97879
2025-04-08 | 3:50 | 0.27389 | 1.0109 | 0.97846
2025-04-08 | 3:50 | 0.27393 | 1.0116 | 0.97826
2025-04-08 | 3:50 | 0.27401 | 1.0123 | 0.97817
2025-04-08 | 3:50 | 0.2741 | 1.013 | 0.97814
2025-04-08 | 3:50 | 0.2742 | 1.0137 | 0.97809
2025-04-08 | 3:50 | 0.27429 | 1.0144 | 0.97803
2025-04-08 | 3:50 | 0.27436 | 1.015 | 0.97801
2025-04-08 | 3:50 | 0.2744 | 1.0155 | 0.97801
2025-04-08 | 3:50 | 0.27438 | 1.0158 | 0.97801
2025-04-08 | 3:50 | 0.27429 | 1.0161 | 0.978
2025-04-08 | 3:50 | 0.27412 | 1.0163 | 0.97794
2025-04-08 | 3:50 | 0.27436 | 1.0164 | 0.97783
2025-04-08 | 3:50 | 0.28057 | 1.0163 | 0.97757
2025-04-08 | 3:50 | 0.30504 | 1.0162 | 0.97726
2025-04-08 | 3:50 | 0.34449 | 1.0161 | 0.97734
2025-04-08 | 3:50 | 0.37909 | 1.016 | 0.97801
2025-04-08 | 3:50 | 0.40477 | 1.0161 | 0.97903
2025-04-08 | 3:50 | 0.42564 | 1.0164 | 0.98008
2025-04-08 | 3:50 | 0.44046 | 1.0167 | 0.98121
2025-04-08 | 3:50 | 0.44935 | 1.0171 | 0.98237
2025-04-08 | 3:50 | 0.45513 | 1.0178 | 0.98298
2025-04-08 | 3:50 | 0.45843 | 1.0185 | 0.98286
2025-04-08 | 3:50 | 0.45923 | 1.0191 | 0.98239
2025-04-08 | 3:50 | 0.45914 | 1.0197 | 0.98185
2025-04-08 | 3:50 | 0.45919 | 1.02 | 0.98134
2025-04-08 | 3:50 | 0.46036 | 1.0201 | 0.98101
2025-04-08 | 3:50 | 0.46393 | 1.0202 | 0.98079
2025-04-08 | 3:50 | 0.47002 | 1.0203 | 0.98037
2025-04-08 | 3:50 | 0.4791 | 1.0203 | 0.97973
2025-04-08 | 3:50 | 0.49258 | 1.0199 | 0.9791
2025-04-08 | 3:50 | 0.51014 | 1.0193 | 0.97863
2025-04-08 | 3:50 | 0.5305 | 1.0183 | 0.97834
2025-04-08 | 3:50 | 0.55379 | 1.0171 | 0.97827
2025-04-08 | 3:50 | 0.57961 | 1.0158 | 0.97844
2025-04-08 | 3:50 | 0.60605 | 1.0148 | 0.97886
2025-04-08 | 3:50 | 0.63209 | 1.0139 | 0.97958
2025-04-08 | 3:50 | 0.65763 | 1.013 | 0.98045
2025-04-08 | 3:50 | 0.68186 | 1.0122 | 0.98131
2025-04-08 | 3:50 | 0.70404 | 1.0117 | 0.98219
2025-04-08 | 3:50 | 0.7244 | 1.0115 | 0.98316
2025-04-08 | 3:50 | 0.74299 | 1.0115 | 0.98451
2025-04-08 | 3:50 | 0.75878 | 1.0116 | 0.98647
2025-04-08 | 3:50 | 0.77103 | 1.0116 | 0.98875
2025-04-08 | 3:50 | 0.77998 | 1.0116 | 0.99081
2025-04-08 | 3:50 | 0.78572 | 1.0116 | 0.99264
2025-04-08 | 3:50 | 0.78865 | 1.0117 | 0.99423
2025-04-08 | 3:50 | 0.7898 | 1.0118 | 0.99533
2025-04-08 | 3:50 | 0.79001 | 1.0114 | 0.99591
2025-04-08 | 3:50 | 0.79004 | 1.0108 | 0.99624
2025-04-08 | 3:50 | 0.79068 | 1.0103 | 0.99653
2025-04-08 | 3:50 | 0.79253 | 1.01 | 0.99676
2025-04-08 | 3:50 | 0.7962 | 1.0101 | 0.9969
2025-04-08 | 3:50 | 0.80236 | 1.0105 | 0.99689
2025-04-08 | 3:50 | 0.81142 | 1.0109 | 0.99673
2025-04-08 | 3:50 | 0.82374 | 1.0111 | 0.99646
2025-04-08 | 3:50 | 0.83957 | 1.0111 | 0.99622
2025-04-08 | 3:50 | 0.85855 | 1.0107 | 0.99617
2025-04-08 | 3:50 | 0.87993 | 1.0102 | 0.99644
2025-04-08 | 3:50 | 0.90304 | 1.0097 | 0.99715
2025-04-08 | 3:50 | 0.92686 | 1.0094 | 0.99834
2025-04-08 | 3:50 | 0.94869 | 1.0093 | 1
2025-04-08 | 3:50 | 0.96393 | 1.0092 | 1.0021
2025-04-08 | 3:50 | 0.97191 | 1.0091 | 1.0039
2025-04-08 | 3:50 | 0.97816 | 1.0091 | 1.0053
2025-04-08 | 3:50 | 0.98438 | 1.009 | 1.0065
2025-04-08 | 3:50 | 0.98937 | 1.0089 | 1.0079
2025-04-08 | 3:50 | 0.99401 | 1.0088 | 1.0093
2025-04-08 | 3:50 | 0.99851 | 1.0086 | 1.0107
2025-04-08 | 3:50 | 1.0018 | 1.008 | 1.0123
2025-04-08 | 3:50 | 1.004 | 1.0075 | 1.0141
2025-04-08 | 3:50 | 1.0054 | 1.0071 | 1.0156
2025-04-08 | 3:50 | 1.0059 | 1.0066 | 1.0167
2025-04-08 | 3:50 | 1.0059 | 1.0065 | 1.0173
2025-04-08 | 3:50 | 1.0056 | 1.0068 | 1.0175
2025-04-08 | 3:50 | 1.005 | 1.0073 | 1.0175
2025-04-08 | 3:50 | 1.0045 | 1.008 | 1.0177
2025-04-08 | 3:50 | 1.0042 | 1.0091 | 1.018
2025-04-08 | 3:50 | 1.0039 | 1.0105 | 1.0182
2025-04-08 | 3:50 | 1.0039 | 1.0118 | 1.0183
2025-04-08 | 3:50 | 1.0047 | 1.0132 | 1.0184
2025-04-08 | 3:50 | 1.0061 | 1.0145 | 1.0184
2025-04-08 | 3:50 | 1.0079 | 1.0155 | 1.0185
2025-04-08 | 3:50 | 1.0106 | 1.0162 | 1.0188
2025-04-08 | 3:50 | 1.0139 | 1.0169 | 1.0192
2025-04-08 | 3:50 | 1.0173 | 1.0175 | 1.0199
2025-04-08 | 3:50 | 1.0204 | 1.0181 | 1.0209
2025-04-08 | 3:50 | 1.0232 | 1.0185 | 1.022
2025-04-08 | 3:50 | 1.0249 | 1.0186 | 1.0231
2025-04-08 | 3:50 | 1.0252 | 1.0186 | 1.0238
2025-04-08 | 3:50 | 1.0249 | 1.0186 | 1.024
2025-04-08 | 3:50 | 1.0246 | 1.0187 | 1.0238
2025-04-08 | 3:50 | 1.0244 | 1.0189 | 1.0237
2025-04-08 | 3:50 | 1.0244 | 1.019 | 1.0237
2025-04-08 | 3:50 | 1.0247 | 1.019 | 1.024
2025-04-08 | 3:50 | 1.0248 | 1.019 | 1.0245
2025-04-08 | 3:50 | 1.0248 | 1.0194 | 1.025
2025-04-08 | 3:50 | 1.0248 | 1.0201 | 1.0251
2025-04-08 | 3:50 | 1.0248 | 1.0209 | 1.0249
2025-04-08 | 3:50 | 1.025 | 1.0219 | 1.0246
2025-04-08 | 3:50 | 1.0253 | 1.0227 | 1.0242
2025-04-08 | 3:50 | 1.0256 | 1.0231 | 1.0239
2025-04-08 | 3:50 | 1.0259 | 1.0235 | 1.0236
2025-04-08 | 3:50 | 1.0262 | 1.0238 | 1.0234
2025-04-08 | 3:50 | 1.0261 | 1.024 | 1.0233
2025-04-08 | 3:50 | 1.0259 | 1.0242 | 1.0234
2025-04-08 | 3:50 | 1.0255 | 1.0242 | 1.0235
2025-04-08 | 3:50 | 1.0249 | 1.024 | 1.0237
2025-04-08 | 3:50 | 1.0239 | 1.0237 | 1.024
2025-04-08 | 3:50 | 1.0228 | 1.0234 | 1.0244
2025-04-08 | 3:50 | 1.0215 | 1.0232 | 1.0249
2025-04-08 | 3:50 | 1.0198 | 1.023 | 1.0254