OPERATING CODE NO. 7

(OC7)

OPERATIONAL LIAISON

CONTENTS

(This contents page does not form part of the Grid Code)

Paragraph No/Title	Page Number

OC7.1   INTRODUCTION	2

OC7.2   OBJECTIVE	2

OC7.3   SCOPE	3

OC7.4   PROCEDURE	3

OC7.4.5   Requirement To Notify Operations	3

OC7.4.6   Requirements To Notify Events	6

OC7.4.7   Significant Incidents	9

OC7.4.8   National Electricity Transmission System Warnings	10

OC7.5   PROCEDURE IN RELATION TO INTEGRAL EQUIPMENT TESTS	14

OC7.6   PROCEDURE IN RESPECT OF OPERATIONAL SWITCHING IN SCOTLAND AND OFFSHORE	16

APPENDIX 1 - NATIONAL ELECTRICITY TRANSMISSION SYSTEM WARNINGS TABLE	20

APPENDIX 2 – Other System Alerts and Warnings per OC7.4.8.15	21

OC7.1	INTRODUCTION

OC7.1.1	Operating Code No. 7 ("OC7") sets out the requirements for the exchange of information in relation to Operations and/or Events on the Total System which have had (or may have had) or will have (or may have) an Operational Effect:

(a)	on the National Electricity Transmission System in the case of an Operation and/or Event occurring on the System of a User or Users; and

(b)	on the System of a User or Users in the case of an Operation and/or Event occurring on the National Electricity Transmission System.

It also describes the types of National Electricity Transmission System Warning which may be issued by The Company.

OC7.1.2	The requirement to notify in OC7 relates generally to notifying of what is expected to happen or what has happened and not the reasons why. However, as OC7 provides, when an Event or Operation has occurred on the National Electricity Transmission System which itself has been caused by (or exacerbated by) an Operation or Event on a User's System, The Company in reporting the Event or Operation on the National Electricity Transmission System to another User can pass on what it has been told by the first User in relation to the Operation or Event on the first User's System.

OC7.1.3	Where an Event or Operation on the National Electricity Transmission System falls to be reported by The Company to an Externally Interconnected System Operator under an Interconnection Agreement, OC7 provides that in the situation where that Event or Operation has been caused by (or exacerbated by) an Operation or Event on a User's System, The Company can pass on what it has been told by the User in relation to the Operation or Event on that User's System.

OC7.1.4	OC7 also deals with Integral Equipment Tests.

OC7.1.5	To reconfigure the National Electricity Transmission System, The Company may reasonably require the assistance of a User to reconfigure parts of the User System. To reconfigure its User System a User may reasonably require the reasonable assistance of The Company to direct the reconfiguration of parts of the National Electricity Transmission System.

OC7.1.6	OC7.6 sets down the arrangements for the exchange of information required when configuring Connection Sites (or in the case of OTSUA operational prior to the OTSUA Transfer Time, Transmission Interface Sites) and parts of the National Electricity Transmission System adjacent to those Connection Sites (or Transmission Interface Sites) in Scotland and Offshore. It also covers the setting up of a Local Switching Procedure. The Company  shall procure that Relevant Transmission Licensees shall comply with section OC7.6 and any relevant Local Switching Procedure where and to the extent that such matters apply to them.

OC7.2	OBJECTIVE

The objectives of OC7 are:

OC7.2.1	To provide for the exchange of information so that the implications of an Operation and/or Event can be considered, possible risks arising from it can be assessed and appropriate action taken by the relevant party in order to maintain the integrity of the Total System. OC7 does not seek to deal with any actions arising from the exchange of information, but merely with that exchange.

OC7.2.2	To provide for types of National Electricity Transmission System Warnings which may be issued by The Company.

OC7.2.3	To provide the framework for the information flow and discussion between The Company  and certain Users in relation to Integral Equipment Tests.

OC7.2.4	To provide the procedure to be followed in respect of Operational Switching

OC7.3	SCOPE

OC7.3.1	OC7 applies to The Company and to Users, which in OC7 means:

(a)	Generators (other than those which only have Embedded Small Power Stations or Embedded Medium Power Stations) and including Generators undertaking OTSDUW;

(b)	Network Operators;

(c)	Non-Embedded Customers;

(d)	Suppliers (for the purposes of National Electricity Transmission System Warnings);

(e)	Externally Interconnected System Operators (for the purposes of National Electricity Transmission System Warnings); and

(f)	DC Converter Station owners and HVDC System Owners.

The procedure for operational liaison by The Company with Externally Interconnected System Operators is set out in the Interconnection Agreement with each Externally Interconnected System Operator.

OC7.6 also applies to Relevant Transmission Licensees.

OC7.4	PROCEDURE

OC7.4.1	The term "Operation" means a scheduled or planned action relating to the operation of a System (including an Embedded Power Station).

OC7.4.2	The term "Event" means an unscheduled or unplanned (although it may be anticipated) occurrence on, or relating to, a System (including an Embedded Power Station) including, without limiting that general description, faults, incidents and breakdowns and adverse weather conditions being experienced.

OC7.4.3	The term "Operational Effect" means any effect on the operation of the relevant other System which causes the National Electricity Transmission System or the Systems of the other User or Users, as the case may be, to operate (or be at a materially increased risk of operating) differently to the way in which they would or may have normally operated in the absence of that effect.

OC7.4.4	References in this OC7 to a System of a User or User's System shall not include Embedded Small Power Stations or Embedded Medium Power Stations, unless otherwise stated.

OC7.4.5	Requirement To Notify Operations

OC7.4.5.1	Operation On The National Electricity Transmission System

In the case of an Operation on the National Electricity Transmission System, which will have (or may have) an Operational Effect on the System(s) of a User or Users, The Company will notify the User or Users whose System(s) will, or may, in the reasonable opinion of The Company, be affected, in accordance with OC7.

OC7.4.5.2	Operation On a User's System

In the case of an Operation on the System of a User which will have (or may have) an Operational Effect on the National Electricity Transmission System (including an equivalent to an Operation on the equivalent of a System of a User or other person connected to that User's System which, via that User System, will or may have an Operational Effect on the National Electricity Transmission System), the User will notify The Company in accordance with OC7. Following notification by the User, The Company will notify any other User or Users on whose System(s) the Operation will have, or may have, in the reasonable opinion of The Company, an Operational Effect, in accordance with OC7 and will notify any Externally Interconnected System Operator on whose System the Operation will have, or may have, in the reasonable opinion of The Company, an Operational Effect, if it is required to do so by the relevant Interconnection Agreement.

OC7.4.5.3	Examples Of Situations Where Notification By The Company  Or a User may be Required

Whilst in no way limiting the general requirement to notify in advance set out in OC7.4.5.1 and OC7.4.5.2, the following are examples of situations where notification in accordance with OC7.4.5 will be required if they will, or may, have an Operational Effect:

(a)	the implementation of a planned outage of Plant and/or Apparatus which has been arranged pursuant to OC2;

(b)	the operation (other than, in the case of a User, at the instruction of The Company) of any circuit breaker or isolator/disconnector or any sequence or combination of the two; or

(c)	voltage control.

OC7.4.5.4	Operations Caused By Another Operation Or By An Event

An Operation may be caused by another Operation or an Event on another's System (including an Embedded Power Station) (or by the equivalent of an Event or Operation on the System of an Externally Interconnected System Operator or Interconnector User) and in that situation the information to be notified is different to that where the Operation arose independently of any other Operation or Event, as more particularly provided in OC7.4.5.6.

OC7.4.5.5	Form

A notification and any response to any questions asked under OC7.4.5, of an Operation which has arisen independently of any other Operation or of an Event, shall be of sufficient detail to describe the Operation (although it need not state the cause) and to enable the recipient of the notification reasonably to consider and assess the implications and risks arising (provided that, in the case of an Operation on a User's System which The Company is notifying to other Users under OC7.4.5.2, The Company will only pass on what it has been told by the User which has notified it) and will include the name of the individual reporting the Operation on behalf of The Company or the User, as the case may be. The recipient may ask questions to clarify the notification and the giver of the notification will, insofar as it is able, answer any questions raised, provided that, in the case of an Operation on a User's System which The Company is notifying to other Users under OC7.4.5.2, in answering any question, The Company  will not pass on anything further than that which it has been told by the User which has notified it. The Company  may pass on the information contained in the notification as provided in OC7.4.5.6.

OC7.4.5.6	(a)	A notification by The Company of an Operation under OC7.4.5.1 which has been caused by another Operation (the "first Operation") or by an Event on a User's System, will describe the Operation and will contain the information which The Company has been given in relation to the first Operation or that Event by the User. The notification and any response to any questions asked (other than in relation to the information which The Company is merely passing on from a User) will be of sufficient detail to enable the recipient of the notification reasonably to consider and assess the implications and risks arising from the Operation on the National Electricity Transmission System and will include the name of the individual reporting the Operation on behalf of The Company. The recipient may ask questions to clarify the notification and The Company will, insofar as it is able, answer any questions raised, provided that in relation to the information which The Company is merely passing on from a User, in answering any question The Company will not pass on anything further than that which it has been told by the User which has notified it.

(b)	Where a User is reporting an Operation or an Event which itself has been caused by an incident or scheduled or planned action affecting (but not on) its System, the notification to The Company will contain the information which the User has been given by the person connected to its System in relation to that incident or scheduled or planned action (which the User must require, contractually or otherwise, the person connected to its System to give to it) and The Company may pass on the information contained in the notification as provided in this OC7.4.5.6.

OC7.4.5.7	Where an Operation on the National Electricity Transmission System falls to be reported by The Company under an Interconnection Agreement and the Operation has been caused by another Operation (the "first Operation") or by an Event on a User's System, The Company will include in that report the information which The Company has been given in relation to the first Operation or that Event by the User (including any information relating to an incident or scheduled or planned action, as provided in OC7.4.5.6).

OC7.4.5.8	(a)	A notification to a User by The Company of an Operation under OC7.4.5.1 which has been caused by the equivalent of an Operation or of an Event on the equivalent of a System of an Externally Interconnected System Operator or Interconnector User, will describe the Operation on the National Electricity Transmission System and will contain the information which The Company  has been given, in relation to the equivalent of an Operation or of an Event on the equivalent of a System of an Externally Interconnected System Operator or Interconnector User, by that Externally Interconnected System Operator or Interconnector User.

(b)	The notification and any response to any question asked (other than in relation to the information which The Company is merely passing on from that Externally Interconnected System Operator or Interconnector User) will be of sufficient detail to enable the recipient of the notification reasonably to consider and assess the implications and risks arising from the Operation on the National Electricity Transmission System and will include the name of the individual reporting the Operation on behalf of The Company. The recipient may ask questions to clarify the notification and The Company  will, insofar as it is able, answer any questions raised, provided that, in relation to the information which The Company is merely passing on from an Externally Interconnected System Operator or Interconnector User, in answering any question The Company will not pass on anything further than that which it has been told by the Externally Interconnected System Operator or Interconnector User which has notified it.

OC7.4.5.9	(a)	A Network Operator may pass on the information contained in a notification to it from The Company under OC7.4.5.1, to a Generator with a Power Generating Module (including a DC Connected Power Park Module), Generating Unit or a Power Park Module connected to its System, or to a DC Converter Station owner with a DC Converter or to a HVDC System Owner with a HVDC System connected to its System,  or to the operator of another User System connected to its System (which, for the avoidance of doubt, could be another Network Operator), in connection with reporting the equivalent of an Operation under the Distribution Code (or the contract pursuant to which that Power Generating Module (including a DC Connecting Power Generating Module), and/or Generating Unit and/or Power Park Module or other User System, or to a DC Converter Station or to an HVDC System is connected to the System of that Network Operator) (if the Operation on the National Electricity Transmission System caused it).

(b)	A Generator may pass on the information contained in a notification to it from The Company under OC7.4.5.1, to another Generator with a Power Generating Module (including a DC Connected Power Park Module) and/or a Generating Unit or a Power Park Module connected to its System, or to the operator of a User System connected to its System (which, for the avoidance of doubt, could be a Network Operator), if it is required (by a contract pursuant to which that Power Generating Module (including a DC Connected Power Park Module) and/or Generating Unit and/or that Power Park Module or that User System is connected to its System) to do so in connection with the equivalent of an Operation on its System (if the Operation on the National Electricity Transmission System caused it).

OC7.4.5.10	(a)	Other than as provided in OC7.4.5.9, a Network Operator or a Generator may not pass on any information contained in a notification to it from The Company under OC7.4.5.1 (and an operator of a User System or Generator receiving information which was contained in a notification to a Generator or a Network Operator, as the case may be, from The Company  under OC7.4.5.1, as envisaged in OC7.4.5.9 may not pass on this information) to any other person, but may inform persons connected to its System (or in the case of a Generator which is also a Supplier, inform persons to which it supplies electricity which may be affected) that there has been an incident on the Total System, the general nature of the incident (but not the cause of the incident) and (if known and if power supplies have been affected) an estimated time of return to service.

(b)	In the case of a Generator which has an Affiliate which is a Supplier, the Generator may inform it that there has been an incident on the Total System, the general nature of the incident (but not the cause of the incident) and (if known and if power supplies have been affected in a particular area) an estimated time of return to service in that area, and that Supplier may pass this on to persons to which it supplies electricity which may be affected).

(c)	Each Network Operator and Generator shall use its reasonable endeavours to procure that any Generator or operator of a User System receiving information which was contained in a notification to a Generator or Network Operator, as the case may be, from The Company under OC7.4.5.1, which is not bound by the Grid Code, does not pass on any information other than as provided above.

OC7.4.5.11	The notification will, if either party requests, be recorded by the sender and dictated to the recipient, who shall record and repeat each phrase as it is received and on completion of the dictation shall repeat back the notification in full to the sender who shall confirm that it has been accurately recorded.

OC7.4.5.12	Timing

A notification under OC7.4.5 will be given as far in advance as possible and in any event shall be given in sufficient time as will reasonably allow the recipient to consider and assess the implications and risks arising.

OC7.4.6 	Requirements To Notify Events

OC7.4.6.1	Events On The National Electricity Transmission System

In the case of an Event on the National Electricity Transmission System which has had (or may have had) an Operational Effect on the System(s) of a User or Users, The Company will notify the User or Users whose System(s) have been, or may have been, in the reasonable opinion of The Company, affected, in accordance with OC7.

OC7.4.6.2	Events On A User's System

In the case of an Event on the System of a User which has had (or may have had) an Operational Effect on the National Electricity Transmission System, the User will notify The Company in accordance with OC7.

OC7.4.6.3	Events Caused By Another Event Or By An Operation

An Event may be caused (or exacerbated by) another Event or by an Operation on another's System (including on an Embedded Power Station) (or by the equivalent of an Event or Operation on the equivalent of a System of an Externally Interconnected System Operator or Interconnector User) and in that situation the information to be notified is different to that where the Event arose independently of any other Event or Operation, as more particularly provided in OC7.4.6.7.

OC7.4.6.4	The Company  or a User, as the case may be, may enquire of the other whether an Event has occurred on the other's System. If it has, and the party on whose System the Event has occurred is of the opinion that it may have had an Operational Effect on the System of the party making the enquiry, it shall notify the enquirer in accordance with OC7.

OC7.4.6.5	Examples Of Situations Where Notification By The Company or a User may be Required

Whilst in no way limiting the general requirement to notify set out in OC7.4.6.1, OC7.4.6.2 and OC7.4.6.3, the following are examples of situations where notification in accordance with OC7.4.6 will be required if they have an Operational Effect:

(a)	where Plant and/or Apparatus is being operated in excess of its capability or may present a hazard to personnel;

(b)	the activation of any alarm or indication of any abnormal operating condition;

(c)	adverse weather conditions being experienced;

(d)	breakdown of, or faults on, or temporary changes in the capabilities of, Plant and/or Apparatus;

(e)	breakdown of, or faults on, control, communication and metering equipment; or

(f)	increased risk of inadvertent protection operation.

Form

OC7.4.6.6	A notification and any response to any questions asked under OC7.4.6.1 and OC7.4.6.2 of an Event which has arisen independently of any other Event or of an Operation, will describe the Event, although it need not state the cause of the Event, and, subject to that, will be of sufficient detail to enable the recipient of the notification reasonably to consider and assess the implications and risks arising and will include the name of the individual reporting the Event on behalf of The Company or the User, as the case may be. The recipient may ask questions to clarify the notification and the giver of the notification will, insofar as it is able (although it need not state the cause of the Event) answer any questions raised. The Company may pass on the information contained in the notification as provided in OC7.4.6.7.

OC7.4.6.7	(a)	A notification (and any response to any questions asked under OC7.4.6.1) by The Company of (or relating to) an Event under OC7.4.6.1 which has been caused by (or exacerbated by) another Event (the "first Event") or by an Operation on a User's System will describe the Event and will contain the information which The Company  has been given in relation to the first Event or that Operation by the User (but otherwise need not state the cause of the Event). The notification and any response to any questions asked (other than in relation to the information which The Company is merely passing on from a User) will be of sufficient detail to enable the recipient of the notification reasonably to consider and assess the implications and risks arising from the Event on the National Electricity Transmission System and will include the name of the individual reporting the Event on behalf of The Company. The recipient may ask questions to clarify the notification and The Company will, insofar as it is able, answer any questions raised, provided that in relation to the information which The Company is merely passing on from a User, in answering any question The Company will not pass on anything further than that which it has been told by the User which has notified it.

(b)	Where a User is reporting an Event or an Operation which itself has been caused by (or exacerbated by) an incident or scheduled or planned action affecting (but not on) its System the notification to The Company will contain the information which the User has been given by the person connected to its System in relation to that incident or scheduled or planned action (which the User must require, contractually or otherwise, the person connected to its System to give to it) and The Company may pass on the information contained in the notification as provided in this OC7.4.6.7.

OC7.4.6.8	Where an Event on the National Electricity Transmission System falls to be reported by The Company under an Interconnection Agreement and the Event has been caused by (or exacerbated by) another Event (the "first Event") or by an Operation on a User's System, The Company will include in that report the information which The Company has been given in relation to the first Event or that Operation by the User (including any information relating to an incident or scheduled or planned action on that User's System, as provided in OC7.4.6.7).

OC7.4.6.9	(a)	A notification to a User (and any response to any questions asked under OC7.4.6.1) by The Company  of (or relating to) an Event under OC7.4.6.1 which has been caused by (or exacerbated by) the equivalent of an Event or of an Operation on the equivalent of a System of an Externally Interconnected System Operator or Interconnector User, will describe the Event on the National Electricity Transmission System and will contain the information which The Company has been given, in relation to the equivalent of an Event or of an Operation on the equivalent of a System of an Externally Interconnected System Operator or Interconnector User, by that Externally Interconnected System Operator or Interconnector User (but otherwise need not state the cause of the Event).

(b)	The notification and any response to any questions asked (other than in relation to the information which The Company is merely passing on from that Externally Interconnected System Operator or Interconnector User) will be of sufficient detail to enable the recipient of the notification reasonably to consider and assess the implications and risks arising from the Event on the National Electricity Transmission System and will include the name of the individual reporting the Event on behalf of The Company. The recipient may ask questions to clarify the notification and The Company will, insofar as it is able (although it need not state the cause of the Event) answer any questions raised, provided that, in relation to the information which The Company is merely passing on from an Externally Interconnected System Operator or Interconnector User, in answering any question The Company will not pass on anything further than that which it has been told by the Externally Interconnected System Operator or Interconnector User which has notified it.

OC7.4.6.10	(a)	A Network Operator may pass on the information contained in a notification to it from The Company under OC7.4.6.1, to a Generator with a Power Generating Module (including a DC Connected Power Park Module) and/or Generating Unit and/or a Power Park Module connected to its System or to a DC Converter Station owner with a DC Converter or to an HVDC System Owner with an HVDC System connected to its System or to the operator of another User System connected to its System (which, for the avoidance of doubt, could be a Network Operator), in connection with reporting the equivalent of an Event under the Distribution Code (or the contract pursuant to which that Power Generating Module and/or Generating Unit and/or Power Park Module or DC Converter or HVDC System or other User System is connected to the System of that Network Operator) (if the Event on the National Electricity Transmission System caused or exacerbated it).

(b)	A Generator may pass on the information contained in a notification to it from The Company under OC7.4.6.1, to another Generator with a Power Generating Module and/or Generating Unit and/or a Power Park Module connected to its System or to the operator of a User System connected to its System (which, for the avoidance of doubt, could be a Network Operator), if it is required (by a contract pursuant to which that Power Generating Module (including a DC Connected Power Park Module) and/or Generating Unit and/or that Power Park Module or that User System is connected to its System) to do so in connection with the equivalent of an Event on its System (if the Event on the National Electricity Transmission System caused or exacerbated it).

OC7.4.6.11	(a)	Other than as provided in OC7.4.6.10, a Network Operator or a Generator, may not pass on any information contained in a notification to it from The Company under OC7.4.6.1 (and an operator of a User System or Generator receiving information which was contained in a notification to a Generator or a Network Operator, as the case may be, from The Company under OC7.4.6.1, as envisaged in OC7.4.6.10 may not pass on this information) to any other person, but may inform persons connected to its System (or in the case of a Generator which is also a Supplier, inform persons to which it supplies electricity which may be affected) that there has been an incident on the Total System, the general nature of the incident (but not the cause of the incident) and (if known and if power supplies have been affected) an estimated time of return to service.

(b)	In the case of a Generator which has an Affiliate which is a Supplier, the Generator may inform it that there has been an incident on the Total System, the general nature of the incident (but not the cause of the incident) and (if known and if power supplies have been affected in a particular area) an estimated time of return to service in that area, and that Supplier may pass this on to persons to which it supplies electricity which may be affected).

(c)	Each Network Operator and Generator shall use its reasonable endeavours to procure that any Generator or operator of a User System receiving information which was contained in a notification to a Generator or Network Operator, as the case may be, from The Company under OC7.4.6.1, which is not bound by the Grid Code, does not pass on any information other than as provided above.

OC7.4.6.12	When an Event relating to a Power Generating Module and/or Generating Unit and/or a Power Park Module or a DC Converter or an HVDC System (or OTSUA operational prior to the OTSUA Transfer Time), has been reported to The Company by a Generator or DC Converter Station owner or HVDC System Owner under OC7.4.6 and it is necessary in order for the Generator or DC Converter Station owner or HVDC System Owner to assess the implications of the Event on its System more accurately, the Generator or DC Converter Station owner or HVDC System Owner may ask The Company for details of the fault levels from the National Electricity Transmission System to that Power Generating Module and/or Generating Unit and/or Power Park Module or DC Converter or HVDC System (or OTSUA operational prior to the OTSUA Transfer Time) at the time of the Event, and The Company will, as soon as reasonably practicable, give the Generator or DC Converter Station owner or HVDC System Owner that information provided that The Company has that information.

OC7.4.6.13	Except in an emergency situation the notification of an Event will, if either party requests, be recorded by the sender and dictated to the recipient, who shall record and repeat each phrase as it is received and on completion of the dictation shall repeat the notification in full to the sender who shall confirm that it has been accurately recorded.

Timing

OC7.4.6.14	A notification under OC7.4.6 shall be given as soon as possible after the occurrence of the Event, or time that the Event is known of or anticipated by the giver of the notification under OC7, and in any event within 15 minutes of such time.

OC7.4.7	Significant Incidents

OC7.4.7.1	Where a User notifies The Company  of an Event under OC7 which The Company considers has had or may have had a significant effect on the National Electricity Transmission System,  The Company will require the User to report that Event in writing in accordance with the provisions of OC10 and will notify that User accordingly.

OC7.4.7.2	Where The Company notifies a User of an Event under OC7 which the User considers has had or may have had a significant effect on that User's System, that User will require The Company  to report that Event in writing in accordance with the provisions of OC10 and will notify The Company accordingly.

OC7.4.7.3	Events which The Company requires a User to report in writing pursuant to OC7.4.7.1, and Events which a User requires The Company to report in writing pursuant to OC7.4.7.2, are known as "Significant Incidents".

OC7.4.7.4	Without limiting the general description set out in OC7.4.7.1 and OC7.4.7.2, a Significant Incident will include Events having an Operational Effect which result in, or may result in, the following:

(a)	operation of Plant and/or Apparatus either manually or automatically;

(b)	voltage outside statutory limits;

(c)	Frequency outside statutory limits; or

(d)	System instability.

OC 7.4.8	National Electricity Transmission System Warnings

OC7.4.8.1	Role Of National Electricity Transmission System Warnings

National Electricity Transmission System Warnings as described below provide information relating to System conditions or Events and are intended to:

(i)	alert Users to possible or actual Plant shortage, System problems and/or Demand or generation Active Power reductions;

(ii)	inform of the applicable period;

(iii)	indicate intended consequences for Users; and

(iv)	enable specified Users to be in a state of readiness to react properly to instructions received from The Company.

A table of National Electricity Transmission System Warnings, set out in Appendix 1 to OC7, summarises the warnings and their usage. In the case of a conflict between the table and the provisions of the written text of OC7, the written text will prevail.

OC7.4.8.2	Recipients Of National Electricity Transmission System Warnings and Notices

(a)	Where National Electricity Transmission System Warnings and Notices,(except those relating to Demand Control Imminent and Embedded Generation Control Imminent), are applicable to System conditions or Events which have widespread effect, The Company will notify all Users under OC7.

(b)	Where in The Company’s judgement System conditions or Events may only have a limited effect, the National Electricity Transmission System Warning or Notice will as a minimum only be issued to those Users who are or may in The Company’s judgement be affected.

(c)	Where a National Electricity Transmission System Warning - Demand Control Imminent is issued it will as a minimum only be sent to those Users who are likely to receive Demand Control instructions from The Company.

- Where a National Electricity Transmission System Warning Embedded Generation Control Imminent is issued it will as a minimum only be sent to those Network Operators who are likely to receive Embedded Generation Control instructions.

OC7.4.8.3	Preparatory Action

(a)	Where possible, and if required, recipients of the warnings should take such preparatory action as they deem necessary taking into account the information contained in the National Electricity Transmission System Warning. All warnings will be of a form determined by The Company and will remain in force from the stated time of commencement until the cancellation, amendment or re-issue, as the case may be, is notified by The Company.

(b)	Where a National Electricity Transmission System Warning has been issued to a Network Operator and is current, Demand Control should not (subject as provided below) be employed unless instructed by The Company. If Demand Control is, however, necessary to preserve the integrity of the Network Operator's System, then the impact upon the integrity of the Total System should be considered by the Network Operator and where practicable discussed with The Company  prior to its implementation.

Where a National Electricity Transmission System Warning has been issued to a Supplier, further Customer Demand Management (in addition to that previously notified under OC1 -  Demand Forecasts) must only be implemented following notification to The Company.

(c) 	National Electricity Transmission System Warnings will be issued by such data transmission facilities as have been agreed between The Company and Users. In the case of Generators with Gensets this will normally be at their Trading Points (if they have notified The Company that they have a Trading Point).

(d) 	Users may at times be informed by telephone of National Electricity Transmission System Warnings and in these circumstances confirmation will be sent to those Users so notified by such data transmission facilities as have been agreed between The Company  and Users, as soon as possible.

OC7.4.8.4	Types Of National Electricity Transmission System Warnings

National Electricity Transmission System Warnings consist of the following types:-

(i)	National Electricity Transmission System Warning - Electricity Margin Notice

(ii)	National Electricity Transmission System Warning - High Risk of Demand Reduction

(iii)	National Electricity Transmission System Warning - Demand Control Imminent

(iv)  National Electricity Transmission System Warning – System NRAPM

(v)   National Electricity Transmission System Warning – Localised NRAPM

(vi) National Electricity Transmission System Warning – High Risk of Embedded Generation Reduction

(vii)  National Electricity Transmission System Warning - Embedded Generation Control Imminent

(viii) National Electricity Transmission System Warning - Risk of System Disturbance

(ix) 	National Electricity Transmission Notice – DCRP Activation

(x)	National Electricity Transmission Notice – DCRP Implementation

(xi)	National Electricity Transmission Notice – DCRP Stand Down

OC7.4.8.5	National Electricity Transmission System Warning - Electricity Margin Notice

A National Electricity Transmission System Warning - Electricity Margin Notice may be issued to Users in accordance with OC7.4.8.2, at times when there is a reduced System Margin, as determined under BC1.5.4. It will contain the following information:

(i)	the period for which the warning is applicable; and

(ii)	the availability shortfall in MW; and

(iii)	intended consequences for Users, including notification that Maximum Generation Service may be instructed.

OC 7.4.8.6	National Electricity Transmission System Warning - High Risk of Demand Reduction

(a)	A National Electricity Transmission System Warning - High Risk of Demand Reduction may be issued to Users in accordance with OC7.4.8.2 at times when there is a reduced System Margin, as determined under BC1.5.4 and in The Company’s judgement there is increased risk of Demand reduction being implemented under OC6.5.1. It will contain the following information in addition to the required information in a National Electricity Transmission System Warning - Electricity Margin Notice:

(i)	the possible percentage level of Demand reduction required; and

(ii)	Specify those Network Operators and Non Embedded Customers who may subsequently receive instructions under OC6.5.1.

(b)	A National Electricity Transmission System Warning - High Risk of Demand Reduction may also be issued by The Company to those Network Operators and Non Embedded Customers who may subsequently receive instructions under OC6.5.1 relating to a Demand reduction in circumstances not related to System Margin (for example Demand reduction required to manage System overloading).

The National Electricity Transmission System Warning - High Risk of Demand Reduction will specify the period during which Demand reduction may be required and the part of the Total System to which it applies and any other matters specified in OC6.5.

OC7.4.8.6.1	Protracted Periods Of Generation Shortage

(a)	Whenever The Company anticipates that a protracted period of generation shortage may exist a National Electricity Transmission System Warning - Electricity Margin Notice or High Risk of Demand Reduction may be issued, to give as much notice as possible to those Network Operators and Non Embedded Customers who may subsequently receive instructions under OC6.5.

(b)	A National Electricity Transmission System Warning - High Risk of Demand Reduction will in these instances include an estimate of the percentage of Demand reduction that may be required and the anticipated duration of the Demand reduction. It may also include information relating to estimates of any further percentage of Demand reduction that may be required.

(c)	The issue of the National Electricity Transmission System Warning - Electricity Margin Notice or High Risk of Demand Reduction is intended to enable recipients to plan ahead on the various aspects of Demand reduction.

OC7.4.8.7	National Electricity Transmission System Warning - Demand Control Imminent

(a)	A National Electricity Transmission System Warning - Demand Control Imminent, relating to a Demand reduction under OC6.5, will be issued by The Company to Users in accordance with OC7.4.8.2. It will specify those Network Operators who may subsequently receive instructions under OC6.5.

(b)	A National Electricity Transmission System Warning - Demand Control Imminent, need not be preceded by any other National Electricity Transmission System Warning and will be issued when a Demand reduction is expected within the following 30 minutes, but will not cease to have effect after 30 minutes from its issue. However, The Company  will either reissue the National Electricity Transmission System Warning - Demand Control Imminent or cancel the National Electricity Transmission System Warning - Demand Control Imminent no later than 2 hours from first issue, or from re-issue, as the case may be.

| OC.7.4.8.8 | National Electricity Transmission System Warning – System NRAPM - Procedures for maintaining System NRAPM are defined in BC1.5.5 but where this is, in the view of The Company and as set out in BC1.5.5, deemed likely to be insufficient this will be communicated to all Users and will be treated as a System Warning. - Such a System Warning will where possible include information on the likely reduction in Active Power that will be required and the timing and duration of this. - A System NRAPM refers to the margin of Active Power across the whole System. |
| --- | --- |
| OC.7.4.8.9 | National Electricity Transmission System Warning – Localised NRAPM - Procedures for maintaining Localised NRAPM are defined in BC1.5.5 but where this is, in the view of The Company and as set out in BC1.5.5, deemed likely to be insufficient this will be communicated to all Users and will be treated as a System Warning. - Such a System Warning will where possible include information on the likely reduction in Active Power that will be required and the timing and duration of this. - A Localised NRAPM refers to the management of transfers to and from a System Constraint Group. |
| OC 7.4.8.10 | National Electricity Transmission System Warning - High Risk of Embedded Generation Reduction - A National Electricity Transmission System Warning - High Risk of Embedded Generation Reduction may be issued to Users in accordance with OC7.4.8.2 at times when in The Company’s judgement there is increased risk of Embedded Generation Control being required as defined in OC6B.5.1. - In addition to any information communicated through a System NRAPM or Localised NRAPM, the National Electricity Transmission System Warning - High Risk of Embedded Generation Reduction will specify the period during which Embedded Generation Control may be required and the part of the Total System to which it applies and any other matters specified in OC6B.5. |
| (c) The issue of the National Electricity Transmission System Warning - High Risk of Embedded Generation Reduction is intended to enable recipients to plan ahead on the various aspects of Embedded Generation Control. OC7.4.8.11 National Electricity Transmission System Warning – Embedded Generation Control |  |

# Imminent

- A National Electricity Transmission System Warning – Embedded Generation Control Imminent will be issued by The Company to Users in accordance with OC7.4.8.2. It will specify those Network Operators who may subsequently receive instructions under OC6B.5.

- A National Electricity Transmission System Warning – Embedded Generation Control Imminent, need not be preceded by any other National Electricity Transmission System Warning and will be issued when an Embedded Generation Control instruction is expected within the following 30 minutes, but will not cease to have effect after 30 minutes from its issue. However, The Company will either reissue the National Electricity Transmission System Warning – Embedded Generation Control Imminent or cancel the National Electricity Transmission System Warning – Embedded Generation Control Imminent no later than 2 hours from first issue, or from re-issue, as the case may be.

OC7.4.8.12	National Electricity Transmission System Warning - Risk of System Disturbance

(a)	A National Electricity Transmission System Warning - Risk of System Disturbance will be issued by The Company to Users who may be affected when The Company knows there is a risk of widespread and serious disturbance to the whole or part of, the National Electricity Transmission System;

(b)	The National Electricity Transmission System Warning - Risk of System Disturbance will contain such information as The Company  deems appropriate;

(c)	For the duration of the National Electricity Transmission System Warning - Risk of System Disturbance, each User in receipt of the National Electricity Transmission System Warning - Risk of System Disturbance shall take the necessary steps to warn its operational staff and to maintain its Plant and/or Apparatus in the condition in which it is best able to withstand the anticipated disturbance;

(d)	During the period that the National Electricity Transmission System Warning - Risk of System Disturbance is in effect, The Company  may issue Emergency Instructions in accordance with BC2 and it may be necessary to depart from normal Balancing Mechanism operation in accordance with BC2 in issuing Bid-Offer Acceptances.

OC7.4.8.13	Cancellation of National Electricity Transmission System Warning

(a)	The Company will give notification of a Cancellation of National Electricity Transmission System Warning to all Users issued with the National Electricity Transmission System Warning when in The Company’s judgement System conditions have returned to normal.

(b)	A Cancellation of National Electricity Transmission System Warning will identify the type of National Electricity Transmission System Warning being cancelled and the period for which it was issued. The Cancellation of National Electricity Transmission System Warning will also identify any National Electricity Transmission System Warnings that are still in force.

OC7.4.8.14	National Electricity Transmission Notice – DCRP Activation

- A National Electricity Transmission Notice – DCRP Activation will be issued by The Company to Network Operators in accordance with OC7.4.8.2. It will specify the instructions required in accordance with OC6.9.4.

- A National Electricity Transmission Notice – DCRP Activation will be issued following confirmation that DCRP is required to manage shortages in electricity supply, after an Emergency Response Team meeting has convened. Network Operators will have eight hours to get their networks ready for DCRP.

OC7.4.8.15	National Electricity Transmission Notice – DCRP Implementation

- A National Electricity Transmission Notice – DCRP Implementation will be issued by The Company to Network Operators in accordance with OC7.4.8.2. It will specify the instructions required in accordance with OC6.9.5.

- A National Electricity Transmission Notice – DCRP Implementation will be issued at least one hour before disconnections are required. Further details on which Load Blocks will be disconnected, shall be provided in the Activation Schedules issued by The Company to Network Operators.

OC7.4.8.16	National Electricity Transmission Notice – DCRP Stand Down

- A National Electricity Transmission Notice – DCRP Stand Down will be issued by The Company to Network Operators in accordance with OC7.4.8.2. It will specify the instructions required in accordance with OC6.9.7.

- A National Electricity Transmission Notice – DCRP Stand Down will be issued when DCRP arrangements are no longer required to manage shortages in electricity supply. This could be because DCRP is no longer required and networks can be reconfigured without Demand Disconnection; or the Demand Control Rotation Period is transitioning to the Electricity Supply Emergency Code.

OC7.4.8.17	General Management of National Electricity Transmission System Warnings

(a)	National Electricity Transmission System Warnings remain in force for the period specified unless superseded or cancelled by The Company.

(b)	A National Electricity Transmission System Warning issued for a particular period may be superseded by further related warnings. This will include National Electricity Transmission System Warning - Electricity Margin Notice being superseded by National Electricity Transmission System Warning - High Risk of Demand Reduction and vice-versa, and National Electricity Transmission System Warning – System NRAPM being superseded by National Electricity Transmission System Warning - High Risk of Embedded Generation Reduction.

(c)	In circumstances where it is necessary for the period of a National Electricity Transmission System Warning to be changed:

(i)	the period applicable may be extended by the issue of a National Electricity Transmission System Warning with a period which follows on from the original period, or

(ii)	revised or updated National Electricity Transmission System Warnings will be issued where there is an overlap with the period specified in an existing National Electricity Transmission System Warning, but only if the revised period also includes the full period of the existing National Electricity Transmission System Warning.

In any other case the existing National Electricity Transmission System Warning will be cancelled and a new one issued.

- A National Electricity Transmission System Warning is no longer applicable once the period has passed and to confirm this The Company will issue a Cancellation of National Electricity Transmission System Warning.

OC7.4.8.18	Publication of Other System Alerts and Warnings

- All instructions, warnings, alerts and notifications upon being received or issued by The Company (whether activating or deactivating an action) as per Appendix 2 of OC7 will be published on the BMRS. Should the BMRS be unavailable, for example due to communications or systems failures, other appropriate channels including email will be utilised until the BMRS can be restored.

- The Company will employ reasonable endeavours to publish such information within 15 minutes of issue or receipt, or if not possible within as short a time as is reasonably practicable.

OC7.5	PROCEDURE IN RELATION TO INTEGRAL EQUIPMENT TESTS

OC7.5.1	This section of the Grid Code deals with Integral Equipment Tests.  It is designed to provide a framework for the exchange of relevant information and for discussion between The Company  and certain Users in relation to Integral Equipment Tests.

OC7.5.2	An Integral Equipment Test :

(a)	is carried out in accordance with the provisions of this OC7.5 at:

(i)	a User Site,

(ii)	a Transmission Site,

(iii)	an Embedded Large Power Station, or,

(iv)	an Embedded DC Converter Station; or

(v)	an Embedded HVDC System

(b)	will normally be undertaken during commissioning or re-commissioning of Plant and/or Apparatus;

(c)	may, in the reasonable judgement of the person wishing to perform the test, cause, or have the potential to cause, an Operational Effect on a part or parts of the Total System but which with prior notice is unlikely to have a materially adverse effect on any part of the Total System; and

(d)	may form part of an agreed programme of work.

In the case of OTSUA operation prior to the OTSUA Transfer Time, a User’s Site or Transmission Site shall, for the purposes of this OC7, include a site at which there is an Interface Point until the OTSUA Transfer Time and the provisions of this OC7.5 and references to OTSUA shall be construed and applied accordingly until the OTSUA Transfer Time.

OC7.5.3	A set of guidance notes is available from The Company on request, which provide further details on suggested procedures, information flows and responsibilities.

Notification Of An IET

OC7.5.4	In order to undertake an Integral Equipment Test (and subject to OC7.5.8 below), the User or The Company, as the case may be, (the proposer) must notify the other (the recipient) of a proposed IET. Reasonable advance notification must be given, taking into account the nature of the test and the circumstances which make the test necessary. This will allow recipients time to adequately assess the impact of the IET on their System.

OC7.5.5	The notification of the IET must normally include the following information:-

(a)	the proposed date and time of the IET;

(b)	the name of the individual and the organisation proposing the IET;

(c)	a proposed programme of testing; and

(d)	such further detail as the proposer reasonably believes the recipient needs in order to assess the effect the IET may have on relevant Plant and/or Apparatus.

OC7.5.6	In the case of an IET in connection with commissioning or re-commissioning, the test should be incorporated as part of any overall commissioning programme agreed between The Company and the User.

Response To Notification of an IET

OC7.5.7	The recipient of notification of an IET must respond within a reasonable timescale prior to the start time of the IET and will not unreasonably withhold or delay acceptance of the IET proposal.

OC7.5.8	(a)	Where The Company receives notification of a proposed IET from a User, The Company will consult those other Users whom it reasonably believes may be affected by the proposed IET to seek their views. Information relating to the proposed IET may be passed on by The Company with the prior agreement of the proposer.  However it is not necessary for The Company to obtain the agreement of any such User as IETs should not involve the application of irregular, unusual or extreme conditions. The Company  may however consider any comments received when deciding whether or not to agree to an IET.

(b)	In the case of an Embedded Large Power Station or Embedded DC Converter Station, or Embedded HVDC System, the Generator or DC Converter Station owner or HVDC System Owner as the case may be, must liaise with both The Company  and the relevant Network Operator. The Company will not agree to an IET relating to such Plant until the Generator or DC Converter Station owner or HVDC System Owner has shown that it has the agreement of the relevant Network Operator.

(c)	A Network Operator will liaise with The Company as necessary in those instances where it is aware of an Embedded Small Power Station or an Embedded Medium Power Station which intends to perform tests which in the reasonable judgement of the Network Operator may cause an Operational Effect on the National Electricity Transmission System.

OC7.5.9	The response from the recipient, following notification of an IET must be one of the following:

(a)	to accept the IET proposal;

(b)	to accept the IET proposal conditionally subject to minor modifications such as date and time;

(c)	not to agree the IET, but to suggest alterations to the detail and timing of the IET that are necessary to make the IET acceptable.

Final Confirmation Of an IET

OC7.5.10	The date and time of an IET will be confirmed between The Company and the User, together with any limitations and restrictions on operation of Plant and/or Apparatus.

OC7.5.11	The IET may subsequently be amended following discussion and agreement between The Company and the User.

Carrying Out an IET

OC7.5.12	IETs may only take place when agreement has been reached and must be carried out in accordance with the agreed programme of testing.

OC7.5.13	The implementation of an IET will be notified in accordance with OC7.4.5.

OC7.5.14	Where elements of the programme of testing change during the IET, there must be discussion between the appropriate parties to identify whether the IET should continue.

OC7.6	PROCEDURE IN RESPECT OF OPERATIONAL SWITCHING

OC7.6.1	This section OC7.6 of the Grid Code sets out the procedure to be followed for Operational Switching. Its provisions are supplementary to the provisions of the rest of this OC7.

It is designed to set down the arrangements for The Company, Users and the Relevant Transmission Licensees in respect of the Operational Switching of Plant and Apparatus at a Connection Site and parts of the National Electricity Transmission System adjacent to that Connection Site.

OC7.6.2	In general:

(i)	The Company is responsible for directing the configuration of the National Electricity Transmission System

(ii) 	Each Relevant Transmission Licensee is responsible for the instruction and operation of its Plant and Apparatus on its Transmission System.

(iii)	Each User is responsible for the configuration, instruction and operation of its Plant and Apparatus.

Definitive schedules of these responsibilities for each Connection Site are contained in the relevant Site Responsibility Schedules.

For the avoidance of doubt, where a User operates Transmission Plant and Apparatus on behalf of a Relevant Transmission Licensee, The Company cannot instruct the User to operate that Plant and Apparatus.

Planned Operational Switching

OC7.6.3	Following the notification of an Operation under OC7.4.5, The Company and the User shall discuss the Operational Switching required. The Company will then discuss and agree the details of the Operational Switching with the Relevant Transmission Licensee. The Relevant Transmission Licensee shall then make contact with the User to initiate the Operational Switching. For the avoidance of doubt, from the time that the Relevant Transmission Licensee makes contact with the User, the Relevant Transmission Licensee shall then become the primary point of operational contact with the User in relation to OC7 for matters which would or could affect, or would or could be affected by the Operational Switching.

OC7.6.4	The User shall be advised by the Relevant Transmission Licensee on the completion of the Operational Switching, that The Company shall again become the primary point of operational contact for the User in relation to OC7.

OC7.6.5	During Operational Switching, either the Relevant Transmission Licensee or the User may need to unexpectedly terminate the Operational Switching.  The Company may also need to terminate the Operational Switching during the Operational Switching.  In the event of unexpected termination of the Operational Switching, The Company  shall become the primary point of operational contact for the User in relation to OC7. Following the termination of the Operational Switching, it will not be permitted to restart that Operational Switching without the parties again  following the process described in OC7.6.3.

Emergencies

OC7.6.6	For Operations and/or Events that present an immediate hazard to the safety of personnel, Plant or Apparatus, the Relevant Transmission Licensee may:

(i)	as permitted by the STC, carry out Operational Switching of Plant and Apparatus on its Transmission System without reference to The Company and the User, and

(ii)	request a User to carry out Operational Switching without the User first receiving notification from The Company.

In such emergency circumstances, communication between the Relevant Transmission Licensee and the User shall normally be by telephone and will include an exchange of names. The User shall use all reasonable endeavours to carry out Operational Switching on its Plant and Apparatus without delay. Following completion of the requested Operational Switching, the Relevant Transmission Licensee shall notify The Company of the Operational Switching which has taken place. In such emergency circumstances, the User may only refuse to carry out Operational Switching on safety grounds (relating to personnel or plant) and this must be notified to the Relevant Transmission Licensee immediately by telephone.

OC7.6.7	For Operations and/or Events that present an immediate hazard to the safety of personnel, Plant or Apparatus, and which require Operational Switching of Plant or Apparatus on a Transmission System in order to remove the hazard, the User should contact the Relevant Transmission Licensee directly to request Operational Switching of Plant or Apparatus on its Transmission System.

In such emergency circumstances, communication between the Relevant Transmission Licensee and the User shall normally be by telephone and will include an exchange of names. The Relevant Transmission Licensee shall use all reasonable endeavours to carry out Operational Switching on its Plant and Apparatus without delay. Following completion of the requested Operational Switching, the User shall notify The Company of the Operational Switching which has taken place. In such emergency circumstances, the Relevant Transmission Licensee may only refuse to carry out Operational Switching on safety grounds (relating to personnel or plant) and this must be notified to the User immediately by telephone.

OC7.6.8	Establishment Of A Local Switching Procedure

(a)	The Company, a User or a Relevant Transmission Licensee may reasonably require a Local Switching Procedure to be established.

(b)	Where the need for a Local Switching Procedure arises the following provisions shall apply:

(i)	The Company, User(s) and the Relevant Transmission Licensee will discuss and agree the detail of the Local Switching Procedure as soon as the requirement for a Local Switching Procedure is identified. The Company will notify the Relevant Transmission Licensee and the affected User(s) and will initiate these discussions.

(ii)	Each Local Switching Procedure shall be in relation to either one or more Connection Sites (or in the case of OTSUA operational prior to the OTSUA Transfer Time, Transmission Interface Sites) and parts of the National Electricity Transmission System adjacent to the Connection Site(s) (or in the case of OTSUA operational prior to the OTSUA Transfer Time, Transmission Interface Sites)

(iii)	A draft Local Switching Procedure shall be prepared by the Relevant Transmission Licensee to reflect the agreement reached and shall be sent to The Company.

(iv)	When a Local Switching Procedure has been prepared, it shall be sent by The Company to the Relevant Transmission Licensee and User(s) for confirmation of its accuracy.

(v)	The Local Switching Procedure shall then be signed on behalf of The Company and on behalf of each User and Relevant Transmission Licensee by way of written confirmation of its accuracy.

(vi)	Once agreed under this OC7.6.8, the procedure will become a Local Switching Procedure under the Grid Code, and (subject to any change pursuant to this OC7) will apply between The Company, Relevant Transmission Licensee and the relevant User(s) as if it were part of the Grid Code.

(vii)	Once signed, The Company  will send a copy of the Local Switching Procedure to the Relevant Transmission Licensee and the User(s).

(viii)	An agreed Local Switching Procedure should be referenced by relevant Site Responsibility Schedules.

(ix)	The Company,the User(s) and the Relevant Transmission Licensee must make the Local Switching Procedure readily available to the relevant operational staff.

(x)	If the Relevant Transmission Licensee or the User(s) become aware that a change is needed to a Local Switching Procedure, they must inform The Company immediately.  Where The Company has been informed of a need for a change, or The Company proposes a change, The Company shall notify both the affected User and the Relevant Transmission Licensee and will initiate discussions to agree a change to the Local Switching Procedure. The principles applying to the establishment of a new Local Switching Procedure shall then apply to the discussion and agreement of any changes.

APPENDIX 1 - NATIONAL ELECTRICITY TRANSMISSION SYSTEM WARNINGS TABLE

| RESPONSE FROM RECIPIENTS | Offers of reduced Active Power infeed from Generators or DC Converter Station owners, HVDC System Owners and Interconnector Users. Generators notify The Company of any reduction in Active Power output that they will initiate. | Offers of reduced Active Power infeed in impacted System Constraint Group from Generators or DC Converter S tation owners, HVDC System Owners and Interconnector Users. Generators notify The Company of any reduction in Active Power output that they will initiate. | Offers of reduced Active Power infeed from Generators or DC Converter Station owners, HVDC System Ow ners and Interconnector Users. Generators notify The Company of any reduction in Active Power output that they will initiate. Specified Network Operators to prepare for Embedded Generation Control actions as | Network Operators specified to prepare to take action as necessary to enable them to comply wi th any subsequent instruction from The Company for Embedded Generation Control. |
| --- | --- | --- | --- | --- |
| WARNING OF/OR CONSEQUENCE | Insufficient margin of Active Power available to allow the largest loss of Load at any time. Notification that if not improved Embedded Generation Control may be instructed. | Insufficient Active Power available to allow transfers to and from a System Constraint Group. Notification that if not improved Embedded Generation Control may be instructed. | Insufficient System NRAPM or Localised NRAPM available and/or a high risk of Embedded Generation Control being instructed. | Possibility of Embedded Generation Control within 30 Minutes |
| TIMESCALE | All timescales when at the time there is not a high risk of Embedded Generation reduction. | All timescales when at the time there is not a high risk of Embedded Generation reduction. | All timescales when at the time there is not a high risk of Embedded Generation reduction. | Within 30 minutes of anticipated instruction. |
| TO: FOR INFORMATION | All Users | All Users | All Users | All Users |
| TO: FOR ACTION | Network Operators | Network Operators | Network Operators | Network Operators |
| FORMAT | Issued via data transmission facilities and, in some cases, by telephone. | Issued via data transmission facilities and, in some cases, by telephone. | Issued via data transmission facilities and, in some cases, by telephone. | Issued via data transmission facilities and, in some cases, by telephone. |
| GRID CODE | OC7.4.8.8 | OC7.4.8.9 | OC7.4.8.10 | OC7.4.8.11 |
| WARNING TYPE | National Electricity Transmissio n System Warning – System NRAPM | National Electricity Transmissio n System Warning – Localised NRAPM | National Electricity Transmissio n System Warning – High Risk of Embedded Generation Reduction | National Electricity Transmissio n System Warning - Embedded Generation Control Imminent |

| RESPONSE FROM RECIPIENTS | Offers of increased availability from Generators or DC Converter Station owners. HVDC System Owners and Interconnector Users. Suppliers notify The Company of any additional Customer Demand Management that they will initiate. | Offers of increased availability from Generators or DC Converter Station owners or HVDC System Owners and Interconnector Users. Suppliers notify The Company of any additional Customer Demand Management that they will initiate. Specified Network Operators and Non-Embedded Customers to prepare their Demand Reduction arrangements and take actions as necessary to enable compliance with The Company instructions that may follow. (Percentages of Demand Reduction above 20% may not be achieved if The Company has not issued the warning by 16:00 hours the previous day.) | Network Operators specified to prepare to take action as necessary to enable them to comply with any subsequent The Company instruction for Demand reduction. | Recipients take steps to warn operational staff and maintain plant or apparatus such that they are best able to withstand the disturbance. |
| --- | --- | --- | --- | --- |
| WARNING OF/OR CONSEQUENCE | Insufficient generation available to meet forecast Demand plus Operating Margin. Notification that if not improved Demand reduction may be instructed. (Normal initial warning of insufficient System Margin | Insufficient generation available to meet forecast Demand plus Operating Margin and/or a high risk of Demand Reduction being instructed. (May be issued locally as demand reduction risk only for circuit overloads) | Possibility of Demand Reduction within 30 minutes | Risk of, widespread system disturbance to whole or part of the National Electricity Transmission System |
| TIMESCALE | All timescales when at the time there is not a high risk of Demand reduction. Primarily 1200 hours onwards for a future period. | All timescales where there is a high risk of Demand Reduction. Primarily 1200 hours onwards for a future period | Within 30 minutes of anticipated instruction | Control room time scales |
| TO: FOR INFORMATION | Network Operators, Non-Embedded Customers |  | None | Suppliers |
| TO: FOR ACTION | Generators, Suppliers, Externally Interconected System Operators, DC Converter Station owners and HVDC System Owners | Generators, Suppliers, Network Operators, Non-Embedded Customers, Externally Interconnected System Operators, DC Converter Station Owners, HVDC System Owners | Specified Users only: (to whom an instruction is to be given) Network Operators, Non-Embedded Customers | Generators, DC Converter Station owners, HVDC System Owners, Network Operators, Non-Embedded Customers, Externally Interconnected System Operators who may be affected. |
| FORMAT | Designated Information Exchange System or other electronic means | Designated Information Exchange System or other electronic means | Designated Information Exchange System/ Telephone or other electronic means | Designated Information Exchange System/ Telephone or other electronic means |
| GRID CODE | OC7.4.8.5 | OC7.4.8.6 | OC7.4.8.7 | OC7.4.8.12 |
| WARNING TYPE | NATIONAL ELECTRICITY TRANSMISSION WARNING – ELECTRICITY MARGIN NOTICE | NATIONAL ELECTRICITY TRANSMISSION SYSTEM WARNING – High risk of Demand Reduction | NATIONAL ELECTRICITY TRANSMISSION SYSTEM WARNING – Demand Control Imminent | NATIONAL ELECTRICITY TRANSMISSION SYSTEM WARNING – Risk of System Disturbance |

| RESPONSE FROM RECIPIENTS | Network Operators specified to take action to prepare the network for DCRP activation. |  | Network Operators specified to take action to ensure the Activation Schedules are implemented. |  |  | Network Operators specified to take action to return the system to conditions before DCRP activation or to transition to arrangements under the Electricity Supply Emergency Code. |
| --- | --- | --- | --- | --- | --- | --- |
| WARNING OF/OR CONSEQUENCE | DCRP to be activated within the timeframe specified. |  | Activation Schedules need to be followed in preparation for DCRP activation. |  |  | DCRP is no longer required, and the network will securely revert their networks back to normal network configuration and operation without Demand Disconnection. |
| TIMESCALE | Within eight hours |  | Within one hour |  |  | Within eight hours |
| TO: FOR INFORMATION | Market Participants, The Authority |  | Market Participants, The Authority |  |  | Market Participants, The Authority |
| TO: FOR ACTION | Specified Users only: (to whom an instruction is to be given) Network Operators |  | Specified Users only: (to whom an instruction is to be given) Network Operators |  |  | Specified Users only: (to whom an instruction is to be given) Network Operators |
| FORMAT | Designated Information Exchange System or other electronic means |  | Designated Information Exchange System or other electronic means |  |  | Designated Information Exchange System or other electronic means |
| GRID CODE | OC7.4.8.14 |  | OC7.4.8.15 |  |  | OC7.4.8.16 |
| NOTICE TYPE | NATIONAL ELECTRICITY TRANSMISSION NOTICE – DCRP Activation |  | NATIONAL ELECTRICITY TRANSMISSION NOTICE – DCRP Implementation |  |  | NATIONAL ELECTRICITY TRANSMISSION NOTICE – DCRP Stand Down |

¹Identification of the specific equipment affected is not required to be included within the published alert.

APPENDIX 2 – Other System Alerts and Warnings per OC7.4.8.15

| Warning ofor Consequence | Demand Disconnection applied | Demand Reduction Applied | Automatic Demand Disconnection Applied | Network Operator Demand Control Activated | Emergency Instruction(s) issued. | May require departure from normal Balancing Market Operation in accordance with BC2 | May require departure from normal Balancing Market Operation in accordance with BC2 | Inadequate Negative Reserve Active Power Margin (nationally) | Inadequate Negative Reserve Active Power Margin (locally) | Noted warning no longer applicable. | Discontinue Outage within Emergency Return to Service Time | Commencing rota disconnection across affected Network Operators licence areas. | Demand Reduction Instruction/Emergency Manual Disconnection Instruction issued to Network Operator(s), or Inadequate System Margin anticipated, or Automatic Low Frequency Demand Disconnection occurred per Capacity Market Rules 8.4.6. | Request to increase Active Energy transferred into the NETS, or reduce Active Energy transferred into its External System |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Reference | Grid Code OC6.5 | Grid Code OC6.5 | Grid Code OC6.6 | Grid Code OC6.4 and DOC6.6 | Grid Code BC2.9.1.4 | Grid Code BC2.9.1.3 | Grid Code BC2.9.1.4 | Grid Code BC1.5.5 | Grid Code BC1.5.5 | Grid Code OC7.4.8.9 | STC Section C Part Two (7) | Grid Code OC6.1.5 | Capacity Market Rules 8.4.6 | Grid Code BC2.9.6 |
| Alert, Instruction, Notification or Warning Type | Demand Control by Demand Disconnection instructed by The Company | Demand Control by voltage reduction instructed by The Company | Automatic Low Frequency Demand Disconnection | Demand Control (including voltage reduction and demand disconnection) - Network Operator activated | Grid Code Emergency Instruction (to Network Operator) | Grid Code Emergency Instruction (to Generators & Demand – BCA, BEGA, & BELLA) | Grid Code Emergency Instruction (to Interconnectors) | System NRAPM | Localised NRAPM | Cancellation of National Electricity System Warning | STC Emergency Instruction to Transmission Owner¹ | ESEC Implementation | EMR Capacity Market Notifications | Emergency Assistance Requests |

< END OF OPERATING CODE NO. 7 >