## Slide 1: GC0139 Consultation
August 2024
Ian Povey, ENWL

## Slide 2: The GC0139 Proposal
Defect
The existing requirements of the Grid Code (in respect of data exchange between DNOs and National Grid ESO) are insufficient for the coordinated and efficient planning of their networks as the industry transitions to a smart energy system and distribution operation activities.
Why
To facilitate the efficient and coordinated planning of the Transmission System, National Grid need a greater understanding of the quantity, type and impact of Distributed Energy Resources connected to Distribution Networks.
To facilitate the efficient and coordinated planning of their Distribution Networks DNOs need a greater understanding of Transmission System flows and fault contributions within a variety of demand/generation scenarios.
If these changes are not made, as the overall system becomes more interactive, with increasing volumes of Embedded Generation, demand side services and active network management, it will become more difficult to achieve coordinated and efficient overall network planning to facilitate the transition to a smart energy system.

## Slide 3: The GC0139 Proposal
What
DNO to National Grid ESO Data Exchange
It is proposed to enhance the Grid Code requirements for week 24 and week 50 data submissions. This will provide National Grid ESO with:
• Full details of the sub-transmission network and any connections directly connected to the sub-transmission network
• Details of all distributed energy resource connections (and those “accepted to be connected”) greater than 1MW to the distribution network and their impact on energy flows at peak demand, summer minimum demand and solar peak/daytime-minimum demand.
• Details of all distributed energy resource connections less than 1MW to the distribution network, aggregated by fuel type and disaggregated by substations connecting to the sub-transmission network.

## Slide 4: The GC0139 Proposal
What
National Grid to DNO Data Exchange
It is proposed to enhance the Grid Code requirements for the week 42 data submission.
The data describing a transmission system model will be a switch level, single boundary format model. This model will cover the whole of the DNO area in detail, together with equivalent networks at agreed boundary points.
It is proposed that the transmission model shall be provided for the following demand points:
• Maximum fault level
• Peak demand
• Summer minimum demand
• Minimum fault Level (Summer)
• Solar-peak/daytime-minimum demand
• National high-power transfer dispatch scenario
• National low power transfer dispatch scenario

## Slide 5: Principles Underpinning the Proposed Solution
The requirements of the PC will remain unchanged until the implementation date for this modification – currently January 2026.
Post implementation date Network Operators will need to comply with the requirements of a new PC.9 and the Company will need to comply with the requirements of a new PC.10.
PC.9 and PC.10 are augmented with a new appendix PC.G, new schedules within the DRC and a suite of new definitions within the Glossary & Definitions.
PC.9 and PC.10 will require the exchange of Power System Models (PSM) in the Common Information Model (CIM) format. The PSMs will represent cardinal system loading points.
PC.9 will also require the completion of several schedules communicating Connection Point demand and generation forecasts.
PC.9 requires information that supports the Evaluation of Transmission Impact assessment process.

## Slide 6: Information Exchange Overview
Data exchanges support activities at The Company and Network Operators:
  Routine grid data exchanges to facilitate efficient system planning
  ‘As needed’ data exchanges to support grid connection or modification activities
Information is supplied in three forms
  As a connected Power System Model (PSM) suitable for analysis calculations (steady state or short circuit). PSM information includes:
    Structural Data: asset, generation and load characteristics, connectivity
    Situation Data: grid condition
    Solution Data: steady state power flow or short circuit calculation results
  PSM data is expressed as both grid snapshots and future projects
  As tabular data – DRC Schedules
  As a narrative – Change Document & Scenario Document

## Slide 7: What parts of the GC are Impacted

## Slide 8: Changes to the PC

## Slide 9: Structure of PC.9
PC.9 details submission requirements placed on Network Operators:
PC.9.1 General information
PC.9.2 Purpose & definitions
PC.9.3 Submissions
  Week 2
  Week 28
  Information for Evaluation of Transmission Impact Assessment
PC.9.4 Subtransmission PSM
  Scope
  Components of Solved PSM (Structural, Situation, Solution), referring to Appendix PC.G.1 for detailed data requirements
PC.9.5 Assessment of Site Compliance
PC.9.6 Confidentiality and Sharing

## Slide 10: Structure of PC.10
PC.10 details submission requirements placed on the Company:
PC.10.1 General Information
PC.10.2 Purpose
PC.10.3 Submissions
  Week 12
  Week 38
  For Distribution Impact assessment or Transmission Licensee-initiated modification
PC.10.4 NETS PSM
  Scope
  Components of Solved PSM (Structural, Situation, Solution), referring to Appendix PC.G.1 for detailed data requirements
PC.10.5 Assessment of Site Compliance
PC.10.6 Confidentiality and Sharing

## Slide 11: Structure of Appendix PC.G
Appendix PC.G provides detail in support of PC.9 and PC.10
PC.G.1 Data to be included in a Solved PSM
PC.G.2 Additional data not included in the Solved PSM
PC.G.3 Organisation of PSM data
PC.G.4 PSM Data Exchange Standards
PC.G.5 PSM Scenario Document
PC.G.6 PSM Change Document
PC.G.7 Assessment of Site Compliance
PC.G.8 Generation

## Slide 12: Data Submissions - Overview
 |  | Routine | As Needed
Network Operators | Power system model (PSM) | Week 2: Solved Subtransmission PSM for historic NETS minimum demand Week 28: Solved Subtransmission PSM for historic NETS peak demand | Evaluation of Transmission Impact assessment: Planned connections and updated network development projects
 | Tabular | Week 2: Schedules 21C-E, 21G-J Week 28: Schedules 21A-B, 21F-I, 17, 10A-C, 11C, 12A-C | 
 | Narrative | Week 2: PSM Scenario Document/PSM Change Document Week 28: PSM Scenario Document/PSM Change Document | 
The Company | Power system model (PSM) | Week 12: Summer Solved NETS PSMs for 4 forecast grid conditions Week 38: Winter Solved NETS PSMs for 3 forecast grid conditions | Distribution Impact assessment or Transmission Licensee-initiated modification: Planned connections/works and updated network development projects
 | Narrative | Week 12: PSM Scenario Document/PSM Change Document Week 38: PSM Scenario Document/PSM Change Document | 

## Slide 13: Network Operator Week 2 Submission
PSM
  Solved Subtransmission Power System Model representing
    Subtransmission System at historic NETS minimum demand condition
    Subtransmission System minimum fault level condition
  Description of Model changes related to each Subtransmission planned (firm) network development project and ‘accepted to connect’ connection
Tabular
  Revised Schedules 21C, D, E (GSP-level demand data – summer conditions)
  Revised Schedules 21G, H (embedded power stations)
  Revised Schedule 21I (embedded generation constraints)
  New Schedule 21J (forecast aggregate registered capacity)
Narrative
  PSM Scenario Document
  PSM Change Document

## Slide 14: Network Operator Week 28 Submission
PSM
  Solved Subtransmission Power System Models representing
    Subtransmission System at historic NETS peak demand
    Subtransmission System maximum fault level condition
  Description of Model changes related to each Subtransmission planned (firm) network development project and ‘accepted to connect’ connection
Tabular
  Revised Schedules 21A, B (GSP-level demand data - winter conditions)
  Revised Schedule 21F (GSP-level demand data – access periods)
  Revised Schedules 21G, H (embedded power stations)
  Revised Schedule 21I (embedded generation constraints)
  Schedule 17 (access period schedule)
  Schedules 10A, B, C (system-level demand profiles – various conditions)
  Schedules 12A, B, C (system demand reduction characteristics)
  Schedule 11C (User’s system active energy per customer type)
Narrative
  PSM Scenario Document
  PSM Change Document

## Slide 15: Evaluation of Transmission Impact Assessment Data Submission by Network Operators
PSM (Structural only)
  Model changes describing each Power Station associated with ETI and any proposed related alteration to the Network Operator System
  Representation of the Network Operator System at the time of connections proposed by the ETI

## Slide 16: The Company’s Week 12 Submission
PSM
  Solved NETS Power System Models representing
    Next summer’s forecast NETS minimum demand condition
    Next summer’s forecast NETS minimum daylight demand condition
    Next summer’s forecast NETS low power transfer condition
    Next summer’s estimated NETS minimum fault level condition
  Description of Model changes related to each NETS planned (firm) network development project and ‘accepted to connect’ connection
Narrative
  PSM Scenario Document
  PSM Change Document

## Slide 17: The Company’s Week 38 Submission
PSM
  Solved NETS Power System Models representing
    Next winter's forecast NETS peak demand condition
    Next winter’s forecast NETS high power transfer condition
    Next winter’s estimated NETS maximum fault level condition
  Description of Model changes related to each NETS planned (firm) network development project and ‘accepted to connect’ connection
Narrative
  PSM Scenario Document
  PSM Change Document

## Slide 18: In support of request for Distribution Impact assessment or Transmission Licensee-initiated modification
PSM
  Model changes describing each new User connection or Transmission Licensee-initiated modification
  Representation of the National Electric Transmission System at the time of proposed connection

## Slide 19: Anatomy of a Solved PSM
PSM Models & their profiles
  Structural Model
    Equipment (EQ) profile: grid asset, generation/load capability, connectivity
    Short Circuit (SC) profile: short circuit characteristics of assets
    Geospatial Location (GL) profile: geo-location of assets and facilities
  Situation Model
    Steady State Hypothesis (EQ) profile: switch states, load/generation injections, control settings
  Solution Model
    Topology (TP) profile: simplified connectivity (needed for calculations)
    State Variable (SV) profile: output of power flow calculations
    Short Circuit Results (SCR) profile: output of short circuit calculations

## Slide 20: Anatomy of a Solved PSM
CGMES (or LTDS) defines the data present in each profile
Structural Model and Situation Model are inputs of grid calculations; Solution Model is output
Many Situation Model/Solution Model pairs can be defined for the same Structural Model
A PSDM describes a proposed future change to a Structural Model

## Slide 21: DRC Expansion
The DRC is proposed to be expanded with a suite of new schedules to support PC.9 and PC.10. These schedules, are based on the ‘Guidance Notes for Network Operator’s Submission of Data’ issued by the Company annually, are as follows:
Schedule 21A – Demand/Generation forecast at time of NETS peak demand
Schedule 21B - Demand/Generation forecast at time of Connection Point peak real demand
Schedule 21C - Demand/Generation forecast at time of NETS minimum demand
Schedule 21D - Demand/Generation forecast at time of Connection Point minimum gross demand
Schedule 21E - Demand/Generation forecast at time of Connection Point summer daylight minimum gross demand
Schedule 21F - Demand/Generation forecast at time of Access Period peak real demand
Schedule 21G - Detail of Embedded Power Stations greater than or equal to 1MW
Schedule 21H - Detail of Embedded Power Stations less than 1MW
Schedule 21I – Embedded Generation Constraints
Schedule 21J – Aggregated Forecast Registered Capacity

## Slide 22: Power Flow Definitions used in PC.9, PC.10 & DRC
M1, M2 - Measurement at the Connection Point
DG - export from embedded generation other than from Electricity Storage
Esi - import to Electricity Storage
ESe - export from Electricity Storage
D - aggregate network / customer demand
∆D - Latent Demand
Where:
Group Demand = D + ∆D [underlying customer demand]
Group Demand = (M1 + M2) + (DG + ESe) – ESi + ∆D = (D + ∆D)
Latent Demand = ∆D [factors that modify the underlying customer demand]
Embedded Generation Export = DG + ESe
Embedded Generation Import = ESi
Measured Import = M1 + M2
Gross Demand = (D + ∆D) + ESi
Net Demand = M1 + M2

## Slide 23: Glossary & Definitions – New Definitions
Term | Definition |  | Term | Definition
Aggregated Energy Source | The aggregation of Energy Source types as defined in PC.G.8.2 |  | Network Data | The data to be provided by The Company to Users in accordance with the PC, as listed in Part 3 of the Appendix A to the PC or PC10 as appropriate.
CIM Standard | A standard published by a standards body (e.g., IEC, BSI) which utilises CIM concepts. CIM Standards describe various facets of CIM and its use: the underlying information model, data exchange and serialisation |  | Power System Difference Model (PSDM) | A digital model that describes changes to the Structural Data of a PSM.
CIM | Common Information Model is an abstract information model that describes and organises electricity power system data. Such a model provides a standard way of representing assets owned and / or operated by a User and assets of customers connected to Users’ Systems and facilitates the integration of independently developed power system modelling applications. |  | Power System Model (PSM) | A digital model of an electricity transmission and/or distribution system created for the purpose of performing studies. It organises the relevant data into: Structural Data, Situation Data, and Solution Data, and facilitates data exchange between relevant parties.
Data Freeze Date | The date at which the Structural Data of a Network Operator’s Solved PSM reflects the Network Operator’s System. |  | PSM Change Document | A document associated with a submission describing changes to the NETS or Network Operator’s system or its operation and changes to the assumptions used in the creation of a Solved PSM and/or the associated schedules forming part of the periodic information exchanges. Additional detail is provided in PC.G.2.
Evaluation of Transmission Impact | as defined in the CUSC. |  | PSM Implementation Date | 1st January 2026 unless otherwise agreed in accordance with PC3.1.2.
Embedded Generation Import | Import to an Embedded Customer’s site where the primary purpose is wholly or mainly that of an Embedded Generator. When establishing the primary purpose, the Network Operator will consider factors including: the maximum export capacity relative to the maximum import capacity; whether the Embedded Customer has a generation licence or licence exemption; and whether the Embedded Customer’s site is categorised as having a demand connection or generation connection as defined in DCUSA Schedule 22. |  | PSM Interface Node | A point in an interconnected electrical system model that defines the boundary either side of which different parties are responsible for data.
Embedded Generation Export | Export from an Embedded Customer’s site. |  | PSM Scenario Document | A document associated with a submission which provides information relating to the assumptions used in preparation of the solved PSM and the associated schedules. Additional detail is provided in PC.G.1.
Energy Source | Any of the sources of energy listed in PC.G.8 used in the production of electricity. |  | Situation Data | Data representing an operational state of an electricity system, including demand and generation output and switch positions.
GB CIM Governance Group | A GB standing group of technical experts who are responsible for the maintenance and coordination of the GB extensions to the CIM and to CGMES profiles, such that they effectively support the Grid Code and other relevant data exchanges. |  | Solved PSM | A PSM which includes Structural Data, Situation Data, and Solution Data.
Gross Demand | The sum of the Group Demand and Embedded Generation Import |  | Solution Data | Data comprising the results of a steady-state power flow calculation and/or short circuit calculation, together with topology, voltage, and power flow data representing a steady-state solution using a coordinated Structural Data and Situation Data.
Group Demand | Aggregate import to Embedded Customers’ sites other than to those where the primary purpose is wholly or mainly that of an Embedded Generator. When establishing the primary purpose the Network Operator will consider factors including: the maximum export capacity relative to the maximum import capacity; whether the Customer has a generation licence or licence exemption; and whether the Customer’s site is categorised as having a demand connection or generation connection as defined in DCUSA Schedule 22. When estimating the Group Demand the Network Operator should, where necessary, take into consideration Latent Demand. |  | Structural Data | Data representing the characteristics of electricity system assets, including their capabilities and connectivity.
Latent Demand | An increase in Group Demand that would appear: If any demand side response was not operating; If any Suppliers’ time of use tariffs were not implemented; If any Network Operator or The Company’s price signals were not implemented; If any other means of suppressing the Embedded Customer’s demand were not operating; orIn the event of Cold Load Pickup. |  | Subtransmission PSM | A PSM with the scope as set out in PC.9.5.1
Measured Demand | Demand measured at the relevant Connection Point. Sometimes referred to as the net demand. |  | Switch-based Model | A PSM that includes all relevant switching devices. Such a model can be used to represent different system topologies, compared to a node and branch model which generally only represents a single system topology.
NETS PSM | A PSM with the scope as set out in PC.10.4 |  |  |