## Slide 1
Dr Yunjie Gu, Lecturer in Power Systems
Imperial College London
Data-led Oscillation Monitoring and Early Warning

## Slide 2: AEMO Oscillations
Sub-synchronous Oscillations in West Murray Zone (WMZ), Australia, since 2019. Source: High level summary of WMZ – Subsynchronous Oscillations.
The sub-synchronous oscillations seem to be intermittent and occurring both with and without any apparent disturbance in the WMZ or surrounding region.
The frequency of oscillations is mostly around 17-19 Hz (RMS).
The oscillations have been identified as contained in the north-west of Victoria and specifically around the Red Cliffs and Wemen area, likely involving the following solar plants: Wemen, Bannerton, Karadoc, Yatpool & Kiamal.
Based on instances when the response of these solar plants was analysed, the Q and V response from the solar plants were sometimes in-phase and sometimes out-of-phase.
The system operator replicated the oscillation in their EMT simulation models, after two years.

## Slide 3: Scotland Oscillations

## Slide 4: Hornsea Oscillations

## Slide 5: Hornsea Oscillations
Before the Hornsea wind farm de-loading, there was an under-damped voltage oscillation

## Slide 6: Defence Lines for Oscillations
This work is supported by National Grid ESO via Network Innovation Allowance projects “Data-Driven Online Monitoring and Early Warning For GB System Stability” (DOME) and “Strength to Connect”
Post-Event: identify the origins of oscillations and deploy mitigation actions to prevent them from happening again
Pre-Event: provide predictions and early warnings of oscillations before they actually occur
Planning: identify the strength and weakness of the network and perform connection planning accordingly

## Slide 7: The Eigenvalue Approach
The stability of linear system
is determined by

## Slide 8: State Sensitivity: Participation Factor
Participation factor: sensitivity of an oscillation mode to a state
Pagola, F.L.; Perez-Arriaga, I.J.; Verghese, George C. (1989). "On sensitivities, residues and participations: Applications to oscillatory stability analysis and control". IEEE Transactions on Power Systems.

## Slide 9: Model? We don’t have a good one
Sensitivity (participation factor) analysis is a powerful tool to understand oscillations, only if we have a good (white-box) model.
The first generation of inverter-based resources (IBRs) do not provide models at all.
Newer IBRs are obliged to provide model, but in a black-box form (compiled executables).

## Slide 10: Port-Based Sensitivity: Impedance Participation Factor
From the residue Lamma, we define an “impedance participation factor”
Residue
Pole/Eigenvalue
The residue Lamma: residue of admittance at node equals the sensitivity of each pole to the device impedance at that node.
: impedance of device connected at bus k
: admittance of whole-system seen at bus k

## Slide 11: Admittance Participation Factor
From the residue Lamma, we define an “admittance participation factor”
Residue
Pole/Eigenvalue
The residue Lamma: residue of impedance at node equals the sensitivity of each pole to the device admittance at that node.
: admittance of device connected at bus k
: impedance of whole-system seen at bus k

## Slide 12: Unified Sensitivity Relationships
If you know the parameters, , you can:
Build the state-space matrix
Find the eigenvalues and identify poorly damped modes
Find the participation factors and determine which states participate in a given mode
Find the sensitivity of the mode to a parameter (parameter participation) and re-tune
If you only know the equipment and network impedances, you can:
Find modes by observation of impedance spectrum
Find the residues of as impedance participation factors
Use a chain-rule to identify sensitivity to a mode to a parameter,

## Slide 13: The Grey-Box Approach

## Slide 14: Case Study: Modified IEEE 68 Bus System

## Slide 15: Case Study: Modified IEEE 68 Bus System

## Slide 16: Impedance Margin Ratio: New Index of System Strength

## Slide 17: Dissipating Energy Flow (DEF)
[1] Chen, L., Min, Y. and Hu, W., 2012. An energy-based method for location of power system oscillation source. IEEE Transactions on Power Systems, 28(2), pp.828-836.
[2] Maslennikov, S., Wang, B. and Litvinov, E., 2017. Dissipating energy flow method for locating the source of sustained oscillations. International Journal of Electrical Power & Energy Systems, 88, pp.55-62.
DEF: Dissipation Energy Flow
DEF indicates the flow of “damping power” in the system.
The sign of the dc component of DEF indicates contribution to damping.
Positive DEF indicates sources of oscillation, and negative DEF indicates sinks of damping.
DEF was proposed in [1] and applied to the New England system in [2], with 100% accuracy.
DEF can be fully calculated from PMU data: model free.
Source
Sink

## Slide 18: DEF may fail for IBRs
“weak grid”
1.5 Hz weak-grid oscillation
Oscillation is induced by IBRs, but DEF points towards synchronous generators (SGs)
A1 (SG)
A2 (SG)
DEF measured at all buses

## Slide 19: Dissipation v.s. Damping
Dissipation: the rate of energy loss (time derivative of the energy function)
Damping: the rate of oscillation decay (real part of eigenvalue)
Dissipation contributes to damping only if they are consistent
  Mechanical dissipation contributes to the damping of angle swing and torsional resonance
  Electrical dissipation contributes to the damping of electromagnetic resonance
Torsional resonance: damped by mechanical dissipation (positive torque coefficient)
Electromagnetic resonance: damped by electrical dissipation (positive resistance)

## Slide 20: Can we adapt DEF to inverters?
Name | Abbreviation | Definition
Original DEF | DEF | 
Complex DEF [1] | cDEF | 
Dual DEF [2] | dDEF | 
Sub/Super-Synchronous DEF [3] | sDEF | 
[1] L Fan, Z Wang, Z Miao, S Maslennikov, Oscillation Source Detection for Inverter-Based Resources via Dissipative Energy Flow, TechRxiv
[2] PG Estevez, Complex dissipating energy flow method for forced oscillation source location, IEEE Trans Power Systems.
[3] X Xie, Y Zhan, J Shair, Z Ka, X Chang, Identifying the source of subsynchronous control interaction via wide-area monitoring of sub/super-synchronous power flows, IEEE Trans Power Delivery.
Multiple attempts have been made to modify DEF to make it work for IBRs. They all succeed in some cases but not in all cases.

## Slide 21: The unified DEF: uDEF
W is to be specified to make uDEF consistent with damping

## Slide 22: uDEF covers all existing DEFs
Existing DEF | Definition | Equivalent W
DEF |  | 
cDEF |  | 
dDEF |  | 
sDEF |  | 

## Slide 23: uDEF covers all possible DEF
Derivative on currents? Not needed.
Higher order derivatives? Not needed.
Other signals (ΔP, ΔQ, Δθ, Δω)? Equivalent.

## Slide 24: uDEF v.s. Damping
uDEF is precisely consistent with damping if W is consistent with the admittance participations factors

## Slide 25: Case Studies
IEEE 7 Bus System
IEEE 14 Bus System
Case 1: Voltage Oscillation (18.8Hz) Voltage control gain of IBRs at bus 4 & 7 tuned high.
Case 2: Weak Grid Oscillation (1.5Hz) Power of IBRs at buses 11-13 tuned high
Case 3: Current-PLL Oscillation (8.8Hz) Current loop of IBRs at buses 11-13 tuned low

## Slide 26: Case 1: Voltage Oscillation
Ground truth from sensitivity analysis
Eight components of uDEF
Two uDEF components give approximately correct indications
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7

## Slide 27: Case 2: Weak Grid Oscillation
Ground truth from sensitivity analysis
Eight components of uDEF
Only one uDEF component gives approximately correct indications
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13

## Slide 28: Case 3: Current-PLL Oscillation
Ground truth from sensitivity analysis
Eight components of uDEF
All of the eight uDEF components give approximately correct indications (subject to signs)
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13

## Slide 29: Takeaway from case studies
The three cases cover a wide range of IBR induced oscillations, involving different control loops and occurring at different frequencies.
The best specifications of uDEF is different for different types of oscillations.
It is encouraging that for all the cases we have studied, one component of uDEF stands out as being correct throughout the cases.
Is there any reasons or just a coincidence?
The uDEF that works for all three cases

## Slide 30: Conclusions
Impedance Margin Ratio: Planning
Black-box models or real system
Unified Dissipating Energy Flow: Post-event
Completely model free
Impedance Participation Factor: Pre-event
Black-box models or real system
Port Sensitivity