## Slide 1
Dr Yunjie Gu, Lecturer in Power Systems
Imperial College London
Data-led Oscillation Monitoring and Early Warning

## Slide 2: AEMO Oscillations
Sub-synchronous Oscillations in West Murray Zone (WMZ), Australia, since 2019. Source: High level summary of WMZ – Subsynchronous Oscillations.
The sub-synchronous oscillations seem to be intermittent and occurring both with and without any apparent disturbance in the WMZ or surrounding region.
The frequency of oscillations is mostly around 17-19 Hz (RMS).
The oscillations have been identified as contained in the north-west of Victoria and specifically around the Red Cliffs and Wemen area, likely involving the following solar plants: Wemen, Bannerton, Karadoc, Yatpool & Kiamal.
Based on instances when the response of these solar plants was analysed, the Q and V response from the solar plants were sometimes in-phase and sometimes out-of-phase.
The system operator replicated the oscillation in their EMT simulation models, after two years.

## Slide 3: Hornsea Oscillations

## Slide 4: Hornsea Oscillations
Before the Hornsea wind farm de-loading, there was an under-damped voltage oscillation

## Slide 5: Defence Lines for Oscillations
This work is supported by National Grid ESO via Network Innovation Allowance projects “Data-Driven Online Monitoring and Early Warning For GB System Stability” (DOME) and “Strength to Connect”
Post-Event: identify the origins of oscillations and deploy mitigation actions to prevent them from happening again
Pre-Event: provide predictions and early warnings of oscillations before they actually strike
Planning: identify the strength and weakness of the network and perform connection planning accordingly
Impedance Participation Factor
Impedance Margin Ratio
?

## Slide 6: Impedance Participation Factor

## Slide 7: Impedance Margin Ratio

## Slide 8: The Challenges for Post-Event Analysis
We cannot trust simulation model: the oscillation should have been detected in beforehand if the model is correct – planning tool not useful for post-event.
We cannot tweak on the physical system: the operating conditions change and there is no way back – pre-event tool not useful for post-event.
System operators prefer a method that works with no model nor physical system available at all – completely data-driven post-event analysis.

## Slide 9: Dissipating Energy Flow (DEF)
[1] Chen, L., Min, Y. and Hu, W., 2012. An energy-based method for location of power system oscillation source. IEEE Transactions on Power Systems, 28(2), pp.828-836.
[2] Maslennikov, S., Wang, B. and Litvinov, E., 2017. Dissipating energy flow method for locating the source of sustained oscillations. International Journal of Electrical Power & Energy Systems, 88, pp.55-62.
DEF: Dissipation Energy Flow
DEF indicates the flow of “damping power” in the system.
The sign of the dc component of DEF indicates contribution to damping.
Positive DEF indicates sources of oscillation, and negative DEF indicates sinks of damping.
DEF was proposed in [1] and applied to the New England system in [2], with 100% accuracy.
DEF can be fully calculated from PMU data: model free.
Source
Sink

## Slide 10: DEF may fail for IBRs
“weak grid”
1.5 Hz weak-grid oscillation
Oscillation is induced by IBRs, but DEF points towards synchronous generators (SGs)
A1 (SG)
A2 (SG)
DEF measured at all buses

## Slide 11: Dissipation v.s. Damping
Dissipation: the rate of energy loss (time derivative of the energy function)
Damping: the rate of oscillation decay (real part of eigenvalue)
Dissipation contributes to damping only if they are consistent
  Mechanical dissipation contributes to the damping of angle swing and torsional resonance
  Electrical dissipation contributes to the damping of electromagnetic resonance
Torsional resonance: damped by mechanical dissipation (positive torque coefficient)
Electromagnetic resonance: damped by electrical dissipation (positive resistance)

## Slide 12: Can we adapt DEF to inverters?
Name | Abbreviation | Definition
Original DEF | DEF | 
Complex DEF [1] | cDEF | 
Dual DEF [2] | dDEF | 
Sub/Super-Synchronous DEF [3] | sDEF | 
[1] L Fan, Z Wang, Z Miao, S Maslennikov, Oscillation Source Detection for Inverter-Based Resources via Dissipative Energy Flow, TechRxiv
[2] PG Estevez, Complex dissipating energy flow method for forced oscillation source location, IEEE Trans Power Systems.
[3] X Xie, Y Zhan, J Shair, Z Ka, X Chang, Identifying the source of subsynchronous control interaction via wide-area monitoring of sub/super-synchronous power flows, IEEE Trans Power Delivery.
Multiple attempts have been made to modify DEF to make it work for IBRs. They all succeed in some cases but not in all cases.

## Slide 13: The unified DEF: uDEF
W is to be specified to make uDEF consistent with damping

## Slide 14: uDEF covers all existing DEFs
Existing DEF | Definition | Equivalent W
DEF |  | 
cDEF |  | 
dDEF |  | 
sDEF |  | 

## Slide 15: uDEF covers all possible DEF
Derivative on currents? Not needed.
Higher order derivatives? Not needed.
Other signals (ΔP, ΔQ, Δθ, Δω)? Equivalent.

## Slide 16: uDEF v.s. Damping
W matrix can be configured as per residues at each node so that uDEF is consistent with damping.
We can classify oscillations as per the characteristics of residue orientations and configure W accordingly.

## Slide 17: Case Studies
IEEE 7 Bus System
IEEE 14 Bus System
Case 1: Voltage Oscillation (18.8Hz) Voltage control gain of IBRs at bus 4 & 7 tuned high.
Case 2: Weak Grid Oscillation (1.5Hz) Power of IBRs at buses 11-13 tuned high
Case 3: Current-PLL Oscillation (8.8Hz) Current loop of IBRs at buses 11-13 tuned low

## Slide 18: Case 1: Voltage Oscillation
Ground truth from sensitivity analysis
Eight components of uDEF
Two uDEF components give approximately correct indications
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7
1 3 4 5 6 7

## Slide 19: Case 2: Weak Grid Oscillation
Ground truth from sensitivity analysis
Eight components of uDEF
Only one uDEF component gives approximately correct indications
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13

## Slide 20: Case 3: Current-PLL Oscillation
Ground truth from sensitivity analysis
Eight components of uDEF
All of the eight uDEF components give approximately correct indications (subject to signs)
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13
1 2 3 6 8 11 12 13

## Slide 21: Takeaway from case studies
The three cases cover a wide range of IBR induced oscillations, involving different control loops and occurring at different frequencies.
The best specifications of uDEF is different for different types of oscillations.
It is encouraging that for all the cases we have studied, one component of uDEF stands out as being correct throughout the cases.
Is there any reasons or just a coincidence?
The uDEF that works for all three cases

## Slide 22: Conclusions
Impedance Margin Ratio: Planning
Black-box models or real system
Unified Dissipating Energy Flow: Post-event
Completely model free
Impedance Participation Factor: Pre-event
Black-box models or real system
Impedance Sensitivity