PLANNING CODE

(PC)

CONTENTS

(This contents page does not form part of the Grid Code)

PC.1	INTRODUCTION	2

PC.2	OBJECTIVE	3

PC.3	SCOPE	3

PC.4	PLANNING PROCEDURES	7

PC.5	PLANNING DATA	11

PC.6	PLANNING STANDARDS	14

PC.7	PLANNING LIAISON	15

PC.8	OTSDUW PLANNING LIAISON	16

PC.9	SUBMISSION OF SYSTEM MODELS AND INFORMATION BY NETWORK OPERATORS TO THE COMPANY	17

PC.10	SUBMISSION OF SYSTEM MODELS AND INFORMATION BY THE COMPANY TO NETWORK OPERATORS	27

APPENDIX A - PLANNING DATA REQUIREMENTS	34

PART 1 - STANDARD PLANNING DATA	38

PC.A.2	USER'S SYSTEM (AND OTSUA) DATA	38

PC.A.3	POWER GENERATING MODULE, GENERATING UNIT, HVDC SYSTEM AND DC CONVERTER DATA	47

PC.A.4	DEMAND AND ACTIVE ENERGY DATA	56

PART 2 - DETAILED PLANNING DATA	63

PC.A.5	POWER GENERATING MODULE, GENERATING UNIT, POWER PARK MODULE (INCLUDING DC CONNECTED POWER PARK MODULES), DC CONVERTER, HVDC EQUIPMENT AND OTSDUW PLANT AND APPARATUS DATA	63

PC.A.6	USERS' SYSTEM DATA	86

PC.A.7	ADDITIONAL DATA FOR NEW TYPES OF POWER STATIONS, DC CONVERTER STATIONS, OTSUA AND CONFIGURATIONS	91

PART 3 - DETAILED PLANNING DATA	92

APPENDIX B - SINGLE LINE DIAGRAMS	101

APPENDIX C - TECHNICAL AND DESIGN CRITERIA	104

PART 1 – SHETL's TECHNICAL AND DESIGN CRITERIA	104

PART 2 - SPT's TECHNICAL AND DESIGN CRITERIA	106

APPENDIX D - DATA NOT DISCLOSED TO A RELEVANT TRANSMISSION LICENSEE	107

APPENDIX E - OFFSHORE TRANSMISSION SYSTEM AND OTSDUW PLANT AND APPARATUS TECHNICAL AND DESIGN CRITERIA	110

APPENDIX F - OTSDUW DATA AND INFORMATION AND OTSDUW NETWORK DATA AND INFORMATION	111

APPENDIX G – NETWORK OPERATOR AND THE COMPANY PLANNING DATA EXCHANGE	113

# PC.1		INTRODUCTION

PC.1.1	The Planning Code ("PC") specifies the technical and design criteria and procedures to be applied by The Company in the planning and development of the National Electricity Transmission System and to be taken into account by Users in the planning and development of their own Systems.  In the case of OTSUA, the PC also specifies the technical and design criteria and procedures to be applied by the User in the planning and development of the OTSUA. It details information to be supplied by Users to The Company, and certain information to be supplied by The Company to Users. The Company has obligations under the STC to inform Relevant Transmission Licensees of data required for the planning of the National Electricity Transmission System. In respect of PC data, The Company may pass on User data to a Relevant Transmission Licensee, as detailed in PC.3.4 and PC.3.5.

PC.1.1A	Provisions of the PC which apply in relation to OTSDUW and OTSUA shall apply up to the OTSUA Transfer Time, whereupon such provisions shall (without prejudice to any prior non-compliance) cease to apply, without prejudice to the continuing application of provisions of the PC applying in relation to the relevant Offshore Transmission System and/or Connection Site.

PC.1.1B	As used in the PC:

(a)	National Electricity Transmission System excludes OTSDUW Plant and Apparatus (prior to the OTSUA Transfer Time) unless the context otherwise requires; and

(b)	User Development includes OTSDUW unless the context otherwise requires.

PC.1.2	The Users referred to above are defined, for the purpose of the PC, in PC.3.1.

PC.1.3	Development of the National Electricity Transmission System, involving its reinforcement or extension, will arise for a number of reasons including, but not limited to:

(a)	a development on a User System already connected to the National Electricity Transmission System;

(b)	the introduction of a new Connection Site or the Modification of an existing Connection Site between a User System and the National Electricity Transmission System;

(c)	the cumulative effect of a number of such developments referred to in (a) and (b) by one or more Users.

PC.1.4	Accordingly, the reinforcement or extension of the National Electricity Transmission System may involve work:

(a)	at a substation at a Connection Site where User's Plant and/or Apparatus is connected to the National Electricity Transmission System (or in the case of OTSDUW, at a substation at an Interface Point);

(b)	on transmission lines or other facilities which join that Connection Site (or in the case of OTSDUW, Interface Point) to the remainder of the National Electricity Transmission System;

(c)	on transmission lines or other facilities at or between points remote from that Connection Site (or in the case of OTSDUW, Interface Point).

PC.1.5	The time required for the planning and development of the National Electricity Transmission System will depend on the type and extent of the necessary reinforcement and/or extension work, the need or otherwise for statutory planning consent, the associated possibility of the need for a public inquiry and the degree of complexity in undertaking the new work while maintaining satisfactory security and quality of supply on the existing National Electricity Transmission System.

PC1.6	For the avoidance of doubt and the purposes of the Grid Code, DC Connected Power Park Modules are treated as belonging to Generators. Generators who own DC Connected Power Park Modules would therefore be expected to supply the same data as required under this PC in respect of Power Stations comprising Power Park Modules other than where specific references to DC Connected Power Park Modules are made.

PC1.7	As defined in the Glossary and Definitions, Electricity Storage Modules are treated as belonging to Storage Users who are a subset of Generators who own or operate Electricity Storage Modules and would therefore be expected to supply the same data as required under this PC in respect of Power Stations. In general, and notwithstanding the requirements in respect of the Glossary and Definitions and the wider requirements specified in the Planning Code, Generators in respect of Synchronous Electricity Storage Modules would be expected to supply the same data as required from Generators in respect of Synchronous Power Generating Modules and Generators in respect of Non-Synchronous Electricity Storage Modules would be expected to supply the same data as required from Generators in respect of Power Park Modules.

# PC.2		OBJECTIVE

PC.2.1	The objectives of the PC are:

(a)	to promote The Company/User interaction in respect of any proposed development on the User System which may impact on the performance of the National Electricity Transmission System or the direct connection with the National Electricity Transmission System; and

(b)	to provide for the supply of information to The Company from Users in order that planning and development of the National Electricity Transmission System can be undertaken in accordance with the relevant Licence Standards, to facilitate existing and proposed connections, and also to provide for the supply of relevant information from The Company to Users in order that planning and development of the User’s System can be undertaken in accordance with their relevant regulatory requirements; and

(c)	to specify the Licence Standards which will be used in the planning and development of the National Electricity Transmission System; and

(d)	to provide for the supply of information required by The Company from Users in respect of the following to enable The Company to carry out its duties under the Act and the ESO Licence:

(i)	Mothballed Generating Units, Mothballed Power Generating Modules; and

(ii)	capability of gas-fired Synchronous Power Generating Modules or Generating Units to run using alternative fuels.

The Company will use the information provided under PC.2.1(d) in providing reports to the Authority and the Secretary of State and, where directed by the Authority or the Secretary of State to do so, The Company may publish the information.  Where it is known by The Company that such information is intended for wider publication the information provided under PC.2.1(d) shall be aggregated such that individual data items should not be identifiable; and

(e)	in the case of OTSUA:

(i)	to specify the minimum technical and design criteria and procedures to be applied by Users in the planning and development of OTSUA; and thereby

(ii)	to ensure that the OTSUA can from the OTSUA Transfer Time be operated as part of the National Electricity Transmission System; and

(iii)	to provide for the arrangements and supply of information and data between The Company and a User to ensure that the User is able to undertake OTSDUW; and

(iv)	to promote The Company/User interaction and co-ordination in respect of any proposed development on the National Electricity Transmission System or the OTSUA, which may impact on the OTSUA or (as the case may be) the National Electricity Transmission System.

# PC.3		SCOPE

PC.3.1	The PC applies to The Company and to Users, which in the PC means:

(a)	Generators;

(b)	Generators undertaking OTSDUW;

(c)	Network Operators;

(d)	Non-Embedded Customers;

(e)	DC Converter Station owners; and

(f)    HVDC System Owners.

The above categories of User will become bound by the PC prior to them generating, operating, or consuming or importing/exporting, as the case may be, and references to the various categories (or to the general category) of User should, therefore, be taken as referring to them in that prospective role as well as to Users actually connected.

PC.3.1.1	Exchanges between The Company and Network Operators

PC.3.1.1.1	From the PSM Implementation Date in relation to information exchanges between The Company and Network Operators, paragraphs PC.3.2.(c) and (d), PC.3.3, PC.3.4, PC.3.5, PC.3.6, PC3.7, PC.4.3.1, PC.4.3.2, PC.4.5, PC.7, PC.A and PC.B shall no longer apply and paragraphs  PC.9, PC.10 and PC.G shall instead apply.

PC.3.1.1.2	In the event that The Company and all Network Operators are not in a position to implement information exchange as described in PC.9, PC.10 and PC.G, by the PSM Implementation Date, The Company and Network Operators shall use their best endeavours to agree an alternative PSM Implementation Date.

PC.3.1.1.3		Subject to written consent between The Company and the relevant Network Operator, nothing shall prevent The Company and that Network Operator from applying the information exchange described in PC.9, PC.10, and PC.G before the PSM Implementation Date.

PC.3.1.1.4	The PSM data exchanges shall conform to the data exchange profile standards and satisfy the implementation requirements outlined in PC.G.4.1. Alternative exchange profile standards and/or appropriate extensions may be used as agreed between The Company and all the Network Operators or as directed by the GB CIM Governance Group, as described in PC.G.4.1.1, where agreed by The Company and all the Network Operators.

PC.3.1.1.5	The Structural Data in the exchanged PSMs shall utilise unique and persistent identifiers. A unique identifier shall be assigned to the role of each grid component within the Structural Data which shall persist throughout the life of that role.

PC.3.1.1.6	For the avoidance of doubt, Network Operators will not be in breach of the obligations imposed by PC.9, PC.10 and PC.G where data is omitted due to the data not yet being supported by the data exchange standard identified in PC.G.4.

PC.3.2	In the case of Embedded Power Stations, Embedded DC Converter Stations and Embedded HVDC Systems, unless provided otherwise, the following provisions apply with regard to the provision of data under this PC:

(a)	each Generator shall provide the data direct to The Company in respect of (i) Embedded Large Power Stations, (ii) Embedded Medium Power Stations subject to a Bilateral Agreement and (iii) Embedded Small Power Stations which form part of a Cascade Hydro Scheme;

(b)	each DC Converter owner or HVDC System Owner shall provide the data direct to The Company in respect of Embedded DC Converter Stations and Embedded HVDC Systems subject to a Bilateral Agreement;

(c)	each Network Operator shall provide the data to The Company in respect of each Embedded Medium Power Station not subject to a Bilateral Agreement or Embedded DC Converter Station not subject to a Bilateral Agreement or Embedded HVDC System not subject to a Bilateral Agreement connected, or proposed to be connected within such Network Operator’s System;

(d)	although data is not normally required specifically on Embedded Small Power Stations  or on Embedded installations of direct current converters which do not form a DC Converter Station or HVDC System under this PC, each Network Operator in whose System they are Embedded should provide the data (contained in Appendix A) to The Company in respect of Embedded Small Power Stations or Embedded installations of direct current converters which do not form a DC Converter Station or Embedded installations of HVDC Systems if:

(i)	it falls to be supplied pursuant to the application for a CUSC Contract or in the Statement of Readiness to be supplied in connection with a Bilateral Agreement and/or Construction Agreement, by the Network Operator; or

(ii)	it is specifically requested by The Company in the circumstances provided for under this PC.

PC.3.3	Certain data does not normally need to be provided in respect of certain Embedded Power Stations, Embedded DC Converter Stations or Embedded HVDC Systems, as provided in PC.A.1.12.

In summary, Network Operators are required to supply the data described in the below listed paragraphs of Appendix A of this PC in respect of Embedded Medium Power Stations not subject to a Bilateral Agreement or Embedded DC Converter Stations not subject to a Bilateral Agreement or Embedded HVDC Systems not subject to a Bilateral Agreement connected, or is proposed to be connected, within such Network Operator’s System:

PC.A.2.1.1

PC.A.2.2.2

PC.A.2.5.5.2

PC.A.2.5.5.7

PC.A.2.5.6

PC.A.3.1.5

PC.A.3.2.2

PC.A.3.3.1

PC.A.3.4.1

PC.A.3.4.2

PC.A.5.2.2

PC.A.5.3.2

PC.A.5.4

PC.A.5.5.1

PC.A.5.6

For the avoidance of doubt Network Operators are required to supply the above data in respect of Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded DC Converter Stations not subject to a Bilateral Agreement and Embedded HVDC Systems not subject to a Bilateral Agreement which are located Offshore and which are connected or proposed to be connected within such Network Operator’s System.  This is because Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded DC Converter Stations not subject to a Bilateral Agreement and Embedded HVDC Systems not subject to a Bilateral Agreement are treated as Onshore Generators or Onshore DC Converter Station owners or HVDC System Owners connected to an Onshore User System Entry Point.

PC.3.4	The Company may provide to the Relevant Transmission Licensees any data which has been submitted to The Company by any Users pursuant to the following paragraphs of the PC.  For the avoidance of doubt, The Company will not provide to the Relevant Transmission Licensees, the types of data specified in Appendix D.  The Relevant Transmission Licensees’ use of such data is detailed in the STC.

PC.A.2.2

PC.A.2.5

PC.A.3.1

PC.A.3.2.1

PC.A.3.2.2

PC.A.3.3

PC.A.3.4

PC.A.4

PC.A.5.1

PC.A.5.2

PC.A.5.3.1

PC.A.5.3.2

PC.A.5.4.1

PC.A.5.4.2

PC.A.5.4.3.1

PC.A.5.4.3.2

PC.A.5.4.3.3

PC.A.5.4.3.4

PC.A.7

(and in addition in respect of the data submitted in respect of the OTSUA)

PC.A.2.2

PC.A.2.3

PC.A.2.4

PC.A.2.5

PC.A.3.2.2

PC.A.3.3.1(d)

PC.A.4

PC.A.5.4.3.1

PC.A.5.4.3.2

PC.A.6.2

PC.A.6.3

PC.A.6.4

PC.A.6.5

PC.A.6.6

PC.A.7

PC.3.5	In addition to the provisions of PC.3.4, The Company may provide to the Relevant Transmission Licensees any data which has been submitted to The Company by any Users in respect of Relevant Units pursuant to the following paragraphs of the PC.

PC.A.2.3

PC.A.2.4

PC.A.5.5

PC.A.5.7

PC.A.6.2

PC.A.6.3

PC.A.6.4

PC.A.6.5

PC.A.6.6

PC.3.6	In the case of Offshore Embedded Power Stations connected to an Offshore User System which directly connects to an Offshore Transmission System, any additional data requirements in respect of such Offshore Embedded Power Stations may be specified in the relevant Bilateral Agreement with the Network Operator or in any Bilateral Agreement between The Company and such Offshore Embedded Power Station.

PC.3.7	In the case of a Generator undertaking OTSDUW connecting to an Onshore Network Operator’s System, any additional requirements in respect of such OTSDUW Plant and Apparatus will be specified in the relevant Bilateral Agreement with the Generator. For the avoidance of doubt, requirements applicable to Generators undertaking OTSDUW and connecting to a Network Operator’s User System, shall be consistent with those applicable requirements of Generators undertaking OTSDUW and connecting to a Transmission Interface Point.

PC.3.8	For the purpose of complying with the requirements of ECC.6.3.17.1.5 and ECC.6.3.17.2.3 The Company may share relevant modelling information with a User based on the following information submitted by a User to The Company:

PC.A.5.3.2(a), (b), (c), (d) and (g)

PC.A.5.4.2

PC.A.5.4.3

PC.A.9

PC.3.9	A User who receives information from The Company under PC.3.8 may only use the information to complete the analysis required by ECC.6.3.17.1 and EEC.6.3.17.2 as applicable and the Bilateral Agreement. Further conditions on the sharing of models are detailed in PC.A.9.

# PC.4	PLANNING PROCEDURES

PC.4.1	Pursuant to condition C12 of the ESO Licence, the means by which Users and proposed Users of the National Electricity Transmission System are able to assess opportunities for connecting to, and using, the National Electricity Transmission System comprise two distinct parts, namely:

(a)	a statement, prepared by The Company in accordance with condition C12 of the ESO Licence, showing for the current Financial Year and each of the nine succeeding Financial Years, the opportunities available for connecting to and using the National Electricity Transmission System and indicating those parts of the National Electricity Transmission System most suited to new connections and transport of further quantities of electricity (the "Electricity Ten Year Statement" or ETYS); and

(b)	an offer, in accordance with its ESO Licence, by The Company to enter into a CUSC Contract.  A Bilateral Agreement is to be entered into for every Connection Site (and for certain Embedded Power Stations and Embedded DC Converter Stations and Embedded HVDC Systems) within the first two of the following categories and the existing Bilateral Agreement may be required to be varied in the case of the third category:

(i)	existing Connection Sites (and for certain Embedded Power Stations) as at the Transfer Date;

(ii)	new Connection Sites (and for certain Embedded Power Stations, Embedded DC Converter Stations and Embedded HVDC Systems) with effect from the Transfer Date;

(iii)	a Modification at a Connection Site (or in relation to the connection of certain Embedded Power Stations, Embedded DC Converter Stations and Embedded HVDC Systems whether or not the subject of a Bilateral Agreement) (whether such Connection Site or connection exists on the Transfer Date or is new thereafter) with effect from the Transfer Date.

In this PC, unless the context otherwise requires, "connection" means any of these 3 categories.

PC.4.2	Introduction to Data

User Data

PC.4.2.1	Under the PC, two types of data to be supplied by Users are called for:

(a)	Standard Planning Data; and

(b)	Detailed Planning Data,

as more particularly provided in PC.A.1.4.

PC.4.2.2	The PC recognises that these two types of data, namely Standard Planning Data and Detailed Planning Data, are considered at three different levels:

(a)	Preliminary Project Planning Data;

(b)	Committed Project Planning Data; and

(c)	Connected Planning Data,

as more particularly provided in PC.5

PC.4.2.3	Connected Planning Data is itself divided into:

(a)	Forecast Data;

(b)	Registered Data; and

(c)	Estimated Registered Data,

as more particularly provided in PC.5.5

PC.4.2.4	Clearly, an existing User proposing a new Connection Site (or Embedded Power Station or Embedded DC Converter Station or Embedded HVDC System) in the circumstances outlined in PC.4.1) will need to supply data both in an application for a Bilateral Agreement and under the PC in relation to that proposed new Connection Site (or Embedded Power Station or Embedded DC Converter Station or Embedded HVDC System in the circumstances outlined in PC.4.1) and that will be treated as Preliminary Project Planning Data or Committed Project Planning Data (as the case may be), but the data it supplies under the PC relating to its existing Connection Sites will be treated as Connected Planning Data.

Network Data

PC.4.2.5	In addition, there is Network Data supplied by The Company in relation to short circuit current contributions in relation to OTSUA.

PC.4.3	Data Provision

PC.4.3.1	Electricity Ten Year Statement

To enable the Electricity Ten Year Statement to be prepared, each User is required to submit to The Company (subject to the provisions relating to Embedded Power Stations and Embedded DC Converter Stations and Embedded HVDC Systems in PC.3.2) both the Standard Planning Data and the Detailed Planning Data as listed in parts l and 2 of Appendix A.  This data should be submitted in calendar week 24 of each year (although Network Operators may delay the submission of data (other than that to be submitted pursuant to PC.3.2(c) and PC.3.2(d)) until calendar week 28) and should cover the current Financial Year and each of the nine succeeding Financial Years. Where, from the date of one submission to another, there is no change in the data (or in some of the data) to be submitted, instead of re-submitting the data, a User may submit a written statement that there has been no change from the data (or in some of the data) submitted the previous time.  In addition, The Company will also use the Transmission Entry Capacity and Connection Entry Capacity data from the CUSC Contract, and any data submitted by Network Operators in relation to an Embedded Medium Power Station not subject to a Bilateral Agreement or Embedded DC Converter Station not subject to a Bilateral Agreement, or Embedded HVDC System not subject to a Bilateral Agreement in the preparation of the Electricity Ten Year Statement and to that extent the data will not be treated as confidential.

PC.4.3.2	Network Data

To enable Users to model the National Electricity Transmission System in relation to short circuit current contributions, The Company is required to submit to Users, the Network Data as listed in Part 3 of Appendix A.  The data will be submitted in week 42 of each year and will cover that Financial Year.

PC.4.3.3 	To enable Users to model the National Electricity Transmission System in relation to OTSUA, The Company is required to submit to Users the Network Data, as listed in Part 3 of Appendix A and Appendix F.  The Company shall provide the Network Data with the offer of a CUSC Contract in the case of the data in PC F2.1 and otherwise in accordance with the OTSDUW Development and Data Timetable.

PC.4.4	Offer of Terms for Connection

PC.4.4.1	CUSC Contract – Data Requirements/Offer Timing

The completed application form for a CUSC Contract to be submitted by a User when making an application for a CUSC Contract will include:

(a)	a description of the Plant and/or Apparatus (excluding OTSDUW Plant and Apparatus) to be connected to the National Electricity Transmission System or of the Modification relating to the User's Plant and/or Apparatus (and prior to the OTSUA Transfer Time, any OTSUA)  already connected to the National Electricity Transmission System or, as the case may be, of the proposed new connection or Modification to the connection within the User System of the User, each of which shall be termed a "User Development" in the PC;

(b)	the relevant Standard Planning Data as listed in Part 1 of Appendix A (except in respect of any OTSUA);

(c)	the desired Completion Date of the proposed User Development; and

(d)	the desired Connection Entry Capacity and Transmission Entry Capacity.

The completed application form for a CUSC Contract will be sent to The Company as more particularly provided in the application form.

PC.4.4.2	Any offer of a CUSC Contract will provide that it must be accepted by the applicant User within the period stated in the offer, after which the offer automatically lapses. Except as provided in the CUSC Contract, acceptance of the offer renders the National Electricity Transmission System works relating to that User Development, reflected in the offer, committed and binds both parties to the terms of the offer. The User shall then provide the Detailed Planning Data as listed in Part 2 of Appendix A (and in the case of OTSUA the Standard Planning Data as listed in Part 1 of Appendix A within the timeline provided in PC.A.1.4). In respect of DPD I this shall generally be provided within 28 days (or such shorter period as The Company may determine, or such longer period as The Company may agree, in any particular case) of acceptance of the offer and in respect of DPD II this shall generally be provided at least two years (or such longer period as The Company may determine, or such shorter period as The Company may agree, in any particular case or in the case of OTSUA such shorter period as The Company shall require) prior to the Completion Date of the User Development.

PC.4.4.3	Embedded Development Agreement - Data Requirements

The Network Operator shall submit the following data in relation to an Embedded Medium Power Station not subject to, or proposed to be subject to, a Bilateral Agreement or Embedded DC Converter Station not subject to, or proposed to be subject to, a Bilateral Agreement as soon as reasonably practicable after receipt of an application from an Embedded Person to connect to its System:

(a)	details of the proposed new connection or variation (having a similar effect on the Network Operator’s System as a Modification would have on the National Electricity Transmission System) to the connection within the Network Operator’s System, each of which shall be termed an “Embedded Development” in the PC (where a User Development has an impact on the Network Operator’s System details shall be supplied in accordance with PC.4.4 and PC.4.5);

(b)	the relevant Standard Planning Data as listed in Part 1 of Appendix A;

(c)	the proposed completion date (having a similar meaning in relation to the Network Operator’s System as Completion Date would have in relation to the National Electricity Transmission System) of the Embedded Development; and

(d)	upon the request of The Company, the relevant Detailed Planning Data as listed in Part 2 of Appendix A.

PC.4.4.4	The Network Operator shall provide the Detailed Planning Data as listed in Part 1 of Appendix A. In respect of DPD I, this shall generally be provided within 28 days (or such shorter period as The Company may determine, or such longer period as The Company may agree, in any particular case) of entry into the Embedded Development Agreement and in respect to DPD II this shall generally be provided at least two years (or such longer period as The Company may determine, or such shorter period as The Company may agree, in any particular case) prior to the Completion Date of the Embedded Development.

PC.4.5	Complex Connections

PC.4.5.1	The magnitude and complexity of any National Electricity Transmission System extension or reinforcement will vary according to the nature, location and timing of the proposed User Development which is the subject of the application and it may, in the event, be necessary for The Company to carry out additional more extensive system studies to evaluate more fully the impact of the proposed User Development on the National Electricity Transmission System. Where The Company judges that such additional more detailed studies are necessary the offer may indicate the areas that require more detailed analysis and before such additional studies are required, the User shall indicate whether it wishes The Company to undertake the work necessary to proceed to make a revised offer within the 3 month period normally allowed or, where relevant, the timescale consented to by the Authority.

PC.4.5.2	To enable The Company to carry out any of the above mentioned necessary detailed system studies, the User may, at the request of The Company, be required to provide some or all of the Detailed Planning Data listed in part 2 of Appendix A in advance of the normal timescale referred in PC.4.4.2 provided that The Company can reasonably demonstrate that it is relevant and necessary.

PC.4.5.3	To enable The Company to carry out any necessary detailed system studies, the relevant Network Operator may, at the request of The Company, be required to provide some or all of the Detailed Planning Data listed in Part 2 of Appendix A in advance of the normal timescale referred in PC.4.4.4 provided that The Company can reasonably demonstrate that it is relevant and necessary.

# PC.5	PLANNING DATA

PC.5.1	As far as the PC is concerned, there are three relevant levels of data in relation to Users.  These levels, which relate to levels of confidentiality, commitment and validation, are described in the following paragraphs.

Preliminary Project Planning Data

PC.5.2	At the time the User applies for a CUSC Contract but before an offer is made and accepted by the applicant User, the data relating to the proposed User Development will be considered as Preliminary Project Planning Data. Data relating to an Embedded Development provided by a Network Operator in accordance with PC.4.4.3, and PC.4.4.4 if requested, will be considered as Preliminary Project Planning Data.  All such data will be treated as confidential within the scope of the provisions relating to confidentiality in the CUSC.

PC.5.3	Preliminary Project Planning Data will normally only contain the Standard Planning Data unless the Detailed Planning Data is required in advance of the normal timescale to enable The Company to carry out additional detailed system studies as described in PC.4.5.

Committed Project Planning Data

PC.5.4	Once the offer for a CUSC Contract is accepted, the data relating to the User Development already submitted as Preliminary Project Planning Data, and subsequent data required by The Company under this PC, will become Committed Project Planning Data.  Once an Embedded Person has entered into an Embedded Development Agreement, as notified to The Company by the Network Operator, the data relating to the Embedded Development already submitted as Preliminary Project Planning Data, and subsequent data required by The Company under the PC, will become Committed Project Planning Data.  Such data, together with Connection Entry Capacity and Transmission Entry Capacity data from the CUSC Contract and other data held by The Company relating to the National Electricity Transmission System will form the background against which new applications by any User will be considered and against which planning of the National Electricity Transmission System will be undertaken.  Accordingly, Committed Project Planning Data, Connection Entry Capacity and Transmission Entry Capacity data will not be treated as confidential to the extent that The Company:

(a)	is obliged to use it in the preparation of the Electricity Ten Year Statement and in any further information given pursuant to the Electricity Ten Year Statement;

(b)	is obliged to use it when considering and/or advising on applications (or possible applications) of other Users (including making use of it by giving data from it, both orally and in writing, to other Users making an application (or considering or discussing a possible application) which is, in The Company's view, relevant to that other application or possible application);

(c)	is obliged to use it for operational planning purposes;

(d)	is obliged under the terms of an Interconnection Agreement to pass it on as part of system information on the Total System;

(e)	is obliged to disclose it under the STC;

(f)	is obliged to use and disclose it in the preparation of the Offshore Development Information Statement;

(g)	is obliged to use it in order to carry out its EMR Functions or is obliged to disclose it under an EMR Document.

To reflect different types of data, Preliminary Project Planning Data and Committed Project Planning Data are themselves divided into:

(a)	those items of Standard Planning Data and Detailed Planning Data which will always be forecast, known as Forecast Data; and

(b)	those items of Standard Planning Data and Detailed Planning Data which relate to Plant and/or Apparatus which upon connection will become Registered Data, but which prior to connection, for the current Financial Year and the nine succeeding Financial Years, will be an estimate of what is expected, known as Estimated Registered Data.

Connected Planning Data

PC.5.5	The PC requires that, at the time that a Statement of Readiness is submitted under the Bilateral Agreement and/or Construction Agreement, any estimated values assumed for planning purposes are confirmed or, where practical, replaced by validated actual values and by updated estimates for the future and by updated forecasts for forecast data items such as Demand.  In the case of an Embedded Development the relevant Network Operator will update any estimated values assumed for planning purposes with validated actual values as soon as reasonably practicable after energisation.  This data is then termed Connected Planning Data.

To reflect the three types of data referred to above, Connected Planning Data is itself divided into:

(a)	those items of Standard Planning Data and Detailed Planning Data which will always be forecast data, known as Forecast Data; and

(b)	those items of Standard Planning Data and Detailed Planning Data which upon connection become fixed (subject to any subsequent changes), known as Registered Data; and

(c)	those items of Standard Planning Data and Detailed Planning Data which for the purposes of the Plant and/or Apparatus concerned as at the date of submission are Registered Data but which for the current Financial Year and the nine succeeding Financial Years will be an estimate of what is expected, known as Estimated Registered Data,

as more particularly provided in Appendix A.

PC.5.6	Connected Planning Data, together with Connection Entry Capacity and Transmission Entry Capacity data from the CUSC Contract, and other data held by The Company relating to the National Electricity Transmission System, will form the background against which new applications by any User will be considered and against which planning of the National Electricity Transmission System will be undertaken.  Accordingly, Connected Planning Data, Connection Entry Capacity and Transmission Entry Capacity data will not be treated as confidential to the extent that The Company:

(a)	is obliged to use it in the preparation of the Electricity Ten Year Statement and in any further information given pursuant to the Electricity Ten Year Statement;

(b)	is obliged to use it when considering and/or advising on applications (or possible applications) of other Users (including making use of it by giving data from it, both orally and in writing, to other Users making an application (or considering or discussing a possible application) which is, in The Company's view, relevant to that other application or possible application);

(c)	is obliged to use it for operational planning purposes;

(d)	is obliged under the terms of an Interconnection Agreement to pass it on as part of system information on the Total System.

(e)	is obliged to disclose it under the STC;

(f)	is obliged to use it in order to carry out its EMR Functions or is obliged to disclose it under an EMR Document.

PC.5.7	Committed Project Planning Data and Connected Planning Data will each contain both Standard Planning Data and Detailed Planning Data.

# PC.6	PLANNING STANDARDS

PC.6.1	The Company shall apply the Licence Standards relevant to it in the planning and development of the National Electricity Transmission System. The Company shall procure that each Relevant Transmission Licensee shall apply the Licence Standards relevant to planning and development, in the planning and development of the Transmission System of each Relevant Transmission Licensee and that a User shall apply the Licence Standards relevant to planning and development, in the planning and development of the OTSUA.

PC.6.2	In relation to Scotland, Appendix C lists the technical and design criteria applied in the planning and development of each Relevant Transmission Licensee's Transmission System.  The criteria are subject to review in accordance with each Relevant Transmission Licensee’s Transmission Licence conditions.  Copies of these documents are available from The Company on request.  The Company will charge an amount sufficient to recover its reasonable costs incurred in providing this service.

PC.6.3	In relation to Offshore, Appendix E lists the technical and design criteria applied in the planning and development of each Offshore Transmission System.  The criteria are subject to review in accordance with each Offshore Transmission Licensee’s Transmission Licence conditions.  Copies of these documents are available from The Company on request.  The Company will charge an amount sufficient to recover its reasonable costs incurred in providing this service.

PC.6.4	In planning and developing the OTSUA, the User shall comply with (and shall ensure that (as at the OTSUA Transfer Time) the OTSUA comply with):

(a)	the Licence Standards; and

(b)	the technical and design criteria in Appendix E.

PC.6.5	In addition the User shall, in the planning and development of the OTSUA, to the extent it is reasonable and practicable to do so, take into account the reasonable requests of The Company (in the context of its obligation to develop an efficient, co-ordinated and economical system) relating to the planning and development of the National Electricity Transmission System.

PC.6.6	In planning and developing the OTSUA the User shall take into account the Network Data provided to it by The Company under Part 3 of Appendix A and Appendix F, and act on the basis that the Plant and Apparatus of other Users complies with:

(a)	the minimum technical design and operational criteria and performance requirements set out in either CC.6.1, CC.6.2, CC.6.3 and CC.6.4 or ECC.6.1, ECC.6.2, ECC.6.3 and ECC.6.4 ; or

(b)	such other criteria or requirements as The Company may from time to time notify the User are applicable to specified Plant and Apparatus pursuant to PC.6.7.

PC.6.7	Where the OTSUA are likely to be materially affected by the design or operation of another User's Plant and Apparatus and The Company:

(a)	becomes aware that such other User has or is likely to apply for a derogation under the Grid Code;

(b)	is itself applying for a derogation under the Grid Code in relation to the Connection Site on which such other User's Plant and Apparatus is located or to which it otherwise relates; or

(c)	is otherwise notified by such other User that specified Plant or Apparatus is normally capable of operating at levels better than those set out in CC.6.1, CC.6.2, CC.6.3 and CC.6.4 or ECC.6.1, ECC.6.2, ECC.6.3 and ECC.6.4,

The Company shall notify the User.

# PC.7	PLANNING LIAISON

PC.7.1	This PC.7 applies to The Company and Users, which in PC.7 means

(a)	Network Operators

(b)	Non-Embedded Customers

PC.7.2	As described in PC.2.1 (b) an objective of the PC is to provide for the supply of information to The Company by Users in order that planning and development of the National Electricity Transmission System can be undertaken in accordance with the relevant Licence Standards.

PC.7.3	Grid Code amendment B/07 (“Amendment B/07”) implemented changes to the Grid Code which included amendments to the datasets provided by both The Company and Users to inform the planning and development of the National Electricity Transmission System.  The Authority has determined that these changes are to have a phased implementation.  Consequently the provisions of Appendix A to the PC include specific years (ranging from 2009 to 2011) with effect from which certain of the specific additional obligations brought about by Amendment B/07 on The Company and Users are to take effect.  Where specific provisions of paragraphs PC.A.4.1.4, PC.A.4.2.2 and PC.A.4.3.1 make reference to a year, then the obligation on The Company and the Users shall be required to be met by the relevant calendar week (as specified within such provision) in such year.

In addition to the phased implementation of aspects of Amendment B/07, Users must discuss and agree with The Company by no later than 31 March 2009 a more detailed implementation programme to facilitate the implementation of Grid Code amendment B/07.

It shall also be noted by The Company and Users that the dates set out in PC.A.4 are intended to be minimum requirements and are not intended to restrict a User and The Company from the earlier fulfilment of the new requirements prior to the specified years.  Where The Company and a User wish to follow the new requirements from earlier dates than those specified, this will be set out in the more detailed implementation programme agreed between The Company and the User.

The following provisions of PC.7 shall only apply with effect from 1 January 2011.

PC.7.4	Following the submission of data by a User in or after week 24 of each year The Company will provide information to Users by calendar week 6 of the following year regarding the results of any relevant assessment that has been made by The Company based upon such data submissions to verify whether Connection Points are compliant with the relevant Licence Standards.

PC.7.5	Where the result of any assessment identifies possible future non-compliance with the relevant Licence Standards, The Company shall notify the relevant User(s) of this fact as soon as reasonably practicable and shall agree with Users any opportunity to resubmit data to allow for a reassessment in accordance with PC.7.6.

PC.7.6	Following any notification by The Company to a User pursuant to PC.7.5 and following any further discussions held between the User and The Company:

(i)	The Company and the User may agree revisions to the Access Periods for relevant Transmission Interface Circuits, such revisions shall not however permit an Access Period to be less than 4 continuous weeks in duration or to occur other than between calendar weeks 10 and 43 (inclusive); and/or,

(ii)	The User shall as soon as reasonably practicable

(a)	submit further relevant data to The Company that is to The Company’s reasonable satisfaction; and/or,

(b)	modify data previously submitted pursuant to this PC, such modified data to be to The Company’s reasonable satisfaction; and/or

(c)	notify The Company that it is the intention of the User to leave the data as originally submitted to The Company to stand as its submission.

PC.7.7	Where an Access Period is amended pursuant to PC.7.6 (i) The Company shall notify The Authority that it has been necessary to do so.

PC.7.8	When it is agreed that any resubmission of data is unlikely to confirm future compliance with the relevant Licence Standards the Modification process in the CUSC may apply.

PC.7.9	A User may at any time, in writing, request further specified National Electricity Transmission System network data in order to provide The Company with viable User network data (as required under this PC).  Upon receipt of such request, The Company shall consider, and where appropriate provide such National Electricity Transmission System network data to the User as soon as reasonably practicable following the request.

# PC.8	OTSDUW PLANNING LIAISON

PC.8.1	This PC.8 applies to The Company and Users, which in PC.8 means Users undertaking OTSDUW.

PC.8.2	As described in PC.2.1 (e) an objective of the PC is to provide for the supply of information between The Company and a User undertaking OTSDUW in order that planning and development of the National Electricity Transmission System can be co-ordinated.

PC.8.3	Where the OTSUA also require works to be undertaken by any Relevant Transmission Licensee on its Transmission System The Company and the User shall throughout the construction and commissioning of such works:

(a)	co-operate and assist each other in the development of co-ordinated construction programmes or any other planning or, in the case of The Company, analysis it undertakes in respect of the works; and

(b)	provide to each other all information relating to, in the case of the User its own works and, in the case of The Company, the works on the Transmission Systems reasonably necessary to assist each other in the performance of that other's part of the works, and shall use all reasonable endeavours to co-ordinate and integrate their respective part of the works; and

the User shall plan and develop the OTSUA, taking into account to the extent that it is reasonable and practicable to do so the reasonable requests of The Company relating to the planning and development of the National Electricity Transmission System.

PC.8.4	Where The Company becomes aware that changes made to the investment plans of any Relevant Transmission Licensee may have a material effect on the OTSUA, The Company shall notify the User and provide the User with the necessary information about the relevant Transmission Systems sufficient for the User to assess the impact on the OTSUA.

# PC.9	SUBMISSION OF SYSTEM MODELS AND INFORMATION BY NETWORK OPERATORS TO THE COMPANY

PC.9.1	General

PC.9.1.1	PC.9 details the minimum planning data to be submitted by Network Operators to The Company.

PC.9.1.2	Compliance with the data submission requirements within PC.9 shall only apply after the PSM Implementation Date.

PC.9.1.3	The Network Operator shall use reasonable endeavours to obtain all applicable information required by PC.9 from any user connected to the Network Operator’s System, such that the information provided is the best information available at the time of submission.

PC.9.2 	Purpose

PC.9.2.1	The purpose of the data submission set out in PC.9 is to ensure that the Network Operators provide sufficient information to The Company so that it:

- Can provide information to the Relevant Transmission Licensee so that they can establish the previous, current, and future year’s compliance of the NETS with the NETS SQSS;

- Can provide information to the Relevant Transmission Licensee so that they can establish that the NETS complies with relevant technical standards;

- Can provide information to the Relevant Transmission Licensee so that they can establish that the NETS has sufficient capability to accommodate the connection of, and export from, Embedded Power Stations as considered in the CUSC Evaluation of Transmission Impact process; and

- Can create operational models for use in operational timescales.

PC.9.2.2	The Data Freeze Date for the submission in calendar week 2 shall be 31 October of the previous year. The Data Freeze Date for the submission in calendar week 28 shall be 31 March of that year.

PC.9.2.3	PC.9 uses definitions of Group Demand, Latent Demand, Measured Demand, Embedded Power Station Export, Embedded Power Station Import and Gross Demand. The interpretation of these definitions is illustrated in the stylised figure PC.9.2.3.

Figure PC.9.2.3

M1, M2 	measurement at the Connection Point

EGi 	import to Large Power Stations, Medium Power Stations and Small Power Stations other than to Electricity Storage Module(s)

EGe 	export from Large Power Stations, Medium Power Stations and Small Power Stations other than from Electricity Storage Module(s)

ESi 	import to Electricity Storage Module(s)

ESe 		export from Electricity Storage Module(s)

D	aggregated Embedded Customer Import

∆D		aggregated Latent Demand of Embedded Customers

Where:

Group Demand = D + ∆D

Group Demand = (M1 + M2) + (EGe + ESe) – (EGi + ESi) + ∆D

Latent Demand = ∆D

Gross Demand = (D + ∆D) + (EGi + ESi)

Embedded Power Station Export = EGe + ESe

Embedded Power Station Import = EGi + ESi

Measured Demand (Net Demand) = M1 + M2

PC.9.3	Submissions

PC.9.3.1	Submissions by the Network Operator to The Company include:

- Routine submissions each year in calendar week 2 and calendar week 28. These are described in PC.9.3.2 and PC.9.3.3 respectively. A diagram illustrating the coordination of submissions between the Network Operators and The Company is provided in PC.G.9; and

- Information provided as part of a CUSC Evaluation of Transmission Impact assessment application. This information is described in PC.9.3.4.

Nothing shall prevent the submission of data detailed in PC.9 at additional points during the year where agreed between The Company and the Network Operator.

At The Company’s reasonable request and where agreed by the Network Operator, additional data on the Network Operator’s System beyond that described in PC.9 shall be provided.

At The Company’s reasonable request and where agreed by the Network Operator additional information on the Network Operator’s forecasting methodologies relevant to PC.9 shall be provided.

PC.9.3.2	The data submitted in calendar week 2 shall comprise:

PC.9.3.2.1	A Solved PSM of the Network Operator’s System, which conforms to the Subtransmission PSM requirements as described in PC.9.4.2 and which includes:

- Structural Data as at the Data Freeze Date for the submission in calendar week 2;

- Situation Data corresponding to the date and time of NETS minimum demand as specified by The Company in calendar week 43 of the previous year;

- Solution Data resulting from a power flow calculation executed on the Structural Data and Situation Data;

- Solution Data which includes results from a minimum fault level study executed on the Structural Data and Situation Data; and

- Diagram Data describing diagrams of Structural Data and a subset of Situational Data.

PC.9.3.2.2	A PSM Scenario Document and a PSM Change Document, conforming with the requirements described in PC.G.5 and PC.G.6, respectively.

PC.9.3.2.3	A collection of individual Power System Difference Models (PSDMs) describing new or modified connections or proposed alterations to the Network Operator’s System that the Network Operator is aware of at the Data Freeze Date. Individual PSDMs shall be supplied for all of the following not represented in the Structural Data of the submitted Solved PSM:

- each new or modified generation and/or load connection where the relevant customer has accepted a connection offer from the Network Operator; and

- each authorised reinforcement, asset replacement scheme or similar related to the Network Operator’s System.

PC.9.3.2.4	A copy of Data Registration Code Schedule 21a, populated with demand and generation data corresponding to the date and time of the NETS minimum demand as specified by The Company in calendar week 43 of the previous year. Schedule 21a provides information including:

  - Group Demand and the export from Embedded Power Stations for each Connection Point at:

    - the date and time of NETS minimum demand specified by The Company; and

    - forecasts for future dates and times of NETS minimum demand specified by The Company.

PC.9.3.2.5	A copy of Data Registration Code Schedule 21b, populated with demand and generation data relating to a date and time established by the Network Operator as being the date and time of the Connection Point summer minimum Group Demand. This summer minimum relates to a time between the hours 04:00 and 06:00 (BST) between April to October inclusive. Schedule 21b provides information including:

  - Group Demand and the export from Embedded Power Stations for each Connection Point at:

    - the date and time of peak Connection Point summer minimum Group Demand.

PC.9.3.2.6	A copy of Data Registration Code Schedule 21c, populated with demand and generation data relating to a date and time established by the Network Operator as being the time and date of the Connection Point summer daylight minimum Group Demand. Summer daylight relates to a time between the hours 10:00 and 16:00 (BST) between April to October inclusive. Schedule 21c provides information including:

- Group Demand and the export from Embedded Power Stations for each Connection Point at:

  - The date and time of peak Connection Point summer daylight minimum Group Demand.

PC.9.3.2.7	A copy of Data Registration Code Schedule 22, populated with:

- The forecast half hourly Measured Demand (Active Power) profile for the Network Operator's System (summated over all Connection Points) for the dates of the forecast NETS minimum demand specified by The Company; and

- The aggregate export from all Embedded Power Stations at the forecast half-hourly NETS minimum demand.

PC.9.3.2.8	A copy of Data Registration Code Schedule 29a, populated with information about Embedded Power Stations with Registered Capacities greater than or equal to 1MW, that provides additional detail related to the generation modelling which is part of the Structural Data of the Solved PSM as described in PC.9.4.2.2.3.

PC.9.3.2.9	A copy of Data Registration Code Schedule 29b, populated with information for each Connection Point about Embedded Power Stations with Registered Capacities less than 1MW, that provides additional detail related to the generation modelling which is part of the Structural Data of the Solved PSM as described in PC.9.4.2.2.3.

PC.9.3.2.10	A copy of Data Registration Code Schedule 30, populated with information for each Connection Point detailing:

- Where a Network Operator’s System imposes constraints on the import to or export from a Generating Unit at an Embedded Large Power Station, the following data:

  - outturn and forecast constrained capacity (MW)

  - any Reactive Dispatch Network Restriction (MVAr)

For the avoidance of doubt, a Generating Unit as referred to above includes:

  - A CCGT Unit or Synchronous Generating Unit within a Synchronous Power Generating Module;

  - A Power Park Module (including DC Connected Power Park Modules);

  - An Offshore Transmission System at an Interface Point; or

  - An Embedded HVDC System or DC Converter at an Embedded DC Converter Station.

Constrained capacity is a limitation of the import to or export from a Generating Unit at an Embedded Large Power Station, due to the Network Operator’s System in which the Large Power Station is Embedded, arising from intrinsic limitations of the Network Operator’s System or an automated or manual control system designed to limit power flows in the Network Operator’s System in certain scenarios.

Where Generating Units are connected to a Network Operator’s System via a busbar arrangement which is or is expected to be operated in separate sections, details of busbar running arrangements and connected circuits at the substation to which the Embedded Generating Unit is connected, sufficient for The Company to determine where the MW generated by each Generating Unit would appear onto the NETS, shall be provided;

- Where a Network Operator System imposes constraints on the operation of an Offshore Transmission System at an Interface Point the following data:

  - outturn and forecast maximum import capacity (MW); and

  - outturn and forecast maximum export capacity (MW).

PC.9.3.3	The data submitted in calendar week 28 shall comprise:

PC.9.3.3.1	A Solved PSM of the Network Operator’s System, which conforms to the Subtransmission PSM requirements as described in PC.9.4.2 and which includes:

- Structural Data as at the Data Freeze Date for the submission in calendar week 28;

- Situation Data corresponding to the date and time of NETS peak demand as specified by The Company in calendar week 17;

- Solution Data resulting from a power flow calculation executed on the Structural Data and Situation Data;

- Solution Data which includes results from a maximum fault level study executed on the Structural Data and Situation Data; and

- Diagram Data describing diagrams of Structural Data and a subset of Situation Data.

PC.9.3.3.2	A PSM Scenario Document and a PSM Change Document, conforming with the requirements described in PC.G.5 and PC.G.6, respectively.

PC.9.3.3.3	A collection of individual PSDMs describing new or modified connections or proposed alterations to the Network Operator’s System that the Network Operator is aware of at the Data Freeze Date. Individual PSDMs shall be supplied for all of the following not represented in the Structural Data of the submitted Solved PSM:

- each new or modified generation and/or demand connection where the relevant customer has accepted a connection offer from the Network Operator; and

- each authorised reinforcement, asset replacement scheme or similar related to the Network Operators’ System.

PC.9.3.3.4	A copy of Data Registration Code Schedule 23a, populated with demand and generation data corresponding to the date and time of NETS peak demand as specified by The Company in calendar week 17. Schedule 23a provides information including:

- Group Demand and the export from Embedded Power Stations for each Connection Point at:

    - the date and time of NETS peak demand specified by The Company; and

    - forecasts for future dates and times of NETS peak demand specified by The Company.

PC.9.3.3.5	A copy of Data Registration Code Schedule 23b, populated with demand and generation data relating to a date and time established by the Network Operator as being the time and date of the Connection Point peak Group Demand. Schedule 23b provides information including:

- Group Demand and the export from Embedded Power Stations for each Connection Point at:

    - the time and date of Connection Point peak Group Demand; and

    - forecasts of the Connection Point peak Group Demand times and dates.

- Associated Connection Point data at the dates and times of Connection Point peak Group Demand. Where an associated Connection Point is normally operated in parallel with the Connection Point, consideration shall be given to presenting data for the associated Connection Point and the Connection Point as if it was a single Connection Point.

- A reference to any post fault actions, associated network reconfigurations and demand transfers which shall be described in more detail in the PSM Scenario Document.

PC.9.3.3.6	A copy of Data Registration Code Schedule 23c, populated with demand and generation data relating to a date and time established by the Network Operator as being the time and date of the Connection Point peak Group Demand during the Access Period. Schedule 23c provides information including:

- Group Demand and the export from Embedded Power Stations for each Connection Point at:

    - the date and time of the Connection Point peak Group Demand during the Access Period; and

    - forecasts for future dates and times of the Connection Point peak Group Demand during the Access Period.

- Associated Connection Point data at the date and time of Connection Point peak Group Demand during the Access Period. Where an associated Connection Point is normally operated in parallel with the Connection Point, consideration shall be given to presenting data for the associated Connection Point and the Connection Point as if it was a single Connection Point.

- A reference to any post fault actions, associated network reconfigurations and demand transfers which shall be described in more detail in the PSM Scenario Document.

PC.9.3.3.7	A copy of Data Registration Code Schedules 24, populated with Access Group(s) and with the associated Access Period data demonstrating the maintainability of the Transmission Interface Circuits.

PC.9.3.3.8	A copy of Data Registration Code Schedules 25a, 25b and 25c, populated in relation to Demand Control as described in OC.6.6.2, OC.6.5.3 and OC.6.7.2 respectively.

PC.9.3.3.9	A copy of Data Registration Code Schedule 26a, populated with:

- The forecast half hourly Measured Demand (Active Power) profile, under Annual ACS Conditions for the Network Operator's System (summated over all Connection Points) for the dates of the forecast yearly peak Measured Demand on the Network Operator's System (as determined by the Network Operator); and

- The forecast half-hourly Measured Demand (Active Power) with generation netted out for the Network Operator's System (summated over all Connection Points) for the days of the forecast yearly peak Measured Demand on the Network Operator's System (as determined by the Network Operator).

PC.9.3.3.10	A copy of Data Registration Code Schedule 26b, populated with:

- The forecast half hourly Measured Demand (Active Power) profile for the Network Operator's System (summated over all Connection Points) for the dates of the forecast NETS peak demand specified by The Company;

- The actual and Weather Corrected outturn half-hourly Measured Demand (Active Power) for the Network Operator’s System (summated over all Connection Points) for the half hour of the date and time of the NETS peak demand specified by The Company;

- The actual outturn Measured Demand (Active Power) with generation netted out on the Network Operator's System for the half-hour of the NETS peak demand specified by The Company; and

- The forecast half-hourly average Measured Demand (Active Power) with generation netted out for the Network Operator's System (summated over all Connection Points) for the dates of the forecast yearly NETS peak demand as specified by The Company.

PC.9.3.3.11	A copy of Data Registration Code Schedule 27, populated with the total Active Energy used on the Network Operator’s System (summated over all Connection Points) in the preceding Financial Year, both outturn and Weather Corrected, together with a forecast for the current Financial Year. Each Active Energy submission shall be subdivided into the following categories of Customer tariff:

      - LV1

      - LV2

      - LV3

      - HV

      - EHV

      - Traction

      - Public Lighting

In addition, the total Network Operator System losses and the Active Energy provided by Embedded Power Stations shall be supplied.

PC.9.3.3.12	A copy of Data Registration Code Schedule 28, populated with the Network Operator’s forecast of Power Station Registered Capacity aggregated by Aggregated Energy Source (as set out in PC.G.8.1), per Connection Point.

PC.9.3.3.13	A copy of Data Registration Code Schedule 29a, as described in PC.9.3.2.8, Schedule 29b as described in PC.9.3.2.9, and Schedule 30, as described in PC.9.3.2.10.

PC.9.3.4	The information in support of a request to The Company by a Network Operator for an Evaluation of Transmission Impact assessment shall comprise:

- Technical information in compliance with PC.9.4.2.2.3, as appropriate, and the proposed connection dates in respect of the Power Stations associated with the Evaluation of Transmission Impact assessment and a description of any proposed alteration to the Network Operator System required to accommodate the proposed connection(s); and

- A representation of the Network Operator System at the time of the proposed connection(s), either as a PSM or a combination of a PSM and PSDMs, as appropriate.

PC.9.4	Network Operator Subtransmission PSM

PC.9.4.1	Scope

PC.9.4.1.1	The Subtransmission PSM is intended to provide data sufficient for power system studies which support the activities outlined in PC.9.2.1, including:

- power flow calculations; and

- short circuit calculations in accordance with Engineering Recommendation G74.

Support for dynamic power system studies, including RMS dynamic stability type studies, is not required by the Subtransmission PSM.

PC.9.4.1.2	The scope of the Network Operator’s System to be represented by a Subtransmission PSM shall include:

- all parts of the Network Operator’s System operating at Supergrid Voltage;

- all parts of the Network Operator’s Subtransmission System operating at a nominal voltage greater than 30kV;

- all parts of the Network Operator’s Subtransmission System at any Transmission Site operating at a voltage of 30kV or less;

- Network Operator’s assets (including transformers and switchgear) at substations connecting the Network Operator’s Subtransmission System to a lower voltage;

- all parts of the Network Operator’s System operating at the voltage level below the Subtransmission System which, under either intact network or Planned Outage conditions:

- interconnects and operates in parallel between Connection Points; or

- interconnects busbars at a Connection Point, which are normally run as separate sections;

- the relevant assets in Power Stations connected to the Network Operator’s Subtransmission System;

- aggregated representation of Power Stations connected to a voltage less than that of the Subtransmission System;

- any OTSUA connected to the Network Operator’s System; and

- any parts of the Offshore Transmission System connected to the Network Operator’s System.

For the avoidance of doubt, any assets owned or operated by a Relevant Transmission Licensee shall not be included in the Subtransmission PSM.

PC.9.4.1.3	The Situation Data of all Subtransmission PSMs shall reflect an intact system, with each switching device in its normal operational state.

PC.9.4.2	Components of the Solved PSM

PC.9.4.2.1	The Solved PSM has three main types of data:

- Structural Data, which represents the components of a Network Operator’s System, including their capabilities and connectivity, at a specified date. The Structural Data of the Solved PSM describes the electrical characteristics of all relevant grid components within the scope set out in PC.9.4.1, including assets (for example overhead lines, underground cables, circuit breakers, switches, power transformers, reactive compensation equipment and similar equipment) including Generators’ assets;

- Situation Data, which represents an operational state of the system, under specific conditions (i.e. NETS peak demand and NETS minimum demand as specified by The Company). The Situation Data of the Solved PSM describes the appropriate circuit breaker and/or switch positions, generation/load injections, and transformer tap positions etc; and

- Solution Data, which represents the results of calculations executed using a coordinated set of Structural Data and Situation Data. The Solution Data of the Solved PSM includes both steady-state power flow calculation results (which include topology, voltage, and power flow data) and short circuit calculation results (which include short circuit power and current data).

PC.9.4.2.2	Structural Data

PC.9.4.2.2.1	All equipment in scope as set out in PC.9.4.1 shall be described by the Structural Data of the Solved PSM, including Network Operator assets, Generators’ assets and the load connection points. Where the Network Operator and The Company agree, a Solved PSM can also contain additional details of the Network Operator’s System.

PC.9.4.2.2.2	The following assets, with their associated data, shall be modelled:

- Circuit breakers and/or switches to facilitate network reconfiguration required to ensure compliance with relevant technical standards. For all circuit breakers and/or switches modelled, the supplied data shall be the data specified in PC.G.1, which includes information relating to any substation infrastructure where it limits the capability of the circuit breaker and/or switch. Alternatively, supplied circuit breaker and/or switch data may relate to the most restrictive equipment at that site;

- All transformers with their associated tap changers within the scope of the model. Supplied data shall be the data specified in PC.G.1;

- All circuits within the scope of the model. Supplied data shall be the data specified in PC.G.1;

- All reactive compensation assets, for example series compensators, shunt compensators and static VAr compensators, within the scope of the model. Supplied data shall be the data as specified in PC.G.1;

- All assets comprising an HVDC System within the scope of the model. Supplied data shall be the data specified in PC.G.1; and

- Any assets not specified above, but considered necessary as part of the Subtransmission PSM. Where the currently utilised data exchange specification does not support data about such assets, the data shall be exchanged by agreement between The Company and the Network Operator.

PC.9.4.2.2.3	Each Synchronous Power Generating Module and Power Park Module in a Power Station shall be modelled as follows:

- Where connected to the Subtransmission System, individually, at its actual grid location, accompanied by information regarding the substation assets via which it is connected to the Subtransmission System. In the case of each Power Park Module, the representation shall be an equivalent; and

- Where connected at a voltage below that of the Subtransmission System, as an aggregated equivalent, connected to the relevant substation busbar in the Subtransmission PSM, grouped by Aggregated Energy Source (as described in PC.G.8.1).

Supplied data shall be the data as specified in PC.G.1.

The sum of the generation Registered Capacities described in a) and b) above should equal the sum of generation Registered Capacities provided in Data Registration Code Schedules 29a and 29b.

Where The Company reasonably requires it, the Network Operator shall supply individual modelling of specific generation connected at a voltage level below the Subtransmission System.

PC.9.4.2.2.4	Load shall be modelled as follows:

- Each load connected to the Subtransmission System shall be represented as an equivalent, together with any associated substation assets, at the relevant Connection Point, recognising the existence of the following:

  - Identifiable large motors;

  - Any Synchronous Power Generating Modules or Power Park Modules in a Non-Embedded Customer’s site; and

  - Asynchronous motors that are not individually represented which form part of the general load, and which are modelled in accordance with Engineering Recommendation G74 requirements as a suitable equivalent motor.

- All load connected at a voltage below that of the Subtransmission System shall be represented as aggregated load equivalents connected to the relevant substation busbar in the Subtransmission PSM. The load object shall be modelled as per Engineering Recommendation G74 requirements.

Supplied data shall be the data specified in PC.G.1.

PC.9.4.2.2.5	Information including nominal voltage ratings and nominal current or Apparent Power ratings shall be provided for relevant equipment. Supplied data shall be the data specified in PC.G.1.

Normal capability/operational ratings, including seasonal and post-fault ratings, shall be stated according to the following guidelines:

- All busbars and connection nodes shall have operational voltage limits; and

- All circuits and transformers shall have current or Apparent Power operational ratings. Transformers shall have both normal direction flow ratings and reverse flow ratings.

The supplied normal capability/operational limits and ratings data shall be as specified in PC.G.1.

PC.9.4.2.2.6	At the Network Operator’s discretion the geospatial location of substations and lines may be included in the Structural Data.

PC.9.4.2.2.7	The Structural Data of the Subtransmission PSM shall connect to the Structural Data of PSMs of adjacent Systems by means of PSM Interface Nodes, which are points that represent a modelling boundary either side of which different parties are responsible for data. The grid locations of PSM Interface Nodes, shall be agreed by the parties based on the ownership boundaries detailed in Appendix A of the relevant Bilateral Agreements. The grid locations of PSM Interface Nodes, between Network Operators, shall be agreed by the parties. Additional detail on the application of PSM Interface Nodes is specified in PC.G.3.

PC.9.4.2.3	Situation Data

PC.9.4.2.3.1	The Solved PSMs required by PC.9.3.2.1 and PC.9.3.3.1 have Situation Data that might need to be adjusted to represent a specific NETS condition, for example NETS minimum or NETS peak demand.  This may arise for example if the Structural Data has changed between the date of the NETS condition and the Data Freeze Date or if there are permanent changes to the network topology.

PC.9.4.2.3.2	Situation Data correlating to the prescribed grid condition shall be provided for each relevant component present in the Structural Data of the Solved PSM as specified in PC.G.1.

PC.9.4.2.4	Solution Data

PC.9.4.2.4.1	Power flow Solution Data shall describe the results of a successful power flow calculation based on each specified set of Situation Data, and its related Structural Data.

PC.9.4.2.4.2	Short circuit Solution Data shall describe the results of a specific short circuit calculation based on each specified set of Situation Data, and its related Structural Data.

PC.9.4.2.5	Diagram Data

The Solved PSM shall include diagrams as described in PC.G.1.6.

PC.9.5	Assessment of Site Compliance

PC.9.5.1	The process that ensures the compliance and operability at Connection Points during the maintenance of Transmission Interface Circuits and the obligations of Network Operators in that process are detailed in PC.G.7.

PC.9.6	Confidentiality and Sharing

PC.9.6.1	The models, supporting documentation and associated data submitted to Network Operators pursuant to PC.10 are provided in order that Network Operators may carry out their responsibilities to meet their Electricity Distribution Licence obligations to develop an efficient, coordinated and economical Network Operator System. A Network Operator may share such models, supporting documents and associated data with companies/contractors employed by the Network Operator to carry out those responsibilities.

PC.9.6.2	A suitable, secure platform, to support the physical exchange of information submitted by Network Operators pursuant to PC.9 and The Company pursuant to PC.10, shall be established by The Company.

PC.9.6.3	A system shall be agreed and implemented by The Company and Network Operators to support the creation, editing, storage and retrieval by appropriate parties, of data related to the PSM Interface Nodes.

# PC.10	SUBMISSION OF SYSTEM MODELS AND INFORMATION BY THE COMPANY TO NETWORK OPERATORS

PC.10.1	General

PC.10.1.1	PC.10 details the planning data to be submitted by The Company to Network Operators.

PC.10.1.2	Compliance with the data submission requirements within PC.10 shall only apply after the PSM Implementation Date.

PC.10.1.3	The Company shall use reasonable endeavours to obtain all applicable information required by PC.10 from any User connected to the NETS and from Relevant Transmission Licensees, such that the information provided is the best information available at the time of submission.

PC.10.2 	Purpose

PC.10.2.1	The purpose of the data submission set out in PC.10 is to ensure that The Company provides sufficient information to Network Operators so that they:

- Have models of the NETS which can be used in the creation of the Network Operator’s own system model;

- Can establish that their distribution system complies with relevant technical standards; and

- Are aware of proposed changes to the NETS and connections to the NETS that may have an impact on the distribution system, hence facilitating a distribution impact assessment.

PC.10.3	Submissions

PC.10.3.1	Submissions by The Company to Network Operators include:

- Routine submissions each year in calendar week 12 and calendar week 38. These are described in PC.10.3.2 and PC.10.3.3 respectively. A diagram illustrating the coordination of submissions between the Network Operators and The Company is provided in PC.G.9; and

- Additional supplementary information when The Company reasonably believes that a new or modified User connection, or proposed alteration to the NETS may have an impact on a Network Operator’s System, or on request by the Network Operator. This information, together with the routine submissions, shall provide sufficient data so that the Network Operator can assess the impact of such a change, modification or alteration. The supplementary information is described in PC.10.3.4.

Nothing shall prevent the submission of data detailed in PC.10 at additional points during the year where agreed between The Company and the Network Operator(s).

At a Network Operator’s reasonable request and where agreed by The Company, additional data on the NETS beyond that described in PC.10 shall be provided by The Company, for example dynamic model data or more detailed HVDC System models.

PC.10.3.1.1	The Company shall use the information in the submission from Network Operators in calendar week 2 and calendar week 28:

- When establishing the forecast dates of the summer and winter Structural Data to be used in the Solved PSMs referred to in PC.10.3.2 and PC.10.3.3 respectively. Those dates shall be provided in the PSM Scenario Document. The Situation Data of the demand scenarios reflecting those dates and times shall be estimated by The Company based on historical information and forecasts of future demand and generation; and

- To derive, in a reasonable manner, a cohesive forecast to be used in preparing forecast demand information in the Electricity Ten Year Statement and for use in The Company's Operational Planning. If a Network Operator believes that the cohesive forecast Demand information in the Electricity Ten Year Statement does not reflect its assumptions on Demand, it should contact The Company to explain their concerns and may request that The Company explain the rationale underpinning these forecasts.

PC.10.3.1.2	The Company shall notify the Network Operators, in calendar week 43, of:

- The date and time of the most recent summer NETS minimum demand; and

- For the current Financial Year and for each of the following nine Financial Years, the forecast date and time of the NETS summer minimum demand.

PC.10.3.1.3	The Company shall notify the Network Operators, in calendar week 17, of:

- The date and time of the most recent winter NETS peak demand; and

- For the current Financial Year and for each of the following nine Financial Years, the forecast date and time of the NETS winter peak demand.

PC.10.3.2	The data submitted in calendar week 12 shall comprise:

PC.10.3.2.1	A set of Solved PSMs of the NETS which conform to the NETS PSM requirements as described in PC.10.4.2. Each Solved PSM shall be based on the same Structural Data, referred to as summer Structural Data, which reflects The Company’s best view of the System as it is expected to be at the date and time of the forthcoming summer minimum NETS demand and which contains asset characteristics sufficient to support both power flow and short circuit calculations. The set of Solved PSMs include:

- A NETS minimum demand Solved PSM which includes:

- Summer Structural Data;

- Situation Data corresponding to the date and time of the forecast NETS minimum demand between calendar weeks 13 and 43;

- Solution Data resulting from a power flow calculation executed on the Structural Data and Situation Data; and

- Diagram Data describing diagrams of Structural Data and a subset of Situational Data.

- A NETS minimum daylight demand Solved PSM which includes:

- Summer Structural Data;

- Situation Data corresponding to the date and time of the forecast NETS minimum demand during the period 10:00 to 16:00 between calendar weeks 13 and 43;

- Solution Data resulting from a power flow calculation executed on the Structural Data and Situation Data; and

- Diagram Data describing diagrams of Structural Data and a subset of Situational Data.

- A NETS low power transfer Solved PSM which includes:

- Summer Structural Data;

- Situation Data corresponding to the date and time of a forecast NETS low power transfer between calendar weeks 13 and 43;

- Solution Data resulting from a power flow calculation executed on the Structural Data and Situation Data; and

- Diagram Data describing diagrams of Structural Data and a subset of Situation Data.

- A NETS minimum fault level Solved PSM which includes:

- Summer Structural Data;

- Situation Data based on Situation Data of the NETS minimum demand Solved PSM, defined under PC.10.3.2.1 a), and additionally includes:

  - Demand short circuit contributions; and

  - All active generation connected and energised to the System;

Solution Data reflecting the theoretical minimum NETS bus fault levels which results from short circuit calculations executed on the Structural Data and Situation Data; and

- Solution Data resulting from a short circuit calculation executed on the Structural Data and Situation Data; and

- Diagram Data describing diagrams of Structural Data and a subset of Situation Data.

Where two or more of the Solved PSMs defined under PC.10.3.2.1 are identical, only a single Solved PSM need be provided for those conditions. The conditions represented by such a single Solved PSM shall be described in the PSM Scenario Document.

PC.10.3.2.2	A PSM Scenario Document and a PSM Change Document, conformant to the requirements described in PC.G.5 and PC.G.6, respectively.

PC.10.3.2.3	A collection of individual PSDMs describing new or modified User connections or proposed alterations to the NETS that The Company reasonably believes may have a material impact on this submission’s set of Solved PSMs. Individual PSDMs shall be supplied for:

- each new or modified generation and/or load connection not represented in the summer Structural Data where the relevant customer has accepted a connection offer from The Company to connect to the NETS; and

- each authorised NETS reinforcement, asset replacement scheme or similar not included in the summer Structural Data.

PC.10.3.3	The data submitted in calendar week 38 shall comprise:

PC.10.3.3.1	A set of Solved PSMs of the NETS which conform to the NETS PSM requirements as described in PC.10.4.2. Each Solved PSM shall be based on the same Structural Data, referred to as winter Structural Data, which reflects The Company’s best view of the System as it is expected to be at the date and time of the forthcoming winter peak NETS demand and which contains asset characteristics sufficient to support both power flow and short circuit calculations. The set of Solved PSMs include:

- A NETS peak demand Solved PSM which includes:

- Winter Structural Data;

- Situation Data corresponding to the date and time of the forecast NETS peak demand between calendar weeks 43 and 13;

- Solution Data resulting from a power flow calculation executed on the Structural Data and Situation Data; and

- Diagram Data describing diagrams of Structural Data and a subset of Situation Data.

- For the current Financial Year and for each of the following nine Financial Years, the forecast date and time of the NETS winter peak demand high power transfer Solved PSM which includes:

- Winter Structural Data;

- Situation Data corresponding to the date and time of a forecast NETS high power transfer between calendar weeks 43 and 13;

- Solution Data resulting from a power flow calculation executed on the Structural Data and Situation Data; and

- Diagram Data describing diagrams of Structural Data and a subset of Situation Data.

- A NETS maximum fault level Solved PSM which includes:

- Winter Structural Data;

- Situation Data based on Situation Data of the maximum demand Solved PSM, defined under PC.10.3.3.1 a), and additionally includes:

  - Demand short circuit contributions; and

  - All generation connected and energised to the System;

Solution Data reflecting the theoretical maximum NETS bus fault levels which results from short circuit calculations executed on the Structural Data and Situation Data; and

- Diagram Data describing diagrams of Structural Data and a subset of Situation Data.

Where two or more of the Solved PSMs defined under PC.10.3.3.1 are identical, only a single Solved PSM need be provided for these conditions. The conditions represented by such a single Solved PSM shall be described in the PSM Scenario Document.

PC.10.3.3.2	A PSM Scenario Document and a PSM Change Document, conformant to the requirements described in PC.G.5 and PC.G.6, respectively.

PC.10.3.3.3	A collection of individual PSDMs describing new or modified User connections or proposed alterations to the NETS that The Company reasonably believes may have a material impact on this submission’s set of Solved PSMs. Individual PSDMs shall be supplied for:

- Each new or modified generation and/or load connection not represented in the winter Structural Data where the relevant customer has accepted a connection offer from The Company to connect to the NETS; and

- Each authorised NETS reinforcement, asset replacement scheme or similar not included in the winter Structural Data.

PC.10.3.4	The supplementary information required under the conditions outlined in PC.10.3.1 b) shall comprise:

- A PSDM describing the new or modified User connection or proposed alteration to the NETS; and

- A representation of the NETS and its User connections at the time the new or modified User connection, or proposed NETS alteration is planned to be commissioned, supplied in the form of an updated Structural Data file or Solved PSM and PSDMs as required, where:

  - The PSM reflects the time of commissioning; or

  - The PSM reflects any earlier time supplemented by PSDMs sufficient to enable updating of the PSM to reflect the time of commissioning.

PC.10.4	The Company’s NETS PSM

PC.10.4.1	Scope

PC.10.4.1.1	The NETS PSM(s) is intended to provide data sufficient for power system studies which support the activities outlined in PC.10.2.1, including:

- power flow calculations; and

- short circuit calculations in accordance with Engineering Recommendation G74.

Support for dynamic power system studies, including RMS dynamic stability type studies, is not required in the NETS PSM.

PC.10.4.1.2	The scope of the NETS PSM includes the entirety of the NETS, including any HVDC Systems, together with equivalent representation of Users’ Systems, connected to the NETS.

PC.10.4.1.3	The Structural Data of the NETS PSM shall include:

- all assets forming the NETS including transformers and switchgear at substations connecting Users to the NETS;

- the relevant assets in Power Stations directly connected to the NETS;

- the relevant assets of Non-Embedded Customers, aggregated;

- a representation of Power Stations and the load, which shall be modelled as per Engineering Recommendation G74 requirements; and

- any OTSUA connected to the NETS.

For the avoidance of doubt, any assets owned or operated by a Network Operator shall not be included in the NETS PSM.

PC.10.4.1.4	The Situation Data of all NETS PSMs shall reflect an intact system, with each switching device in its normal operational state.

PC.10.4.2	Components of the Solved PSM

PC.10.4.2.1	The Solved PSM has three main types of data:

- Structural Data, which represents the equipment forming the NETS, including their capabilities and connectivity, at a specified date. The Structural Data of the Solved PSM describes the electrical characteristics of all relevant NETS equipment within the scope set out in PC.10.4.1, including assets (for example overhead lines, underground cables, circuit breakers, switches, power transformers, reactive compensation equipment, quadrature boosters, and similar equipment) as well as Generators’ assets and the load connection points;

- Situation Data, which represents an operational state of the System, under specific conditions (i.e. NETS peak and NETS minimum as specified by The Company). The Situation Data of the Solved PSM describes the appropriate circuit breaker and/or switch positions, generation/load injections, and transformer tap positions etc.; and

- Solution Data, which represents the results of calculations executed using a coordinated set of Structural Data and Situation Data. The Solution Data of the Solved PSM can represent either steady-state power flow calculation results (which include topology, voltage, and power flow data) or short circuit calculation results (which include short circuit power and current data).

PC.10.4.2.2	Structural Data

PC.10.4.2.2.1	All equipment in scope as set out in PC.10.4.1 shall be described by the Structural Data of the Solved PSM.

PC.10.4.2.2.2	The following assets, with their associated data, shall be modelled:

- All circuit breakers within the scope of the model and switches that are required to facilitate system reconfiguration. For all circuit breakers and/or switches modelled, the supplied data shall be the data specified in PC.G.1, which includes information relating to any substation infrastructure where it limits the capability of the circuit breaker and/or switch. Alternatively, supplied circuit breaker and/or switch data may relate to the most restrictive equipment at that site;

- All transformers (including quadrature boosters) with their associated tap changers within the scope of the model. Supplied data shall be the data specified in PC.G.1;

- All circuits within the scope of the model. Supplied data shall be the data specified in PC.G.1;

- All reactive compensation assets, for example series compensators, shunt compensators and static VAr compensators, within the scope of the model. Supplied data shall be the data specified in PC.G.1;

- All assets comprising an HVDC System within the scope of the model. Supplied data shall be the data specified in PC.G.1.

In relation to HVDC Systems where not all the HVDC Interface Points connect to the NETS, the model may include an equivalent representation of the HVDC System. Reference to the operation of these equivalents shall be made in the PSM Scenario Document; and

- Any assets not specified above, but considered necessary as part of the NETS PSM. Where the currently utilised data exchange specification does not support data about such assets, the data shall be exchanged by agreement.

PC.10.4.2.2.3	Synchronous Power Generating Modules in Power Stations shall be individually represented, and accompanied by information regarding the substation assets, at the relevant Connection Point. Power Park Modules in Power Stations shall be represented as an equivalent, together with any associated substation assets, at the relevant Connection Point. Supplied data shall be the data specified in PC.G.1.

PC.10.4.2.2.4	Non-Embedded Customer’s assets shall be represented as an equivalent, together with any associated substation assets, at the relevant Connection Point, recognising the existence of the following:

  - Identifiable large motors;

  - Any Synchronous Power Generating Modules or Power Park Modules in a Non-Embedded Customer’s site; and

  - Asynchronous motors that are not individually represented which form part of the general load and which are modelled, in accordance with Engineering Recommendation G74 requirements as a suitable equivalent motor.

Supplied data shall be the data specified in PC.G.1.

PC.10.4.2.2.5 	Information including nominal voltage ratings and nominal current or Apparent Power ratings shall be provided for relevant equipment. Supplied data shall be the data specified in PC.G.1.

Normal capability/operational ratings, including seasonal and post-fault ratings, shall be stated according to the following guidelines:

- All busbars and connection nodes shall have operational voltage limits; and

- All circuits and transformers shall have current or Apparent Power operational ratings. Transformers shall have both normal direction flow ratings and reverse flow ratings.

The supplied normal capability/operational limits and ratings data shall be as specified in PC.G.1.

PC.10.4.2.2.6	At The Company’s discretion the geospatial location of substations and lines may be modelled.

PC.10.4.2.2.7	The Structural Data of the NETS PSM shall connect to the Structural Data of Subtransmission PSMs by means of PSM Interface Nodes, which are points that represent a modelling boundary either side of which different parties are responsible for data. The grid locations of PSM Interface Nodes shall be agreed by the relevant parties based on the ownership boundaries detailed in Appendix A of the relevant Bilateral Agreements. Additional detail on the application of PSM Interface Nodes is specified in PC.G.3.

PC.10.4.2.3	Situation Data

PC.10.4.2.3.1	Both the summer and winter Structural Data sets shall have one or more sets of related Situation Data reflecting each of the forecast operational conditions set out in PC.10.3.2.1 and PC.10.3.3.1.

PC.10.4.2.3.2	Situation Data correlating to the prescribed grid condition shall be provided for each relevant component present in the Structural Data of the Solved PSM as specified in PC.G.1.

PC.10.4.2.4	Solution Data

PC.10.4.2.4.1	Power flow Solution Data shall describe the results of a successful power flow calculation based on each specified set of Situation Data, and its related Structural Data.

PC.10.4.2.4.2	Short circuit Solution Data shall describe the results of a specific short circuit calculation based on each specified set of Situation Data, and its related Structural Data.

PC.10.4.2.5	Diagram Data

The Solved PSM shall include diagrams as described in PC.G.1.6.

PC.10.5	Assessment of Site Compliance

PC.10.5.1	The process to ensure the compliance and operability at Connection Points during the maintenance of Transmission Interface Circuit and the obligations of The Company in that process are detailed in PC.G.7.

PC.10.5.2	The Company shall, no later than calendar week 7 of each year, in accordance with the requirements of PC.G.7.5, provide each Network Operator with a proposed Transmission Interface Circuit outage plan in the form of a draft version of Schedule 24.

PC.10.5.3	The Company shall notify The Authority, where an Access Period is amended pursuant to PC.G.7.11 (b).

PC.10.5.4	Following the submission of data by a Network Operator by calendar week 28 of each year, The Company shall, by calendar week 6 of the following year, submit in writing to the Network Operator, the assessment results detailed in PC.G.7.13.

PC.10.6	Confidentiality and Sharing

PC.10.6.1	The models, supporting documentation and associated data submitted to The Company pursuant to PC.9 are provided in order that The Company and Transmission Licensees may carry out their responsibilities to meet their electricity transmission Licence obligations to develop efficient, coordinated and economical NETS and Transmission Systems. The Company and Transmission Licensees may share such models, supporting document and associated data with companies/contractors employed by The Company and Transmission Licensees to carry out those responsibilities.

PC.10.6.2	A suitable, secure platform shall be agreed and implemented by The Company and Network Operators to support the physical exchange of information submitted by Network Operators and The Company.

PC.10.6.3	A system shall be agreed and implemented by The Company and Network Operators to support the creation, editing, storage and retrieval by appropriate parties, of data related to the PSM Interface Nodes.

# APPENDIX A - PLANNING DATA REQUIREMENTS

PC.A.1	INTRODUCTION

PC.A.1.1	Appendix A specifies data requirements to be submitted to The Company by Users, and in certain circumstances to Users by The Company.

PC.A.1.2	Submissions by Users

(a)	Planning data submissions by Users shall be:

(i)	with respect to the current Financial Year and each of the nine succeeding Financial Years (other than in the case of Registered Data which will reflect the current position and data relating to Demand forecasts which relates also to the current year);

(ii)	provided by Users in connection with a CUSC Contract (PC.4.1, PC.4.4 and PC.4.5 refer);

(iii)	provided by Users on a routine annual basis in calendar week 24 of each year to maintain an up-to-date data bank (although Network Operators may delay the submission of data (other than that to be submitted pursuant to PC.3.2(c) and PC.3.2(d)) until calendar week 28).  In addition the structural data in DRC Schedule 5 Tables 5(a), 5(b), 5(d), 5(e) , 5(f) and DRC Schedule 13 (Lumped system susceptance (PC.A.2.3) only) provided by Network Operators by calendar week 28 shall be updated by calendar week 50 of each year (again which may be delayed as above until week 2 of the following calendar year). Where from the date of one annual (or in the case of Schedule 5 or Schedule 13 the calendar week 50) submission to another there is no change in the data (or in some of the data) to be submitted, instead of re-submitting the data, a User may submit a written statement that there has been no change from the data (or some of the data) submitted the previous time; and

(iv)	provided by Network Operators in connection with Embedded Development (PC.4.4 refers).

(b)	Where there is any change (or anticipated change) in Committed Project Planning Data or a significant change in Connected Planning Data in the category of Forecast Data or any change (or anticipated change) in Connected Planning Data in the categories of Registered Data or Estimated Registered Data supplied to The Company under the PC, notwithstanding that the change may subsequently be notified to The Company under the PC as part of the routine annual update of data (or that the change may be a Modification under the CUSC), the User shall, subject to PC.A.3.2.3 and PC.A.3.2.4, notify The Company in writing without delay.

(c)	The notification of the change will be in the form required under this PC in relation to the supply of that data and will also contain the following information:

(i)	the time and date at which the change became, or is expected to become, effective;

(ii)	if the change is only temporary, an estimate of the time and date at which the data will revert to the previous registered form.

(d)	The routine annual update of data, referred to in (a)(iii) above, need not be submitted in respect of Small Power Stations or Embedded installations of direct current converters which do not form a DC Converter Station or HVDC System (except as provided in PC.3.2.(c)), or unless specifically requested by The Company, or unless otherwise specifically provided.

PC.A.1.3	Submissions by The Company

Network Data release by The Company shall be:

(a)	with respect to the current Financial Year;

(b)	provided by The Company on a routine annual basis in calendar week 42 of each year. Where from the date of one annual submission to another there is no change in the data (or in some of the data) to be released, instead of repeating the data, The Company may release a written statement that there has been no change from the data (or some of the data) released the previous time.

The three parts of Appendix A

PC.A.1.4	The data requirements listed in this Appendix are subdivided into the following four parts:

(a)	Standard Planning Data

This data (as listed in Part 1 of Appendix A) is first to be provided by a User at the time of an application for a CUSC Contract or in accordance with PC.4.4.3.  It comprises data which is expected normally to be sufficient for The Company to investigate the impact on the National Electricity Transmission System of any User Development or Embedded Development associated with an application by the User for a CUSC Contract.  Users should note that the term Standard Planning Data also includes the information referred to in PC.4.4.1.(a) and PC.4.4.3.(a). In the case of OTSUA, this data is first to be provided by a User in accordance with the time line in Appendix F.

(b)	Detailed Planning Data

This data (as listed in Part 2 of Appendix A) includes both DPD I and DPD II and is to be provided in accordance with PC.4.4.2 and PC.4.4.4.  It comprises additional, more detailed, data not normally expected to be required by The Company to investigate the impact on the National Electricity Transmission System of any User Development associated with an application by the User for a CUSC Contract or Embedded Development Agreement.  Users and Network Operators in respect of Embedded Developments should note that the term Detailed Planning Data also includes Operation Diagrams and Site Common Drawings produced in accordance with the CC and ECC.

The User may, however, be required by The Company to provide the Detailed Planning Data in advance of the normal timescale before The Company can make an offer for a CUSC Contract, as explained in PC.4.5.

(c)	Network Data

The data requirements for The Company in this Appendix are in Part 3.

(d)	Offshore Transmission System (OTSDUW) Data

Generators who are undertaking OTSDUW are required to submit data in accordance with Appendix A as summarised in Schedule 18 of the Data Registration Code.

Forecast Data, Registered Data and Estimated Registered Data

PC.A.1.5	As explained in PC.5.4 and PC.5.5, Planning Data is divided into:

(i)	those items of Standard Planning Data and Detailed Planning Data known as Forecast Data; and

(ii)	those items of Standard Planning Data and Detailed Planning Data known as Registered Data; and

(iii)	those items of Standard Planning Data and Detailed Planning Data known as Estimated Registered Data.

PC.A.1.6	The following paragraphs in this Appendix relate to Forecast Data:

3.2.2(b),  (h), (i) and (j)

4.2.1

4.3.1

4.3.2

4.3.3

4.3.4

4.3.5

4.5

4.7.1

5.2.1

5.2.2

5.6.1

PC.A.1.7	The following paragraphs in this Appendix relate to Registered Data and Estimated Registered Data:

2.2.1

2.2.4

2.2.5

2.2.6

2.3.1

2.4.1

2.4.2

3.2.2(a), (c), (d), (e), (f), (g), (i)(part) and (j)

3.4.1

3.4.2

4.2.3

4.5(a)(i), (a)(iii), (b)(i) and (b)(iii)

4.6

5.3.2

5.4

5.4.2

5.4.3

5.5

5.6.3

6.2

6.3

PC.A.1.8	The data supplied under PC.A.3.3.1, although in the nature of Registered Data, is only supplied either upon application for a CUSC Contract, or in accordance with PC.4.4.3, and therefore does not fall to be Registered Data, but is Estimated Registered Data.

PC.A.1.9	Forecast Data must contain the User's best forecast of the data being forecast, acting as a reasonable and prudent User in all the circumstances.

PC.A.1.10	Registered Data must contain validated actual values, parameters or other information (as the case may be) which replace the estimated values, parameters or other information (as the case may be) which were given in relation to those data items when they were Preliminary Project Planning Data and Committed Project Planning Data, or in the case of changes, which replace earlier actual values, parameters or other information (as the case may be).  Until amended pursuant to the Grid Code, these actual values, parameters or other information (as the case may be) will be the basis upon which the National Electricity Transmission System is planned, designed, built and operated in accordance with, amongst other things, the Transmission Licence and the ESO Licence, the STC and the Grid Code, and on which The Company therefore relies.  In following the processes set out in the BC, The Company will use the data which has been supplied to it under the BC and the data supplied under OC2 in relation to Gensets, but the provision of such data will not alter the data supplied by Users under the PC, which may only be amended as provided in the PC.

PC.A.1.11	Estimated Registered Data must contain the User's best estimate of the values, parameters or other information (as the case may be), acting as a reasonable and prudent User in all the circumstances.

PC.A.1.12	Certain data does not need to be supplied in relation to Embedded Power Stations or Embedded DC Converter Stations or Embedded HVDC Systems where these are connected at a voltage level below the voltage level directly connected to the National Electricity Transmission System except in connection with a CUSC Contract, or unless specifically requested by The Company.

PC.A.1.13	In the case of OTSUA, Schedule 18 of the Data Registration Code shall be construed in such a manner as to achieve the intent of such provisions by reference to the OTSUA and the Interface Point and all Connection Points.

## PART 1 - STANDARD PLANNING DATA

### PC.A.2	USER'S SYSTEM (AND OTSUA) DATA

PC.A.2.1	Introduction

PC.A.2.1.1	Each User, whether connected directly via an existing Connection Point to the National Electricity Transmission System, or seeking such a direct connection, or providing terms for connection of an Offshore Transmission System to its User System to The Company, shall provide The Company with data on its User System (and any OTSUA) which relates to the Connection Site (and in the case of OTSUA, the Interface Point)  and/or which may have a system effect on the performance of the National Electricity Transmission System. Such data, current and forecast, is specified in PC.A.2.2 to PC.A.2.5. In addition each Generator in respect of its Embedded Large Power Stations and its Embedded Medium Power Stations subject to a Bilateral Agreement and each Network Operator in respect of Embedded Medium Power Stations within its System not subject to a Bilateral Agreement connected to the Subtransmission System, shall provide The Company with fault infeed data as specified in PC.A.2.5.5 and each DC Converter owner with Embedded DC Converter Stations subject to a Bilateral Agreement and Embedded HVDC System Owner subject to a Bilateral Agreement, or Network Operator in the case of Embedded DC Converter Stations not subject to a Bilateral Agreement or Embedded HVDC Systems not subject to a Bilateral Agreement, connected to the Subtransmission System shall provide The Company with fault infeed data as specified in PC.A.2.5.6.

PC.A.2.1.2	Each User must reflect the system effect at the Connection Site(s) of any third party Embedded within its User System whether existing or proposed.

PC.A.2.1.3	Although not itemised here, each User with an existing or proposed Embedded Small Power Station, Embedded Medium Power Station,  Embedded DC Converter Station or HVDC System with a Registered Capacity of less than 100MW or an Embedded installation of direct current converters which does not form a DC Converter Station or HVDC System in its User System may, at The Company's reasonable discretion, be required to provide additional details relating to the User's System between the Connection Site and the existing or proposed Embedded Small Power Station, Embedded Medium Power Station, Embedded DC Converter Station, Embedded HVDC System or Embedded installation of direct current converters which does not form a DC Converter Station or Embedded installation which does not form an HVDC System.

PC.A.2.1.4	At The Company’s reasonable request, additional data on the User’s System (or OTSUA) will need to be supplied.  Some of the possible reasons for such a request, and the data required, are given in PC.A.6.2, PC.A.6.4, PC.A.6.5 and PC.A.6.6.

PC.A.2.2	User's System (and OTSUA) Layout

PC.A.2.2.1	Each User shall provide a Single Line Diagram, depicting both its existing and proposed arrangement(s) of load current carrying Apparatus relating to both existing and proposed Connection Points (including in the case of OTSUA, Interface Points).

PC.A.2.2.2	The Single Line Diagram (three examples are shown in Appendix B) must include all parts of the User System operating at Supergrid Voltage throughout Great Britain and, in Scotland and Offshore, also all parts of the User System operating at 132kV or greater, and those parts of its Subtransmission System at any Transmission Site. In the case of OTSDUW, the Single Line Diagram must also include the OTSUA. In addition, the Single Line Diagram must include all parts of the User’s Subtransmission System (and any OTSUA) throughout Great Britain operating at a voltage greater than 50kV, and, in Scotland and Offshore, also all parts of the User’s Subtransmission System (and any OTSUA) operating at a voltage greater than 30kV, which, under either intact network or Planned Outage conditions:

(a) 	normally interconnects separate Connection Points, or busbars at a Connection Point which are normally run in separate sections; or

(b)	connects Embedded Large Power Stations, or Embedded Medium Power Stations, or Embedded DC Converter Stations, or Embedded HVDC Systems or Offshore Transmission Systems connected to the User’s Subtransmission System, to a Connection Point or Interface Point.

At the User’s discretion, the Single Line Diagram can also contain additional details of the User’s Subtransmission System (and any OTSUA) not already included above, and also details of the transformers connecting the User’s Subtransmission System to a lower voltage.  With The Company’s agreement, the Single Line Diagram can also contain information about the User’s System (and any OTSUA) at a voltage below the voltage of the Subtransmission System.

The Single Line Diagram for a Power Park Module (including DC Connected Power Park Modules) must include all parts of the System connecting generating equipment to the Grid Entry Point (or User System Entry Point if Embedded). As an alternative, the User may choose to submit a Single Line Diagram with the equipment between the equivalent Power Park Unit and the Common Collection Busbar reduced to an electrically equivalent network.  The format for a Single Line Diagram for a Power Park Module (including DC Connected Power Park Modules) electrically equivalent system is shown in Appendix B.

The Single Line Diagram must include the points at which Demand data (provided under PC.A.4.3.4 and PC.A.4.3.5, or in the case of Generators, PC.A.5.) and fault infeed data (provided under PC.A.2.5) are supplied.

PC.A.2.2.3	The above-mentioned Single Line Diagram shall include:

(a)	electrical circuitry (i.e. overhead lines, identifying which circuits are on the same towers, underground cables, power transformers, reactive compensation equipment and similar equipment); and

(b)	substation names (in full or abbreviated form) with operating voltages.

In addition, for all load current carrying Apparatus operating at Supergrid Voltage throughout Great Britain and, in Scotland and Offshore, also at 132kV or greater, (and any OTSUA) the Single Line Diagram shall include:

(a)	circuit breakers

(b)	phasing arrangements.

PC.A.2.2.3.1	For the avoidance of doubt, the Single Line Diagram to be supplied is in addition to the Operation Diagram supplied pursuant to CC.7.4 or ECC.7.4.

PC.A.2.2.4	For each circuit shown on the Single Line Diagram provided under PC.A.2.2.1, each User shall provide the following details relating to that part of its User System and OTSUA:

Circuit Parameters:

Rated voltage (kV)

Operating voltage (kV)

Positive phase sequence reactance

Positive phase sequence resistance

Positive phase sequence susceptance

Zero phase sequence reactance (both self and mutual)

Zero phase sequence resistance (both self and mutual)

Zero phase sequence susceptance (both self and mutual)

In the case of a Single Line Diagram for a Power Park Module (including DC Connected Power Park Modules) electrically equivalent system the data should be on a 100MVA base. Depending on the equivalent system supplied an equivalent tap changer range may need to be supplied. Similarly mutual values, rated voltage and operating voltage may be inappropriate. Additionally in the case of OTSUA, seasonal maximum continuous ratings and circuit lengths are to be provided in addition to the data required under PC.A.2.2.4.

PC.A.2.2.5	For each transformer shown on the Single Line Diagram provided under PC.A.2.2.1, each User (including those undertaking OTSDUW) shall provide the following details:

Rated MVA

Voltage Ratio

Winding arrangement

Positive sequence reactance (max, min and nominal tap)

Positive sequence resistance (max, min and nominal tap)

Zero sequence reactance

PC.A.2.2.5.1.	In addition, for all interconnecting transformers between the User's Supergrid Voltage System and the User's Subtransmission System throughout Great Britain and, in Scotland and Offshore, also for all interconnecting transformers operating at 132kV or greater between the User’s System and the User’s Subtransmission System (and any OTSUA) the User shall supply the following information:-

Tap changer range

Tap change step size

Tap changer type: on load or off circuit

Earthing method: Direct, resistance or reactance

Impedance (if not directly earthed )

PC.A.2.2.6	Each User shall supply the following information about the User’s equipment installed at a Transmission Site (or in the case of OTSUA, all OTSDUW Plant and Apparatus):-

(a)	Switchgear.  For all circuit breakers:-

Rated voltage (kV)

Operating voltage (kV)

Rated 3-phase rms short-circuit breaking current, (kA)

Rated 1-phase rms short-circuit breaking current, (kA)

Rated 3-phase peak short-circuit making current, (kA)

Rated 1-phase peak short-circuit making current, (kA)

Rated rms continuous current (A)

DC time constant applied at testing of asymmetrical breaking abilities (secs)

In the case of OTSDUW Plant and Apparatus operating times for circuit breaker, Protection, trip relay and total operating time should be provided.

(b)	Substation Infrastructure.  For the substation infrastructure (including, but not limited to, switch disconnectors, disconnectors, current transformers, line traps, busbars, through bushings, etc):-

Rated 3-phase rms short-circuit withstand current (kA)

Rated 1-phase rms short-circuit withstand current (kA).

Rated 3-phase short-circuit peak withstand current (kA)

Rated 1- phase short-circuit peak withstand current (kA)

Rated duration of short circuit withstand (secs)

Rated rms continuous current (A)

A single value for the entire substation may be supplied, provided it represents the most restrictive item of current carrying apparatus.

PC.A.2.2.7	In the case of OTSUA the following should also be provided

(a)	Automatic switching scheme schedules including diagrams and an explanation of how the System will operate and what plant will be affected by the schemes Operation.

(b)	Intertripping schemes both generation and Demand.  In each case a diagram of the scheme and an explanation of how the System will operate and what Plant will be affected by the schemes Operation.

PC.A.2.3	Lumped System Susceptance

PC.A.2.3.1	For all parts of the User’s Subtransmission System (and any OTSUA) which are not included in the Single Line Diagram provided under PC.A.2.2.1, each User shall provide the equivalent lumped shunt susceptance at nominal Frequency.

PC.A.2.3.1.1	This should include shunt reactors connected to cables which are not normally in or out of service independent of the cable (ie. they are regarded as part of the cable).

PC.A.2.3.1.2	This should not include:

(a)	independently switched reactive compensation equipment connected to the User's System specified under PC.A.2.4, or;

(b)	any susceptance of the User's System inherent in the Demand (Reactive Power) data specified under PC.A.4.3.1.

PC.A.2.4	Reactive Compensation Equipment

PC.A.2.4.1	For all independently switched reactive compensation equipment (including any OTSUA), including that shown on the Single Line Diagram, not operated by The Company and connected to the User's System at 132kV and above in England and Wales and 33kV and above in Scotland and Offshore (including any OTSDUW Plant and Apparatus operating at High Voltage), other than Power Factor correction equipment associated directly with Customers' Plant and Apparatus, the following information is required:

(a)	type of equipment (eg. fixed or variable);

(b)	capacitive and/or inductive rating or its operating range in MVAr;

(c)	details of any automatic control logic to enable operating characteristics to be determined;

(d)	the point of connection to the User's System (including OTSUA) in terms of electrical location and System voltage.

(e)	In the case of OTSDUW Plant and Apparatus the User should also provide:-

(i)	Connection node,  voltage, rating, power loss, tap range and connection arrangement.

(ii)	A mathematical representation in block diagram format to model the control of any dynamic compensation plant.  The model should be suitable for RMS dynamic stability type studies where each time constant should be no less than 10ms.

(iii)	For Static Var Compensation equipment the User should provide:

HV Node

LV Node

Control Node

Nominal Voltage (kV)

Target Voltage (kV)

Maximum MVAr at HV

Minimum MVAr at HV

Slope %

Voltage dependant Q Limit

Normal Running Mode

Positive and zero phase sequence resistance and reactance

Transformer winding type

Connection arrangements

PC.A.2.4.2	DC Converter Station owners, HVDC System Owners (and a User where the OTSUA includes an OTSDUW DC Converter) are also required to provide information about the reactive compensation and harmonic filtering equipment required to ensure that their Plant and Apparatus (and the OTSUA) complies with the criteria set out in CC.6.1.5 or ECC.6.1.5 (as applicable).

PC.A.2.5	Short Circuit Contribution to National Electricity Transmission System

PC.A.2.5.1	General

(a)	To allow The Company to calculate fault currents, each User is required to provide data, calculated in accordance with Good Industry Practice, as set out in the following paragraphs of PC.A.2.5.

(b)	The data should be provided for the User's System with all Generating Units (including Synchronous Generating Units), Power Park Units, HVDC Systems and DC Converters Synchronised to that User's System (and any OTSUA where appropriate).   The User must ensure that the pre-fault network conditions reflect a credible System operating arrangement.

(c)	The list of data items required, in whole or part, under the following provisions, is set out in PC.A.2.5.6.  Each of the relevant following provisions identifies which data items in the list are required for the situation with which that provision deals.

The fault currents in sub-paragraphs (a) and (b) of the data list in PC.A.2.5.6 should be based on an a.c. load flow that takes into account any pre-fault current flow across the Point of Connection (and in the case of OTSUA, Interface Points and Connection Points) being considered.

Measurements made under appropriate System conditions may be used by the User to obtain the relevant data.

(d)	The Company may at any time, in writing, specifically request for data to be provided for an alternative System condition, for example minimum plant, and the User will, insofar as such request is reasonable, provide the information as soon as reasonably practicable following the request.

PC.A.2.5.2	Network Operators and Non-Embedded Customers are required to submit data in accordance with PC.A.2.5.4.  Generators, DC Converter Station owners, HVDC System Owners and Network Operators, in respect of Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded DC Converter Stations not subject to a Bilateral Agreement and Embedded HVDC Systems within such Network Operator’s Systems are required to submit data in accordance with PC.A.2.5.5.

PC.A.2.5.3	Where prospective short-circuit currents on Transmission equipment are close to the equipment rating, and in The Company’s reasonable opinion more accurate calculations of the prospective short circuit currents are required, then The Company will request additional data as outlined in PC.A.6.6 below.

PC.A.2.5.4	Data from Network Operators and Non-Embedded Customers

PC.A.2.5.4.1	Data is required to be provided at each node on the Single Line Diagram provided under PC.A.2.2.1 at which motor loads and/or Embedded Small Power Stations and/or Embedded Medium Power Stations and/or Embedded installations of direct current converters which do not form a DC Converter Station or HVDC System are connected, assuming a fault at that location, as follows:-

The data items listed under the following parts of PC.A.2.5.6:-

(a)	(i), (ii), (iii), (iv), (v) and (vi);

and the data items shall be provided in accordance with the detailed provisions of PC.A.2.5.6(c) - (f).

PC.A.2.5.4.2	Network Operators shall provide the following data items in respect of each Interface Point within their User System:

(a)	Maximum Export Capacity;

(b)	Maximum Import Capacity; and,

(c)	Interface Point Target Voltage/Power Factor

Network Operators shall alongside these parameters include details of any manual or automatic post fault actions to be taken by the owner / operator of the Offshore Transmission System connected to such Interface Point that are required by the Network Operator.

PC.A.2.5.5	Data from Generators (including Generators undertaking OTSDUW and those responsible for DC Connected Power Park Modules), DC Converter Station owners, HVDC System Owners and from Network Operators in respect of Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded DC Converter Stations not subject to a Bilateral Agreement and Embedded HVDC Systems within such Network Operator’s Systems.

PC.A.2.5.5.1	For each Generating Unit (including Synchronous Generating Units forming part of a Synchronous Power Generating Module) with one or more associated Unit Transformers, the Generator, or the Network Operator in respect of Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded DC Converter Stations not subject to a Bilateral  Agreement and Embedded HVDC Systems within such Network Operator’s System is required to provide values for the contribution of the Power Station Auxiliaries (including Auxiliary Energy Supplies) to the fault current flowing through the Unit Transformer(s).

The data items listed under the following parts of PC.A.2.5.6(a) should be provided:-

(i), (ii) and (v);

(iii)	if the associated Generating Unit (including Synchronous Generating Units forming part of a Synchronous Power Generating Module)  step-up transformer can supply zero phase sequence current from the Generating Unit side to the National Electricity Transmission System;

(iv)	if the value is not 1.0 p.u;

and the data items shall be provided in accordance with the detailed provisions of PC.A.2.5.6(c) - (f), and with the following parts of this PC.A.2.5.5.

PC.A.2.5.5.2	Auxiliary motor short circuit current contribution and any Auxiliary Gas Turbine Unit contribution through the Unit Transformers must be represented as a combined short circuit current contribution at the Generating Unit's (including Synchronous Generating Units forming part of a Synchronous Power Generating Module)  terminals, assuming a fault at that location.

PC.A.2.5.5.3	If the Power Station or HVDC System or DC Converter Station (or OTSDUW Plant and Apparatus which provides a fault infeed) has separate Station Transformers, data should be provided for the fault current contribution from each transformer at its high voltage terminals, assuming a fault at that location, as follows:-

The data items listed under the following parts of PC.A.2.5.6

(a)	(i), (ii), (iii), (iv), (v) and (vi);

and the data items shall be provided in accordance with the detailed provisions of PC.A.2.5.6(b) - (f).

PC.A.2.5.5.4	Data for the fault infeeds through both Unit Transformers and Station Transformers shall be provided for the normal running arrangement when the maximum number of Generating Units (including Synchronous Generating Units forming part of a Synchronous Power Generating Module) are Synchronised to the System or when all the DC Converters at a DC Converter Station or HVDC Converters within an HVDC System are transferring Rated MW in either direction.  Where there is an alternative running arrangement (or transfer in the case of a DC Converter Station or HVDC System) which can give a higher fault infeed through the Station Transformers, then a separate data submission representing this condition shall be made.

PC.A.2.5.5.5	Unless the normal operating arrangement within the Power Station is to have the Station and Unit Boards interconnected within the Power Station, no account should be taken of the interconnection between the Station Board and the Unit Board.

PC.A.2.5.5.6	Auxiliary motor short circuit current contribution and any auxiliary DC Converter Station contribution or HVDC System contribution through the Station Transformers must be represented as a combined short circuit current contribution through the Station Transformers.

PC.A.2.5.5.7	Where a Manufacturer’s Data & Performance Report exists in respect of the model of the Power Park Unit, the User may opt to reference the Manufacturer’s Data & Performance Report as an alternative to the provision of data in accordance with this PC.A.2.5.5.7. For the avoidance of doubt, all other data provision pursuant to the Grid Code shall still be provided including a Single Line Diagram and those data pertaining thereto.

For each Power Park Module (including DC Connected Power Park Modules) and each type of Power Park Unit (eg. a Doubly Fed Induction Generator) (and any OTSDUW Plant and Apparatus which provides a fault infeed), including any Auxiliaries, positive, negative and zero sequence root mean square current values are to be provided of the contribution to the short circuit current flowing at:

(i)	the Power Park Unit terminals, or the Common Collection Busbar if an equivalent Single Line Diagram and associated data as described in PC.A.2.2.2 is provided, and

(ii)	the Grid Entry Point (and in case of OTSUA, Transmission Interface Point), or User System Entry Point if Embedded

for the following solid faults at the Grid Entry Point (and in case of OTSUA, Interface Point), or User System Entry Point if Embedded:

(i)	a symmetrical three phase short circuit

(ii)	a single phase to earth short circuit

(iii)	a phase to phase short circuit

(iv)	a two phase to earth short circuit

For a Power Park Module (including DC Connected Power Park Modules) in which one or more of the Power Park Units utilise a protective control such as a crowbar circuit, the data should indicate whether the protective control will act in each of the above cases and the effects of its action shall be included in the data. For any case in which the protective control will act, the data for the fault shall also be submitted for the limiting case in which the protective circuit will not act, which may involve the application of a non-solid fault, and the positive, negative and zero sequence retained voltages at;

(i)	the Power Park Unit terminals, or the Common Collection Busbar if an equivalent Single Line Diagram and associated data is provided and

(ii)	the Grid Entry Point, or User System Entry Point if Embedded

in this limiting case shall be provided.

For each fault for which data is submitted, the data items listed under the following parts of PC.A.2.5.6(a) shall be provided:-

(iv), (vii), (viii), (ix), (x);

In addition, if an equivalent Single Line Diagram has been provided the data items listed under the following parts of PC.A.2.5.6(a) shall be provided:-

(xi), (xii), (xiii);

In addition, for a Power Park Module (including DC Connected Power Park Modules) in which one or more of the Power Park Units utilise a protective control such as a crowbar circuit:-

the data items listed under the following parts of PC.A.2.5.6(a) shall be provided:-

(xiv), (xv);

All of the above data items shall be provided in accordance with the detailed provisions of PC.A.2.5.6(c), (d), (f).

Should actual data in respect of fault infeeds be unavailable at the time of the application for a CUSC Contract or Embedded Development Agreement, a limited subset of the data, representing the maximum fault infeed that may result from all of the plant types being considered, shall be submitted. This data will, as a minimum,  represent the root mean square of the positive, negative and zero sequence components of the fault current for both single phase and three phase solid faults at the Grid Entry Point (or User System Entry Point if Embedded) at the time of fault application and 50ms following fault application.  Actual data in respect of fault infeeds shall be submitted to The Company as soon as it is available, in line with PC.A.1.2

PC.A.2.5.6	Data Items

(a)	The following is the list of data utilised in this part of the PC.  It also contains rules on the data which generally apply:-

(i)	Root mean square of the symmetrical three-phase short circuit current infeed at the instant of fault, (I1");

(ii)	Root mean square of the symmetrical three-phase short circuit current after the subtransient fault current contribution has substantially decayed, (I1');

(iii)	the zero sequence source resistance and reactance values of the User's System as seen from the node on the Single Line Diagram provided under PC.A.2.2.1 (or Power Generating Module or Station Transformer high voltage terminals or Generating Unit terminals or DC Converter terminals or HVDC System terminals, as appropriate) consistent with the infeed described in PC.A.2.5.1.(b);

(iv)	root mean square of the pre-fault voltage at which the maximum fault currents were calculated;

(v)	the positive sequence X/R ratio at the instant of fault;

(vi)	the negative sequence resistance and reactance values of the User's System seen from the node on the Single Line Diagram provided under PC.A.2.2.1 (or Power Generating Module or Station Transformer high voltage terminals, or Generating Unit terminals or DC Converter terminals or HVDC System terminals as appropriate) if substantially different from the values of positive sequence resistance and reactance which would be derived from the data provided above;

(vii)	A continuous trace and a table showing the root mean square of the positive, negative and zero sequence components of the short circuit current between zero and 140ms at 10ms intervals;

(viii)	The Active Power (or Interface Point Capacity being exported pre-fault by the OTSDUW Plant and Apparatus) being generated pre-fault by the Power Park Module (including DC Connected Power Park Modules) and by each type of Power Park Unit;

(ix)	The reactive compensation shown explicitly on the Single Line Diagram that is switched in;

(x)	The Power Factor of the Power Park Module (including DC Connected Power Park Modules)  and of each Power Park Unit type;

(xi)	The positive sequence X/R ratio of the equivalent at the Common Collection Busbar or Interface Point in the case of OTSUA;

(xii)	The minimum zero sequence impedance of the equivalent seen from the Common Collection Busbar or Interface Point in the case of OTSUA;

(xiii)	The number of Power Park Units represented in the equivalent Power Park Unit;

(xiv)	The additional rotor resistance and reactance (if any) that is applied to the Power Park Unit under a fault condition;

(xv)	A continuous trace and a table showing the root mean square of the positive, negative and zero sequence components of the retained voltage at the fault point and Power Park Unit terminals, or the Common Collection Busbar if an equivalent Single Line Diagram and associated data as described in PC.A.2.2.2 is provided or Interface Point in the case of OTSUA, representing the limiting case, which may involve the application of a non-solid fault, required to not cause operation of the protective control;

(b)	In considering this data, unless the User notifies The Company accordingly at the time of data submission, The Company will assume that the time constant of decay of the subtransient fault current corresponding to the change from I1" to I1', (T") is not significantly different from 40ms. If that assumption is not correct in relation to an item of data, the User must inform The Company at the time of submission of the data.

(c)	The value for the X/R ratio must reflect the rate of decay of the d.c. component that may be present in the fault current and hence that of the sources of the initial fault current. All shunt elements and loads must therefore be deleted from any system model before the X/R ratio is calculated.

(d)	In producing the data, the User may use "time step analysis" or "fixed-point-in-time analysis" with different impedances.

(e)	If a fixed-point-in-time analysis with different impedances method is used, then in relation to the data submitted under (a) (i) above, the data will be required for "time zero" to give I1".  The figure of 120ms is consistent with a decay time constant T" of 40ms, and if that figure is different, then the figure of 120ms must be changed accordingly.

(f)	Where a "time step analysis" is carried out, the X/R ratio may be calculated directly from the rate of decay of the d.c. component. The X/R ratio is not that given by the phase angle of the fault current if this is based on a system calculation with shunt loads, but from the Thévenin equivalent of the system impedance at the instant of fault with all non-source shunts removed.

### PC.A.3	POWER GENERATING MODULE, GENERATING UNIT, HVDC SYSTEM AND DC CONVERTER DATA

PC.A.3.1	Introduction

Directly Connected

PC.A.3.1.1	Each Generator, HVDC System Owner and DC Converter Station owner (and a User where the OTSUA includes an OTSDUW DC Converter) with an existing, or proposed, Power Station or DC Converter Station or HVDC System directly connected, or to be directly connected, to the National Electricity Transmission System (or in the case of OTSUA, the Interface Point), shall provide The Company with data relating to that Power Station or DC Converter Station or HVDC System, both current and forecast, as specified in PC.A.3.2 to PC.A.3.4.

Embedded

PC.A.3.1.2	(a)	Each Generator, HVDC System Owner and DC Converter Station owner in respect of its existing, and/or proposed, Embedded Large Power Stations and/or Embedded HVDC Systems and/or Embedded DC Converter Stations and/or its Embedded Medium Power Stations subject to a Bilateral Agreement and each Network Operator in respect of its Embedded Medium Power Stations not subject to a Bilateral Agreement and/or Embedded DC Converter Stations not subject to a Bilateral Agreement and/or Embedded HVDC Systems not subject to a Bilateral Agreement within such Network Operator’s System in each case connected to the Subtransmission System, shall provide The Company with data relating to that Power Station or DC Converter Station or HVC System, both current and forecast, as specified in PC.A.3.2 to PC.A.3.4.

(b)	No data need be supplied in relation to any Small Power Station or any Medium Power Station or installations of direct current converters which do not form a DC Converter Station or HVDC System, connected at a voltage level below the voltage level of the Subtransmission System except:-

(i)	in connection with an application for, or under, a CUSC Contract, or

(ii)	unless specifically requested by The Company under PC.A.3.1.4.

PC.A.3.1.3	(a)	Each Network Operator shall provide The Company with the data specified in 	PC.A.3.2.2(c)(i) and (ii) and PC.A.3.2.2(i).

(b)	Network Operators need not submit planning data in respect of an Embedded Small Power Station unless required to do so under PC.A.1.2(b) or unless specifically requested under PC.A.3.1.4 below, in which case they will supply such data.

PC.A.3.1.4	(a)	PC.A.4.2.4(b) and PC.A.4.3.2(a) explain that the forecast Demand submitted by each 	Network Operator must be net of the export of all Small Power Stations and Medium 	Power Stations and Customer Generating Plant and all installations of direct current 	converters which do not form a DC Converter Station or HVDC System,  Embedded 	within that Network Operator’s System. The Network Operator must inform The 	Company of:

(i)	the number of such Embedded Power Stations and such Embedded  installations of direct current converters (including the number of Generating Units or Power Park Modules (including DC Connected Power Park Modules) or DC Converters or HVDC Systems) together with their summated capacity; and

(ii)	beginning from the 2015 Week 24 data submission, for each Embedded Small Power Station of registered capacity (as defined in the Distribution Code) of 1MW or more:

1.	A reference which is unique to each Network Operator;

2.	The production type as follows:

a) 	In the case of an Embedded Small Power Station first connected on or after 1 January 2015, the production type must be selected from the list below:

- 	Biomass;

- 	Fossil brown coal/lignite;

- 	Fossil coal-derived gas;

- 	Fossil gas;

-	Fossil hard coal;

-	Fossil oil;

- 	Fossil oil shale;

- 	Fossil peat;

- 	Geothermal;

- 	Hydro pumped storage;

- 	Hydro run-of-river and poundage;

- 	Hydro water reservoir;

- 	Marine;

-	Nuclear;

- 	Other renewable;

- 	Solar;

- 	Waste;

- 	Wind offshore;

- 	Wind onshore; or

- 	Other;

together with a statement as to whether the generation forms part of a CHP scheme;

(iii) 	beginning from the 2019 Week 24 data submission, for Embedded Power Stations with Registered Capacity of less than 1MW, their best estimate of the aggregated capacity of all such Embedded Power Stations per production type as defined in the list in PC.A.3.1.4 (a)(ii)(2)(a).

b) 	In the case of an Embedded Small Power Station first connected to the Users’ System before 1 January 2015, as an alternative to the production type, the technology type(s) used, selected from the list set out at paragraph 2.23 in Version 2 of the Regulatory Instructions and Guidance relating to the distributed generation incentive, innovation funding incentive and registered power zones, reference 83/07, published by Ofgem in April 2007;

c)	In   the   case   of   an Embedded   Small   Power   Station comprising Electricity   Storage   Modules or Electricity Storage Units first connected the User’s System on or after May 20 2020, the storage type must be selected from the list below:

-Chemical

Ammonia

Hydrogen

Synthetic Fuels

Drop-in Fuels

Methanol

Synthetic Natural Gas

-Electrical

Supercapacitors

Superconducting Magnetic ES (SMES)

-Mechanical

Adiabatic Compressed Air

Diabatic Compressed Air

Liquid Air Energy Storage

Pumped Hydro

Flywheels

-Thermal

Latent Heat Storage

Thermochemical Storage

Sensible Heat Storage

-Electrochemical

Classic Batteries

Lead Acid

Lithium Polymer (Li-Polymer)

Metal Air

Nickle Cadmium (Ni-Cd)

Sodium Nickle Chloride (Na-NiCl2)

Lithium Ion (Li–ion)

Sodium Ion (Na–ion)

Lithium Sulphur (Li-S)

Sodium Sulphur(Na-S

Nickle –Metal Hydride (Ni-MH)

Flow Batteries

Vanadium Red-Oxide

Zinc – Iron (Zn –Fe)

Zinc – Bromine (Zn –Br)

Other

together with a statement as to whether the storage forms part of a CHP scheme. Where this information is not held by the Network Operator it should provide its best view of the type of storage technology.

3. 	The registered capacity (as defined in the Distribution Code) in MW;

4. 	The lowest voltage level node that is specified on the most up-to-date Single Line Diagram to which it connects or where it will export most of its power;

5. 	Where it generates electricity from wind or PV, the geographical location using either latitude or longitude or grid reference coordinates of the primary or higher voltage substation to which it connects;

6. 	The reactive power and voltage control mode, including the voltage set-point and reactive range, where it operates in voltage control mode, or the target Power Factor, where it operates in Power Factor mode;

7. 	Details of the types of loss of mains Protection in place and their relay settings which in the case of Embedded Small Power Stations first connected to the Users’ System before 1 January 2015 shall be provided on a reasonable endeavours basis.

(b)	On receipt of this data, the Network Operator or Generator (if the data relates to Power Stations referred to in PC.A.3.1.2) may be further required, at The Company's reasonable discretion, to provide details of Embedded Small Power Stations and Embedded Medium Power Stations and Customer Generating Plant and Embedded installations of direct current converters which do not form a DC Converter Station or HVDC System, both current and forecast, as specified in PC.A.3.2 to PC.A.3.4.  Such requirement would arise where The Company reasonably considers that the collective effect of a number of such Embedded Power Stations and Customer Generating Plants and Embedded installations of direct current converters may have a significant system effect on the National Electricity Transmission System.

Busbar Arrangements

PC.A.3.1.5	Where Generating Units, which term includes CCGT Units and Synchronous Generating Units within a Synchronous Power Generating Module and Power Park Modules (including DC Connected Power Park Modules), and DC Converters, and HVDC Systems are connected to the National Electricity Transmission System via a busbar arrangement which is or is expected to be operated in separate sections, the section of busbar to which each Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module), DC Converter, HVDC System or Power Park Module (including DC Connected Power Park Modules) is connected is to be identified in the submission.

PC.A.3.2	Output Data

PC.A.3.2.1	(a)	Large Power Stations and Gensets

Data items PC.A.3.2.2 (a), (b), (c), (d), (e), (f) and (h) are required with respect to each Large Power Station and each Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module) and Power Park Module (including DC Connected Power Park Modules) of each Large Power Station and for each Genset (although (a) is not required for CCGT Units and (b), (d) and (e) are not normally required for CCGT Units and (a), (b), (c), (d), (e), (f) and (h) are not normally required for Power Park Units).

(b)	Embedded Small Power Stations and Embedded Medium Power Stations

Data item PC.A.3.2.2 (a) is required with respect to each Embedded Small Power Station and Embedded Medium Power Station and each Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module) and Power Park Module (including DC Connected Power Park Modules) of each Embedded Small Power Station and Embedded Medium Power Station (although (a) is not required for CCGT Units or Power Park Units). In addition, data item PC.A.3.2.2(c)(ii) is required with respect to each Embedded Medium Power Station.

(c)	CCGT Units/Modules

(i)	Data item PC.A.3.2.2 (g) is required with respect to each CCGT Unit;

(ii)	data item PC.A.3.2.2 (a) is required with respect to each CCGT Module; and

(iii)	data items PC.A.3.2.2 (b), (c), (d) and (e) are required with respect to each CCGT Module unless The Company informs the relevant User in advance of the submission that it needs the data items with respect to each CCGT Unit for particular studies, in which case it must be supplied on a CCGT Unit basis.

Where any definition utilised or referred to in relation to any of the data items does not reflect CCGT Units, such definition shall be deemed to relate to CCGT Units for the purposes of these data items.  Any Schedule in the DRC which refers to these data items shall be interpreted to incorporate the CCGT Unit basis where appropriate;

(d)	Cascade Hydro Schemes

Data item PC.A.3.2.2(i) is required with respect to each Cascade Hydro Scheme.

(e)	Power Park Units/Modules

Data items PC.A.3.2.2 (k) is required with respect to each Power Park Module (including DC Connected Power Park Modules).

(f)	DC Converters and HVDC Systems

Data items PC.A.3.2.2 (a), (b), (c), (d) (e) (f) (h) and (i) are required with respect of each HVDC System, each DC Converter Station and each DC Converter in each DC Converter Station. For installations of direct current converters which do not form a DC Converter Station only data item PC.A.3.2.2.(a) is required.

PC.A.3.2.2	Items (a), (b), (d), (e), (f), (g), (h), (i), (j) and (k) are to be supplied by each Generator, DC Converter Station owner, HVDC System Owner or Network Operator (as the case may be) in accordance with PC.A.3.1.1, PC.A.3.1.2, PC.A.3.1.3 and PC.A.3.1.4. Items (a), and (f)(iv) are to be supplied (as applicable) by a User in the case of OTSUA which includes an OTSDUW DC Converter. Item (c) is to be supplied by each Network Operator in all cases:-

(a)	Registered Capacity (MW), Maximum Capacity (in the case of Power Generating Modules in addition to Registered Capacity on a Power Station basis) or Interface Point Capacity in the case of OTSDUW;

(b)	Output Usable (MW) on a monthly basis;

(c)	(i)	System Constrained Capacity (MW) ie. any constraint placed on the capacity of the Embedded Generating Unit (including a Synchronous Generating Unit within a Synchronous Power Generating Module), Embedded Power Park Module (including DC Connected Power Park Modules) an Offshore Transmission System at an Interface Point, Embedded HVDC System or DC Converter at an Embedded DC Converter Station due to the Network Operator’s System in which it is Embedded. Where Generating Units (which term includes CCGT Units and Synchronous Generating Units within a Synchronous Power Generating Module), Power Park Modules (including DC Connected Power Park Modules), Offshore Transmission Systems at an Interface Point, HVDC Systems or DC Converters are connected to a Network Operator’s User System via a busbar arrangement which is or is expected to be operated in separate sections, details of busbar running arrangements and connected circuits at the substation to which the Embedded Generating Unit (including Synchronous Generating Units within an Embedded Synchronous Power Generating Module), Embedded Power Park Module (including DC Connected Power Park Modules), Offshore Transmission System at an Interface Point, or Embedded HVDC System or Embedded DC Converter is connected sufficient for The Company to determine where the MW generated by each Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module), Power Park Module (including DC Connected Power Park Modules), HVDC System or DC Converter at that Power Station or DC Converter Station or Offshore Transmission System at an Interface Point would appear onto the National Electricity Transmission System;

(ii)	any Reactive Despatch Network Restrictions;

(d)	Minimum Generation (MW), and in the case of Power Generating Modules only Minimum Stable Operating Level (MW) and Minimum Regulating Level;

(e)	MW obtainable from Generating Units (including Synchronous Generating Units within a Synchronous Power Generating Module), Power Park Modules (including DC Connected Power Park Modules), HVDC Systems or DC Converters at a DC Converter Station in excess of Registered Capacity or Maximum Capacity;

(f)	Generator Performance Chart:

(i)	GB Code User(s) in respect of Generating Units shall provide a Generator Performance Chart and EU Code Users in respect of Power Generating Modules shall provide a Power Generating Module Performance Chart and a Synchronous Generating Unit Performance Chart.

(ii)	at the electrical point of connection to the Offshore Transmission System for an Offshore Synchronous Generating Unit and Offshore Synchronous Power Generating Module.

(iii)	at the electrical point of connection to the National Electricity Transmission System (or User System if Embedded) for a Non Synchronous Generating Unit (excluding a Power Park Unit), Power Park Module (including DC Connected Power Park Modules), HVDC System and DC Converter at a DC Converter Station;

(iv)	at the Interface Point for OTSDUW Plant and Apparatus

Where a Reactive Despatch Network Restriction applies, its existence and details should be highlighted on the Generator Performance Chart, in sufficient detail for The Company to determine the nature of the restriction.

(g)	a list of the CCGT Units within a CCGT Module, identifying each CCGT Unit, and the CCGT Module of which it forms part, unambiguously.  In the case of a Range CCGT Module, details of the possible configurations should also be submitted, together:-

(i)	(in the case of a Range CCGT Module connected to the National Electricity Transmission System) with details of the single Grid Entry Point (there can only be one) at which power is provided from the Range CCGT Module;

(ii)	(in the case of an Embedded Range CCGT Module) with details of the single User System Entry Point (there can only be one) at which power is provided from the Range CCGT Module;

Provided that, nothing in this sub-paragraph (g) shall prevent the busbar at the relevant point being operated in separate sections;

(h)	expected running regime(s) at each Power Station, HVDC System or DC Converter Station and type of Power Generating Module or Generating Unit (as applicable), eg. Steam Unit, Gas Turbine Unit, Combined Cycle Gas Turbine Unit, Power Park Module (including DC Connected Power Park Modules), Novel Units (specify by type), etc;

(i)	a list of Power Stations and Generating Units within a Cascade Hydro Scheme, identifying each Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module) and Power Station and the Cascade Hydro Scheme of which each form part unambiguously.  In addition:

(i)	details of the Grid Entry Point at which Active Power is provided, or if Embedded the Grid Supply Point(s) within which the Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module) is connected;

(ii)	where the Active Power output of a Generating Unit is split between more than one Grid Supply Points the percentage that would appear under normal and outage conditions at each Grid Supply Point.

(j)	The following additional items are only applicable to DC Converters at DC Converter Stations and HVDC Systems.

Registered Import Capacity (MW);

Import Usable (MW) on a monthly basis;

Minimum Import Capacity (MW);

MW that may be absorbed by a DC Converter or HVDC System in excess of Registered Import Capacity and Maximum HVDC Active Power Transmission Capacity under importing conditions and the duration for which this is available;

(k)	the number and types of the Power Park Units within a Power Park Module (including DC Connected Power Park Modules), identifying each Power Park Unit, the Power Park Module of which it forms part and identifying the BM Unit of which each Power Park Module forms part, unambiguously.  In the case of a Power Station directly connected to the National Electricity Transmission System with multiple Power Park Modules (including DC Connected Power Park Modules) where Power Park Units can be selected to run in different Power Park Modules and/or Power Park Modules can be selected to run in different BM Units, details of the possible configurations should also be submitted. In addition, for Offshore Power Park Modules (including DC Connected Power Park Modules), the number of Offshore Power Park Strings that are aggregated into one Offshore Power Park Module should also be submitted.

(l)	the number and types of the Synchronous Generating Units within a Synchronous Power Generating Module, identifying each Synchronous Generating Unit, the Synchronous Power Generating Module of which it forms part and identifying the BM Unit of which each Synchronous Power Generating Module forms part, unambiguously.  In the case of a Power Station directly connected to the National Electricity Transmission System with multiple Synchronous Power Generating Modules where Synchronous Generating Units can be selected to run in different Synchronous Power Generating Modules and/or Synchronous Power Generating Modules can be selected to run in different BM Units, details of the possible configurations should also be submitted.

PC.A.3.2.3	Notwithstanding any other provision of this PC, the CCGT Units within a CCGT Module, details of which are required under paragraph (g) of PC.A.3.2.2, can only be amended in accordance with the following provisions:-

(a)	if the CCGT Module is a Normal CCGT Module, the CCGT Units within that CCGT Module can only be amended such that the CCGT Module comprises different CCGT Units if The Company gives its prior consent in writing.  Notice of the wish to amend the CCGT Units within such a CCGT Module must be given at least 6 months before it is wished for the amendment to take effect;

(b)	if the CCGT Module is a Range CCGT Module, the CCGT Units within that CCGT Module and the Grid Entry Point at which the power is provided can only be amended as described in BC1.A1.6.4.

PC.A.3.2.4	Notwithstanding any other provision of this PC, the Power Park Units within a Power Park Module (including DC Connected Power Park Modules), and the Power Park Modules (including DC Connected Power Park Modules) within a BM Unit, details of which are required under paragraph (k) of PC.A.3.2.2, can only be amended in accordance with the following provisions:-

(a)	if the Power Park Units within that Power Park Module can only be amended such that the Power Park Module comprises different Power Park Units due to repair/replacement of individual Power Park Units if The Company gives its prior consent in writing.  Notice of the wish to amend a Power Park Unit within such a Power Park Module (including DC Connected Power Park Modules) must be given at least 4 weeks before it is wished for the amendment to take effect;

(b)	if the Power Park Units within that Power Park Module (including DC Connected Power Park Modules) and/or the Power Park Modules (including DC Connected Power Park Modules) within that BM Unit can be selected to run in different Power Park Modules and/or BM Units as an alternative operational running arrangement the Power Park Units within the Power Park Module, the BM Unit of which each Power Park Module forms part, and the Grid Entry Point at which the power is provided can only be amended as described in BC1.A.1.8.4.

PC.A.3.2.5	Notwithstanding any other provision of this PC, the Synchronous Generating Units within a Synchronous Power Generating Module, and the Synchronous Power Generating  Modules  within a BM Unit, details of which are required under paragraph (l) of PC.A.3.2.2, can only be amended in accordance with the following provisions:-

(a)	if the Synchronous Generating Units within that Synchronous Power Generating  Module can only be amended such that the Synchronous Power Generating Module comprises different Synchronous Generating Units due to repair/replacement of individual Synchronous Generating Units if The Company gives its prior consent in writing.  Notice of the wish to amend a Synchronous Generating Unit within such a Synchronous Power Generating Module must be given at least 4 weeks before it is wished for the amendment to take effect;

(b)	if the Synchronous Generating  Units within that Synchronous Power Generating Module  and/or the Synchronous Power Generating Modules  within that BM Unit can be selected to run in different Synchronous Power Generating Modules and/or BM Units as an alternative operational running arrangement the Synchronous Generating Units within the Synchronous Power Generating  Module, the BM Unit of which each Synchronous Power Generating Module forms part, and the Grid Entry Point at which the power is provided can only be amended as described in BC1.A.1.9.4(c).The requirements of PC.A.3.2.5 need not be satisfied if Generators have already submitted data in respect of PC.A.3.2.3, PC.A.3.2.4 and PC.A.3.2.5 for the same Power Generating Module.

PC.A.3.3.	Rated Parameters Data

PC.A.3.3.1	The following information is required to facilitate an early assessment, by The Company, of the need for more detailed studies;

(a)	for all Generating Units (excluding Power Park Units) and Power Park Modules (including DC Connected Power Park Modules):

Rated MVA

Rated MW;

(b)	for each Synchronous Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module):

Short circuit ratio

Direct axis transient reactance;

Inertia constant (for whole machine), MWsecs/MVA;

(c)	for each Synchronous Generating Unit step-up transformer (including the step up transformer of a Synchronous Generating Unit within a Synchronous Power Generating Module):

Rated MVA

Positive sequence reactance (at max, min and nominal tap);

(d)	for each DC Converter at a DC Converter Station, HVDC System, DC Converter connecting a Power Park Module (including a DC Connected Power Park Module) and Transmission DC Converter  (forming part of an OTSUA).

DC Converter or HVDC Converter type (e.g. current/voltage sourced)

Rated MW per pole for import and export

Number of poles and pole arrangement

Rated DC voltage/pole (kV)

Return path arrangement

Remote AC connection arrangement (excluding OTSDUW DC Converters)

Maximum HVDC Active Power Transmission Capacity

Minimum Active Power Transmission Capacity

(e)	for each type of Power Park Unit in a Power Park Module not connected to the Total System by a DC Converter or HVDC System:

Rated MVA

Rated MW

Rated terminal voltage

Inertia constant, (MWsec/MVA)

Additionally, for Power Park Units that are squirrel-cage or doubly-fed induction generators driven by wind turbines:

Stator reactance.

Magnetising reactance.

Rotor resistance (at rated running)

Rotor reactance (at rated running)

The generator rotor speed range (minimum and maximum speeds in RPM) (for doubly-fed induction generators only)

Converter MVA rating (for doubly-fed induction generators only)

For a Power Park Unit consisting of a synchronous machine in combination with a back-to-back DC Converter or HVDC Converter, or for a Power Park Unit not driven by a wind turbine, the data to be supplied shall be agreed with The Company in accordance with PC.A.7.

This information should only be given in the data supplied in accordance with PC.4.4 and PC.4.5.

PC.A.3.4	General Generating Unit, Power Park Module (including DC Connected Power Park Modules), Power Generating Module, HVDC System and DC Converter Data

PC.A.3.4.1	The point of connection to the National Electricity Transmission System or the Total System, if other than to the National Electricity Transmission System, in terms of geographical and electrical location and system voltage is also required.

PC.A.3.4.2	(a)	Type of Generating Unit (ie Synchronous Power Generating Unit within a Power Generating Module, Synchronous Generating Unit, Non-Synchronous Generating Unit, DC Converter, Power Park Module (including DC Connected Power Park Modules) or HVDC System).

(b)	In the case of a Synchronous Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module) details of the Exciter category, for example whether it is a rotating Exciter or a static Exciter or in the case of a Non-Synchronous Generating Unit the voltage control system.

(c)	Whether a Power System Stabiliser is fitted.

PC.A.3.4.3	Each Generator shall supply The Company with the production type(s) used as the primary source of power in respect of each Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module), selected from the list set out below:

- Biomass

- Fossil brown coal/lignite

- Fossil coal-derived gas

- Fossil gas

- Fossil hard coal

- Fossil oil

- Fossil oil shale

- Fossil peat

- Geothermal

- Hydro pumped storage

- Hydro run-of-river and poundage

- Hydro water reservoir

- Marine

- Nuclear

- Other renewable

- Solar

- Waste

- Wind offshore

- Wind onshore

- Other

PC.A.3.4.4	In the case of an Electricity Storage Module or Electricity Storage Unit, each Generator shall supply The Company with the production type(s) used as the primary Electricity Storage source (including Synchronous Electricity Storage Units within a Synchronous Electricity Storage Module), selected from the list set out below:

-Chemical

Ammonia

Hydrogen

Synthetic Fuels

Drop-in Fuels

Methanol

Synthetic Natural Gas

-Electrical

Supercapacitors

Superconducting Magnetic ES (SMES)

-Mechanical

Adiabatic Compressed Air

Diabatic Compressed Air

Liquid Air Energy Storage

Pumped Hydro

Flywheels

-Thermal

Latent Heat Storage

Thermochemical Storage

Sensible Heat Storage

-Electrochemical

Classic Batteries

Lead Acid

Lithium Polymer (Li-Polymer)

Metal Air

Nickle Cadmium (Ni-Cd)

Sodium Nickle Chloride (Na-NiCl2)

Lithium Ion (Li–ion)

Sodium Ion (Na–ion)

Lithium Sulphur (Li-S)

Sodium Sulphur(Na-S

Nickle –Metal Hydride (Ni-MH)

Flow Batteries

Vanadium Red-Oxide

Zinc – Iron (Zn –Fe)

Zinc – Bromine (Zn –Br)

Other

### PC.A.4	DEMAND AND ACTIVE ENERGY DATA

PC.A.4.1	Introduction

PC.A.4.1.1	Each User directly connected to the National Electricity Transmission System with Demand shall provide The Company with the Demand data, historic, current and forecast, as specified in PC.A.4.2 and PC.A.4.3. Paragraphs PC.A.4.1.2 and PC.A.4.1.3 apply equally to Active Energy requirements as to Demand unless the context otherwise requires.

PC.A.4.1.2	Data will need to be supplied by:

(a)	each Network Operator, in relation to Demand and Active Energy requirements on its User System;

(b)	each Non-Embedded Customer, Pumped Storage Generators (with respect to Pumping Demand) and Generators in  relation  to Electricity  Storage  Modules in relation to their Demand and Active Energy requirements.

(c)	each DC Converter Station owner or HVDC System Owner in relation to Demand and Active Energy  transferred (imported) to its DC Converter Station or HVDC System.

(d)	each OTSDUW DC Converter in relation to the Demand at each Interface Point and Connection Point.

Demand of Power Stations directly connected to the National Electricity Transmission System is to be supplied by the Generator under PC.A.5.2.

PC.A.4.1.3	References in this PC to data being supplied on a half hourly basis refer to it being supplied for each period of 30 minutes ending on the hour or half-hour in each hour.

PC.A.4.1.4	Access Periods and Access Groups

PC.A.4.1.4.1	Each Connection Point must belong to one, and only one, Access Group.

PC.A.4.1.4.2	Each Transmission Interface Circuit must have an Access Period.

PC.A.4.1.4.3	The Access Period shall

(a)	normally be a minimum of 8 continuous weeks and can occur in any one of three maintenance years during the period from calendar week 13 to calendar week 43 (inclusive) in each year; or,

(b)	exceptionally and provided that agreement is reached between The Company and the relevant User(s), such agreement to be sought in accordance with PC.7, the Access Period  may be of a period not less than 4 continuous weeks and can occur in any one of three maintenance years during the period from calendar week 10 to calendar week 43 (inclusive) in each year.

PC.A.4.1.4.4	The Company shall submit in writing no later than calendar week 6 in each year:

(a)	the calendar weeks defining the proposed start and finish of each Access Period for each Transmission Interface Circuit; and

(b)	the Connection Points in each Access Group.

The submission by The Company under PC.A.4.1.4.4 (a) above shall commence in 2010 and shall then continue each year thereafter.  The submission by The Company under PC.A.4.1.4.4 (b) shall commence in 2009 and then continue each year thereafter.

PC.A.4.1.4.5	It is permitted for Access Periods to overlap in the same Access Group and in the same maintenance year. However, where possible Access Periods will be sought by The Company that do not overlap with any other Access Period within that Access Group for each maintenance year. Where it is not possible to avoid overlapping Access Periods, The Company will indicate to Users by calendar week 6 its initial view of which Transmission Interface Circuits will need to be considered out of service concurrently for the purpose of assessing compliance to Licence Standards.  The obligation on The Company to indicate which Transmission Interface Circuits will need to be considered out of service concurrently for the purpose of assessing compliance to Licence Standards shall commence in 2010 and shall continue each year thereafter.

PC.A.4.1.4.6	Following the submission(s) by The Company by week 6 in each year and where required by either party, both The Company and the relevant User(s) shall use their reasonable endeavours to agree the appropriate Access Group(s) and Access Period for each Transmission Interface Circuit prior to week 17 in each year.  The requirement on The Company and the relevant User(s) to agree, shall commence in respect of Access Groups only in 2010.  This paragraph PC.A.4.1.4.6 shall apply in its entirety in 2011 and shall then continue each year thereafter.

PC.A.4.1.4.7	In exceptional circumstances, and with the agreement of all parties concerned, where a Connection Point is specified for the purpose of the Planning Code as electrically independent Subtransmission Systems, then data submissions can be on the basis of two (or more) individual Connection Points.

PC.A.4.2	User’s User System Demand (Active Power) and Active Energy Data

PC.A.4.2.1	Forecast daily Demand (Active Power) profiles, as specified in (a), (b) and (c) below, in respect of each of the User's User Systems (each summated over all Grid Supply Points in each User System) are required for:

(a)	peak day on each of the User's User Systems (as determined by the User) giving the numerical value of the maximum Demand (Active Power) that in the Users' opinion could reasonably be imposed on the National Electricity Transmission System;

(b)	day of peak National Electricity Transmission System Demand (Active Power) as notified by The Company pursuant to PC.A.4.2.2;

(c)	day of minimum National Electricity Transmission System Demand (Active Power) as notified by The Company pursuant to PC.A.4.2.2.

In addition, the total Demand (Active Power) in respect of the time of peak National Electricity Transmission System Demand in the preceding Financial Year in respect of each of the User's User Systems (each summated over all Grid Supply Points in each User System) both outturn and weather corrected shall be supplied.

PC.A.4.2.2	No later than calendar week 17 each year, The Company shall notify each Network Operator and Non-Embedded Customer in writing of the following, for the current Financial Year and for each of the following nine Financial Years, which will, until replaced by the following year’s notification, be regarded as the relevant specified days and times under PC.A.4.2.1:

(a)	the date and time of the annual peak of the National Electricity Transmission System Demand;

(b)	the date and time of the annual minimum of the National Electricity Transmission System Demand;

(c)	the relevant Access Period for each Transmission Interface Circuit; and,

(d)	concurrent Access Periods of two or more Transmission Interface Circuits (if any) that are situated in the same Access Group.

The submissions by The Company made under PC.A.4.2.1 (c) and PC.A.4.2.1 (d) above shall commence in 2010 and shall then continue in respect of each year thereafter.

PC.A.4.2.3	The total Active Energy used on each of the Network Operators’ or Non-Embedded Customers’ User Systems (each summated over all Grid Supply Points in each User System) in the preceding Financial Year, both outturn and weather corrected, together with a prediction for the current financial year, is required.  Each Active Energy submission shall be subdivided into the following categories of Customer tariff:

LV1

LV2

LV3

HV

EHV

Traction

Lighting

In addition, the total User System losses and the Active Energy provided by Embedded Small Power Stations and Embedded Medium Power Stations shall be supplied.

PC.A.4.2.4	All forecast Demand (Active Power) and Active Energy specified in PC.A.4.2.1 and PC.A.4.2.3 shall:

(a)	in the case of PC.A.4.2.1(a), (b) and (c), be such that the profiles comprise average Active Power levels in 'MW' for each time marked half hour throughout the day;

(b)	in the case of PC.A.4.2.1(a), (b) and (c), be that remaining after any deductions reasonably considered appropriate by the User to take account of the output profile of all Embedded Small Power Stations and Embedded Medium Power Stations and Customer Generating Plant and imports across Embedded External Interconnections including imports across Embedded installations of direct current converters which do not form a DC Converter Station or HVDC System and Embedded DC Converter Stations and Embedded HVDC Systems with a Registered Capacity  or HVDC Active Power Transmission Capacity of less than 100MW;

(c)	be based upon Annual ACS Conditions for times that occur during week 44 through to week 12 (inclusive) and based on Average Conditions for weeks 13 to 43 (inclusive).

PC.A.4.3 	Connection Point Demand (Active and Reactive Power)

PC.A.4.3.1 	Forecast Demand (Active Power) and Power Factor (values of the Power Factor at maximum and minimum continuous excitation may be given instead where more than 95% of the total Demand at a Connection Point is taken by synchronous motors) to be met at each Connection Point within each Access Group is required for:

(a)	the time of the maximum Demand (Active Power) at the Connection Point (as determined by the User) that in the User's opinion could reasonably be imposed on the National Electricity Transmission System;

(b)	the time of peak National Electricity Transmission System Demand as provided by The Company under PC.A.4.2.2;

(c)	the time of minimum National Electricity Transmission System Demand as provided by The Company under PC.A.4.2.2;

(d)	the time of the maximum Demand (Apparent Power) at the Connection Point (as determined by the User) during the Access Period of each Transmission Interface Circuit;

(e)	at a time specified by either The Company or a User insofar as such a request is reasonable.

Instead of such forecast Demand to be met at each Connection Point within each Access Group the User may (subject to PC.A.4.3.4) submit such Demand at each node on the Single Line Diagram.

In addition, the Demand in respect of each of the time periods referred to in PC.A.4.3.1 (a) to (e) in the preceding Financial Year in respect of each Connection Point within each Access Group both outturn and weather corrected shall be supplied.  The “weather correction” shall normalise outturn figures to Annual ACS Conditions for times that occur during calendar week 44 through to calendar week 12 (inclusive) or Average Conditions for the period calendar weeks 13 to calendar week 43 (inclusive) and shall be performed by the relevant User on a best endeavours basis.

The submission by a User pursuant to PC.A.4.3.1 (d) shall commence in 2011 and shall then continue each year thereafter.

PC.A.4.3.2	All forecast Demand specified in PC.A.4.3.1 shall:

(a)	be that remaining after any deductions reasonably considered appropriate by the User to take account of the output of all Embedded Small Power Stations and Embedded Medium Power Stations and Customer Generating Plant and imports across Embedded External Interconnections, including Embedded installations of direct current converters which do not form a DC Converter Station, HVDC System  and Embedded DC Converter Stations and Embedded HVDC Systems and such deductions should be separately stated;

(b)	include any User's System series reactive losses but exclude any reactive compensation equipment specified in PC.A.2.4 and exclude any network susceptance specified in PC.A.2.3;

(c)	be based upon Annual ACS Conditions for times that occur during calendar week 44 through to calendar week 12 (inclusive) and based on Average Conditions for calendar weeks 13 to calendar week 43 (inclusive), both corrections being made on a best endeavours basis;

(d)	reflect the User’s opinion of what could reasonably be imposed on the National Electricity Transmission System.

PC.A.4.3.3	The date and time of the forecast maximum Demand (Apparent Power) at the Connection Point as specified in PC.A.4.3.1 (a) and (d) is required.

PC.A.4.3.4	Each Single Line Diagram provided under PC.A.2.2.2 shall include the Demand (Active Power) and Power Factor (values of the Power Factor at maximum and minimum continuous excitation may be given instead where more than 95% of the Demand is taken by synchronous motors) at the time of the peak National Electricity Transmission System Demand (as provided under PC.A.4.2.2) at each node on the Single Line Diagram. These Demands shall be consistent with those provided under PC.A.4.3.1(b) above for the relevant year.

PC.A.4.3.5	The Single Line Diagram must represent the User’s User System layout under the period specified in PC.A.4.3.1(b) (at the time of peak National Electricity Transmission System Demand).  Should the User’s User System layout during the other times specified in PC.A.4.3.1 be planned to be materially different from the Single Line Diagram submitted to The Company pursuant to PC.A.2.2.1 the User shall in respect of such other times submit:

(i)	an alternative Single Line Diagram that accurately reflects the revised layout and in such case shall also include appropriate associated data representing the relevant changes, or;

(ii)	submit an accurate and unambiguous description of the changes to the Single Line Diagram previously submitted for the time of peak National Electricity Transmission System Demand.

Where a User does not submit any changes, The Company will assume that the Single Line Diagram (and associated circuit and node data) provided at the time of peak National Electricity Transmission System Demand will be valid for all other times.  In respect of such other times, where the User does not submit such nodal demands at the times defined in PC.A.4.3.1(a), (c), (d) and (e), the nodal demands will be pro-rata, to be consistent with the submitted Connection Point Demands.

PC.A.4.4	The Company will assemble and derive in a reasonable manner, the forecast information supplied to it under PC.A.4.2.1, PC.A.4.3.1, PC.A.4.3.4 and PC.A.4.3.5 above into a cohesive forecast and will use this in preparing Forecast Demand information in the Electricity Ten Year Statement and for use in The Company's Operational Planning. If any User believes that the cohesive forecast Demand information in the Electricity Ten Year Statement does not reflect its assumptions on Demand, it should contact The Company to explain its concerns and may require The Company, on reasonable request, to discuss these forecasts. In the absence of such expressions, The Company will assume that Users concur with The Company's cohesive forecast.

PC.A.4.5	Post Fault User System Layout

PC.A.4.5.1	Where for the purposes of The Company assessing against the Licence Standards an Access Group, the User reasonably considers it appropriate that revised post fault User System layouts should be taken into account by The Company, the following information is required to be submitted by the User:

(i)	the specified Connection Point assessment period (PC.A.4.3.1,(a)-(e)) that is being evaluated;

(ii)	an accurate and unambiguous description of the Transmission Interface Circuits considered to be switched out due to a fault;

(iii)	appropriate revised Single Line Diagrams and/or associated revised nodal Demand and circuit data detailing the revised User System(s) conditions;

(iv)	where the User’s planned post fault action consists of more than one component, each component must be explicitly identified using the Single Line Diagram and associated nodal Demand and circuit data;

(v)	the arrangements for undertaking actions (eg the time taken, automatic or manual and any other appropriate information);.

The User must not submit any action that it does not have the capability or the intention to implement during the assessment period specified (subject to there being no further unplanned outages on the User’s User System).

PC.A.4.6	Control of Demand or Reduction of Pumping Load Offered as Reserve

| Magnitude of Demand or pumping load or Electricity Storage Module charging load which is tripped | MW |
| --- | --- |
| System Frequency at which tripping is initiated | Hz |
| Time duration of System Frequency below trip setting for tripping to be initiated | S |
| Time delay from trip initiation to tripping | S |

PC.A.4.7	General Demand Data

PC.A.4.7.1	The following information is infrequently required and should be supplied (wherever possible) when requested by The Company:

(a)	details of any individual loads (including (as  applicable) the load  behaviour  of  an Electricity  Storage  Module when  operating  in  a  mode  analogous  to  demand) which have characteristics significantly different from the typical range of Domestic, Commercial , Electricity Storage or Industrial loads supplied;

(b)	the sensitivity of the Demand (Active and Reactive Power) to variations in voltage and Frequency on the National Electricity Transmission System at the time of the peak Demand (Active Power). The sensitivity factors quoted for the Demand (Reactive Power) should relate to that given under PC.A.4.3.1 and, therefore, include any User's System series reactive losses but exclude any reactive compensation equipment specified in PC.A.2.4 and exclude any network susceptance specified in PC.A.2.3;

(c)	details of any traction loads, e.g. connection phase pairs and continuous load variation with time;

(d)	the average and maximum phase unbalance, in magnitude and phase angle, which the User would expect its Demand to impose on the National Electricity Transmission System;

(e)	the maximum harmonic content which the User would expect its Demand to impose on the National Electricity Transmission System;

(f)	details of all loads which may cause Demand fluctuations greater than those permitted under Engineering Recommendation P28 Issue 2, Stage 1 at a Point of Common Coupling including the Flicker Severity Short Term and the Flicker Severity Long Term.

(g) In the case of Electricity Storage Modules, details of the Maximum Capacity, Maximum Import Power, Registered Import Capability, charge time, discharge time and operating periods.

## PART 2 - DETAILED PLANNING DATA

### PC.A.5	POWER GENERATING MODULE, GENERATING UNIT, POWER PARK MODULE (INCLUDING DC CONNECTED POWER PARK MODULES), DC CONVERTER, HVDC EQUIPMENT AND OTSDUW PLANT AND APPARATUS DATA

PC.A.5.1	Introduction

Directly Connected

PC.A.5.1.1	Each Generator (including those undertaking OTSDUW), with existing or proposed Power Stations directly connected, or to be directly connected, to the National Electricity Transmission System, shall provide The Company with data relating to that Plant and Apparatus, both current and forecast, as specified in PC.A.5.2, PC.A.5.3, PC.A.5.4 and PC.A.5.7 as applicable.

Each DC Converter Station owner or HVDC System Owner, with existing or proposed DC Converter Stations or HVDC Systems (including Generators undertaking OTSDUW which includes an OTSDUW DC Converter) directly connected, or to be directly connected, to the National Electricity Transmission System, shall provide The Company with data relating to that Plant and Apparatus, both current and forecast, as specified in PC.A.5.2 and PC.A.5.4.

GB Generators, DC Converter Station owners, EU Generators and HVDC System Owners shall ensure that the models supplied in respect of their Plant and Apparatus provide a true and accurate behaviour of the plant as built as required under PC.A.5.3.2(c), PC.A.5.4.2(a) and PC.A.5.4.3 and verified through the Compliance Processes (CP) or European Compliance Processes (ECP) as applicable.

Embedded

PC.A.5.1.2	Each Generator, in respect of its existing, or proposed, Embedded Large Power Stations and its Embedded Medium Power Stations subject to a Bilateral Agreement and each Network Operator in respect of Embedded Medium Power Stations not subject to a Bilateral Agreement within its System shall provide The Company with data relating to each of those Large Power Stations and Medium Power Stations, both current and forecast, as specified in PC.A.5.2, PC.A.5.3, PC.A.5.4 and PC.A.5.7 as applicable.

Each DC Converter Station owner or HVDC System Owner, or Network Operator in the case of an Embedded DC Converter Station or Embedded HVDC System not subject to a Bilateral Agreement within its System with existing or proposed HVDC Systems or DC Converter Stations shall provide The Company with data relating to each of those HVDC Systems or DC Converter Stations, both current and forecast, as specified in PC.A.5.2 and PC.A.5.4.

However, no data need be supplied in relation to those Embedded Medium Power Stations or Embedded DC Converter Stations or Embedded HVDC Systems if they are connected at a voltage level below the voltage level of the Subtransmission System except in connection with an application for, or under a, CUSC Contract or unless specifically requested by The Company under PC.A.5.1.4.

GB Generators, DC Converter Station owners, EU Generators and HVDC System Owners shall ensure that the models supplied in respect of their Plant and Apparatus provide a true and accurate behaviour of the plant as built as required under PC.A.5.3.2(c), PC.A.5.4.2(a) and PC.A.5.4.3 and verified through the Compliance Processes (CP) or European Compliance Processes (ECP) as applicable

PC.A.5.1.3	Each Network Operator need not submit Planning Data in respect of Embedded Small Power Stations unless required to do so under PC.A.1.2(b), PC.A.3.1.4 or unless specifically requested under PC.A.5.1.4 below, in which case they will supply such data.

PC.A.5.1.4	PC.A.4.2.4(b) and PC.A.4.3.2(a) explained that the forecast Demand submitted by each Network Operator must be net of the output of all Medium Power Stations and Small Power Stations and Customer Generating Plant Embedded within that User's System.  In such cases, the Network Operator must provide The Company with the relevant information specified under PC.A.3.1.4 .  On receipt of this data further details may be required at The Company's discretion as follows:

(i)	in the case of details required from the Network Operator for Embedded Medium Power Stations not subject to a Bilateral Agreement and Embedded DC Converter Stations not subject to a Bilateral Agreement and Embedded HVDC Systems not subject to a Bilateral Agreement and Embedded Small Power Stations and Embedded DC Converters and Embedded HVDC Systems in each case within such Network Operator’s System and Customer Generating Plant; and

(ii)	in the case of details required from the Generator of Embedded Large Power Stations and Embedded Medium Power Stations subject to a Bilateral Agreement; and

(iii)	in the case of details required from the DC Converter Station owner of an Embedded DC Converter or DC Converter Station or HVDC System Owner of an Embedded HVDC System Owner subject to a Bilateral Agreement.

both current and forecast, as specified in PC.A.5.2 and PC.A.5.3.  Such requirement would arise when The Company reasonably considers that the collective effect of a number of such Embedded Small Power Stations, Embedded Medium Power Stations, Embedded DC Converter Stations, Embedded HVDC Systems, DC Converters and Customer Generating Plants may have a significant system effect on the National Electricity Transmission System.

PC.A.5.1.5	DPD I and DPD II

The Detailed Planning Data described in this Part 2 of Appendix A comprises both DPD I and DPD II. The required data is listed and collated in the Data Registration Code. The Users need to refer to the DRC to establish whether data referred to here is DPD I or DPD II.

PC.A.5.2	Demand

PC.A.5.2.1	For each Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module) which has an associated Unit Transformer, the value of the Demand supplied through this Unit Transformer when the Generating Unit is at Rated MW output is to be provided.

PC.A.5.2.2	Where the Power Station or DC Converter Station or HVDC System has associated Demand additional to the unit-supplied Demand of PC.A.5.2.1 which is supplied from either the National Electricity Transmission System or the Generator's User System the Generator, DC Converter Station owner, HVDC System Owner or the Network Operator (in the case of Embedded Medium Power Stations not subject to a Bilateral Agreement within its System), as the case may be, shall supply forecasts for each Power Station or DC Converter Station or HVDC System of:

(a)	the maximum Demand that, in the User's opinion, could reasonably be imposed on the National Electricity Transmission System or the Generator's User System as appropriate;

(b)	the Demand at the time of the peak National Electricity Transmission System Demand

(c)	the Demand at the time of minimum National Electricity Transmission System Demand.

PC.A.5.2.3	No later than calendar week 17 each year The Company shall notify each Generator in respect of its Large Power Stations and its Medium Power Stations and each DC Converter owner in respect of its DC Converter Station and each HVDC System Owner in respect of its HVDC System subject to a Bilateral Agreement and each Network Operator in respect of each Embedded Medium Power Station not subject to a Bilateral Agreement and each Embedded DC Converter Station or Embedded HVDC System not subject to a Bilateral Agreement within such Network Operator’s System in writing of the following, for the current Financial Year and for each of the following nine Financial Years, which will be regarded as the relevant specified days and times under PC.A.5.2.2:

(a)	the date and time of the annual peak of the National Electricity Transmission System Demand at Annual ACS Conditions;

(b)	the date and time of the annual minimum of the National Electricity Transmission System Demand at Average Conditions.

PC.A.5.2.4	At its discretion, The Company may also request further details of the Demand as specified in PC.A.4.6

PC.A.5.2.5	In the case of OTSDUW Plant and Apparatus the following data shall be supplied:

(a)	The maximum Demand that could occur at the Interface Point and each Connection Point (in MW and MVAr);

(b)	Demand at specified time of annual peak half hour of National Electricity Transmission System Demand at Annual ACS Conditions (in MW and MVAr); and

(c)	Demand at specified time of annual minimum half-hour of National Electricity Transmission System Demand (in MW and MVAr).

For the avoidance of doubt, Demand data associated with Generators undertaking OTSDUW which utilise an OTSDUW DC Converter should supply data under PC.A.4.

PC.A.5.3	Synchronous Power Generating Modules, Synchronous Generating Unit and Associated Control System Data

PC.A.5.3.1	The data submitted below are not intended to constrain any Ancillary Services Agreement

PC.A.5.3.2	The following Synchronous Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module) and Power Station data should be supplied:

(a)	Synchronous Generating Unit Parameters

Rated terminal volts (kV)

Maximum terminal voltage set point (kV)

Terminal voltage set point step resolution –  if not continuous (kV)

*	Rated MVA

*	Rated MW

*	Minimum Generation MW

*	Short circuit ratio

Direct axis synchronous reactance

*	Direct axis transient reactance

Direct axis sub-transient reactance

Direct axis short-circuit transient time constant

Direct axis short-circuit sub-transient time constant

Quadrature axis synchronous reactance

Quadrature axis sub-transient reactance

Quadrature axis short-circuit sub-transient time constant.

Stator time constant

Stator leakage reactance

Armature winding direct-current resistance.

Note: The above data item relating to armature winding direct-current resistance need only be supplied with respect to Generating Units commissioned after 1st March 1996 and in cases where, for whatever reason, the Generator or the Network Operator, as the case may be is aware of the value of the relevant parameter.

*	Turbogenerator inertia constant (MWsec/MVA)

Rated field current (amps) at Rated MW and MVAr output and at rated terminal voltage.

Field current (amps) open circuit saturation curve for Generating Unit terminal voltages ranging from 50% to 120% of rated value in 10% steps as derived from appropriate manufacturers test certificates.

(b)	Parameters for Generating Unit Step-up Transformers

*	Rated MVA

Voltage ratio

*	Positive sequence reactance (at max, min, & nominal tap)

Positive sequence resistance (at max, min, & nominal tap)

Zero phase sequence reactance

Tap changer range

Tap changer step size

Tap changer type: on load or off circuit

(c)	Excitation Control System parameters

Note: The data items requested under Option 1 below may continue to be provided in relation to Generating Units connected to the System at 09 January 1995 (in this paragraph, the "relevant date") or the new data items set out under Option 2 may be provided.  Generators or Network Operators, as the case may be, must supply the data as set out under Option 2 (and not those under Option 1) for Generating Unit excitation control systems commissioned after the relevant date, those Generating Unit excitation control systems recommissioned for any reason such as refurbishment after the relevant date and Generating Unit excitation control systems where, as a result of testing or other process, the Generator or Network Operator, as the case may be, is aware of the data items listed under Option 2 in relation to that Generating Unit.

For any excitation control systems associated with a Generating Unit or Synchronous Power Generating Module with a Completion Date after 1 September 2022 and any Generating Unit or Synchronous Power Generating Module excitation control systems subject to a control system change or Modification after 1 September 2022, the Generator should supply the control system model in accordance with PC.A.9. For the avoidance of doubt, excitation control system models as detailed in PC.A.9 maybe submitted for any Generating Unit regardless of Completion Date as an alternative to block diagrams detailed below. The control system model of the Excitation System  shall include but not limited to, the PSS if fitted, Over-excitation Limiter, Under-excitation Limiter and should have been verified as far as reasonably practicable by simulation studies as representing the expected behaviour of the control system. Additionally the data items listed under Option 2 below are also required.

Option 1

DC gain of Excitation Loop

Rated field voltage

Maximum field voltage

Minimum field voltage

Maximum rate of change of field voltage (rising)

Maximum rate of change of field voltage (falling)

Details of Excitation Loop described in block diagram form showing transfer functions of individual elements.

Dynamic characteristics of Over-excitation Limiter

Dynamic characteristics of Under-excitation Limiter

Option 2

Excitation System Nominal Response

Rated Field Voltage

No-Load Field Voltage

Excitation System On-Load Positive Ceiling Voltage

Excitation System No-Load Positive Ceiling Voltage

Excitation System No-Load Negative Ceiling Voltage

Stator Current Limiter (applicable only to Synchronous Power Generating Modules)

Details of Excitation System (including PSS if fitted) described in block diagram form showing transfer functions of individual elements.

Details of Over-excitation Limiter described in block diagram form showing transfer functions of individual elements.

Details of Under-excitation Limiter described in block diagram form showing transfer functions of individual elements.

The block diagrams submitted after 1 January 2009 in respect of the Excitation System (including the Over-excitation Limiter and the Under-excitation Limiter) for Generating Units with a Completion date after 1 January 2009 or subject to a Modification to the Excitation System after 1 January 2009, should have been verified as far as reasonably practicable by simulation studies as representing the expected behaviour of the system.

(d)	Governor Parameters

Incremental Droop values (in %) are required for each Generating Unit at six MW loading points (MLP1 to MLP6) as detailed in PC.A.5.5.1 (this data item needs only be provided for Large Power Stations).

Note: The data items requested under Option 1 below may continue to be provided by Generators in relation to Generating Units on the System at 09 January 1995 (in this paragraph, the "relevant date") or they may provide the new data items set out under Option 2.  Generators must supply the data as set out under Option 2 (and not those under Option 1) for Generating Unit governor control systems commissioned after the relevant date, those Generating Unit governor control systems recommissioned for any reason such as refurbishment after the relevant date and Generating Unit governor control systems where, as a result of testing or other process, the Generator is aware of the data items listed under Option 2 in relation to that Generating Unit. EU Generators are also required to submit the data as set out in option 2.  Additional data required from EU Generators which own or operate Type C or Type D Power Generating Modules are marked in brackets with an asterisk (eg (*)).  For the avoidance of doubt,  items marked as (*) need not be supplied by GB Generators.

For any governor control systems associated with a Generating Unit or Synchronous Power Generating Module with a Completion Date after 1 September 2022 and any Generating Unit or Synchronous Power Generating Module governor control systems subject to a control system change or Modification after  1 September 2022, the Generator should supply the control system model in accordance with PC.A.9. For the avoidance of doubt, governor control system models as detailed in PC.A.9 maybe submitted for any Generating Unit regardless of Completion Date as an alternative to governor block diagrams. The control system model shall include but not limited to, the governor and prime mover dynamics such as steam flow, boiler, water flow which could impact on representation of the requirements required by the Grid Code. Additional the data items listed under Option 2 are also required.

Option 1

(i)	Governor Parameters (for Reheat Steam Units)

HP governor average gain MW/Hz

Speeder motor setting range

HP governor valve time constant

HP governor valve opening limits

HP governor valve rate limits

Reheater time constant (Active Energy stored in reheater)

IP governor average gain MW/Hz

IP governor setting range

IP governor valve time constant

IP governor valve opening limits

IP governor valve rate limits

Details of acceleration sensitive elements in HP & IP governor loop.

A governor block diagram showing transfer functions of individual elements.

(ii)	Governor Parameters (for Non-Reheat Steam Units and Gas Turbine Units)

Governor average gain

Speeder motor setting range

Time constant of steam or fuel governor valve

Governor valve opening limits

Governor valve rate limits

Time constant of turbine

Governor block diagram

The following data items need only be supplied for Large Power Stations:

(iii)	Boiler & Steam Turbine Data

Boiler Time Constant (Stored Active Energy) 	s

HP turbine response ratio:

proportion of Primary Response arising from HP turbine	%

HP turbine response ratio:

proportion of High Frequency Response arising from HP turbine	%

[End of Option 1]

Option 2

(i)	Governor and associated prime mover Parameters - All Generating Units (including Synchronous Generating Units within a Synchronous Power Generating Module)

Governor Block Diagram showing transfer function of individual elements including acceleration sensitive elements.

Governor Time Constant (in seconds)

Speeder Motor Setting Range (%)

Average Gain (MW/Hz)

Governor Deadband  need only be provided for Large Power Stations owned and operated by GB Generators (and both Frequency Response Deadband and Frequency Response Insensitivity should be supplied in respect of Type C and D Power Generating Modules within Large Power Stations and Medium Power Stations excluding Embedded Medium Power Stations not subject to a Bilateral Agreement*) owned and operated by EU Code Generators.

- Maximum Setting 	Hz

- Normal Setting	Hz

- Minimum Setting	Hz

Where the Generating Unit governor does not have a selectable Governor Deadband (or Frequency Response Deadband and  Frequency Response Insensitivity)* facility as specified above, then the actual value of the Governor Deadband or (Frequency Response Deadband and Frequency Response Insensitivity)* need only be provided.

The block diagrams submitted after 1 January 2009 in respect of the governor system for Generating Units with a Completion date after 1 January 2009 or subject to a Modification to the governor system after 1 January 2009, should have been verified as far as reasonably practicable by simulation studies as representing the expected behaviour of the system.

(ii)	Governor and associated prime mover Parameters - Steam Units

HP Valve Time Constant (in seconds)

HP Valve Opening Limits (%)

HP Valve Opening Rate Limits (%/second)

HP Valve Closing Rate Limits (%/second)

HP Turbine Time Constant (in seconds)

IP Valve Time Constant (in seconds)

IP Valve Opening Limits (%)

IP Valve Opening Rate Limits (%/second)

IP Valve Closing Rate Limits (%/second)

IP Turbine Time Constant (in seconds)

LP Valve Time Constant (in seconds)

LP Valve Opening Limits (%)

LP Valve Opening Rate Limits (%/second)

LP Valve Closing Rate Limits (%/second)

LP Turbine Time Constant (in seconds)

Reheater Time Constant (in seconds)

Boiler Time Constant (in seconds)

HP Power Fraction (%)

IP Power Fraction (%)

(iii)	Governor and associated prime mover Parameters - Gas Turbine Units

Inlet Guide Vane Time Constant (in seconds)

Inlet Guide Vane Opening Limits (%)

Inlet Guide Vane Opening Rate Limits (%/second)

Inlet Guide Vane Closing Rate Limits (%/second)

Fuel Valve Constant (in seconds)

Fuel Valve Opening Limits (%)

Fuel Valve Opening Rate Limits (%/second)

Fuel Valve Closing Rate Limits (%/second)

Waste Heat Recovery Boiler Time Constant (in seconds)

(iv)	Governor and associated prime mover Parameters - Hydro Generating Units

Guide Vane Actuator Time Constant (in seconds)

Guide Vane Opening Limits (%)

Guide Vane Opening Rate Limits (%/second)

Guide Vane Closing Rate Limits (%/second)

Water Time Constant (in seconds)

(v) Governor Parameters – Synchronous Electricity Storage Units

For Synchronous Electricity Storage Modules which are derived from compressed air energy storage systems, the following data should be  provided. For other Synchronous Electricity Storage Modules, data should be supplied as required by The Company in accordance with PC.A.7

Valve Actuator Time Constant (in seconds)

Valve Opening Limits (%)

Valve Opening Rate Limits (%/second)

Valve Closing Rate Limits (%/second)

[End of Option 2]

(e)	Unit Control Options

The following data items need only be supplied with respect to Large Power Stations:

Maximum Droop					%

Normal Droop					%

Minimum Droop					%

Maximum Governor Deadband or (maximum Frequency Response Deadband and maximum Frequency Response Insensitivity*)			Hz

Normal Governor Deadband or (normal Frequency Response Deadband and normal Frequency Response Insensitivity*)				Hz

Minimum Governor Deadband or (minimum Frequency Response Deadband and minimum Frequency Response Insensitivity*)			Hz

Maximum output Governor Deadband (or maximum output Frequency Response Deadband and maximum Frequency Response Insensitivity*)	MW

Normal output Governor Deadband (or normal output Frequency Response Deadband and normal output Frequency Response Insensitivity*)	MW

Minimum output Governor Deadband or (minimum output Frequency Response Deadband and minimum output Frequency Response Insensitivity*) 	MW

Frequency settings between which Unit Load Controller Droop applies:

- Maximum	Hz

- Normal	Hz

- Minimum	Hz

State if sustained response is normally selected.

(* GB Generators which are not required to satisfy the requirements of the European Connection Conditions are not required to supply Frequency Response Insensitivity or Frequency Response Deadband data but should instead supply Governor Deadband data). For the avoidance of doubt, EU Code Generators in respect of Type C and Type D Power Generating Modules are required to supply Frequency Response Deadband and Frequency Response Insensitivity data).

(f)	Plant Flexibility Performance

The following data items need only be supplied with respect to Large Power Stations, and should be provided with respect to each Genset:

#	Run-up rate to Registered Capacity,

#	Run-down rate from Registered Capacity,

#	Synchronising Generation,

Regulating range

Load rejection capability while still Synchronised and able to supply Load.

Data items marked with a hash (#) should be applicable to a Genset which has been Shutdown for 48 hours.

*	Data items marked with an asterisk are already requested under partx1, PC.A.3.3.1, to facilitate an early assessment by The Company as to whether detailed stability studies will be required before an offer of terms for a CUSC Contract can be made.  Such data items have been repeated here merely for completeness and need not, of course, be resubmitted unless their values, known or estimated, have changed.

(g)	Generating Unit Mechanical Parameters

It is occasionally necessary for The Company to assess the interaction between the Total System and the mechanical components of Generating Units.  For Generating Units (including Synchronous Generating Units within a Synchronous Power Generating Module) with a Completion Date on or after 01 April 2015,

or;

with a Completion Date before 01 April 2015 when requested by The Company in accordance with good industry practice and without undue delay,

the following data items should be supplied:

The number of turbine generator masses.

Diagram showing the Inertia and parameters for each turbine generator mass (kgm2) and Stiffness constants and parameters between each turbine generator mass for the complete drive train (Nm/rad).

Number of poles.

Relative power applied to different parts of the turbine (%).

Torsional mode frequencies (Hz).

Modal damping decrement factors for the different mechanical modes.

PC.A.5.4	Power Park Module, Non-Synchronous Generating Unit and Associated Control System Data

PC.A.5.4.1	The data submitted below are not intended to constrain any Ancillary Services Agreement

PC.A.5.4.2	The following Power Park Unit, Power Park Module and Power Station data should be supplied in the case of a Power Park Module not connected to the Total System by a DC Converter or HVDC System (and in the case of PC.A.5.4.2(f) any OTSUA):

Where a Manufacturer’s Data & Performance Report exists in respect of the model of the Power Park Unit, the User may subject to The Company’s agreement, opt to reference the Manufacturer’s Data & Performance Report as an alternative to the provision of data in accordance with PC.A.5.4.2 except for:

(1)	the section marked thus # at sub paragraph (b); and

(2)	all of the harmonic and flicker parameters required under sub paragraph (h); and

(3)	all of the site specific model parameters relating to the voltage or frequency control systems required under sub paragraphs (d) and (e),

which must be provided by the User in addition to the Manufacturer’s Data & Performance Report reference.

(a)	Power Park Unit model

A mathematical model of each type of Power Park Unit (including Electricity Storage Units) capable of representing its transient and dynamic behaviour under both small and large disturbance conditions. The model shall include non-linear effects and represent all equipment relevant to the dynamic performance of the Power Park Unit as agreed with The Company. The model shall be suitable for the study of balanced, root mean square, positive phase sequence time-domain behaviour, excluding the effects of electromagnetic transients, harmonic and sub-harmonic frequencies.

The model shall accurately represent the overall performance of the Power Park Unit over its entire operating range including that which is inherent to the Power Park Unit and that which is achieved by use of supplementary control systems providing either continuous or stepwise control. Model resolution should be sufficient to accurately represent Power Park Unit behaviour both in response to operation of Transmission System protection and in the context of longer-term simulations.

The overall structure of the model shall include:

(i)	any supplementary control signal modules not covered by (c), (d) and (e) below.

(ii)	any blocking, deblocking and protective trip features that are part of the Power Park Unit (e.g. “crowbar”).

(iii)	any other information required to model the Power Park Unit behaviour to meet the model functional requirement described above.

The model shall be submitted in the form of a transfer function block diagram and may be accompanied by dynamic and algebraic equations.

This model shall display all the transfer functions and their parameter values, any non wind-up logic, signal limits and non-linearities.

The submitted Power Park Unit model and the supplementary control signal module models covered by (c), (d) and (e) below shall have been validated and this shall be confirmed by the Generator. The validation shall be based on comparing the submitted model simulation results against measured test results. Validation evidence shall also be submitted and this shall include the simulation and measured test results. The latter shall include appropriate short-circuit tests.  In the case of an Embedded Medium Power Station not subject to a Bilateral Agreement the Network Operator will provide The Company with the validation evidence if requested by The Company.  The validation of the supplementary control signal module models covered by (c), (d) and (e) below applies only to a Power Park Module with a Completion Date after 1 January 2009 or Power Park Modules within a Power Generating Module.

(b)	Power Park Unit parameters

*	Rated MVA

*	Rated MW

*	Rated terminal voltage

*	Average site air density (kg/m3), maximum site air density (kg/m3) and minimum site air density (kg/m3) for the year (as applicable)

Year for which the air density is submitted (as applicable)

Number of pole pairs (as applicable)

Blade swept area (m2) (as applicable)

Gear box ratio (as applicable)

Mechanical drive train (as applicable)

For each Power Park Unit, details of the parameters of the drive train (as applicable) represented as an equivalent two mass model should be provided.  This model should accurately represent the behaviour of the complete drive train for the purposes of power system analysis studies and should include the following data items:-

Equivalent inertia constant (MWsec/MVA) of the first mass (e.g. wind turbine rotor and blades) at minimum, synchronous and rated speeds

Equivalent inertia constant (MWsec/MVA) of the second mass (e.g. generator rotor) at minimum, synchronous and rated speeds

Equivalent shaft stiffness between the two masses (Nm/electrical radian)

Additionally, for Power Park Units that are induction generators (e.g. squirrel cage, doubly-fed) driven by wind turbines:

*	Stator resistance

*	Stator reactance

*	Magnetising reactance.

*	Rotor resistance.(at starting)

*	Rotor resistance.(at rated running)

*	Rotor reactance (at starting)

*	Rotor reactance (at rated running)

Additionally for doubly-fed induction generators only:

The generator rotor speed range (minimum and maximum speeds in RPM)

The optimum generator rotor speed versus wind speed submitted in tabular format

Power converter rating (MVA)

The rotor power coefficient (Cp) versus tip speed ratio () curves for a range of blade angles (where applicable) together with the corresponding values submitted in tabular format.  The tip speed ratio () is defined as R/U where  is the angular velocity of the rotor, R is the radius of the wind turbine rotor and U is the wind speed.

The electrical power output versus generator rotor speed for a range of wind speeds over the entire operating range of the Power Park Unit, together with the corresponding values submitted in tabular format.

The blade angle versus wind speed curve together with the corresponding values submitted in tabular format.

The electrical power output versus wind speed over the entire operating range of the Power Park Unit, together with the corresponding values submitted in tabular format.

Transfer function block diagram, including parameters and description of the operation of the power electronic converter and fault ride through capability (where applicable). For any Power Park Units in a Power Park Module with a Completion Date after 1 September 2022 and any Power Park Units subject to a control system change or Modification after 1 September 2022 control system models in accordance with PC.A.9 should be supplied. For the avoidance of doubt, a User may submit control system models as detailed in PC.A.9 for any Power Park Unit regardless of Power Park Module Completion Date as an alternative to this paragraph.

For a Power Park Unit consisting of a synchronous machine in combination with a back to back DC Converter or HVDC System,  or for a Power Park Unit not driven by a wind turbine, the data to be supplied shall be agreed with The Company in accordance with PC.A.7.

(c)	Torque / speed and blade angle control systems and parameters

For the type of Power Park Unit (as applicable), details of the torque / speed controller and blade angle controller in the case of a wind turbine and power limitation functions (where applicable) described in block diagram form showing transfer functions and parameters of individual elements.

(d)	Voltage/Reactive Power/Power Factor control system parameters

For the Power Park Unit and Power Park Module details of voltage/Reactive Power/Power Factor controller (and PSS if fitted) described in block diagram form showing transfer functions and parameters of individual elements.

(e)	Frequency control system parameters

For the Power Park Unit and Power Park Module details of the Frequency controller described in block diagram form showing transfer functions and parameters of individual elements.

(f)	Protection

Details of settings for the following Protection relays (to include): Under Frequency, over Frequency, under voltage, over voltage, rotor over current, stator over current, high wind speed shut down level.

(g)	Complete Power Park Unit model, parameters and controls

(i) For any Power Park Units in a Power Park Module with a Completion Date after 1 September 2022 and any Power Park Units and/or Power Park Module(s) subject to a control system change or Modification after 1 September 2022, control system models in accordance with PC.A.9 should be supplied covering the full information required under PC.A.5.4.2 (a), (b), (c), (d), (e) and (f).

(ii) For any Power Park Units in a Power Park Module with a Completion Date before 1 September 2022 as an alternative to PC.A.5.4.2 (a), (b), (c), (d), (e) and (f), is the submission of a single complete model that consists of the full information required under PC.A.5.4.2 (a), (b), (c), (d), (e) and (f) provided that all the information required under PC.A.5.4.2 (a), (b), (c), (d), (e) and (f) individually is clearly identifiable. For the avoidance of doubt, a User may submit control system models as detailed in PC.A.9 for any Power Park Unit or Power Park Module regardless of Completion Date as an alternative to this clause.

(h)	Harmonic and flicker parameters

When connecting a Power Park Module, it is necessary for The Company to evaluate the production of flicker and harmonics on the National Electricity Transmission System and User's Systems.  At The Company's reasonable request, the User (a Network Operator in the case of an Embedded Power Park Module not subject to a Bilateral Agreement) is required to submit the following data (as defined in IEC 61400-21 (2001)) for each Power Park Unit:-

Flicker coefficient for continuous operation.

Flicker step factor.

Number of switching operations in a 10 minute window.

Number of switching operations in a 2 hour window.

Voltage change factor.

Current Injection at each harmonic for each Power Park Unit and for each Power Park Module.

* Data items marked with an asterisk are already requested under part 1, PC.A.3.3.1, to facilitate an early assessment by The Company as to whether detailed stability studies will be required before an offer of terms for a CUSC Contract can be made.  Such data items have been repeated here merely for completeness and need not, of course, be resubmitted unless their values, known or estimated, have changed.

PC.A.5.4.3	DC Converter and HVDC Systems

PC.A.5.4.3.1	For a DC Converter at a DC Converter Station or an HVDC System connected to the Total System by a DC Converter or HVDC System (or in the case of OTSUA which includes an OTSDUW DC Converter) the following information for each DC Converter, HVDC System  and DC Network should be supplied:

(a)	DC Converter and HVDC System parameters

*	Rated MW per pole for transfer in each direction;

*	DC Converter type (i.e. current or voltage source (including a HVDC Converter in an HVDC System));

*	Number of poles and pole arrangement;

*	Rated DC voltage/pole (kV);

*	Return path arrangement;

(b)	DC Converter and HVDC System transformer parameters

Rated MVA

Nominal primary voltage (kV);

Nominal secondary (converter-side) voltage(s) (kV);

Winding and earthing arrangement;

Positive phase sequence reactance at minimum, maximum and nominal tap;

Positive phase sequence resistance at minimum, maximum and nominal tap;

Zero phase sequence reactance;

Tap-changer range in %;

number of tap-changer steps;

(c)	DC Network parameters

Rated DC voltage per pole;

Rated DC current per pole;

Single line diagram of the complete DC Network and HVDC System;

Details of the complete DC Network, including resistance, inductance and capacitance of all DC cables and/or DC lines and HVDC System;

Details of any DC reactors (including DC reactor resistance), DC capacitors and/or DC-side filters that form part of the DC Network and/or HVDC System;

(d)	AC filter reactive compensation equipment parameters

Note: The data provided pursuant to this paragraph must not include any contribution from reactive compensation plant.

Total number of AC filter banks.

Type of equipment (e.g. fixed or variable)

Single line diagram of filter arrangement and connections;

Reactive Power rating for each AC filter bank, capacitor bank or operating range of each item of reactive compensation equipment, at rated voltage;

Performance chart showing Reactive Power capability of the DC Converter and HVDC System, as a function of MW transfer, with all filters and reactive compensation plant, belonging to the DC Converter Station or HVDC System working correctly.

Note: Details in PC.A.5.4.3.1 are required for each DC Converter connected to the DC Network and HVDC System, unless each is identical or where the data has already been submitted for an identical DC Converter or HVDC System at another Connection Point.

Note: For a Power Park Module and DC Connected Power Park Module connected to the Grid Entry Point or (User System Entry Point if Embedded) by a DC Converter or HVDC System the equivalent inertia and fault infeed at the Power Park Unit should be given.

DC Converter and HVDC System Control System Models

PC.A.5.4.3.2	The following data is required by The Company to represent DC Converters and associated DC Networks and HVDC Systems (and including OTSUA which includes an OTSDUW DC Converter) in dynamic power system simulations,

(a)   For DC Converters and HVDC Systems with a Completion Date before 1 September 2022 in which the AC power system is typically represented by a positive sequence equivalent, it is acceptable to represent DC Converters and HVDC Systems by simplified equations rather than to the switching device level.

(i)	Static VDC-IDC (DC voltage - DC current) characteristics, for both the rectifier and inverter modes for a current source converter. Static VDC-PDC (DC voltage - DC power) characteristics, for both the rectifier and inverter modes for a voltage source converter. Transfer function block diagram including parameters representation of the control systems of each DC Converter and of the DC Converter Station and the HVDC System, for both the rectifier and inverter modes. A suitable model would feature the DC Converter or HVDC Converter firing angle as the output variable.

(ii)	Transfer function block diagram representation including parameters of the DC Converter or HVDC Converter transformer tap changer control systems, including time delays

(iii)	Transfer function block diagram representation including	parameters of AC filter and reactive compensation equipment control systems, including any time delays.

(iv)	Transfer function block diagram representation including parameters of any Frequency and/or load control systems.

(v)	Transfer function block diagram representation including parameters of any small signal modulation controls such as power oscillation damping controls or sub-synchronous oscillation damping controls, that have not been submitted as part of the above control system data.

(vi)	Transfer block diagram representation of the Reactive Power control at converter ends for a voltage source converter.

In addition and where not provided for above, HVDC System Owners and Generators in respect of OTSDUW DC Converters who are also EU Code Users shall also provide the following dynamic simulation sub-models

- HVDC Converter unit models

- AC component models

- DC Grid models

- Voltage and power controller

- Special control features if applicable (eg power oscillation damping (POD) function, subsynchronous torsional interaction (SSTI) control;

- Multi terminal control, if applicable

- HVDC System protection models as agreed between The Company and the HVDC System Owner

HVDC System Owners are also required to supply an equivalent model of the control system when adverse control interactions may result with HVDC Converter Stations and other connections in close proximity if requested by The Company.  The equivalent model shall contain all necessary data for the realistic simulation of the adverse control interactions.

(b) 	For any DC Converters and HVDC Systems with a Completion Date after 1 September 2022 and any DC Converters and HVDC Systems subject to a control system change or Modification after 1 September 2022, control system models in accordance with PC.A.9 should be supplied covering the full functionality required under PC.A.5.4.3.2 (a).

For the avoidance of doubt a User may submit control system models as detailed in PC.A.9 for any DC Converters and HVDC Systems regardless of Completion Date as an alternative to PC.A.5.4.3.2(a).

Plant Flexibility Performance

PC.A.5.4.3.3	The following information on plant flexibility and performance should be supplied (and also in respect of OTSUA which includes an OTSDUW DC Converter):

(i)	Nominal and maximum (emergency) loading rate with the DC Converter or HVDC Converter in rectifier mode.

(ii)	Nominal and maximum (emergency) loading rate with the DC Converter or HVDC Converter in inverter mode.

(iii)	Maximum recovery time, to 90% of pre-fault loading, following an AC system fault or severe voltage depression.

(iv)	Maximum recovery time, to 90% of pre-fault loading, following a transient DC Network fault.

Harmonic Assessment Information

PC.A.5.4.3.4	DC Converter owners and HVDC System Owners shall provide such additional further information as required by The Company in order that compliance with CC.6.1.5 or ECC.6.1.5 can be demonstrated.

* Data items marked with an asterisk are already requested under part 1, PC.A.3.3.1, to facilitate an early assessment by The Company as to whether detailed stability studies will be required before an offer of terms for a CUSC Contract can be made.  Such data items have been repeated here merely for completeness and need not, of course, be resubmitted unless their values, known or estimated, have changed.

PC.A.5.5	Response Data For Frequency Changes

The information detailed below is required to describe the actual frequency response capability profile as illustrated in Figure CC.A.3.1 of the Connection Conditions or Figure   ECC.A.3.1 of  the European Connection Conditions, and need only be provided for each:

(i)	Genset at Large Power Stations; and

(ii)	Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module), Power Park Module (including a DC Connected Power Park Module) or CCGT Module at a Medium Power Station or DC Converter Station or HVDC System that has agreed to provide Frequency response in accordance with a CUSC Contract.

In the case of (ii) above for the rest of this PC.A.5.5 where reference is made to Gensets, it shall include such Generating Units (including Synchronous Generating Units within a Synchronous Power Generating Module), CCGT Modules, Power Park Modules (including DC Connected Power Park Modules), HVDC Systems and DC Converters as appropriate, but excludes OTSDUW Plant and Apparatus utilising OTSDUW DC Converters.

In this PC.A.5.5, for a CCGT Module with more than one Generating Unit, the phrase Minimum Generation or Minimum Regulating Level applies to the entire CCGT Module operating with all Generating Units (including Synchronous Generating Units within a Synchronous Power Generating Module) Synchronised to the System. Similarly for a Power Park Module (including a DC Connected Power Park Module) with more than one Power Park Unit, the phrase Minimum Generation or Minimum Regulating Level applies to the entire Power Park Module operating with all Power Park Units Synchronised to the System.

PC.A.5.5.1	MW Loading Points At Which Data Is Required

Response values are required at six MW loading points (MLP1 to MLP6) for each Genset.  Primary and Secondary Response values need not be provided for MW loading points which are below Minimum Generation or Minimum Stable Operating Level.  MLP1 to MLP6 must be provided to the nearest MW.

Prior to the Genset being first Synchronised, the MW loading points must take the following values :

MLP1	Designed Minimum Operating Level or Minimum Regulating Level

MLP2	Minimum Generation or Minimum Stable Operating Level

MLP3	70% of Registered Capacity or Maximum Capacity

MLP4	80% of Registered Capacity or Maximum Capacity

MLP5	95% of Registered Capacity or Maximum Capacity

MLP6	Registered Capacity or Maximum Capacity

When data is provided after the Genset is first Synchronised, the MW loading points may take any value between the Designed Minimum Operating Level or Minimum Regulating Level and Registered Capacity or Maximum Capacity but the value of the Designed Minimum Operating Level or Minimum Regulating Level must still be provided if it does not form one of the MW loading points.

PC.A.5.5.2	Primary And Secondary Response To Frequency Fall

Primary and Secondary Response values for a -0.5Hz ramp are required at six MW loading points (MLP1 to MLP6) as detailed above

PC.A.5.5.3	High Frequency Response To Frequency Rise

High Frequency Response values for a +0.5Hz ramp are required at six MW loading points (MLP1 to MLP6) as detailed above.

PC.A.5.5.4	Each Generator or Defence Service Provider or Restoration Contractor or Non-Embedded Customer in respect of an Electricity Storage Module, shall provide Frequency response curves that demonstrate the ability of their Electricity Storage Modules to transition from a mode analogous to Demand to a mode analogous to generation (excluding Auxiliary Supplies) within a period of 20 seconds or less in accordance with the requirements of ECC.6.3.7.2.3, unless the provisions of ECC.6.3.7.2.3.1 apply where the requirements of OC6.6.6. relate.

PC.A.5.6	Mothballed Power Generating Module, Mothballed Generating Unit, Mothballed Power Park Module (including DC Connected Power Park Modules), Mothballed HVDC Systems or Mothballed DC Converter at a DC Converter Station And Alternative Fuel Information

Data identified under this section PC.A.5.6 must be submitted as required under PC.A.1.2 and at The Company’s reasonable request.

In the case of Embedded Medium Power Stations not subject to a Bilateral Agreement, Embedded HVDC Systems not subject to a Bilateral Agreement and Embedded DC Converter Stations not subject to a Bilateral Agreement, upon request from The Company each Network Operator shall provide the information required in PC.A.5.6.1, PC.A.5.6.2, PC.A.5.6.3 and PC.A.5.6.4 on respect of such Embedded Medium Power Stations and Embedded DC Converters Stations and Embedded HVDC Systems with their System.

PC.A.5.6.1	Mothballed Generating Unit Information

Generators, HVDC System Owners and DC Converter Station owners must supply with respect to each Mothballed Power Generating Module, Mothballed Generating Unit, Mothballed Power Park Module (including a DC Connected Power Park Module), Mothballed HVDC System or Mothballed DC Converter at a DC Converter Station the estimated MW output which could be returned to service within the following time periods from the time that a decision to return was made:

< 1 month;

1-2 months;

2-3 months;

3-6 months;

6-12 months; and

>12 months.

The return to service time should be determined in accordance with Good Industry Practice assuming normal working arrangements and normal plant procurement lead times. The MW output values should be the incremental values made available in each time period as further described in the DRC.

PC.A.5.6.2	Generators, HVDC System Owners and DC Converter Station owners must also notify The Company of any significant factors which may prevent the Mothballed Power Generating Module, Mothballed Generating Unit, Mothballed Power Park Module (including DC Connected Power Park Modules), Mothballed HVDC Systems or Mothballed DC Converter at a DC Converter Station achieving the estimated values provided under PC.A.5.6.1 above, excluding factors relating to Transmission Entry Capacity.

PC.A.5.6.3	Alternative Fuel Information

The following data items must be supplied with respect to each Generating Unit (including Synchronous Generating Units within a Synchronous Power Generating Module) whose main fuel is gas.

For each alternative fuel type (if facility installed):

(a)	Alternative fuel type e.g. oil distillate, alternative gas supply

(b)	For the changeover from main to alternative fuel:

-	Time to carry out off-line and on-line fuel changeover (minutes).

-	Maximum output following off-line and on-line changeover (MW).

-	Maximum output during on-line fuel changeover (MW).

-	Maximum operating time at full load assuming typical and maximum possible stock levels (hours).

-	Maximum rate of replacement of depleted stocks (MWh electrical/day) on the basis of Good Industry Practice.

-	Is changeover to alternative fuel used in normal operating arrangements?

-	Number of successful changeovers carried out in the last of The Company’s Financial Year (choice of 0, 1-5, 6-10, 11-20, >20).

(c)	For the changeover back to main fuel:

-	Time to carry out off-line and on-line fuel changeover (minutes).

-	Maximum output during on-line fuel changeover (MW).

PC.A.5.6.4	Generators must also notify The Company of any significant factors and their effects which may prevent the use of alternative fuels achieving the estimated values provided under PC.A.5.6.3 above (e.g. emissions limits, distilled water stocks etc.)

PC.A.5.7	System Restoration Related Information

PC.A.5.7.1	Data identified under this section PC.A.5.7.1 must be submitted as required under PC.A.1.2. This information may also be requested by The Company during System Restoration and should be provided by Generators, HVDC System Owners and DC Converter Station Owners where reasonably possible.  For the avoidance of doubt, Generators in this section PC.A.5.7.1 means each Generator in respect of their BM Unit at any directly connected Power Station or Large Power Station (excluding Generators in respect of Embedded Medium Power Stations and Embedded Small Power Stations).

The data items/text in (a) and (b) below must be supplied, by each Generator and HVDC System Owner and DC Converter Station owner to The Company. In the case of Generators, the data supplied should be with respect to each BM Unit at any directly connected Power Station or Large Power Station.  For the avoidance of doubt, the data required under PC.A.5.7.1(a) and (b) below, i) does not need to be supplied in respect of Restoration Contractors Plant  and ii), only needs to be supplied in respect of each BM Unit at a Large Power Station or any directly connected Power Station and does not need to include Generating Unit data;

(a) 	The expected time for each BM Unit to be Synchronised following a Total Shutdown or Partial Shutdown.  The assessment should include the Power Stations or HVDC Systems or DC Converter Stations ability to re-synchronise all BM Units, if all were running immediately prior to the Total Shutdown or Partial Shutdown once auxiliary supplies have been restored, or supplies have been restored to the User’s Site where the Plant was running immediately prior to the Shutdown) and at time intervals of 12 hours, 24 hours, 36 hours, 48 hours and 72 hours before the BM Unit had been Shutdown. Additionally this should highlight any specific issues (i.e. those that would have an impact on the BM Unit’s time to be Synchronised) that may arise, as time progresses without external supplies being restored or the availability of primary fuel supplies.  In submitting this data, Generators, HVDC System Owners and DC Converter Station owners should be aware of the requirements in CC.7.11 or ECC.7.11.

(b)	Block Loading Capability. This should be provided in either graphical or tabular format showing the estimated block loading capability from 0MW to Registered Capacity and the time between each incremental step. Any particular Active Power loading points at which the BM Unit should be operated until further changes in output can be accommodated should also be identified. The data of each BM Unit should be provided for the condition of a Generating Unit (which was running immediately prior to the Shutdown) and at time intervals of 12 hours, 24 hours, 36 hours, 48 hours and 72 hours before the BM Unit had been Shutdown.  In the case of an HVDC System or DC Converter Station, data should be provided when the HVDC System or DC Converter Station (which was running immediately prior to the Shutdown) and at time intervals of 12 hours, 24 hours, 36 hours, 48 hours and 72 hours prior to the HVDC System or DC Converter Station had been Shutdown. The block loading assessment should be done against a frequency variation of 47.5Hz – 52Hz.

PC.A.5.7.2	Where a Network Operator has a Distribution Restoration Zone Plan in place, the data specified in this section shall be submitted as required under PC.A.1.2 by Network Operators to The Company annually by calendar week 28.  This information may also be requested by The Company from the relevant Network Operator during System Restoration and should be provided by Network Operators where reasonably practicable.  Restoration Contractors party to a Distribution Restoration Zone Plan shall, where reasonably practicable, submit the relevant information to the Network Operator who shall then supply the relevant information to The Company.  The following data shall be provided;

- The expected time for each Restoration Contractor’s Plant to Re-Synchronise to the Network Operator’s System following a Total Shutdown or Partial Shutdown.  The assessment should include the Restoration Contractor’s ability to Re-Synchronise all their Plant, if all were running immediately prior to the Total Shutdown or Partial Shutdown.  Additionally, the data and supporting text should highlight any specific issues (eg those that would affect the time before which the Restoration Contractor’s Plant could be energised) that may arise as time progresses from Shutdown without external supplies being restored or the availability of primary fuel supplies.

- The Restoration Contractor’s Plants Block Loading Capability as required in        PC.A.5.7.1(b).

PC.A.5.7.3	From 31st December 2026 onwards, all Users and Restoration Contractors are required to confirm annually they comply with the applicable requirements of OC5.7.  In the case of Generators, HVDC System Owners, DC Converter owners, Non-Embedded Customers, and Network Operators this confirmation shall be provided in their Week 24 submission.  From 1st January 2024 until 31st December 2026, evidence to support the work Generators, HVDC System Owners, DC Converter owners, Non-Embedded Customers, and Network Operators are carrying out to achieve these requirements on or after 31st  December 2026 shall be provided in their Week 24 submission.

PC.A.5.7.4	From 1st January 2025 onwards, Restoration Contractors, Generators, HVDC System Owners and DC Converter owners, shall supply the governor setting information in accordance with the applicable requirements of CC.6.3.7(g), (h) and (i) or ECC.6.3.7.3.8.

PC.A.5.8	Grid Forming Related Information

PC.A.5.8.1	The following data need only be supplied by Users (be they a GB Code User or EU Code User) or Non-CUSC Parties who wish to offer a Grid Forming Capability as provided for ECC.6.3.19.3.  Where such a Grid Forming Capability is provided then the following data items and models are to be supplied.

- Each GBGF-I shall be designed so as not to interact and affect the operation, performance, safety or capability of other User’s Plant and Apparatus connected to the Total System. To achieve this requirement, each User shall be required to submit a Network Frequency Perturbation Plot and Nichols Chart (or equivalent as agreed with The Company) which shall be assessed in accordance with the requirements of ECP.A.3.9.3.

Each User or Non-CUSC Party is required to supply a high level equivalent architecture diagram of their Grid Forming Plant as shown in Figure PC.A.5.8.1 together with the equivalent linear classical block diagram model (using the Laplace Operator) of their Grid Forming Plant which should preferably be in the general form shown in Figure PC.A.5.8.1 (a) or Figure PC.A.5.8.1 (b).  When submitting either Figure PC.A.5.8.1 (a) or Figure PC.A.5.8.1 (b), each User or Non-CUSC Party can use their own design, that may be very different to Figures PC.A.5.8.1 (a) or PC.A.5.8.1 (b), but should contain all relevant functions that can include simulation models and other equivalent data and documentation.

Each User or Non-CUSC Party shall provide a model of their Grid Forming Plant which provides a true and accurate reflection of its Grid Forming Capability.

Figure PC.A.5.8.1

Figure PC.A.5.8.1 (a) Preferred simplified diagram of a GBGF-I with a Power System Stabiliser “PSS” that can add damping to the GBGF-I’s closed loop function shown by the solid red line and the dotted blue line.

Figure PC.A.5.8.1 (b) – Preferred simplified diagram of a system with a droop control ability that can add Control-Based Active Droop Power. This diagram does not add extra closed loop damping to the GBGF-I’s closed loop function shown by the solid red line and the dotted blue line.

- In order to participate in the Grid Forming Capability market, User’s and Non-CUSC Parties are required to provide data of their GBGF-I in accordance with Figures PC.A.5.8.1(a) and PC.A.5.8.1(b). Users and Non-CUSC Parties in respect of Grid Forming Plants should indicate if the data is submitted on a unit or aggregated basis.   Table PC.A.5.8.1(a) defines the notation used in Figure PC.5.8.1

| Parameter | Symbol | Units |
| --- | --- | --- |
| The primary reactance of the Grid Forming Unit, in pu. | Xin or Xts | pu on MVA Rating of Grid Forming Unit |
| The additional reactance, in pu, between the terminals of the Grid Forming Unit and the Grid Entry Point or User System Entry Point (if Embedded). | Xtr | pu on MVA Rating of Grid Forming Unit |
| The rated angle between the Internal Voltage Source and the input terminals of the Grid Forming Unit. |  | radians |
| The rated angle between the Internal Voltage Source and Grid Entry Point or User System Entry Point (if Embedded). |  | radians |
| The rated voltage and phase of the Internal Voltage Source of the Grid Forming Unit. |  | Voltage - pu Phase - radians |
| The rated electrical angle between current and voltage at the input to the Grid transformer. |  | radians |

Table PC.A.5.8.1

- In order to participate in a Grid Forming Capability market, User’s and Non-CUSC Parties are also required to provide the data of their GBGF-I in accordance with Table PC.A.5.8.1.2 to The Company. The details and arrangements for Users and Non-CUSC Parties participating in this market shall be published on The Company’s Website.

| Quantity | Units | Range (where Applicable) | User Defined Parameter |
| --- | --- | --- | --- |
| Type of Grid Forming Plant (eg Generating Unit, Electricity Storage Module, Dynamic Reactive Compensation Equipment etc) | N/A |  |  |
| Maximum Continuous Rating at Registered Capacity or Maximum Capacity | MVA |  |  |
| Primary reactance Xin or Xts (see Table PC.A.5.8.1) | pu on MVA |  |  |
| Additional reactance Xtr (See Table PC.A.5.8.1) | pu on MVA |  |  |
| Maximum Capacity | MW |  |  |
| Active ROCOF Response Power (MW) injected or absorbed at 1Hz/s System Frequency change (which is the maximum frequency change for linear operation of the Grid Forming Plant) | MW |  |  |
| Phase Jump Angle Withstand | degrees |  | 60 degrees specified |
| Phase Jump Angle limit | degrees |  | 5 degrees recommended |
| Phase Jump Power (MW) at the rated angle | MW |  |  |
| Defined Active Damping Power for a Grid Oscillation Value of 0.05 Hz peak to peak at 1 Hz | MW |  |  |
| The cumulative energy delivered for a 1Hz/s System Frequency fall from 52 Hz to 47 Hz. This is the total Active Power transient output of the Grid Forming Plant | MWs or MJ |  |  |
| Inertia Constant (H) using equation 1 or declared in accordance with the simulation results of ECP.A.3.9.4 | MWs/MVA |  |  |
| Inertia Constant (He) using equation 2 or declared in accordance with the simulation results of ECP.A.3.9.4 | MWs/MVA |  |  |
| Continuous Overload Capability | % on MVA |  |  |
| Short Term duration Overload capability |  |  |  |
| Duration of Short Term Overload Capability | s |  |  |
| Peak Current Rating | Pu |  |  |
| Nominal Grid Entry Point or User System Entry Point voltage | kV |  |  |
| Grid Entry Point or User System Entry Point | - Location |  |  |
| Continuous or defined time duration MVA Rating | MVA |  |  |
| Continuous or defined time duration MW Rating | MW |  |  |
| For a GBGF-I the inverters maximum Internal Voltage Source (IVS) for the worst case condition – for example operation at maximum exporting Reactive Power at the maximum AC System voltage | pu |  |  |
| Maximum Three Phase Short Circuit Infeed at Grid Entry Point or User System Entry Point | kA |  |  |
| Maximum Single Phase Short Circuit Infeed at Grid Entry Point or User System Entry Point | kA |  |  |
| Will the Grid Forming Plant contribute to any other form of commercial service – for example Dynamic Containment, Firm Frequency Response, | Details to be provided |  |  |
| Equivalent Damping Factor. | Ζ |  | 0.2 to 5.0 allowed |

Table PC.A.5.8.2

H = Installed MWs / Rated installed MVA

(equation 1)

He = (Active ROCOF Response Power at 1 Hz / s x System Frequency) / ( Installed MVA x 2 )

(equation 2)

### PC.A.6	USERS' SYSTEM DATA

PC.A.6.1	Introduction

PC.A.6.1.1	Each User, whether connected directly via an existing Connection Point to the National Electricity Transmission System or seeking such a direct connection, or providing terms for connection of an Offshore Transmission System to its User System to The Company or undertaking OTSDUW, shall provide The Company with data on its User System or OTSDUW Plant and Apparatus which relates to the Connection Site containing the Connection Point (or Interface Points or Connection Points  in the case of OTSUA) both current and forecast, as specified in PC.A.6.2 to PC.A.6.6.

PC.A.6.1.2	Each User must reflect the system effect at the Connection Site(s) of any third party Embedded within its User System whether existing or proposed.

PC.A.6.1.3	PC.A.6.2, and PC.A.6.4 to PC.A.6.7 consist of data which is only to be supplied to The Company at The Company’s reasonable request. In the event that The Company identifies a reason for requiring this data, The Company shall write to the relevant User(s), requesting the data, and explaining the reasons for the request. If the User(s) wishes, The Company shall also arrange a meeting at which the request for data can be discussed, with the objective of identifying the best way in which The Company’s requirements can be met.  In respect of EU Code User(s) only, The Company may request the need for electromagnetic transient simulations at The Company’s reasonable request. Users  with EU Grid Supply Points may be required to provide electromagnetic transient simulations in relation to those EU Grid Supply Points at The Company’s reasonable request.

Where The Company makes a request to a User for dynamic models under PC.A.6.7, each relevant User shall ensure that the models supplied in respect of their Plant and Apparatus reflect the true and accurate behaviour of the Plant and Apparatus as built and verified through the Compliance Processes (CP’s) or European Compliance Processes (ECP).

PC.A.6.2	Transient Overvoltage Assessment Data

PC.A.6.2.1	It is occasionally necessary for The Company to undertake transient overvoltage assessments (e.g. capacitor switching transients, switchgear transient recovery voltages, etc).  At The Company’s reasonable request, each User is required to provide the following data with respect to the Connection Site (and in the case of OTSUA, Interface Points and Connection Points), current and forecast, together with a Single Line Diagram where not already supplied under PC.A.2.2.1, as follows:

(a)	busbar layout plan(s), including dimensions and geometry showing positioning of any current and voltage transformers, through bushings, support insulators, disconnectors, circuit breakers, surge arresters, etc. Electrical parameters of any associated current and voltage transformers, stray capacitances of wall bushings and support insulators, and grading capacitances of circuit breakers;

(b)	Electrical parameters and physical construction details of lines and cables connected at that busbar.  Electrical parameters of all plant e.g., transformers (including neutral earthing impedance or zig-zag transformers, if any), series reactors and shunt compensation equipment connected at that busbar (or to the tertiary of a transformer) or by lines or cables to that busbar;

(c)	Basic insulation levels (BIL) of all Apparatus connected directly, by lines or by cables to the busbar;

(d)	characteristics of overvoltage Protection devices at the busbar and at the termination points of all lines, and all cables connected to the busbar;

(e)	fault levels at the lower voltage terminals of each transformer connected directly or indirectly to the National Electricity Transmission System (including OTSUA at each Interface Point and Connection Point) without intermediate transformation;

(f)	the following data is required on all transformers operating at Supergrid Voltage throughout Great Britain and, in Scotland and Offshore, also at 132kV or greater (including OTSUA): three or five limb cores or single phase units to be specified, and operating peak flux density at nominal voltage;

(g)	an indication of which items of equipment may be out of service simultaneously during Planned Outage conditions.

PC.A.6.3	User's Protection Data

PC.A.6.3.1	Protection

The following information is required which relates only to Protection equipment which can trip or inter-trip or close any Connection Point circuit-breaker or any Transmission circuit-breaker (or in the case of OTSUA, any Interface Point or Connection Point circuit breaker).  This information need only be supplied once, in accordance with the timing requirements set out in PC.A.1.4(b), and need not be supplied on a routine annual basis thereafter, although The Company should be notified if any of the information changes;

(a)	a full description, including estimated settings, for all relays and Protection systems installed or to be installed on the User's System;

(b)	a full description of any auto-reclose facilities installed or to be installed on the User's System, including type and time delays;

(c)	a full description, including estimated settings, for all relays and Protection systems or to be installed on the generator, generator transformer, Station Transformer and their associated connections;

(d)	for Generating Units (including Synchronous Generating Units forming part of a Synchronous Power Generating Module but excluding Power Park Units) or Power Park Modules (including DC Connected Power Park Modules) or HVDC Systems or DC Converters at a DC Converter Station or OTSDUW Plant and Apparatus having (or intended to have) a circuit breaker at the generator terminal voltage, clearance times for electrical faults within the Generating Unit (including Synchronous Generating Units forming part of a Synchronous Power Generating Module but excluding a Power Park Unit) or Power Park Module (including DC Connected Power Park Modules) zone, or within the OTSDUW Plant and Apparatus;

(e)	the most probable fault clearance time for electrical faults on any part of the User's System directly connected to the National Electricity Transmission System including OTSDUW Plant and Apparatus; and

(f)	in the case of OTSDUW Plant and Apparatus, synchronisation facilities and delayed auto reclose sequence schedules (where applicable).

(g)	Restoration Contractors and Network Operators shall provide the above Protection data where different settings are used in respect of their Plant and Apparatus which are associated with a Restoration Plan.

PC.A.6.4	Harmonic Studies

PC.A.6.4.1	It is occasionally necessary for The Company to evaluate the production/magnification of harmonic distortion on the National Electricity Transmission System and User’s Systems (and OTSUA), especially when The Company is connecting equipment such as capacitor banks. At The Company’s reasonable request, each User is required to submit data with respect to the Connection Site (and in the case of OTSUA, each Interface Point and Connection Point), current and forecast, and where not already supplied under PC.A.2.2.4 and PC.A.2.2.5, as follows:

PC.A.6.4.2	Overhead lines and underground cable circuits of the User's Subtransmission System must be differentiated and the following data provided separately for each type:

Positive phase sequence resistance;

Positive phase sequence reactance;

Positive phase sequence susceptance;

and for all transformers connecting the User's Subtransmission System and OTSDUW Plant and Apparatus to a lower voltage:

Rated MVA;

Voltage Ratio;

Positive phase sequence resistance;

Positive phase sequence reactance;

and at the lower voltage points of those connecting transformers:

Equivalent positive phase sequence susceptance;

Connection voltage and MVAr rating of any capacitor bank and component design parameters if configured as a filter;

Equivalent positive phase sequence interconnection impedance with other lower voltage points;

The minimum and maximum Demand (both MW and MVAr) that could occur;

Harmonic current injection sources in Amps at the Connection voltage points. Where the harmonic injection current comes from a diverse group of sources, the equivalent contribution may be established from appropriate measurements;

Details of traction loads, eg connection phase pairs, continuous variation with time, etc;

An indication of which items of equipment may be out of service simultaneously during Planned Outage conditions.

PC.A.6.5	Voltage Assessment Studies

It is occasionally necessary for The Company to undertake detailed voltage assessment studies (e.g., to examine potential voltage instability, voltage control co-ordination or to calculate voltage step changes).  At The Company’s reasonable request, each User is required to submit the following data where not already supplied under PC.A.2.2.4 and PC.A.2.2.5:

For all circuits of the User’s Subtransmission System (and any OTSUA):-

Positive Phase Sequence Reactance;

Positive Phase Sequence Resistance;

Positive Phase Sequence Susceptance;

MVAr rating of any reactive compensation equipment;

and for all transformers connecting the User's Subtransmission System to a lower voltage (and any OTSUA):

Rated MVA;

Voltage Ratio;

Positive phase sequence resistance;

Positive Phase sequence reactance;

Tap-changer range;

Number of tap steps;

Tap-changer type: on-load or off-circuit;

AVC/tap-changer time delay to first tap movement;

AVC/tap-changer inter-tap time delay;

and at the lower voltage points of those connecting transformers (and any OTSUA):-

Equivalent positive phase sequence susceptance;

MVAr rating of any reactive compensation equipment;

Equivalent positive phase sequence interconnection impedance with other lower voltage points;

The maximum Demand (both MW and MVAr) that could occur;

Estimate of voltage insensitive (constant power) load content in % of total load at both winter peak and 75% off-peak load conditions.

PC.A.6.6	Short Circuit Analysis

PC.A.6.6.1	Where prospective short-circuit currents on Transmission equipment are greater than 90% of the equipment rating, and in The Company’s reasonable opinion more accurate calculations of short-circuit currents are required, then at The Company’s request each User is required to submit data with respect to the Connection Site (and in the case of OTSUA, each  Interface Point and Connection Point), current and forecast, and where not already supplied under PC.A.2.2.4 and PC.A.2.2.5, as follows:

PC.A.6.6.2	For all circuits of the User’s Subtransmission System (and any OTSUA):

Positive phase sequence resistance;

Positive phase sequence reactance;

Positive phase sequence susceptance;

Zero phase sequence resistance (both self and mutuals);

Zero phase sequence reactance (both self and mutuals);

Zero phase sequence susceptance (both self and mutuals);

and for all transformers connecting the User's Subtransmission System to a lower voltage (and any OTSUA):

Rated MVA;

Voltage Ratio;

Positive phase sequence resistance (at max, min and nominal tap);

Positive Phase sequence reactance (at max, min and nominal tap);

Zero phase sequence reactance (at nominal tap);

Tap changer range;

Earthing method: direct, resistance or reactance;

Impedance if not directly earthed;

and at the lower voltage points of those connecting transformers (and any OTSUA):

The maximum Demand (in MW and MVAr) that could occur;

Short-circuit infeed data in accordance with PC.A.2.5.6 unless the User’s lower voltage network runs in parallel with the User’s Subtransmission System, when to prevent double counting in each node infeed data, a  equivalent comprising the data items of PC.A.2.5.6 for each node together with the positive phase sequence interconnection impedance between the nodes shall be submitted.

PC.A.6.7	Dynamic Models

PC.A.6.7.1	It is occasionally necessary for The Company to evaluate the dynamic performance of User’s Plant and Apparatus at each EU Grid Supply Point or in the case of EU Code Users, their System. At The Company’s reasonable request and as agreed between The Company and the relevant Network Operator or Non-Embedded Customer, each User is required to provide the following data. Where such data is required, The Company will work with the Network Operator or Non-Embedded Customer to establish the scope of the dynamic modelling work and share the required information where it is available:-

- Dynamic model structure and block diagrams including parameters, 	transfer   functions and individual elements (as applicable);

- Power control functions and block diagrams including parameters, 		transfer functions and individual elements (as applicable);

- Voltage control functions and block diagrams including parameters, 	transfer functions and individual elements (as applicable);

- Converter control models and block diagrams including parameters, 	transfer functions and individual elements (as applicable).

### PC.A.7	ADDITIONAL DATA FOR NEW TYPES OF POWER STATIONS, DC CONVERTER STATIONS, OTSUA AND CONFIGURATIONS

Notwithstanding the Standard Planning Data and Detailed Planning Data set out in this Appendix, as new types of configurations and operating arrangements of Power Stations, HVDC Systems, DC Converter Stations and OTSUA emerge in future, The Company may reasonably require additional data to represent correctly the performance of such Plant and Apparatus on the System, where the present data submissions would prove insufficient for the purpose of producing meaningful System studies for the relevant parties.

## PART 3 - DETAILED PLANNING DATA

PC.A.8	To allow a User to model the National Electricity Transmission System, The Company will provide, upon request, the following Network Data to Users, calculated in accordance with Good Industry Practice:

To allow a User to assess undertaking OTSDUW and except where provided for in Appendix F, The Company will provide upon request the following Network Data to Users, calculated in accordance with Good Industry Practice:

PC.A.8.1	Single Point of Connection

For a Single Point of Connection to a User's System (and OTSUA), as a Transmission System voltage source, the data (as at the HV side of the Point of Connection (and in the case of OTSUA, each Interface Point and Connection Point) reflecting data given to The Company by Users) will be given to a User as follows:

The data items listed under the following parts of PC.A.8.3:

(a) (i), (ii), (iii), (iv), (v) and (vi) and the data items shall be provided in accordance with the detailed provisions of PC.A.8.3 (b) - (e).

PC.A.8.2	Multiple Point of Connection

For a Multiple Point of Connection to a User's System equivalents suitable for use in loadflow and fault level analysis shall be provided.  These equivalents will normally be in the form of a π model or extension with a source (or demand for a loadflow equivalent) at each node and a linking impedance. The boundary nodes for the equivalent shall be either at the Connection Point (and in the case of OTSDUW, each Interface Point and Connection Point) or (where The Company agrees) at suitable nodes (the nodes to be agreed with the User) within the National Electricity Transmission System. The data at the Connection Point (and in the case of OTSDUW, each Interface Point and Connection Point) will be given to a User as follows:

The data items listed under the following parts of PC.A.8.3:-

(a)	(i), (ii), (iv), (v), (vi), (vii), (viii), (ix), (x) and (xi)

and the data items shall be provided in accordance with the detailed provisions of PC.A.8.3 (b) - (e).

When an equivalent of this form is not required The Company will not provide the data items listed under the following parts of PC.A.8.3:-

(a)	(vii), (viii), (ix), (x) and (xi)

PC.A.8.3	Data Items

(a)	The following is a list of data utilised in this part of the PC.  It also contains rules on the data which generally apply.

(i)	symmetrical three-phase short circuit current infeed at the instant of fault from the National Electricity Transmission System, (I1");

(ii)	symmetrical three-phase short circuit current from the National Electricity Transmission System after the subtransient fault current contribution has substantially decayed, (I1');

(iii)	the zero sequence source resistance and reactance values at the Point of Connection (and in case of OTSUA, each Interface Point and Connection Point), consistent with the maximum infeed below;

(iv)	the pre-fault voltage magnitude at which the maximum fault currents were calculated;

(v)	the positive sequence X/R ratio at the instant of fault;

(vi)	the negative sequence resistance and reactance values of the National Electricity Transmission System seen from the Point of Connection (and in case of OTSUA, each Interface Point and Connection Point), if substantially 	different from the values of positive sequence resistance and reactance which 	would be derived from the data provided above;

(vii)	the initial positive sequence resistance and reactance values of the two (or more) sources and the linking impedance(s) derived from a fault study constituting the (π) equivalent and evaluated without the User network and load and where appropriate without elements of the National Electricity Transmission System between the User network and agreed boundary nodes (and in case of OTSUA, each Interface Point and Connection Point);

(viii)	the positive sequence resistance and reactance values of the two (or more) sources and the linking impendence(s) derived from a fault study, considering the short circuit current contributions after the subtransient fault current contribution has substantially decayed, constituting the (π) equivalent and evaluated without the User network and load, and where appropriate without elements of the National Electricity Transmission System between the User network and agreed boundary nodes (and in case of OTSUA, each Interface Point and Connection Point);

(ix)	the corresponding zero sequence impedance values of the (π) equivalent produced for use in fault level analysis;

(x)	the Demand and voltage at the boundary nodes and the positive sequence resistance and reactance values of the linking impedance(s) derived from a loadflow study considering National Electricity Transmission System peak Demand constituting the (π) loadflow equivalent; and,

(xi)	where the agreed boundary nodes are not at a Connection Point (and in case of OTSUA, Interface Point or Connection Point), the positive sequence and zero sequence impedances of all elements of the National Electricity Transmission System between the User network and agreed boundary nodes that are not included in the equivalent (and in case of OTSUA, each Interface Point and Connection Point).

(b)	To enable the model to be constructed, The Company will provide data based on the following conditions.

(c)	The initial symmetrical three phase short circuit current and the transient period three phase short circuit current will normally be derived from the fixed impedance studies.  The latter value should be taken as applying at times of 120ms and longer.  Shorter values may be interpolated using a value for the subtransient time constant of 40ms.  These fault currents will be obtained from a full System study based on load flow analysis that takes into account any existing flow across the point of connection being considered.

(d)	The Company will provide the appropriate supergrid transformer data for the National Electricity Transmission System associated with equivalent voltage source data.

(e)	The positive sequence X/R ratio and the zero sequence impedance value will correspond to The Company’s source network only, that is with the section of network if any with which the equivalent is to be used excluded.  These impedance values will be derived from the condition when all Generating Units (including Synchronous Generating Units forming part of a Synchronous Power Generating Module) are Synchronised to the National Electricity Transmission System or a User's System and will take account of active sources only including any contribution from the load to the fault current.  The passive component of the load itself or other system shunt impedances should not be included.

(f)	A User may at any time, in writing, specifically request for an equivalent to be prepared for an alternative System condition, for example where the User's System peak does not correspond to the National Electricity Transmission System peak, and The Company will, insofar as such request is reasonable, provide the information as soon as reasonably practicable following the request.

PC.A.9	CONTROL SYSTEM MODEL REQUIREMENTS FOR USERS

PC.A.9.1	OBJECTIVE

PC.A.9.1.1	Control and protection system models, along with other Plant and Apparatus information are required by this PC, with supporting documentation provided to The Company in order for The Company and Transmission Licensees to assess the impact of the User’s Plant and Apparatus on the transient performance, security and stability of the Transmission System.

PC.A.9.1.2	The control and protection system models submitted by the User shall be representative of the User’s Plant and Apparatus at the Connection Point appropriate to the type of model eg. RMS or EMT. All control and protection system models must take into account all communication, controller and processing delays relevant to modelling the performance of the User’s Plant and Apparatus. If all Power Park Units or DC Convertors or HVDC Converters contained within the Users Plant and Apparatus are not identical, the control system model shall account for this by accurately representing the overall performance of the Users Plant and Apparatus at the Connection Point.

PC.A.9.1.3	The control and protection system models shall include representation of all relevant functionality required by the Grid Code including services provided to The Company. For example, this includes voltage control, LFSM-O, LFSM-U, frequency response, fault ride through, fast fault current injection, protection and automatic switching of shunt devices. Where modes of operation are selectable, the ability to select the mode of operation shall be included within the control system model. Additional guidance on relevant functionality will be published on The Company website.

PC.A.9.2.	SCOPE

PC.A.9.2.1	All Users shall provide root mean-square (RMS) models which represent the Users Plant and Apparatus and controllers in balanced, RMS, positive phase-sequence, time domain studies.

PC.A.9.2.2	All Generators, HVDC Convertor Station Owners, or HVDC System Owners directly connected to the Transmission System or Generators with Large Power Stations and HVDC Convertor Station Owners or HVDC System Owners with DC Converter Stations or HVDC Systems embedded within a User system which employ convertors/invertors to import or export  power to or from the System shall provide Electro-Magnetic Transient (EMT) models which represent the Users Plant and Apparatus in electromagnetic transient studies on the transmission and distribution system. For the avoidance of doubt this includes Generators who own and operate a Power Park Module comprising doubly fed induction generators and may include the excitation and governor control systems associated with Synchronous Generating Units if these impact on the types of study described on The Company website.

PC.A.9.2.3	The Company may specify requirements for other models in the Bilateral Agreement if required for specific connections in accordance with good industry practice. For example Real Time Dynamic Simulator (RTDS) Models may be required for protection co-ordination.

PC.A.9.3	Balanced Root Mean Squared (RMS) Control System Model

PC.A.9.3.1	The balanced, root mean-square positive sequence time-domain models shall be able to calculate how aspects, (including but not limited to; Active Power and Reactive Power) of the User’s Plant and Apparatus vary due to changes in System Frequency and voltage at the Connection Point.

PC.A.9.3.2	The RMS models shall include all electrical and mechanical phenomena that impact on the Active Power and/or Reactive Power of the User’s Plant and Apparatus for sub-transient, transient and synchronous dynamics within the context of an RMS study assumptions up to and including Primary and Secondary Response timeframes or when post-event steady state conditions have been achieved.

PC.A.9.3.3	The User shall provide RMS models in the software package specified in PC.A.9.8.1.

PC.A.9.3.4	The RMS models maybe either a User specific model or a standard open-source models, such as a standard WECC, IEEE or IEC control system model available in the software format as specified by The Company provided this model represents the User’s Plant and Apparatus at the Connection Point. Where the User is referencing a standard model, the User will submit an unambiguous reference to the model and a full set of parameters for the control system model representing the control system performance of the real Plant and Apparatus.

PC.A.9.3.4.1	Where a User specific model is provided sufficient information shall be provided by the User to allow for The Company to redevelop RMS models in the event of future software environment changes or version updates. All models shall be accompanied with appropriate documentation with sufficient detail as specified and deemed complete by The Company (such agreement not to be unreasonably withheld).

PC.A.9.3.4.2	Where a User specific model is provided the User shall provide information:

(i) a full description of the models structure, functionality and the User’s Plant and Apparatus represented.

(ii) inputs/outputs and functionality,

(iii) the information described in PC.A.5 relevant to the technology modelled.

PC.A.9.3.5	The Company may, when necessary, require the User to provide details of the proper operation of its complete RMS system representation or to facilitate its understanding of the results of a RMS dynamic simulation or request additional information concerning the RMS control system model. This should take place no later than the issuance of the FON.

PC.A.9.3.5	The performance requirements for the RMS models are included in Appendix PC.A.9.8

PC.A.9.4	Electromagnetic Transient (EMT) Model

PC.A.9.4.1	The three-phase electromagnetic transient control and supporting informtion shall include all material aspects of the User’s Plant and Apparatus that affect the voltage and current outputs, including those of the control and protection response from the User’s Plant and Apparatus. The models shall represent phenomena that materially affect the voltage and Frequency on the Total System over timeframes of sub-cycle up to 50 cycles including, but not limited to, switching electronic devices, transformer saturation and equipment energisation.

PC.A.9.4.2	The User shall provide EMT models in the software package specified in PC.A.9.9.1.

PC.A.9.4.3	The performance requirements for the EMT control system model are included in Appendix PC.A.9.9

PC.A.9.5	Replica Control Systems, RTDS, RSCAd

PC.A.9.5.1	Where required by the Bilateral Agreement, the User shall provide replica and/or suitable Real Time Dynamic Simulator models. The details of any such models will be included in the Bilateral Agreement.

PC.A.9.6	CONFIDENTIALITY AND SHARING

PC.A.9.6.1	CONFIDENTIALITY AND SHARING RMS TYPE MODELS

PC.A.9.6.1.1	The models, supporting documentation and associated data are provided to The Company in order to carry out its duties to meet its ESO Licence and Grid Code obligations. In that regard, the Company is entitled to share the models, supporting documentation and associated data with the Transmission Licensees. The Company and/or Transmission Licensees may share the models with companies/contractors employed by the Company or Transmission Licensees to carry out licensed activities. Where such data is shared with third parties working with The Company or Transmission Licensees, this data will be shared as provided in GC.12.

PC.A.9.6.1.2	It is the responsibility of the User to provide the RMS models, supporting documentation and associated data to The Company. The Company will accept the models, supporting documentation and associated data from a manufacturer as a Manufacturers Data and Performance Report (See ECP.10). The Company will only accept this information from a third party manufacturer provided the third party manufacturer agrees to enter into The Company’s standard confidentiality agreement for Users for sharing of the model as outlined in PC.A.9.6.1. In the event the third party manufacturer is unable to enter into The Company’s standard confidentiality agreement, the User shall be responsible for the provision of the RMS models, supporting documentation and associated data to The Company.

PC.A.9.6.1.3		It may also be necessary for The Company to share a representative RMS model with another User to comply with applicable Grid Code requirements (e.g. ECC.6.3.17.1.5 and ECC.6.3.17.2.3) and Bilateral Agreement. For these purposes the User must recorded in the Compliance Statements either:

(i)	A declaration that the models submitted for compliance purposes may be shared; or,

(ii)	provide an equivalent encrypted version of the model that may be shared. In this event the User shall demonstrate that the performance of the models and the encrypted model are comparable.

PC.A.9.6.1.4	The User shall notify The Company of any changes to RMS models in accordance with PC.A.1.2. Unless specified otherwise in the Bilateral Agreement, RMS models must be submitted:

(i) 	at least 3 months prior to date requested for issue of the Interim Operational Notification

(ii) 	at least 1 month prior to date of issue of a Limited Operational Notification

for the Users Plant and Apparatus.

PC.A.9.6.2	CONFIDENTIALITY AND SHARING EMT TYPE MODELS

PC.A.9.6.2.1	The EMT model, supporting documentation and associated data are provided to The Company in order to carry out its duties to meet its ESO Licence and Grid Code obligations. In that regard, the Company is entitled to share the EMT models, supporting documentation and associated data with the Transmission Licensees. The Company and/or Transmission Licensees may share the EMT model with companies/contractors employed by the Company or Transmission Licensees to carry out licensed activities. Where such data is shared with third parties working with The Company or Transmission Licensees, this data will be shared and protected as provided in GC.12.

PC.A.9.6.2.2	It is the responsibility of the User to provide the EMT models, supporting documentation and associated data to The Company. The Company will accept the EMT models, supporting documentation and associated data from a manufacturer as a Manufacturers Data and Performance Report (See ECP.10). The Company will only accept this information from a third party manufacturer provided the third party manufacturer agrees to enter into The Company’s standard confidentiality agreement for Users for sharing of the model as outlined in PC.A.9.6.2. In the event the third party manufacturer is unable to enter into The Company’s standard confidentiality agreement, the User shall be responsible for the provision of the EMT models, supporting documentation and associated data to The Company.

PC.A.9.6.2.3	It may be necessary for The Company to share a representative EMT model with another User to comply with applicable Grid Code requirements (e.g. ECC.6.3.17.1.5 and ECC.6.3.17.2.3) and Bilateral Agreement. For these purposes the User must record in the Compliance Statements either:

(i)	a declaration that the EMT model submitted for compliance purposes (PC.A.9.6.2.1) may be shared with another User for the purpose of fulfilling relevant Grid Code requirements; or,

(ii)	provide an equivalent EMT model that maybe shared with another User for  the purpose of fulfilling relevant Grid Code requirements. In this event the User shall declare that the performance of the equivalent EMT model is adequate for the purposes of fulfilling relevant Grid Requirements as published on The Company website.

PC.A.9.6.2.4     Where it is necessary for The Company to share a representative EMT model with another User, the User in receipt of the model shall:

(i)	limit of the use of the EMT model to a specific purpose agreed with The Company (e.g. simulation requirements to demonstrate compliance with Grid Code including ECC.6.3.17.1 and ECC.6.3.17.2 and Bilateral Agreement)

(ii)	control access to the EMT model to only those individuals who are strictly necessary for the execution of the specific purpose.

(iii)	establish and maintain security measures to restrict access to and prevent distribution of the EMT model (e.g. single computer terminal containing the EMT model and restricting access to file areas where the model resides)

(iv)	ensure any publication is only for demonstrating compliance with the specific purpose agreed with The Company and shall not include any data directly derived from the EMT model

(v)	not disclose the EMT model

(vi)	destroy all copies of the EMT model and supporting material in a confidentially secure manner after the execution of the specific purpose is complete. Destruction of the EMT model and supporting material shall be confirmed to The Company in writing.

PC.A.9.6.2.5	The User shall notify The Company of any changes to EMT models in accordance with PC.A.1.2. Unless specified otherwise in the Bilateral Agreement, EMT models must be submitted:

(i) 	at least 3 months prior to date requested for issue of the Interim Operational Notification

(ii) 	at least 1 month prior to date of issue of a Limited Operational Notification

for the Users Plant and Apparatus.

PC.A.9.7	VALIDATION

PC.A.9.7.1	The User shall submit evidence that the models have been validated demonstrating that the models under simulation conditions is representative of the User’s Plant and Apparatus under equivalent conditions. Validation of models before commissioning may be against test results at other comparable sites, Factory Acceptance Tests of comparable equipment, or type test results to show that the responses shown by the models are representative of the Users Plant and Apparatus. Results from model validation in accordance internationally recommended standards (for example IEC) where applicable are also acceptable.

PC.A.9.7.2	A User may request agreement from The Company on the process for validating the models. In particular, for Users Plant and Apparatus where Factory Acceptance Testing is to be carried out details of any additional model validation at this stage should be agreed in a timely manner prior to the testing being carried out. Tests should generally include steady state Reactive Power capability, voltage control, Fault Ride Through and Frequency response.

PC.A.9.7.3	After final compliance testing  as required under the CP or ECP, the User shall carry out validation of the model simulation results against measurements from final compliance testing in accordance with CP.A.3 or ECP.A.3, to ensure the model responses are representative of the Users Plant and Apparatus.

PC.A.9.7.4	If these tests show the models are not representative of the User’s Plant and Apparatus, the User shall provide updated models, supporting documentation and associated data to ensure the responses shown by the model is representative of the responses shown by User’s Plant and Apparatus during testing.

PC.A.9.7.5	In the event The Company identifies through lifetime monitoring (OC5) that that the response of the models are not representative of the User’s Plant and Apparatus, The Company shall notify the User. The User shall provide the revised models, supporting documentation and associated data whose response is representative of the Users Plant and Apparatus as soon as reasonably practicable, but in any case no longer than 54 days after notification by The Company. In the event of revised models not being made available a Limited Operational Notification (as detailed in CP.9 or ECP.9 as applicable) may be issued with appropriate restrictions.

PC.A.9.7.6	The User is responsible for ensuring the models remain representative of the User’s Plant and Apparatus throughout the operational lifetime of the User’s Plant and Apparatus. In the event of the User modifying hardware/software which affects the control and/or operation of the Users Plant and Apparatus, the User shall provide The Company with updated models, supporting documentation and associated data to enable The Company to assess the impact of the modification of the Users Plant and Apparatus on the Total System. Such changes may require other compliance activity as described in the CP or ECP as applicable.

PC.A.9.7.7	The User shall demonstrate that the representation of a User’s Plant and Apparatus and models perform correctly in a sample network model published by The Company before being accepted. The User should represent the User’s Plant and Apparatus modelled in accordance with the Single Line Diagram and parameters submitted under the Planning Code and DRC in Schedules 1, 5 or 18 aggregating multiple Power Park Units and the collector grid to a single Power Park Unit representing a Power Park Module.

PC.A.9.8	RMS Model Performance Specification

PC.A.9.8.1	The RMS models shall be provided in the format required by The Company. The Company shall publish on The Company website acceptable software versions. The Company will act reasonable in determining acceptable software versions or compatible formats. In accordance with good industry practice The Company will consult with the industry prior to changing the format required. Prior to the start of model development the User may request formal agreement from The Company of the software version. The RMS models shall be compatible with Objectives as outlined in Grid Code PC.A.9.1 Additional guidance on RMS model is published on The Company website.

PC.A.9.8.2	General

PC.A.9.8.2.1	User RMS models shall interface with the software in a manner that is consistent with the behaviour of standard library models.

PC.A.9.8.2.1	The models shall use standard library functional blocks representing using standard Laplace block diagram format to the extent practicable. Where user defined functional blocks have been submitted the User must provide The Company with the relevant documentation for the model including transfer block diagrams and an explanation of any coding to the satisfaction of The Company.

PC.A.9.8.2.2	The use of any "black boxes" encrypted code or external DLLs is not acceptable. An additional RMS model with these features maybe provided for comparison but for the avoidance of doubt does not meet the requirements of PC.A.9.

PC.A.9.8.2.3	The User shall specify the operating ranges for the model and shall be consistent with the real physical values and the actual performance of the Plant and Apparatus. This may include Reactive Power limits and allowable voltage ranges with control mode and Droop settings configured according to the usual operation. This information shall be provided either on the appropriate per unit base or in physical units.

PC.A.9.8.2.4	The RMS model must compile without errors. Warnings must be kept to a minimum.

PC.A.9.8.3	Initialisation

PC.A.9.8.3.1	The RMS model shall be self contained. The combined load-flow and dynamic model shall solve with minimal warnings without the need for manual adjustment or to run external software routines that adjust parameters in either the load-flow case or the dynamic case or both. External software or automation routines to integrate the model are not acceptable.

PC.A.9.8.3.2	The RMS model shall automatically initialise its parameters from load flow simulations without errors and with minimal warnings , must not result in run time errors and run with minimal warnings , and there must not be any interactions or conflicts with other models. The RMS models initialisation shall be invariant to simulation start time (i.e. not require the simulation to be initialised at a particular time). External software or automation routines to initialise the model are not acceptable.

PC.A.9.8.3.3	The RMS model is expected to be numerically stable and must adequately represent the expected equipment behaviour over the operational range of the Plant and Apparatus at the Connection Point. This includes the full load and Reactive Power range of the Plant and Apparatus, the range of system voltage and frequency operating range (described in Grid Code CC.6.1/ECC.6.1), short circuit levels and X/R ratio at the Connection Point where it would be in operation.  These values maybe requested from The Company or the Distribution Network Owner during the compliance process. If necessary, the User shall provide a supplementary model for specific conditions. All information on the model capabilities shall be addressed in the model documentation provided to The Company.

PC.A.9.8.4	Output Messages

PC.A.9.8.4.1	It is not acceptable for the models to crash catastrophically and provide no documentary evidence as to why the simulation failed.

PC.A.9.8.4.2	RMS models shall allow all appropriate internal variables to be requested for output for the duration of the simulation.

PC.A.9.8.4.3	In the case where the User’s Plant trips during simulation, the relevant RMS models shall set the flag that indicates that the User’s Plant has tripped.

PC.A.9.8.4.4	For protection events (e.g. crow bar controller operation) the simulation events, including initial detection, operation, and time-out, should be reported to the PowerFactory output window during the simulation.

PC.A.9.8.5	Integration Time Step

PC.A.9.8.5.1	The dynamic model must support time domain simulations with a minimum integration step size of 0.01 s.

PC.A.9.8.5.2	The models must not include algorithms that require use of a particular integration step size (for example the control system model should not fail to solve, or the response be materially different for an integration step size of 0.005 s).

PC.A.9.8.5.3	Time constants below 0.01 s should only be included if their inclusion is critical to the performance of the dynamic model and should be agreed with The Company. In this case, an alternative model may be requested according to PC.A.9.8.3.3, if required.

PC.A.9.8.5.4	Internal integration algorithms should only be included if their inclusion is critical to meeting the accuracy requirements, and should not materially detract from model simulation speed performance.

PC.A.9.9	EMT Model Performance Specification

PC.A.9.9.1	The User shall provide EMT models in the format required by The Company. The Company shall maintain a list of acceptable software versions, and compiler version which shall be published on The Company website. The Company will act reasonable in determining acceptable software versions or compatible formats. In accordance with good industry practice The Company will consult with the industry prior to changing the format required. The EMT models shall be compatible with Objectives as outlined in Grid Code PC.A.9.1 and The Company shall also publish on The Company website a description of the types of study that The Company and Transmission Licensees will use the EMT control system models in. Additional guidance on EMT model is also published on The Company website.

PC.A.9.9.2	The EMT models maybe encrypted. The scope, behaviour and performance of all encrypted elements must be documented. Documentation should include behaviour and performance of all encrypted inner and outer loop control functionality such as voltage control, frequency control, protection systems, convertor controls and phase locked loop controllers (PLL).  Aspects of the control system may be omitted provided the study objectives published by The Company in accordance with PC.A.9.4.2 are met in which case the documentation should explain any functionality not included in the EMT control system model.

PC.A.9.9.3	The EMT model shall:

i)	have adjustable operational control parameters. For example this would be expected to include setpoints, control drops, operational limits, relay thresholds. The User may seek agreement from The Company on the list of adjustable parameters prior to submission of the model.

ii)	be based on plant design and validated against testing of the Plant and Apparatus (See Model Validation )

iii)	include all control systems from outer loop control down to inner and switching functions

iv)	represent all electrical, mechanical and control features appropriate for the Plant and Apparatus including switching algorithms of power convertors applicable to studies described by The Company.

v)	Have all appropriate protection systems modelled for power system transient stability analysis including balanced and unbalanced fault conditions, Frequency and voltage disturbances configured to match the site specific installation of the Plant and Apparatus. Any protections which relate to multiple disturbances should have an option to be disabled.

vi)	Allow Plant and Apparatus to be scaled where appropriate in accordance with good industry practice. For example representation of multiple Power Park Units by a single equivalent unit.

vii)	Have time steps which must be appropriate for the accurate representation of the switching algorithms used in the Plant and Apparatus and compatible with study time steps down to 10us.

viii)	Be portable between network models which may be any size between a single machine infinite bus power system representation and a full multi node power system network depending on the studies that need to be undertaken.

ix)	Allow multiple instances within a network and be compatible with other control system models within a network.

x)	Be capable of self initiation to User defined terminal conditions within 4 seconds of the simulation time when connected to an equivalent Thevenin source. In the case of complex models The Company may agree a self initiation simulation time within 6 seconds.

xi)	Warn the User by way of an output message when System conditions exceed the operational limits of the Plant and Apparatus or are not valid for continued operation.

xii)	Be able to be initialised from a snapshot of network conditions

# APPENDIX B - SINGLE LINE DIAGRAMS

PC.B.1	The diagrams below show three examples of single line diagrams, showing the detail that should be incorporated in the diagram. The first example is for an Network Operator connection, the second for a Generator connection, the third for a Power Park Module electrically equivalent system.

Network Operator Single Line Diagram

Generator Single Line Diagram

Power Park Module Single Line Diagram

Notes:

(1)	The electrically equivalent Power Park Unit consists of a number of actual Power Park Units of the same type ie. any equipment external to the Power Park Unit terminals is considered as part of the equivalent network. Power Park Units of different types shall be included in separate electrically equivalent Power Park Units. The total number of equivalent Power Park Units shall represent all of the actual Power Park Units in the Power Park Module (which could be a DC Connected Power Park Module).

(2)	Separate electrically equivalent networks are required for each different type of electrically equivalent Power Park Unit. The electrically equivalent network shall include all equipment between the Power Park Unit terminals and the Common Collection Busbar.

(3)	All Plant and Apparatus including the circuit breakers, transformers, lines, cables and reactive compensation plant between the Common Collection Busbar and Substation A shall be shown.

# APPENDIX C - TECHNICAL AND DESIGN CRITERIA

PC.C.1	Planning and design of the SPT and SHETL Transmission Systems is based generally, but not totally, on criteria which evolved from joint consultation among various Transmission Licensees responsible for design of the National Electricity Transmission System.

PC.C.2 	The above criteria are set down within the standards, memoranda, recommendations and reports and are provided as a guide to system planning.  It should be noted that each scheme for reinforcement or modification of the Transmission System is individually designed in the light of economic and technical factors associated with the particular system limitations under consideration.

PC.C.3	The tables below identify the literature referred to above, together with the main topics considered within each document.

## PART 1 – SHETL's TECHNICAL AND DESIGN CRITERIA

| ITEM No. | DOCUMENT | REFERENCE No. |
| --- | --- | --- |
| 1 | National Electricity Transmission System Security and Quality of Supply Standard | Version [ ] |
| 2 | System Phasing | TPS 13/4 |
| 3 | Not used |  |
| 4 | Voltage fluctuations and the connection of disturbing equipment to transmission systems and distribution networks in the United Kingdom | EREC P28 Issue 2 |
| 5 | EHV or HV Supplies to Induction Furnaces Voltage unbalance limits. Harmonic current limits. | ER P16 (Supported by ACE Report No.48) |
| 6 | Planning Levels for Harmonic Voltage Distortion and the Connection of Non-Linear Loads to Transmission Systems and Public Electricity Supply Systems in the United Kingdom Harmonic distortion (waveform). Harmonic voltage distortion. Harmonic current distortion. Stage 1 limits. Stage 2 limits. Stage 3 Limits Addition of Harmonics Short Duration Harmonics Site Measurements | ER G5 (Supported by ACE Report No.73) |
| 7 | AC Traction Supplies to British Rail Type of supply point to railway system. Estimation of traction loads. Nature of traction current. System disturbance estimation. Earthing arrangements. | ER P24 |
| 8 | Operational Memoranda Main System operating procedure. Operational standards of security. Voltage and reactive control on main system. System warnings and procedures for instructed load reduction. Continuous tape recording of system control telephone messages and instructions. Emergency action in the event of an exceptionally serious breakdown of the main system. | (SOM) SOM 1 SOM 3 SOM 4 SOM 7 SOM 10 SOM 15 |
| 9 | Planning Limits for Voltage Unbalance in the United Kingdom. | ER P29 |

## The applicable SHETL’s technical and design criteria shall also be used in the design and development of a Competitively Appointed Transmission Licensee’s System having a Competitively Appointed Transmission Licensee’s Interface Point to SHETL’s Transmission System.
PART 2 - SPT's TECHNICAL AND DESIGN CRITERIA

| ITEM No. | DOCUMENT | REFERENCE No. |
| --- | --- | --- |
| 1 | National Electricity Transmission System Security and Quality of Supply Standard | Version [ ] |
| 2 | System Phasing | TDM 13/10,002 Issue 4 |
| 3 | Not used |  |
| 4 | Voltage fluctuations and the connection of disturbing equipment to transmission systems and distribution networks in the United Kingdom | EREC P28 Issue 2 |
| 5 | EHV or HV Supplies to Induction Furnaces Voltage Unbalance limits. Harmonic current limits. | ER P16 (Supported by ACE Report No.48) |
| 6 | Planning Levels for Harmonic Voltage Distortion and the Connection of Non-Linear Loads to Transmission Systems and Public Electricity Supply Systems in the United Kingdom Harmonic distortion (waveform). Harmonic voltage distortion. Harmonic current distortion. Stage 1 limits. Stage 2 limits. Stage 3 Limits Addition of Harmonics Short Duration Harmonics Site Measurements | ER G5 (Supported by ACE Report No.73) |
| 7 | AC Traction Supplies to British Rail Type of supply point to railway system. Estimation of traction loads. Nature of traction current. System disturbance estimation. Earthing arrangements. | ER P24 |

The applicable SPT’s technical and design criteria shall also be used in the design and development of a Competitively Appointed Transmission System having a Competitively Appointed Transmission Licensee Interface Point to SPT’s Transmission System.

# APPENDIX D - DATA NOT DISCLOSED TO A RELEVANT TRANSMISSION LICENSEE

PC.D.1	Pursuant to PC.3.4, The Company will not disclose to a Relevant Transmission Licensee data items specified in the below extract:

| PC REFERENCE | DATA DESCRIPTION | UNITS | DATA CATEGORY |
| --- | --- | --- | --- |
| PC.A.3.2.2 (f) (i) | - For GB Code Users The Generator Performance Chart at the Generating Unit stator terminals - For EU Code Users:- The Power Generating Module Performance Chart, and Synchronous Generating Unit Performance Chart; |  | SPD |
| PC.A.3.2.2 (b) | Output Usable (on a monthly basis) | MW | SPD |
| PC.A.5.3.2 (d) Option 1 (iii) | GOVERNOR AND ASSOCIATED PRIME MOVER PARAMETERS Option 1 BOILER & STEAM TURBINE DATA |  |  |
|  | Boiler time constant (Stored Active Energy) | S | DPD II |
|  | HP turbine response ratio: (Proportion of Primary Response arising from HP turbine) | % | DPD II |
|  | HP turbine response ratio: (Proportion of High Frequency Response arising from HP turbine) | % | DPD II |
| Part of PC.A.5.3.2 (d) Option 2 (i) | Option 2 All Generating Units (including Synchronous Generating Units forming part of a Synchronous Power Generating Module) Governor Deadband or (Frequency Response Deadband and Frequency Response Insensitivity)* |  |  |
|  | - Maximum Setting | Hz | DPD II |
|  | - Normal Setting | Hz | DPD II |
|  | - Minimum Setting *(Note GB Generators who are not required to satisfy the requirements of the European Connection Conditions do not need to supply Frequency Response Deadband or Frequency Response Insensitivity data). | Hz | DPD II |
| Part of PC.A.5.3.2 (d) Option 2 (ii) | Steam Units |  |  |
|  | Reheater Time Constant | sec | DPD II |
|  | Boiler Time Constant | sec | DPD II |
|  | HP Power Fraction | % | DPD II |
|  | IP Power Fraction | % | DPD II |
| Part of PC.A.5.3.2 (d) Option 2 (iii) | Gas Turbine Units Waste Heat Recovery Boiler Time Constant |  |  |
| Part of PC.A.5.3.2 (e) | UNIT CONTROL OPTIONS |  |  |
|  | Maximum droop | % | DPD II |
|  | Minimum droop | % | DPD II |
|  | Maximum Governor Deadband or (Maximum Frequency Response Deadband and Maximum Frequency Response Insensitivity)* | ±Hz | DPD II |
|  | Normal Governor Deadband or (normal Frequency Response Deadband and normal Frequency Response Insensitivity)* | ±Hz | DPD II |
|  | Minimum Governor Deadband or (minimum Frequency Response Deadband and minimum Frequency Response Insensitivity)* | ±Hz | DPD II |
|  | Maximum Output Governor Deadband or (Maximum Output Frequency Response Deadband and Maximum Output Frequency Response Insensitivity)* | ±MW | DPD II |
|  | Normal Output Governor Deadband or (Normal Output Frequency Response Deadband and Normal Output Frequency Response Insensitivity)* | ±MW | DPD II |
|  | Minimum Output Governor Deadband or (Minimum Output Frequency Response Deadband and Minimum Output Frequency Response Insensitivity)* | ±MW | DPD II |
|  | (Note Generators who are not required to satisfy the requirements of the European Connection Conditions do not need to supply Frequency Response Deadband and Frequency Response Insensitivity data). Frequency settings between which Unit Load Controller droop applies: |  |  |
|  | Maximum | Hz | DPD II |
|  | Normal | Hz | DPD II |
|  | Minimum | Hz | DPD II |
|  | Sustained response normally selected | Yes/No | DPD II |
| PC.A.3.2.2 (f) (ii) | Performance Chart of a Power Park Modules (including DC Connected Power Park Modules) at the connection point |  | SPD |
| PC.A.3.2.2 (b) | Output Usable (on a monthly basis) | MW | SPD |
| PC.A.3.2.2 (e) and (j) | DC CONVERTER STATION AND HVDC SYSTEM DATA ACTIVE POWER TRANSFER CAPABILITY (PC.A.3.2.2) |  |  |
|  | Import MW available in excess of Registered Import Capacity. | MW | SPD |
|  | Time duration for which MW in excess of Registered Import Capacity is available | Min | SPD |
|  | Export MW available in excess of Registered Capacity. | MW | SPD |
|  | Time duration for which MW in excess of Registered Capacity is available | Min | SPD |
| Part of PC.A.5.4.3.3 | LOADING PARAMETERS |  |  |
|  | MW Export | MW | SPD |
|  | Nominal loading rate | MW/s | DPD I |
|  | Maximum (emergency) loading rate | MW/s | DPD I |
|  | MW Import |  |  |
|  | Nominal loading rate | MW/s | DPD I |
|  | Maximum (emergency) loading rate | MW/s | DPD I |

# APPENDIX E - OFFSHORE TRANSMISSION SYSTEM AND OTSDUW PLANT AND APPARATUS TECHNICAL AND DESIGN CRITERIA

PC.E.1	In the absence of any relevant Electrical Standards, Offshore Transmission Licensees and Generators undertaking OTSDUW are required to ensure that all equipment used in the construction of their network is:

(i)	Fully compliant and suitably designed to any relevant Technical Specification;

(ii)	Suitable for use and operation in an Offshore environment, where such parts of the Offshore Transmission System and OTSDUW Plant and Apparatus are located in Offshore Waters and are not installed in an area that is protected from that Offshore environment, and

(iii)	Compatible with any relevant Electrical Standards or Technical Specifications at the Offshore Grid Entry Point and Interface Point.

PC.E.2	The table below identifies the technical and design criteria that will be used in the design and development of an Offshore Transmission System and OTSDUW Plant and Apparatus.

| ITEM No. | DOCUMENT | REFERENCE No. |
| --- | --- | --- |
| 1 | National Electricity Transmission System Security and Quality of Supply Standard | Version [ ] |
| 2* | Voltage fluctuations and the connection of disturbing equipment to transmission systems and distribution networks in the United Kingdom | EREC P28 Issue 2 |
| 3* | Planning Levels for Harmonic Voltage Distortion and the Connection of Non-Linear Loads to Transmission Systems and Public Electricity Supply Systems in the United Kingdom | ER G5 |
| 4* | Planning Limits for Voltage Unbalance in the United Kingdom | ER P29 |

* Note:- Items 2, 3 and 4 above shall only apply at the Interface Point.

# APPENDIX F - OTSDUW DATA AND INFORMATION AND OTSDUW NETWORK DATA AND INFORMATION

PC.F.1	Introduction

PC.F.1.1	Appendix F specifies data requirements to be submitted to The Company by Users and Users by The Company in respect of OTSDUW.

PC.F.1.2	Such User submissions shall be in accordance with the OTSDUW Development and Data Timetable in a Construction Agreement.

PC.F.1.3	Such submissions shall be issued to The Company with the offer of a CUSC Contract in the case of the data in Part 1 and otherwise in accordance with the OTSDUW Development and Data Timetable in a Construction Agreement.

PC.F.2.	OTSDUW Network Data and Information

PC.F.2.1	With the offer of a CUSC Contract under the OTSDUW Arrangements The Company shall provide:

(a)	the site specific technical design and operational criteria for the Connection Site;

(b)	the site specific technical design and operational criteria for the Interface Point, and

(c)	details of The Company’s preliminary identification and consideration of the options available for the Interface Point in the context of the User’s application for connection or modification, the preliminary costs used by The Company in assessing such options and the Offshore Works Assumptions including the assumed Interface Point identified during these preliminary considerations.

PC.F.2.2	In accordance with the OTSDUW Development and Data Timetable in a Construction Agreement The Company shall provide the following information and data to a User:

(a)	equivalent of the fault infeed or fault level ratings at the Interface Point (as identified in the Offshore Works Assumptions)

(b)	notification of numbering and nomenclature of the HV Apparatus comprised in the OTSDUW;

(i)	past or present physical properties, including both actual and designed physical properties, of Plant and Apparatus forming part of the National Electricity Transmission System at the Interface Point at which the OTSUA will be connected to the extent it is required for the design and construction of the OTSDUW, including but not limited to:

(ii)	the voltage of any part of such Plant and Apparatus;

(iii)	the electrical current flowing in or over such Plant and Apparatus;

(iv)	the configuration of any part of such Plant and Apparatus

(v)	the temperature of any part of such Plant and Apparatus;

(vi)	the pressure of any fluid forming part of such Plant and Apparatus

(vii)	the electromagnetic properties of such Plant and Apparatus; and

(viii)	the technical specifications, settings or operation of any Protection Systems forming part of such Plant and Apparatus.

(c)	information necessary to enable the User to harmonise the OTSDUW with construction works elsewhere on the National Electricity Transmission System that could affect the OTSDUW;

(d)	information related to the current or future configuration of any circuits of the Onshore Transmission System with which the OTSUA are to connect;

(e)	any changes which are planned on the National Electricity Transmission System in the current or following six Financial Years and which will materially affect the planning or development of the OTSDUW.

PC.F.2.3	At the Users reasonable request, additional information and data in respect of the National Electricity Transmission System shall be provided.

PC.F.2.4	OTSDUW Data And Information

PC.F.2.4.1 	In accordance with the OTSDUW Development and Data Timetable in a Construction Agreement, the User shall provide to The Company, the following information and data relating to the OTSDUW Plant and Apparatus in accordance with Appendix A of the Planning Code.

# APPENDIX G – NETWORK OPERATOR AND THE COMPANY PLANNING DATA EXCHANGE

PC.G.1   	Data to be Included in the Solved PSM

PC.G.1.1	The Solved PSM:

- Shall include Structural Data, Situation Data, and Solution Data relating to all relevant equipment within the scope of the Network Operator Subtransmission PSM or The Company NETS PSM as set out in PC.9.4 and PC.10.4, respectively.

- Shall conform to the data exchange definitions and implementation requirements described in PC.G.4.

- May include additional data if supported by the data exchange definitions.

PC.G.1.2	PSM data shall meet the following general requirements regarding Structural Data:

  - Define the connectivity of all relevant equipment;

  - Have identifiers which are unique and remain consistent throughout the life of the data as required in PC.3.1.1.5; and

  - Have a name and description sufficient to provide human readability.

PC.G.1.3	Equipment

PC.G.1.3.1	For all equipment the following data shall be included in the PSM:

- Structural Data:

  - The line, substation or substation voltage level, as applicable, of which it is a part.

- Situation Data:

  - In-service status, which indicates whether or not the equipment is to be included in the development of Solution Data. Status “false” means that the equipment is considered as being disconnected from the System.

PC.G.1.3.2	For each busbar the following data shall be included in the PSM:

- Structural Data:

    - Node by which it is represented;

    - Nominal voltage; and

    - Maximum and minimum operational voltage limits.

- Situation Data:

- Operational voltage limits to be used as power flow solution violation limits.

- Solution Data:

- Voltage magnitude and angle if energised.

PC.G.1.3.2.1	For each busbar designated as a PSM Interface Node, or by exception at alternative points agreed by the relevant parties, the following data shall additionally be included in the PSM:

- Solution Data (short circuit) (as defined in Engineering Recommendation G74):

    - Fault kind (single- or 3-phase);

    - Steady state current;

    - Maximum steady state current;

    - Minimum steady state current;

    - Peak current;

    - Decaying component current ;

    - Initial symmetrical current; and

    - Symmetrical breaking current.

PC.G.1.3.3	For each switching device required to facilitate System reconfiguration, the following data shall be included in the PSM:

- Structural Data:

  - For all devices:

    - Normal operating status (open/closed).

  - For all circuit breakers or circuit switchers inclusive of their relevant substation infrastructure:

    - Rated RMS continuous current;

    - Rated 3-phase RMS short-circuit withstand current and duration;

    - Rated 1-phase RMS short-circuit withstand current and duration;

    - Rated 3-phase short-circuit peak withstand current; and

    - Rated 1-phase short-circuit peak withstand current.

  - Additionally, for all circuit breakers or circuit switchers:

    - DC time constant applied at testing of asymmetrical breaking abilities;

    - Break time;

    - Rated 3-phase RMS short-circuit breaking current; and

    - Rated 1-phase RMS short-circuit breaking current.

  - Additionally, for all circuit breakers or circuit switchers with current making capability:

    - Rated 3-phase peak short-circuit making current; and

    - Rated 1-phase peak short-circuit making current.

- Situation Data:

  - Operational position.

- Solution Data:

  - Operational position.

PC.G.1.3.4	For each transformer (including step-up transformers, auto transformers, and phase shifting transformers) the following data shall be included in the PSM:

- Structural Data:

  - For each transformer winding:

    - Rated Apparent Power;

    - Rated voltage;

    - Positive sequence reactance and resistance;

    - Zero sequence reactance and resistance;

    - Positive sequence susceptance and conductance;

    - Zero sequence susceptance and conductance;

    - Connection type, for instance type D, Y, Yn, including any tertiary winding;

    - Vector group;

    - Grounding reactance and resistance;

    - Earthing method (direct, resistance, reactance, through earthing transformer or none);

    - Positive sequence reactance and resistance at minimum and maximum tap;

    - Normal seasonal operational Apparent Power limits (Winter, Spring, Summer and Autumn):

      - For two-winding transformer, of the HV winding;

      - For multi-winding transformers, of all windings; and

      - Date of commencement of each season.

    - Reverse power-flow operational limits (applied to the HV winding).

  - For the tap changer:

    - Tap changer steps information (high step, low step, neutral step);

    - Tap changer on-load change capability;

    - Type of phase tap changer: symmetrical, asymmetrical described in a linear, non-linear, or tabular way;

    - Tap changer control mode;

    - Impedance information per tap step, if applicable;

    - Operational limit per tap step, if applicable; and

    - Transformer winding on which tap-changer operates.

- Situation Data:

  - For each winding:

    - Operational apparent power limits to be used as power flow solution violation limits:

      - For two-winding transformer, of the HV winding; and

      - For multi-winding transformers, of all windings.

  - For the tap changer:

    - Tap changer regulating status;

    - Tap changer regulating quantity target value;

    - Tap changer regulating deadband; and

    - Tap changer step.

- Solution Data:

  - For the tap changer:

    - Tap changer step.

PC.G.1.3.5	For each circuit the following data shall be included in the PSM:

  - Structural Data:

    - For all circuits, to support power flow and short circuit calculations:

- Nominal voltage;

- Length of circuit;

- Max permitted temperature at the end of the short circuit ;

- Circuit composition: Overhead/underground/mixed;

- Normal seasonal operational current limits (Winter, Spring, Summer and Autumn):

    - Date of commencement of each season.

- Positive sequence resistance, reactance and susceptance;

- Negative sequence resistance, reactance and susceptance; and

- Zero sequence resistance, reactance and susceptance.

- In addition to the information presented in PC.G.1.3.5.a).i, for overhead lines where applicable:

      - Relevant zero sequence mutual coupling resistance, reactance and susceptance.

  - Situation Data:

    - Operating limits to be used in the analysis of the power flow solution.

  - Solution Data:

    - Calculated Active Power and Reactive Power flows for the circuit.

PC.G.1.3.6	For each compensating equipment (including linear and non-linear shunts, series compensators, and static var compensators), the following data shall be included in the PSM:

- Structural Data:

  - Operating type of compensation equipment (switched equipment with automated module activation or fixed equipment that can only be operated manually);

  - For shunt compensators, the compensation type (for instance, R-L, R-L-C, C, R-L-C);

  - Nominal voltage;

  - For controllable compensating equipment, the regulating mode and regulating range;

  - For discrete shunt compensating equipment:

    - Positive sequence conductance and susceptance per section;

    - Zero sequence conductance and susceptance per section; and

    - Number of maximum sections.

  - For series compensating equipment:

    - Positive sequence reactance and resistance;

    - Zero sequence reactance and resistance; and

    - Rated current and voltage threshold, if a variable resistor is present.

  - For continuous compensating equipment, for instance static Var compensators:

    - Nominal compensation range;

    - Capacitive and inductive rating;

    - Slope characteristics is the slope that defines how the Reactive Power output changes in proportion to the difference between the regulated bus voltage and the voltage setpoint;

    - Positive and zero sequence reactance; and

    - Positive and zero sequence resistance.

- Situation Data:

  - Section or initial compensation setting according to the type of compensating equipment;

  - Regulating status; and

  - Regulating quantity target value.

- Solution Data:

  - Section or final compensation setting according to the type of compensating equipment

PC.G.1.3.7	For each HVDC System, the following data shall be included in the PSM:

- Structural Data:

  - A reduced representation of the HVDC System comprised of:

    - information on the power output including active and reactive regulation range; and

    - voltage regulation capabilities, if applicable.

- Situation Data:

  - Active Power;

  - Reactive Power;

  - Regulating status, if applicable; and

  - Regulating quantity target value, if applicable.

- Solution Data:

  - Reactive Power.

- Specific requirements to related to representation in The Company NETS PSM:

  - For HVDC Systems internal to the NETS losses need to be accounted for and defined in the PSM Scenario Document.

PC.G.1.4	Generation and Storage

PC.G.1.4.1	For each Synchronous Power Generating Module, which is not an Electricity Storage Module, the following data shall be included in the PSM:

- Structural Data:

  - Nominal Apparent Power;

  - Nominal Active Power;

  - Nominal terminal voltage;

  - Nominal Power Factor;

  - Rotor type by construction;

  - Rotor type for the purpose of short circuit calculation in accordance with Engineering Recommendation G74;

  - Relevant points from the Generator Performance Chart defining a reactive capability curve, including Active Power and Reactive Power limits at nominal voltage;

  - Direct axis reactances (saturated and unsaturated):

    - Subtransient reactance (Xd'');

    - Transient reactance (Xd’); and

    - Synchronous reactance (Xd).

  - Direct axis time constants (saturated and unsaturated):

    - Subtransient time constants (Td"); and

    - Transient time constant (Td).

  - Quadrature axis reactances (saturated and unsaturated):

    - Subtransient reactance (Xq'');

    - Transient reactance (Xq'); and

    - Synchronous reactance (Xq).

  - Quadrature time constants (saturated and unsaturated):

    - Subtransient time constants (Tq"); and

    - Transient time constant (Tq').

  - Zero sequence reactance and resistance;

  - Negative sequence reactance and resistance;

  - Stator resistance;

  - Inertia constant (H);

  - Primary Energy Source (from the list given in PC.G.8.1);

  - Control mode; and

  - Earthing star point reactance and resistance, if applicable.

- Situation Data:

  - Active and reactive power;

  - Regulating status (enabled/disabled); and

  - Regulating quantity target value.

- Solution Data:

  - Calculated Active Power and Reactive Power output.

PC.G.1.4.2	For each Power Park Module, which is not an Electricity Storage Module, comprising Non-Synchronous Generating Units or Offshore Power Park Strings none of which are connected through power electronic conversion technology, the following data shall be included in the PSM:

- Structural Data:

  - Nominal Apparent Power;

  - Nominal Active Power;

  - Nominal mechanical power;

  - Nominal terminal voltage;

  - Nominal speed;

  - Nominal frequency ;

  - Nominal Power Factor;

  - Pole pair number;

  - Locked r/x rotor ratio;

  - Nominal efficiency;

  - Ratio of locked-rotor current to the rated current of the motor;

  - Information if it is converter fed drive and reversable capability;

  - Primary Energy Source (from the list given in PC.G.8.1);

  - Energy conversion technology (from the list given in PC.G.8.2); and

  - Regulating mode and regulating range.

- Situation Data:

  - Active Power and Reactive Power;

  - Regulating status; and

  - Regulating quantity target value.

- Solution Data:

  - Calculated Active Power and Reactive Power output.

PC.G.1.4.3	For each Power Park Module, which is not an Electricity Storage Module, comprising Non-Synchronous Generating Units or Offshore Power Park Strings which are all connected through power electronic conversion technology, the following data shall be included in the PSM:

- Structural Data:

  - Nominal Apparent Power;

  - Nominal Active Power;

  - Nominal terminal voltage;

  - Primary Energy Source (from the list given in PC.G.8.1);

  - Energy conversion technology (from the list given in PC.G.8.2); and

  - Regulating mode and regulating range.

- Situation Data:

  - Active Power and Reactive Power;

  - Regulating status; and

  - Regulating quantity target value.

- Solution Data:

  - Calculated Active Power and Reactive Power output.

PC.G.1.4.4	For each Synchronous Electricity Storage Module the following data shall be included in the PSM:

- Structural Data:

  - Nominal energy capability;

  - Nominal Apparent Power when supplying;

  - Nominal Apparent Power when consuming;

  - Nominal terminal voltage;

  - Primary Energy Source (from the list given in PC.G.8.1);

  - Energy conversion technology (from the list given in PC.G.8.2);

  - Regulating mode and regulating range; and

  - Minimum and maximum Active Power and Reactive Power.

- Situation Data:

  - Stored energy;

  - Storage status;

  - Active Power and Reactive Power;

  - Regulating status; and

  - Regulating quantity target value.

- Solution Data:

  - Calculated Active Power and Reactive Power output.

PC.G.1.4.5	For each Non-Synchronous Electricity Storage Module the following data shall be included in the PSM:

- Structural Data:

  - Nominal energy capability;

  - Nominal Apparent Power when supplying;

  - Nominal apparent power when consuming;

  - Nominal terminal voltage;

  - Primary Energy Source (from the list given in PC.G.8.1);

  - Energy conversion technology (from the list given in PC.G.8.2);

  - Regulating mode and regulating range; and

  - Minimum and maximum Active Power and Reactive Power.

- Situation Data:

  - Stored energy;

  - Storage status ;

  - Active Power and Reactive Power;

  - Regulating status; and

  - Regulating quantity target value.

- Solution Data:

  - Calculated Active Power and Reactive Power output.

PC.G.1.4.6	For each connection between a Power-Generating Module and either the NETS or the Subtransmission System, the equipment providing that connection, including the Station Transformer data and the auxiliary load it serves, shall be included in the PSM. The following data shall be included for the auxiliary load:

- Structural Data:

  - Subtransient short-circuit current maximum and minimum;

  - Transient short-circuit current maximum and minimum;

  - X/R maximum and minimum ratios;

  - Indication of whether the auxiliary load is scalable (conform type) or not (non-conform type); and

  - Load response components i.e. constant power, constant impedance, constant current components.

- Situation Data:

  - Active Power and Reactive Power.

- Solution Data:

  - Calculated Active Power and Reactive Power output.

PC.G.1.4.7	The detail specified in PC.G.1.4.1 through PC.G.1.4.5 is required only for Power Generating Modules connected to the NETS or the Subtransmission System. Power Generating Modules connected at a voltage level below that of the Subtransmission System shall be represented as aggregated equivalents, grouped by Aggregated Energy Source. The following data shall be included in the PSM for such equivalents:

- Structural Data:

- Aggregated Energy Source, reflecting the dominant generation type of the aggregation (synchronous, asynchronous, inverter-based) (from the list given in PC.G.8.1);

- Aggregate short circuit current;

- X/R ratio of the equivalent;

- Control capability and mode; and

- Relevant points from an assumed Generator Performance Chart relating to the aggregated equivalent defining a reactive capability curve, including active and reactive power limits at nominal voltage.

- Situation Data:

- Active Power and Reactive Power; and

- Control (enabled or disabled).

- Solution Data:

- Calculated Active Power and Reactive Power output.

PC.G.1.5	Load

PC.G.1.5.1	For each Demand Facility connected to the Subtransmission System or the NETS, the following data shall be included in the PSM:

- Structural Data:

  - Indication of whether the load is scalable (conform type) or not (non-conform type);

  - Load response components i.e. constant power, constant impedance, constant current components;

- Transient short-circuit current maximum and minimum;

- Subtransient short-circuit current maximum and minimum; and

- X/R maximum and minimum ratios.

- Situation Data:

  - Active Power and Reactive Power.

- Solution Data:

  - Calculated Active Power and Reactive Power output; and

  - Short circuit current results.

PC.G.1.5.2	The detail specified in PC.G.1.5.1 is required only for Demand Facilities connected to the Subtransmission System or the NETS. Any demand connected at a voltage below that of the Subtransmission System shall be represented as an aggregated demand equivalent connected to the lower voltage busbar at substations connecting the Subtransmission System to a lower voltage. The following data shall be included in the PSM for such equivalents:

- Structural Data:

  - Indication of whether the load is scalable (conform type) or not (non-conform type);

  - Transient short-circuit current maximum and minimum level;

  - Subtransient short-circuit current maximum and minimum level; and

  - X/R maximum and minimum ratios.

- Situation Data:

  - Active Power and Reactive Power.

- Solution Data:

  - Calculated Active Power and Reactive Power output; and

  - Short circuit current results.

PC.G.1.6	Diagram Data

PC.G.1.6.1	For each of the following types of diagrams, Diagram Data shall be included in the PSM. The diagram data shall define the arrangement of the listed Structural Data on the diagram:

- A PSM overview diagram containing references to Structural Data representing:

        - All major substations in the PSM;

        - Lines connecting the above substations;

        - Names of the substations and lines; and

        - Voltage levels of lines.

- A schematic diagram for each substation in the PSM containing references to Structural Data representing:

- All equipment (e.g., lines, transformers, switches, busbars, compensation equipment), load, and generation/storage, both AC and DC, in the substation;

- Connectivity of equipment, load and generation/storage;

- Normal operating status (open/closed) of switches; and

- Voltage levels of busses.

PC.G.2   	Additional Data Not Included in the Solved PSM

PC.G.2.1	Several sections of the Planning Code, including PC.9.3.1 and PC.10.3.1, anticipate the need for the exchange of PSM-related data which is not yet supported by the data exchange standard specified in PC.G.4. Several types of such data are described below.

PC.G.2.2	Full Technical HVDC System Models

PC.G.2.2.1	Due to the complexity of modelling HVDC Systems, The Company will model HVDC System Connection Points using a simplistic method. This will comprise of either:

        - A single generator connection for HVDC Systems that connect the NETS to an EU Grid Supply Point;

        - A single generator connection for HVDC Systems that connect the NETS to an Offshore Transmission System which provides the connection to one or more Offshore Power Park Modules;

        - For HVDC Systems which form part of the NETS and have only two Onshore Grid Entry Points, both these points will be represented by a simple generation but with additional information around system loss allowance listed in the PSM Scenario Document;

        - For HVDC Systems which form part of the NETS and have more than two Onshore Grid Entry Points:

          - Those Onshore Grid Entry Points which are located on the GB mainland shall be represented by a simple generator with additional information detailing relevant system loss allowances listed in the PSM Scenario Document; or

          - Those Onshore Grid Entry Points which are located outside the GB mainland shall be represented by a simple generator, relevant NETS data and additional information detailing relevant system loss allowances listed in the PSM Scenario Document.

PC.G.2.2.2	The Company will consider any request from a Network Operator for a full HVDC System model connected to the NETS. The Company will, where possible, use the data exchange profile standard specified in PC.G.4.1.1 to make this HVDC System model available. A PSM Scenario Document will be provided with this model to assist the Network Operator to use this data.

PC.G.2.2.3	Should The Company be unable to facilitate a Network Operator’s request, an alternative method to provide data will be agreed.

PC.G.2.2.4	The provision of models representing HVDC System(s), with more than two Onshore Grid Entry Points, by The Company shall be agreed with the relevant Network Operator(s). These models may be outside of the NETS Solved PSM. At such time as the GB CIM Governance Group update the GB CIM profile, these models may be exchanged as part of the NETS Solved PSM.

PC.G.2.3	General Demand Data

PC.G.2.3.1	The following information is infrequently required and should be supplied (wherever possible) when requested by The Company:

(a)	Details of any individual loads (including (as applicable) the load behaviour of an Electricity Storage Module when operating in a mode analogous to demand) which have characteristics significantly different from the typical range of domestic, commercial, Electricity Storage or industrial loads;

(b)	The sensitivity of the Demand to variations in voltage and Frequency on the NETS at the time of the NETS peak demand. The sensitivity factors quoted for the Reactive Power should relate to that given under PC.G.2.5;

(c)	Details of any traction loads, e.g. connection phase pairs and continuous load variation with time;

(d)	The average and maximum phase unbalance, in magnitude and phase angle, which the User would expect its Demand to impose on the NETS;

(e)	The maximum harmonic content which the User would expect its Demand to impose on the NETS;

(f)	Details of all loads which may cause Demand fluctuations greater than those permitted under Engineering Recommendation P28 Issue 2, Stage 1 at a Point of Common Coupling including the Flicker Severity (Short Term) and the Flicker Severity (Long Term).

(g) 	In the case of Electricity Storage Modules, details of the Maximum Capacity, Maximum Import Power, Registered Import Capability, charge time, discharge time and operating periods.

PC.G.2.4	Import to Embedded Power Stations

PC.G.2.4.1	Introduction

PC.G.2.4.1.1	The import to Embedded Power Stations (excluding the import to Electricity Storage Module(s)) shall be treated, for the purpose of providing Demand related data to The Company, in the same manner as import to other types of Demand Facility.

PC.G.2.4.1.2	In relation to Embedded Large Power Stations and Embedded Medium Power Stations (excluding the import to Electricity Storage Module(s)), The Company may request the Network Operator to provide the following:

(a)	the maximum Demand that, in the Network Operator's opinion, could reasonably be imposed on the NETS;

(b)	the Demand at the time of the NETS peak demand; and

(c)	the Demand at the time of the NETS minimum demand.

PC.G.2.4.1.3	At its discretion The Company may also request the following details of the control of demand or reduction of pumping load offered as reserve:

(a) Magnitude of Demand or pumping load or Electricity Storage Module charging load which is tripped

(b) System Frequency at which tripping is initiated

(c) Time duration of System Frequency below trip setting for tripping to be initiated

(d) Time delay from trip initiation to tripping

PC.G.2.5	Network Operators' System Data

PC.G.2.5.1	Introduction

PC.G.2.5.2, PC.G.2.5.4 to PC.G.2.5.5 consist of data which is only to be supplied to The Company at The Company’s reasonable request. In the event that The Company identifies a reason for requiring this data, The Company shall write to the relevant Network Operator(s), requesting the data, and explaining the reasons for the request. If the Network Operator(s) wishes, The Company shall also arrange a meeting at which the request for data can be discussed, with the objective of identifying the best way in which The Company’s requirements can be met.

Where The Company makes a request to a Network Operator for dynamic models under PC.G.2.5.5, each relevant Network Operator shall ensure that the models supplied in respect of their Plant and Apparatus reflect the true and accurate behaviour of the Plant and Apparatus as built and verified through the Compliance Processes.

PC.G.2.5.2	Network Operator's Protection Data

The following information is required which relates only to Protection equipment which can trip or inter-trip or close any Connection Point circuit-breaker or any Transmission circuit-breaker. This information need only be supplied once, in accordance with the timing requirements set out in PC.A.1.4(b), and need not be supplied on a routine annual basis thereafter, although The Company should be notified if any of the information changes;

(a)	a full description, including actual or estimated settings as appropriate, for all relays and Protection systems installed or to be installed on the Network Operator's System;

(b)	a full description of any auto-reclose facilities installed or to be installed on the Network Operator's System, including type and time delays; and

(c)	the most probable fault clearance time for electrical faults on any part of the Network Operator's System directly connected to the NETS including OTSDUW Plant and Apparatus.

PC.G.2.5.3	Harmonic Studies

PC.G.2.5.3.1	It is occasionally necessary for The Company to evaluate the production/magnification of harmonic distortion on the NETS, OTSUA and Network Operator’s Systems, especially when equipment such as capacitor banks are being connected to the NETS. At The Company’s reasonable request, each Network Operator shall submit data with respect to the Connection Site, relating to the existing and forecast harmonic distortion levels, and:

        - At the lower voltage busbar at substations connecting the Subtransmission System to a lower voltage:

          - Connection voltage and MVAr rating of any capacitor bank and component design parameters if configured as a filter;

          - The minimum and maximum Demand (both MW and MVAr) that could occur;

          - Harmonic current injection sources in Amps at locations agreed between Network Operators and The Company. Where the harmonic injection current comes from a diverse group of sources, the equivalent contribution may be established from appropriate measurements; and

          - Details of traction loads, eg connection phase pairs, continuous variation with time, etc;

        - An indication of which items of equipment may be out of service simultaneously during Planned Outage conditions.

PC.G.2.5.4	Dynamic Models

It is occasionally necessary for The Company to evaluate the dynamic performance of Network Operator’s Plant and Apparatus at each EU Grid Supply Point or in the case of EU Code Users, their System. At The Company’s reasonable request and as agreed between The Company and the relevant Network Operator, each Network Operator is required to provide the following data. Where such data is required, The Company will work with the Network Operator to establish the scope of the dynamic modelling work and share the required information where it is available:

- Dynamic model structure and block diagrams including parameters, transfer functions and individual elements (as applicable);

- Power control functions and block diagrams including parameters, transfer functions and individual elements (as applicable);

- Voltage control functions and block diagrams including parameters, transfer functions and individual elements (as applicable); and

- Converter control models and block diagrams including parameters, transfer functions and individual elements (as applicable).

Where The Company makes a request to a Network Operator for dynamic models, the Network Operator, to the best of its ability, shall ensure that the models supplied in respect of the Plant and Apparatus reflect the true and accurate behaviour of the Plant and Apparatus as built and verified through the Compliance Processes.

PC.G.2.5.5	Transient Overvoltage Assessment Data

It is occasionally necessary for The Company to undertake transient overvoltage assessments (e.g. capacitor switching transients, switchgear transient recovery voltages, etc). At The Company’s reasonable request, each Network Operator is required to provide the following data with respect to the Connection Site, as follows:

    - busbar layout plan(s), including dimensions and geometry showing positioning of any current and voltage transformers, through bushings, support insulators, disconnectors, circuit breakers, surge arresters, etc. Electrical parameters of any associated current and voltage transformers, stray capacitances of wall bushings and support insulators, and grading capacitances of circuit breakers;

    - Electrical parameters and physical construction details of lines and cables connected at that busbar. Electrical parameters of all plant not previously supplied as part of the Structural Data e.g., transformers (including neutral earthing impedance or zig-zag transformers, if any), series reactors and shunt compensation equipment connected at that busbar (or to the tertiary of a transformer) or by lines or cables to that busbar;

    - Basic insulation levels (BIL) of all Apparatus connected directly, by lines or by cables to the busbar;

    - characteristics of overvoltage protection devices at the busbar and at the termination points of all lines, and all cables connected to the busbar;

    - the following data is required on all transformers operating at Supergrid Voltage throughout Great Britain and, in Scotland, also at 132kV or greater: three or five limb cores or single phase units to be specified, and operating peak flux density at nominal voltage; and

    - an indication of which items of equipment may be out of service simultaneously during Planned Outage conditions.

PC.G.2.6 	System Restoration Related Information

PC.G.2.6.1 	Data identified under this section PC.G.2.6.1 must be submitted as required under OC9.5.

PC.G.2.6.2 	Where a Network Operator has a Distribution Restoration Zone Plan in place, the data specified in this section shall be submitted as required by Network Operator(s) to The Company annually by calendar week 28. This information may also be requested by The Company from the relevant Network Operator(s) during System Restoration and should be provided by Network Operator(s) were reasonably practicable. Restoration Contractors party to a Distribution Restoration Zone Plan shall, where reasonably practicable, submit the relevant information to the Network Operator who shall then supply the relevant information to The Company. The following data shall be provided;

- The expected time for each Restoration Contractor’s Plant to Re-Synchronise to the Network Operator’s System following a Total Shutdown or Partial Shutdown. The assessment should include the Restoration Contractor’s ability to Re-Synchronise all their Plant if all were running immediately prior to the Total Shutdown or Partial Shutdown. Additionally, the data and supporting text should highlight any specific issues (e.g., those that would affect the time before which the Restoration Contractor’s Plant could be energised) that may arise as time progresses from Shutdown without external supplies being restored or the availability of primary fuel supplies; and

(b) 	The Restoration Contractor’s Plants Block Loading Capability as required in PC.G.2.6.1(b).

PC.G.2.6.3 	From 31st December 2026 onwards, all Network Operators are required to confirm annually they comply with the applicable requirements of OC5.7. In the case of Network Operators this confirmation shall be provided in their Week 28 submission. From 1st January 2024 until 31st December 2026, evidence to support the work Network Operators are carrying out to achieve these requirements on or after 31st December 2026 shall be provided in their week 24 submission.

PC.G.3		Organisation of PSM data

PC.G.3.1		Sections 9 and 10 of the Planning Code require The Company and Network Operators to use Solved PSMs to describe the equipment, connectivity and operating condition of their portion of the System. This section describes how the data of a Solved PSM is organised and is included for information purposes.

Four main organizational concepts work together to allow the description of grid model data in building block ‘modules’. These organizational constructs are:

- Profiles – Profiles divide data by type (Structural, Situation or Solution).

- Frames and Boundaries – Frames and Boundaries represent grid extents (sometimes call territories). A Frame is typically used to define a grid extent under the data mastership of one modelling party. A Boundary exists between Frames whose systems are connected.

- Models – Models are snapshots of grid objects representing a specific system or system operating condition.

- Assembly – Assemblies are collections of Models, typically for a specific purpose.

Planning Code Section 9, Section 10, and Appendix G.1 reference the concept of CIM profiles in their definition of data requirements. This Appendix will explore the other organisational concepts.

PC.G.3.2	Frame, Boundary, Model and Assembly concepts

Frames and Boundaries define grid extents which enable the maintenance of power system models in ‘modules’ which can be easily combined to create cohesive input data for various network analysis studies. Every Boundary is associated with two or more Frames. (Two is the most common number of Frames per Boundary, however, three or more Frames can be associated with a Boundary if necessary to accurately express the relationships among the systems of the various modelling-responsible parties.) There is an electrical connection between one or more pieces of equipment in the grid extent defined by each Frame and the equipment in the Boundary. All connections between the equipment of one Frame and that of another Frame (or set of Frames) are defined using a single Boundary.

Models contain grid objects which represent some facet of the portion of the power system contained in a Frame or Boundary. The grid objects in a Model all conform to a Profile describing a type of data. The Structural Profile describes information about the characteristics of electricity system equipment, including their capabilities and connectivity. The Situation Profile describes information about the operational state of an electricity system, including demand and generation output and switch positions. The Solution Profile describes information regarding the results of a steady-state power flow calculation and/or short circuit calculation performed by a power system modelling application.

Assemblies are collections of Models grouped to support a purpose. An Assembly can contain multiple Models whose data conforms to the same Profile or Models conforming to multiple different Profiles.

PC.G.3.3	Organising grid model data using the four concepts

Figure 1 illustrates how an electrical power system composed of a transmission system and seven distribution systems could be divided into the Frames and Boundaries which delineate modelling responsibility.

Figure 1 - Frames and Boundaries of a typical transmission and distribution power system

In this diagram, seven Network Operators each have modelling responsibility for their own system – their Frames are labelled DNO1 Frame through DNO7 Frame. The Company has modelling responsibility for the transmission system - its Frame is called The Company Frame. There is a Boundary defined wherever the system of one Frame connects to the system of another Frame. In Figure 1, the system of every DNO Frame connects to the system of The Company Frame. These connections are reflected by the presence of The Company-DNO1, The Company-DNO2, The Company-DNO3, The Company-DNO4, The Company-DNO5, The Company-DNO6, and The Company-DNO7 Boundaries. The systems of the DNO2 and the DNO3 Frames connect to each other and the systems of the DNO6 and DNO7 Frames connect to each other - the DNO2-DNO3 Boundary and DNO6-DNO7 Boundary, respectively, reflect these connections. Additionally, the systems of the DNO2 and DNO3 Frames happen to have shared connection points with the system of The Company Frame, thus there is one tri-lateral Boundary, The Company-DNO2-DNO3.

In the straightforward situation where a detailed master Structural Model of the entire system is being constructed, each modelling-responsible party would create a Structural Model (a model of the equipment and connectivity of its system) describing the power system in its Frame. Each set of modelling-responsible parties whose Frames adjoin a given Boundary would agree on the modelling of their connections and would create a Structural Model for that Boundary. Each Structural Model would essentially ‘fit into’ or ‘fill’ its Frame or Boundary. This is illustrated in Figure 2.

Figure 2 - Models ‘fit into’ Frames and Boundaries

The Structural grid model data that results from combining all the Models is complete model of the system, which is modular, and reflective of each parties modelling responsibility.

This collection of Models – the Structural Models which together describe the complete, master Structural data of the power system – could be shared as an Assembly (a collection of Models for a purpose), as shown in Figure 3.

Figure 3 - An Assembly of Structural Models describing the equipment and connectivity of the complete power system

To describe the operating condition for a given study, the set of Structural Models could be augmented with Situation Models for each of the Frames. The Situation Models are shown in the upper portion of Figure 4.

Figure 4 - A set of Situation Models augmenting their relevant Structural Models

Situation Models are typically needed only for Frames because Boundaries should not include equipment that needs to have Situation (system operating condition) data defined for it. An Assembly, made up of the Structural and Situation Models shown in Figure 4, could be created to facilitate the sharing of the inputs necessary to run a given type of network analysis.

If the appropriate type of network analysis were run using the set of Structural and Situation Models shown in Figure 4 as input, a single Solution Model for the entire power system would be created. It is shown at the top of Figure 5, which, for context, also shows the Structural and Situation Models.

Figure 5 – A Solution Model created by network analysis using the relevant Structural and Situation Models as input

This complete case, composed of Models describing both the inputs and outputs of a specific network analysis execution, could also be shared as an Assembly.

PC.G.3.4	A Great Britain example

PC.G.3.4.1.	Structural Models and their Frames and Boundaries

This section explores how grid objects in Models can connect across Frames and Boundaries using a very small, hypothetical portion of a system as an example. The red outline in Figure 6 indicates the portion of the power system presented in PC.G.3.3 which the small system example encompasses.

Figure 6 – Portion of the power system represented by the small system example

The small system example, whose schematic is shown in Figure 7, reflects a variety of system configuration characteristics found in the GB System. It focuses on points of connection among three Network Operator Systems and the NETS. The example has three substations:

- Substation A – A GSP substation where the DNO1 Network Operator System connects to the NETS. It is connected at a voltage level lower than that of Substation B and C and could be viewed as representing a GSP in Scotland.

- Substation B – A GSP substation where the Systems of the DNO2 and DNO3 Network Operators both connect to the NETS. It reflects an uncommon connection configuration, but one that is present in England

- Substation C – A GSP substation where the DNO3 Network Operator System connects to the NETS. It reflects a connection configuration commonly present in England.

The example also includes three types of connection configurations between the Systems of the DNO2 and DNO3 Network Operators. Additionally it contains a subtransmission line operated by The Company, which is connected to the low-voltage bus of Substation B and the high-voltage bus of Substation A.

Figure 7 - Schematic of the small system example

The major grid objects used in a PSM representation of the small system example are superimposed on the schematic in Figure 8.

Figure 8 – Foundational grid objects used to represent the equipment and connectivity of small system example

Figure 9 illustrates, using the small system example, the philosophy typically followed in allocating grid operating responsibility among The Company and Network Operators. The circuit breakers and switches which couple busbars and those which connect the main and reserve busbars are the operating responsibility of the relevant Network Operators for Substations A and C because only one Network Operator System connects to the NETS at those substations. At Substation B, however, The Company has operating responsibility for the busbar circuit breakers and switches because two Network Operators’ Systems connect to the NETS there.

Figure 9 – Allocation of operating responsibility for the small system example

The decision has been taken to align modelling responsibility with operating responsibility in Planning Code data exchanges. The four Frames (The Company Frame, DNO1 Frame, DNO2 Frame and DNO3 Frame) and four Boundaries (The Company-DNO1, The Company-DNO2-DNO3, The Company-DNO3, and DNO2-DNO3) outlined in Figure 10 reflect that decision.

Figure 10 - The Frames and Boundaries of the small system example

Figure 11 shows the major grid objects contained in the various master Structural Models which ‘fit into’ each of the Frames and Boundaries of the small system example.

Figure 11 – Major grid objects comprising the master Structural Models which ‘fit into’ each Frame and Boundary

Note that the only grid objects in the Structural Boundary Models in Figure 11 are the Connectivity Nodes representing PSM Interface Nodes which are shown as gold oblongs with green glow.

PC.G.3.4.2	Assemblies for the exchange of Solved PSMs

The Solved PSMs required by PC.9 and PC.10 are exchanged using Assemblies of Models. In creating their Solved PSMs, it is anticipated that both The Company and the Network Operators will execute a process similar to the following:

The Solved PSM creator performs studies in its own power systems analysis software tool using appropriately detailed models representing both its portion of the System and adjacent portions. When a study solution of suitable quality is achieved, the Solved PSM is created by trimming off the adjacent portions, leaving only the Structural, Situation and Solution Models which ‘fit into’ the creator’s Frame along with the Structural Models which ‘fit into’ all Boundaries adjacent to their Frame.

The resulting Solved PSMs are then submitted to the receiving party as an Assembly. Within the Assembly, there are references by grid objects in one Model to grid objects in other Models:

- Situation and Solution Frame Model grid objects point to grid objects in the Structural Frame Model.

- Structural Frame Model grid objects point to grid objects representing PSM Interface Nodes in Structural Boundary Models.

However, for the Assembly as a whole, there are no dangling references.

The receiving party typically uses the Assembly in the following manner:

- The Structural Frame Model is incorporated into the model of the receiving party’s study tool, replacing the previous modelling for that Frame and connecting to the PSM Interface Nodes contained in the study tool model.

- The Situation and Solution Models are used as reference inputs into various studies set up and run by the receiver as part of its own business processes.

For the small system example outlined in PC.G.3.4.1, the Models shown in Figure 12 would comprise the Solved PSMs submitted by The Company and by the DNO1, DNO2 and DNO3 Network Operators.

Figure 12 – Models appearing the Solved PSMs from The Company and Network Operators

PC.G.4	PSM/PSDM data exchange standards

PC.G.4.1	The data of the Solved PSMs or PSDMs required under PC.9, PC.10, PC.G.1 and whose organisation is described in PC.G.3 shall conform to the schema and constraints defined by the designated data exchange profile standards listed in PC.G.4.1.1.

PC.G.4.1.1	The currently designated data exchange profile standard is defined by a combination of:

- IEC 61970-600-2:2021 Common Grid Model Exchange Specification (CGMES) - Exchange profiles specification, commonly known as CGMES v3.0; plus

- Planning Code-specific extensions to CGMES v3.0 as identified and managed by the GB CIM Governance Group.

PC.G.5		PSM Scenario Document

PC.G.5.1	A PSM Scenario Document shall be submitted to The Company as part of each Network Operator’s submission in calendar weeks 2 and 28. A PSM Scenario Document, tailored to the individual Network Operator, shall be submitted to each Network Operator by The Company as part of its submission in calendar weeks 12 and 38. The aim of the PSM Scenario Document is to provide contextual information to help the receiving party better understand the submission and the assumptions made in developing it. The PSM Scenario Document shall contain:

PC.G.5.1.1	Information related to the content and creation of Solved PSMs, including:

PC.G.5.1.1.1	For the Structural Data underlying the Solved PSMs of a submission, the following:

- To be supplied by Network Operators:

  - Descriptions of the simple representation of HVDC Systems.

- To be supplied by The Company:

- Descriptions of the simple representation of HVDC Systems; and

- The identification of all schemes which are nearing completion as of the time of submission which are included in the Structural Data of the Solved PSM. Such schemes include NETS reinforcement, asset replacement, or similar schemes and new generation or load schemes where the relevant customer has accepted a connection offer from The Company to connect to the NETS but is not yet connected at the time of submission.

PC.G.5.1.1.2	For each Solved PSM in a submission, the following:

- To be supplied by Network Operators:

- A summary of the Network Operator's System conditions reflected by the Solved PSM and any general information regarding the Solved PSM that would aid in its use;

- Description of running arrangements where they are different to that described by the Situation Data of the Solved PSM (e.g. where there is a different post outage running arrangement, or modifications to the Network Operator’s System due to the commissioning of a system reinforcement project);

- Demand and generation assumptions used in developing the Situation Data (e.g., generation dispatch assumptions like PV generation export being zero at the time of the NETS peak demand on the basis that the NETS peak demand occurs when it’s dark). Describing these assumptions should address any differences in Demand and generation values between the Solved PSM and Schedule 21;

- Where the information is known by the Network Operator, the extent to which any customer demand has been influenced by a flexible demand contract with any party; and

- For fault level Solved PSMs, a description of the assumptions made in the process of developing the Situation Data used in the fault level Solved PSM e.g. generation energisation / export and running arrangement assumption.

- To be supplied by The Company

- A summary of the condition(s) specified in PC.10.3.2.1 a) or PC.10.3.3.1 a), as applicable, which are represented by each Solved PSM and any general information regarding the Solved PSM that would aid in its use. In the case of the low power transfer and high power transfer Solved PSMs, this would include an indication of the direction of flow (e.g., north to south);

- Description of changes to current running arrangements as a result of   planned modifications to the NETS which are included in the summer or winter Structural Data, and which reflect future not-yet-commissioned reinforcement or asset replacement schemes or generator or load connections;

- Demand and generation assumptions used in developing the Situation Data (e.g., generation dispatch assumptions, or how generation injections were adjusted to accommodate new, not-yet-connected generation included in the summer/winter Structural Data, or how demand and/or generation injections supplied by Network Operators were modified to facilitate power flow convergence or specific Real Power (P) and Reactive Power (Q) results at the PSM Interface Nodes);

- Dispatch assumptions for external HVDC Systems, including both export and import;

- For fault level Solved PSMs, a description of the assumptions made in the process of developing the Situation Data used in the fault level Solved PSM e.g. generation energisation / dispatch and running arrangement assumptions; and

- An identification of known discrepancies in the Structural Data, Situation Data or Solution Data due to changes occurring during the timeframe the Solved PSM was being built. Such discrepancies are assumed to be minor as any change occurring during the construction process with significant impact should have been incorporated into the Solved PSM.

PC.G.5.1.2	Information helpful in utilising the Solved PSMs, including:

PC.G.5.1.2.1	Descriptions of network constraints:

- To be supplied by Network Operators:

- Any constraints which could impact the capability of the Network Operator’s Subtransmission System to accommodate import to demand customers or export from generation under normal operational conditions.  For example, this could include a limit of the import from and/or the export to a Connection Point implemented by an Active Network Management scheme. The Network Operator may provide further information about other constraints on their System operating at voltages below the Substansmission System.

- To be supplied by The Company:

- Any NETS operational schemes that could have an impact on the Network Operator’s System.

PC.G.5.1.2.2	Modelling guidance:

- To be supplied by The Company:

- Guidance that would assist recipients using the model, e.g. guidance on the generation connected to the NETS whose modelled output may be modified by a Network Operator to facilitate studies outside the standard exchanged scenarios; and

- Guidance that would assist recipients using the model, e.g. guidance on the HVDC plant connected to the NETS whose modelled output may be modified by a Network Operator to facilitate studies outside the standard exchanged scenarios.

PC.G.5.1.2.3	Descriptions of contingency actions:

- To be supplied by The Company:

- A description of changes to the NETS so that the Network Operator may undertake analysis of the impact of additional operational arrangements other than that included in the Situational Data of the Solved PSM.

PC.G.5.1.2.4	Descriptions of additional network constraint actions:

- To be supplied by Network Operators:

- Where agreed with The Company a description of additional actions that would be taken with respect to their System when analysing a scenario outside the ones included in the information exchanges defined in PC.9

- To be supplied by The Company:

- Where agreed with the Network Operator a description of additional actions that would be taken with respect to the NETS when analysing a scenario outside the ones included in the information exchanges defined in PC.10.

PC.G.5.1.3 	Information related to Schedules 23b and 23c:

PC.G.5.1.3.1	For Schedules 23b and 23c, the following post fault Network Operator System information, relating to the Connection Point Access Period, shall be provided by the Network Operators:

- An accurate and unambiguous description of the Transmission Interface Circuits considered to be switched out due to a planned outage being assessed; and

- The reconfiguration plan to transfer demand from one Connection Point to another Connection Point. Details of the switching operation or reconfiguration which implements any demand transfer, including arrangements for undertaking actions (e.g. the time taken, automatic or manual and any other appropriate information), shall be provided for:

- Those actions which would be implemented for a first planned outage; and

- Those actions that would be implemented following a subsequent fault outage during a planned outage.

The Network Operator must not submit any action that it does not have the capability or the intention to implement during the assessment period specified (subject to there being no further unplanned outages on the Network Operator's System).

PC.G.6		PSM Change Document

PC.G.6.1	A PSM Change Document shall be submitted as part of each Network Operator submission in calendar weeks 2 and 28 and each submission made by The Company in calendar weeks 12 and 38. The aim of the PSM Change Document is to provide contextual information to help the receiving party understand what has changed in the Solved PSMs of this submission relative to the preceding submitted Solved PSMs. The PSM Change Document shall contain:

PC.G.6.1.1	Information related to the content of Solved PSMs, including:

PC.G.6.1.1.1	An overview of the major changes to Structural Data.

- To be supplied by Network Operators:

- A description, including the purpose and in-service date, of any new or modified connections or alterations to the Network Operator’s System whose changes are included in the Structural Data of this submission; and

- A description of any other changes to the Structural Data of this submission, for example, the inclusion of new network data, or changes to operating parameters like ratings or normal positions of transformer taps or switches.

- To be supplied by The Company:

- A description, including the purpose and in-service date, of any new or modified connections or alterations to the NETS whose changes are included in the Structural Data of this submission;

- A description including the purpose and reason for non-implementation of each delayed or cancelled connection or alteration to the NETS whose changes were included in the Structural Data of the preceding submitted Solved PSM(s) but which are not included in the Structural Data of this submission’s Solved PSM(s); and

- A description of any other changes to the Structural Data of this submission, for example, the renaming of an asset, the inclusion of a new type of data, or changes to operating parameters like ratings or normal positions of taps or switches.

PC.G.6.1.1.2	An overview of any significant changes in the assumptions, approach, or inputs used in the creation of Situation Data.

- To be supplied by Network Operators:

- A description of significant differences of demand or generation patterns, constraints, or running arrangements (e.g., commissioning of a new Active Network Management scheme in Network Operator’s System to manage power flow at a Connection Point, or a newly implemented curtailment agreement, or unusual growth of EV-related demand at a given substation);

- For the Situation Data of Solved PSM(s) providing steady state power flow information, a description of any changes made to the process by which the Situation Data is created (e.g., changes have been made in the treatment of the import to Electricity Storage, or a new technique is being used for calculating historic demand or generation values from field monitoring data, or improved mechanics are being used to ‘fit’ Situation Data reflective of a particular grid condition to the Structural Data reflective of the Data Freeze Date); and

- For the Situation Data of Solved PSM(s) providing fault level information, a description of any changes made to the process by which fault level data is created (e.g., new software or a new process is being used to perform fault level calculations, or an improved mechanism is being used to determine demand short circuit contributions).

- To be supplied by The Company:

  - A description of significant differences of demand or generation patterns, constraints, or running arrangements (e.g., a change to the permitted export from parts of the NETS due to dispatch related constraints on the NETS becoming permanent, or a changed summer operating arrangement due to a new demand customer);

  - For the Situation Data of Solved PSM(s) providing steady state power flow information, a description of any changes made to the process by which the Situation Data is created (e.g., changes have been made to demand or generation prediction techniques, or a new philosophy for designing off-normal running arrangements has been implemented); and

  - For the Situation Data of Solved PSM(s) providing fault level information, a description of any changes made to the process by which fault level data is created (e.g., new software or a new process is being used to perform fault level calculations, or an improved mechanism is being used to determine demand short circuit contributions).

PC.G.7	Assessment of Connection Point Compliance process

Overview of the assessment of Access Group

PC.G.7.1	An Access Group is a group of Connection Points,  which are either permanently interconnected or are interconnected following a pre or post outage action, and hence there is transfer of demand from one Connection Point to another.

PC.G.7.2	All Connection Points are considered as either an Access Group on their own (if they are not interconnected through the Network Operator’s System to another Connection Point), or as a group of interconnected Connection Points to be considered as an Access Group.  Each Connection Point is only in one Access Group.

PC.G.7.3	Once Access Groups have been identified, The Company carries out assessments on each Access Group to identify those Connection Points (and the associated Transmission Interface Circuits) which need to be assessed simultaneously and whether each Transmission Interface Circuit is theoretically maintainable in accordance with the SQSS.

PC.G.7.4	For planning purposes, The Company assumes that the maintenance season is during British Summer Time i.e., calendar weeks 13 to 43.

PC.G.7.5	The Company shall submit to the Network Operator no later than calendar week 7 in each year, a proposed Transmission Interface Circuit outage plan, including:

- the calendar weeks defining the proposed start and finish of each Access Period for each Transmission Interface Circuit; and

- the Connection Points in each Access Group.

This information shall be provided by populating the appropriate cells in Schedule 24. Where it is not possible to avoid overlapping Access Periods, The Company will indicate to Network Operators its initial view of which Transmission Interface Circuits shall be considered as being out of service concurrently for the purpose of assessing compliance to Licence Standards.

PC.G.7.6	Each Connection Point must belong to one, and only one, Access Group.

PC.G.7.6.1	Each Transmission Interface Circuit must have an Access Period.

PC.G.7.6.2	The Access Period shall:

- normally be a minimum of 8 continuous weeks and can occur in any one of three maintenance years during the period from calendar week 13 to calendar week 43 (inclusive) in each year; or

- exceptionally and provided that agreement is reached between The Company and the relevant User(s), such agreement to be sought in accordance with PC.7, the Access Period may be of a period not less than 4 continuous weeks and can occur in any one of three maintenance years during the period from calendar week 10 to calendar week 43 (inclusive) in each year.

PC.G.7.7	The Company and the relevant Network Operator(s) shall use their reasonable endeavours to agree the appropriate Access Group(s) and Access Period for each Transmission Interface Circuit prior to calendar week 17 in each year.

PC.G.7.8	Network Operators, in calendar week 28, shall submit the data detailed in PC.9.3.3.6 and PC.9.3.3.7.

PC.G.7.9	Following the submission of data by a Network Operator, The Company shall perform assessments to verify whether Connection Points are compliant with the relevant Licence Standards. This shall include identifying which Transmission Interface Circuits will need to be considered out of service concurrently for the purpose of assessing compliance.

PC.G.7.10	Where the result of any assessment identifies possible future non-compliance with the relevant Licence Standards, The Company shall notify the relevant Network Operator(s) of this fact as soon as reasonably practicable and shall agree with Network Operator(s) any requirement to resubmit data to allow for a reassessment.

PC.G.7.11	Following any notification by The Company to a Network Operator pursuant to PC.G.7.7, and following any further discussions between the Network Operator and The Company;

- The Company and the Network Operator may agree revisions to the Access Periods, provided they are not less than 4 continuous weeks in duration and occur between calendar weeks 10 and 43 (inclusive), for relevant Transmission Interface Circuits.

- The Company and the Network Operator may agree revisions to the Access Periods less than 4 continuous weeks in duration and which occur other than between calendar weeks 10 and 43 (inclusive), for relevant Transmission Interface Circuits. In such cases The Company shall notify The Authority where this has been necessary.

- The Network Operator shall as soon as reasonably practicable:

- submit further relevant data to The Company that is to The Company’s reasonable satisfaction; and/or

- modify data previously submitted pursuant to this PC, such modified data to be to The Company’s reasonable satisfaction; and/or

- notify The Company that it is the intention of the Network Operator to leave the data as originally submitted to The Company to stand as its submission.

PC.G.7.12	When it is agreed that any resubmission of data is unlikely to confirm future compliance with the relevant Licence Standards the Modification process in the CUSC may apply.

PC.G.7.13	By calendar week 6 of the following year, as specified in PC.10.5.4, The Company shall notify the Network Operator of the results of any relevant assessment.

PC.G.7.14	Where The Company or Network Operator(s) agree that any resubmission of data is unlikely to confirm future compliance with the relevant Licence Standards, The Company and the Network Operator(s) shall agree the best way of addressing non-compliance.

PC.G.8	Generation

PC.G.8.1	Table of Aggregated Energy Source types to be used for developing aggregated equivalent model as required by PC.G.1.4.7:

| Energy Source | Aggregated Energy Source (for aggregated equivalent modelling required by PC.G.1.4.7) | Aggregate equivalent modelled as: |  |  |
| --- | --- | --- | --- | --- |
|  |  | Synchronous | Asynchronous | Inverter-Based |
| Advanced Fuel (produced via gasification or pyrolysis of biofuel or waste) | Advanced Fuel | Default |  |  |
| Biofuel - Biogas from anaerobic digestion (excluding landfill & sewage) | Biofuel | Default |  |  |
| Biofuel - Landfill gas |  |  |  |  |
| Biofuel - Sewage gas |  |  |  |  |
| Biofuel - Other |  |  |  |  |
| Biomass | Biomass | Default |  |  |
| Fossil - Brown coal/lignite | Fossil | Default |  |  |
| Fossil - Coal gas |  |  |  |  |
| Fossil - Gas |  |  |  |  |
| Fossil - Hard coal |  |  |  |  |
| Fossil - Oil |  |  |  |  |
| Fossil - Oil shale |  |  |  |  |
| Fossil - Peat |  |  |  |  |
| Fossil - Other |  |  |  |  |
| Geothermal | Geothermal | Default |  |  |
| Hydrogen | Hydrogen | Optional |  | Default |
| Nuclear | Nuclear | Default |  |  |
| Solar | Solar |  |  | Default |
| Stored Energy (all stored energy irrespective of the original energy source) | Stored Energy | Optional |  | Default |
| Waste | Waste | Default |  |  |
| Water (flowing water or head of water) | Water | Default |  |  |
| Wind | Wind |  | Optional | Default |
| Other | Other | Default |  |  |

PC.G.8.2	Table of Energy Source types and energy conversion technology to be used for Power Generation Modules as required in PC.G.1.4.1 to PC.G.1.4.5:

| Energy Source | Energy Conversion Technology |
| --- | --- |
| Advanced Fuel (produced via gasification or pyrolysis of biofuel or waste) | Engine (Combustion/reciprocating) Gas Turbine Steam Turbine (Thermal Power Plant) Steam-gas Turbine (CCGT) Other |
| Biofuel - Biogas from anaerobic digestion (excluding landfill & sewage) |  |
| Biofuel - Landfill gas |  |
| Biofuel - Sewage gas |  |
| Biofuel - Other |  |
| Fossil - Coal gas |  |
| Fossil - Gas |  |
| Fossil - Oil |  |
| Fossil - Oil shale |  |
| Fossil - Other |  |
| Biomass | Steam Turbine (Thermal Power Plant) Other |
| Fossil - Brown coal/lignite |  |
| Fossil - Hard coal |  |
| Fossil - Peat |  |
| Nuclear |  |
| Waste |  |
| Geothermal | Geothermal Power Plant Other |
| Hydrogen | Engine (Combustion/reciprocating) Gas Turbine Steam Turbine (Thermal Power Plant) Steam-gas Turbine (CCGT) Fuel Cell Other |
| Solar | Photovoltaic Other |
| Stored Energy (all stored energy irrespective of the original energy source) | Storage – Chemical Storage – Electrical Storage – Mechanical - Compressed Air (Adiabatic & Diabatic) Storage – Mechanical – Liquid Air Storage – Mechanical – Pumped Hydro Storage – Mechanical – Flywheels Storage – Thermal Storage – Electrochemical (Batteries) Storage - Other |
| Water (flowing water or head of water) | Hydro – Reservoir (not pumped) Hydro – Run of River Hydro – Other Tidal Lagoons Tidal Steam Devices Wave Devices Other |
| Wind | Offshore Wind Turbines Onshore Wind Turbines Other |
| Other | Interconnector Engine (Combustion/reciprocating) Gas Turbine Steam Turbine (Thermal Power Plant) Steam-gas Turbine (CCGT) Other |

PC.G.9	Submission Cycle

PC.G.9.1	The diagram below illustrates the annual, coordinated process of submissions between Network Operators and The Company.

< END OF PLANNING CODE >