NGESO and NGED

# Coordinated Operational Methodology for Managing and Accessing Network Distributed Energy Resources (COMMANDER)

Workstream 3 Report – Impact Assessment of Coordination Schemes

Type of document (version): Confidential

WSP Project no. 70083589

NG reference: NIA2_NGESO012

Date: October 2023

WSP WSP House 70 Chancery Lane London WC2A 1AF Phone: +44 20 7314 5000 Fax: +44 20 7314 5111 WSP.com

Quality control

| Issue/revision | First issue | Revision 1 | Revision 2 | Revision 3 |
| --- | --- | --- | --- | --- |
| Prepared by | Duncan Josh (WSP) Matt Yates (WSP) Garima Yadav (WSP) Danny Pudjianto (ICL) | Duncan Josh (WSP) Matt Yates (WSP) Garima Yadav (WSP) Danny Pudjianto (ICL) |  |  |
| Checked by | Nuno Pedro, Goran Strbac (ICL) | Nuno Pedro, Goran Strbac (ICL) |  |  |
| Authorised by | Nuno Pedro | Nuno Pedro |  |  |
| Project number | 70083589 |  |  |  |
| Report number | 3 |  |  |  |

Contents

Executive summary

Glossary	5

1	Workstream 3 approach	9

2	Qualitative Assessment	11

2.1	Approach	11

2.2	Development of qualitative criteria	12

2.2.1	Future Worlds Impact Assessment	12

2.2.2	SmartNet	13

2.2.3	Ofgem Consultation: The Future of Distributed Flexibility Consultation	13

2.2.3.1	Archetype Definitions	13

2.2.4	Qualitative Criteria	15

2.3	Qualitative Assessment Responses	18

2.3.1	ESO Feedback and Results for Qualitative Assessment Matrix	18

2.3.2	NGED Feedback and Results for Qualitative Assessment Matrix	22

2.3.3	WSP Results for Qualitative Assessment Matrix	24

2.3.4	Imperial College Feedback and Results for Qualitative Assessment Matrix	26

2.4	Qualitative Assessment Combined Results	29

2.5	Qualitative Assessment Summary	32

2.6	Ofgem Consultation on The Future of Distributed Flexibility, Key Stakeholder Feedback	33

2.6.1	Industry Feedback	33

2.6.2	Summary of Ofgem Consultation Responses 	36

2.6.3	Consideration of Ofgem TFDF Consultation Responses for WP3 	37

3	Quantitative Assessment of Implementation Costs	39

3.1	ENA Future World Implementation Cost Review	39

3.1.1	Overall Scheme Implementation Costs Summary	45

4	Quantitative Assessment of Schemes 1 and 2	46

4.1	Overview	46

4.2	Key differences between the selected schemes	48

4.2.1	Annual system costs of the ESO/DSO coordination schemes	48

4.2.2	System costs and benefits of departing from the Business-as-Usual approach	50

4.2.3	Distribution capacity development under selected schemes	51

4.2.4	Flexibility resources deployed in different schemes	54

4.2.5	Utilisation of distributed flexibility resources under different use cases	58

4.2.6	Annual Utilisation of flexibility services	62

4.2.7	Impact of different ESO/DSO coordination schemes on the optimal power generation portfolio	64

4.2.8	Impact on other flexibility technologies	67

5	Stakeholder Consultation - Workshop	69

6	Overall Impact Assessment	71

6.1	Impact Assessment Key Findings	71

6.1.1	Quantitative Assessment	71

6.1.2	Qualitative Assessment Findings	72

6.2	Recommendation: preferred Coordination Scheme	73

7	Next steps: Work Package 4 - Roadmap for the deployment of the ESO/DSO coordination scheme	75

7.1	Additional Sensitivity Analysis with IWES	75

Glossary

| Term | Definition |
| --- | --- |
| ADE | Association for Decentralised Energy |
| ANM | Active Network Management |
| BEIS | Department for Business, Energy and Industrial Strategy |
| CER | Capacity Expansion Reserves |
| DER | Distributed Energy Resource |
| DNO | Distribution Network Operator |
| DSO | Distribution System Operator |
| ENA | Energy Networks Association |
| ENTSO-E | European Network of Transmission System Operators for Electricity |
| ESO | Electricity System Operator |
| TFDF | The Future of Distributed Flexibility |
| FSO | Future System Operator |
| ICL | Imperial College London |
| IWES | Integrated Whole Energy System |
| Ofgem | Office of Gas and Electricity Markets |
| ON | Open Networks (ENA initiative) |
| NGED | National Grid Electricity Distribution |
| NGESO | National Grid Electricity System Operator |
| STOR | Short Term Operating Reserve |

Executive summary The increase in distributed energy resources connecting to the distribution networks increases the ability of National Grid Electricity System Operator (ESO) and the Distribution Network Operators (DNOs) to utilise flexibility services to manage and operate their networks. Coordinating DERs to provide flexibility services to both transmission and distribution networks, while minimising conflicts and enhancing synergies will be complex and challenging. The ESO and National Grid Electricity Distribution (NGED) engaged WSP and ICL to deliver the Commander project that undertook a techno-economic analysis and an impact assessment of a selection of ESO-DSO coordination schemes and then will develop an engineering roadmap for the preferred scheme. It is expected that the roadmap changes could be scaled up to be applied across other DNOs as well. The idea of Project Commander is to initiate and promote debate and provide expert insights to develop roadmaps - it is not intended as a position statement by either ESO or NGED and it doesn’t contain any official policy recommendations. Both parties acknowledge that this is a complex space and more informed discussion needs to take place in order to design the optimal answer for customers. In Commander Workstream 1 and 2, two coordination schemes were identified and developed: - Scheme 1, “ESO-DSO Enhanced Coordination”, where ESO and DSO manage access to DERs via a set of primacy rules and share and/or hold DERs capacity, supported by data management processes agreed with the wider industry; and - Scheme 2, “Distributed Flexibility Coordinator”, a new entity or role that supervises and manages access to DERs, in close collaboration with ESO and DSOs, and ensures settlement and compliance, as well as information transparency and visibility. In terms of other studies and work in this area scheme 1 is most aligned with ENA Future Worlds B and Ofgem Distributed Flex Archetype ‘Thin’ with some elements of Archetype ‘Medium’. Key differences between scheme 1 and the Ofgem “The Future of Distributed Flexibility” (TFDF) Archetype Medium being that the latter has an independently managed and regulated coordination platform, facilitating market activities between the electricity network operators and the flex service providers. Scheme 2 is most aligned with ENA Future Worlds E and largely with the Ofgem TFDF Thick Archetype, with some aspects of the Medium Archetype. This report presents the outcomes of an impact assessment of the previously selected coordination schemes. The impact assessment contains the following key steps: - Qualitative Assessment - Quantitative Assessment - Combined Impact Assessment Qualitative Assessment Approach The qualitative assessment includes a review of previous work in this field followed by a rationalisation and selection of criteria which is relevant to a comparative evaluation of the selected schemes. An assessment was undertaken which includes the application of a score, and associated justification comments. The assessment has been shared with selected representatives from the ESO and NGED for feedback, approval and refinement of the approach and to capture the perspectives of the relevant parties. A workshop has been held with a range of industry stakeholders to further establish feedback and perspectives from other DNOs. A summary of key qualitative assessment metrics was developed to be used in conjunction with the quantitative assessment to form an Overall Impact Assessment. Quantitative Assessment Approach A quantitative assessment has been conducted, building on the findings from Workstream 2, additional analysis based on the Workstream 2 and 3 IWES modelling and scheme implementation costs drawn from previous studies and validated via engagement with the ESO and NGED. Quantitative comparisons of key scheme capital and operational costs have been developed accordingly. These are accompanied by an assessment of when enhanced flexibility coordination schemes are projected to significantly impact whole system electricity costs, to ensure that end consumers are not adversely impacted from the operation of future flexibility market operations. Key Findings The key findings from the Qualitative and Quantitative Assessments have been combined to provide an overall Scheme Impact Assessment, highlighting the key differences between the schemes and drawing key conclusions on critical scheme features, including a recommendation for a preferred scheme, whose implementation will be developed further in Workstream 4. The quantitative assessment undertaken with the IWES modelling shows clear long-term benefits for Scheme 2, partly due to the significant annualised system cost reductions projected when the scheme is mature. This is exacerbated in the deep electrification pathway which considers the electrification of heating, unlike in the hydrogen pathway. Scheme 2 also provides an overall energy network with greater capacity and ability to manage energy flows than Scheme 1, providing increased overall system resilience and flexibility to adapt. Scheme 1 tends to minimise the distribution network reinforcement costs, and this may constrain the use of distributed flexibility. The ENA Future Worlds implementation cost analysis showed that the total costs to implement World B (aligned with Scheme 1) are slightly higher than the costs to implement World E (aligned with Scheme 2), as well as the average annual costs. Although, the implementation costs of both schemes are marginal within the context of overall system costs and related savings against business as usual (~1%). Therefore, variations in the projections of the ENA Future World costs will have marginal impact on whole system costs. The qualitative assessment has shown a strong consensus for Scheme 2, when mature, albeit there are multiple concerns over the potential complexity of its implementation. Considering all inputs from this impact assessment and, incidentally, in line with Ofgem’s TFDF consultation, it is recommended to develop the ESO-DSO Coordination in line with Scheme 1 in the short term (until 2035) and prepare the implementation and transition to Scheme 2 in the later stages of the energy transition (from 2035 onwards). The strategic direction of the ESO-DSO Coordination is subject to external factors and initiatives that are being developed in parallel with this project. These include policy changes (e.g. Ofgem consultations and guidelines on TFDF and Local Institutions Governance, and DESNZ Flexibility Innovation Programme outcomes), technology readiness levels and markets evolution. The strategic direction of the ESO-DSO Coordination roadmap may vary depending on the factors mentioned above. Project Commander recommendations are underpinned by the principles of Whole Energy System Planning and Flexibility Coordination which will continue to be the key drivers for an optimal ESO-DSO Coordination roadmap. In Workstream 4, this roadmap will be developed, and will include the key initiatives in the development of systems, regulation, and market interfaces to be established in an effective and well managed approach for the transition.

# Workstream 3 approach

The overall impact assessment merges the results from qualitative and quantitative assessments. The overall assessment is shown in Figure 1-1.

Figure 1-1 - Combined Impact Assessment

The development and selection of coordination schemes considered a complex range of inputs from previous projects, literature and stakeholder engagement. For Commander we have undertaken a range of activities, and these are described in the relevant report sections:

- Chapter 2 – Review the approach taken to Qualitative Assessment in previous and ongoing industry initiatives focused on ESO-DSO coordination, in particular, the Energy Networks Association (ENA’s) Open Networks project developing future “worlds” and Ofgem’s consideration of potential DSO models. The findings will be utilised to develop a review approach for this study and to capture and contrast the key findings from previous studies. Stakeholder feedback will be sought from both the ESO and NGED client representatives and the wider DSO peer group via an ENA workshop. The IWES Whole System Energy Model will be enhanced and additional scenarios will be analysed, these will include an interim 2035 analysis run and alternative use case analysis. Additional Flexibility analysis results will be produced to facilitate the Quantitative Assessment.

- Chapter 3 - Scheme Implementation costs from the previous ENA Open Networks studies will be reviewed and, where practicable, refreshed from new data from the ESO and NGED.

- Chapter 4 – Review the approach taken to Quantitative Assessment in previous and ongoing industry initiatives focused on ESO-DSO coordination, in particular, the Energy Networks Association (ENA’s) Open Networks project developing future “worlds” and Ofgem’s consideration of potential DSO models and other standardised Ofgem CBA assessment approaches. The analysis results from IWES WS3 results and the previous WS2 analysis will be combined with the Scheme Implementation analysis to generate insight into a comparison of the two schemes and to identify when the projected flexibility volumes become the dominating factor in driving whole system costs, and therefore help to inform the programme needs for system conversion to improved more efficient coordination platforms.

- Chapter 5 – Engagement with key stakeholders (e.g. ESO and NGED and other DNOs at the ENA workshop) through a review and invitation to use the developed Qualitative Assessment approach. Assessment scores and comments will be captured and consolidated and presented in this chapter.

- Chapter 6 – Findings from Chapters 3 to 6 will be used to conduct an Overall Impact Assessment, providing insight into the key benefits of the two selected coordination schemes as well a review of areas for further consideration. A summary of Qualitative and Quantitative Assessment will be presented to support the overall Impact Assessment. The overall impact assessment will also seek to identify and set out key drivers for specific activities in the development of the schemes and when these will need to be considered and implemented.  The driving factors and associated schedules will then be further analysed and developed in WS4. The overall assessment will conclude with a recommended proposed scheme for WS4, and identify key criteria and scheme improvements that may be needed for the development of the scheme. These criteria will consider the current Ofgem review and the wider industry stakeholder feedback that has been captured under the Ofgem TFDF programme.

- Chapter 7 – Will set out the requirements and approach for WS4 and the identified next steps, whilst providing a summary of the identified data and information inputs for WS4.

# Qualitative Assessment

WS1 provides a review of Coordination Schemes which have been proposed by other industry focus groups, both from the UK and European programmes. WS1 identified two preferred approaches to be taken forward for detailed analysis and comparison, and WS2 undertook detailed Whole System flexibility modelling of the two selected schemes in a specifically enhanced IWES model.

In this chapter a qualitative assessment of the two schemes is undertaken, which draws on previous industry assessments for coordination schemes and the latest stakeholder feedback from the Ofgem TFDF programme which has been published during the delivery schedule of this project.

## Approach

The qualitative assessment will include the following steps:

- Identify four key ESO-DSO and flexibility services coordination studies.

- Review the approach undertaken for the qualitative assessments within the selected studies.

- Identify the common categories of assessment and their indicated relevance and significance in the overall solution assessment.

- Generate a combined assessment criteria list, with significance weightings for this ESO-DSO coordination assessment.

- Review, refine and finalise the draft approach with the ESO and NGED immediate project team.

- Undertake an assessment of Scheme 1 and Scheme 2 utilising the developed assessment criteria, producing scores, weighted scores, RAG ratings and review comments.

- Circulate the output of the assessment to relevant parties within ESO and NGED to seek their comments on the approach, noting any refinements, and to capture assessment scores, and associated score justifications against each criteria, for each scheme and phase.

- The feedback and assessment results will then be used to further refine the approach and to produce a final assessment process.

- Assessment results will be consolidated, and available analysis will also be shared in the peer review workshop for feedback.

- All feedback will be captured and added to the WS3 report.

Figure 2-1 - Qualitative Assessment Approach

## Development of qualitative criteria

The sources used to create the criteria for the qualitative assessment are described in this section, along with any additional consolidation of information required.

### Future Worlds Impact Assessment

The Impact Assessment of the Future Worlds includes a qualitative assessment of each world against several criteria, which were based on the HM Treasury’s five case model. Results for each world were based on a relative ranking of performance against each criterion. The summary of this ranking is displayed in Figure A, and a more in-depth discussion of each criterion can be found in Appendix A of the Impact Assessment.

The qualitative assessment undertaken for the two schemes in Commander considered these criteria as a starting point. Reductions were made according to two criteria:

- Identical rankings: There were five Future Worlds to consider in the original qualitative assessment, whereas we only consider two potential coordination schemes in Commander. Previous work has highlighted that these correspond most closely to Future Worlds B and E. Therefore, in cases where the previous impact assessment identified a similar ranking between these worlds, criteria are considered a low priority and deselected. An example of this is “Facilitates decarbonisation of generation”, which primarily functions to distinguish World C from the alternatives.

- Duplication: From analysis of reasoning in Appendix A, there are criteria which can be combined since the arguments presented are largely similar or share common themes. For example, in relation to Worlds B and E, the criteria “Facilitates decarbonisation of heat and transport” and “More electricity consumed closer to the point of generation” both depend upon establishing levels of capability within a new organisation, rather than relying upon existing competencies in the energy sector. Based on these two criteria, plus a few others, a new category called “Competencies and Capabilities” is created which encompasses a number of these existing criteria.

### SmartNet

SmartNet was a project funded under the Horizon 2020 research and innovation programme, which compared five TSO-DSO coordination schemes, implementing four within simulation to compare technical and economic performance. Further information on this project, and its relevance to Commander, can be found in the WS1 deliverable .

Deliverable 1.3 of the SmartNet project outlines the chosen schemes . Section 5.1 of this deliverable includes some assessment of benefits and ‘attention points’, which can be broadly considered as negatives associated with any scheme.

Of particular interest for Commander were the Common TSO-DSO AS market model and the Integrated Flexibility market model. These share many features with the schemes under investigation within Commander. These cannot be mapped directly onto the Commander schemes, but the identified criteria used to describe the SmartNet schemes have been used as an input when compiling the list of criteria for the coordination scheme qualitative assessments.

### Ofgem Consultation: The Future of Distributed Flexibility Consultation

In March 2023, Ofgem published a Call for Input on the topic of “The Future of Distributed Flexibility” (TFDF). This presents four archetypes, for a future digital infrastructure which can support distributed flexibility, including a BAU archetype.

#### Archetype Definitions

Thin archetype

The thin archetype describes a directory that aims to help Flexibility Service Providers (FSPs) and Market Operators (MOs) find one another. All other flexibility market data exchange is bilateral or via third parties. The common digital energy infrastructure does not play any role in improving any stage of procurement, operations or reporting. The process flow for the Thin archetype can be found in Appendix B1.

Medium archetype

The medium archetype describes a flexibility exchange. Here, data transfer relevant to procurement, operations and reporting stages of delivery is made visible via the exchange to coordinate more market activities and enable improved visibility on asset performance.

As shown in Appendix B, Figure 2, the flexibility exchange acts as a layer, coordinating the data transfers in one place, creating a trusted ‘single source of truth’ for flexibility services.

The exchange acts to coordinate activities across many markets, and by focussing on the data transfers, can accommodate changes to these markets. Activities themselves, such as auctions, dispatch, settlement, and payment continue to take place via established institutions, with the exchange model providing a means to coordinate and share this data to improve market outcomes.

Thick archetype

The thick archetype describes a single, central platform for all flexibility markets, enabling end-to-end delivery of market activities. This would be enabled by ingesting functions across commercial interfaces, dispatch and metering systems and settlement and payment systems. The role for independent market platforms across flexibility service delivery remains unclear in this archetype.

Appendix B, Figure 3 shows the data flows for the central platform. The common energy digital infrastructure integrates data across many markets and flexible assets, and provides optimised outcomes based on the internal algorithms of the platform.
These archetypes were assessed within the CFI against the delivery of three critical functions, and also against criteria related to desirability and feasibility. The table related to delivery against the three critical functions is shown in Figure 2-2

Figure 2-2 - Rating of four proposed archetypes in Future of Distributed Flexibility CFI against three defined critical functions

Of most interest for the analysis within Commander is the relative performance of the “Medium” and “Thick” archetypes. As with the SmartNet schemes, there is no exact mapping between Commander schemes and the archetypes suggested within the Ofgem TFDF document since features of these suggested solutions are often combined differently. However, the comparison between Medium and Thick provides some useful analogues to the assessment being made within Commander.

With regards to selecting criteria, greater focus was therefore given to those criteria within the CFI which differentiated between the “Medium” and “Thick” archetypes.

Further analysis was also performed on the responses to the CFI, which were submitted for May 2023 . Given the number of responses received, this was a non-exhaustive exercise, which placed greater emphasis on replies from network operators, and then incorporated a random sample of the remaining responses. Again, particular attention is given to responses to the “Medium” and “Thick“ archetypes, particularly where features align with the schemes proposed by Commander.

### Qualitative Criteria

Once these sources were all consulted, a shortlist of criteria was drafted to reflect the information found. A weighting is also applied to the categories based on prevalence across the sources considered – therefore, any criteria which has been identified multiple times will receive a larger weighting towards overall scheme score.

This created a set of fourteen criteria against which each of the Commander schemes would be assessed. In summary, these are:

- Competencies and Capabilities

- Structure and regulatory requirements and changes

- Complexity of system operation

- Service availability and reliability

- Whole system optimisation – coordination platform

- Whole system optimisation – electricity system investment

- Clarity of accountability for technical performance

- Resilience and recovery

- Time required for delivery of proposed solution

- Adaptability and enabler of innovation

- Neutrality and resolution of conflicts of interest

- Conflict management (operational)

- Complexity of market participation and contractual arrangements

- Market liquidity

More detailed descriptions of these criteria, along with the applied weightings towards overall scheme score, and provided in Appendix N.

| Criteria Number | Criteria | Details/Notes |
| --- | --- | --- |
| 01 | Competencies & Capabilities | High Score = Very Competent/Very Good Capability Competencies and capabilities regarding *Coordination of flexibility services and market operation *Knowledge and understanding of local, regional and national network management requirements *Provision of Consumer benefit from markets *Ability to unlock uptake of LCTs and facilitate decarbonisation of heat and transport *Increased Consumption of locally generated electricity *Knowledge of DNO networks and consumers |
| 02 | Structural and regulatory requirements/change | High Score = Lower amount of/less impacting changes required Representing depth of changes required to be able to implement either Scheme: *Appropriate regulatory frameworks in place *Appropriate Funding Mechanisms in place *Level of Required Regulation for approach/scheme *System Operators - difficulty level to implement changes |
| 03 | Complexity of system operation | High Score = Simpler/more straight forward system operation *Management and coordination of data from many sources and potential overlapping boundaries/requirements *High volumes of data collection, management, analysis and security requirements *Managing / dispatching increased flex volumes from lower voltages |
| 04 | Service availability and reliability | High Score = High Availability and Reliability Ability to maintain or enhance service availability and reliability in a future network management scenario which relies extensively on flexibility services to maintain effective and efficient operation. (note: reliability is a concern we would argue across the board as we don't know how reliable people will be) |
| 05 | Whole System Optimisation - Coordination Platform | High Score = High Level of Whole System Optimisation for Operational Coordination *Coordination - Avoids/Limits Duplication *Coordination - Exploits Synergies Note - Conflict Management is scored separately below (to discuss whether to combine here) *Level of Independence in decision making |
| 06 | Whole System Optimisation - Electricity System Investment | High Score = High Level of Whole System Optimisation for Investment *Electricity system - Efficient Network Investment *Electricity system - Efficient Supply and Storage Investment *Electricity system - Efficient Use of Assets *Level of Independence in network investment decision making |
| 07 | Clear accountability for technical performance | High Score = Good Level of Accountability for Technical Performance (at least as good as current) *The ability of all parties to have clear visibility, responsibility and accountability for the technical performance of their operational assets. *Including regarding the risk management associated with under or over procurement of flexibility services (e.g. full responsibility for ESO and DSO for accountability under scheme 1 for assessing needs and associated procurement of flex services, whereas for scheme 2 the ESO and DSOs would have full responsibility for assessing needs, but the delivery (and procurement) would be the responsibility of the independent distributed flex coordinator. |
| 08 | Resilience and recovery | High Score = High Level of Resilience and Ability to Recover from Faults/Outage Events *Considers overall resilience and recovery of network services in typical and extreme fault events. For example, storm events which affect a wide area and multiple network components across voltage levels. *Consider the impact of lower network headroom (facilitated by optimised flexibility services), on exposure level to high impact infrequent events. Also, may increase exposure to security risks. *Post fault recovery may benefit from an optimised, fluent flexibility service. |
| 09 | Time required for delivery | High Score = Less time to deliver *Time required to deliver the Scheme *Accounting for structural, policy and regulatory change and development of existing or new coordinator organisations and platforms. |
| 10 | Adaptability and enabler of innovation | High Score = Good enabler of innovation and ability of scheme to adapt to changing conditions and market opportunities Will a scheme provide an adaptable environment that encourages and facilitates innovation in the provision and management of flexibility services |
| 11 | Neutrality/resolving conflict of interest | High Score = High level of Neutrality and Good Ability to Address Conflicts of Interest *Clear Neutrality *Resolution of commercial conflicts of interest *Confidence and trust for market actors and consumers |
| 12 | Conflict management (Operational, not long term planning) | High Score = Good Ability to Manage and Resolve potential operational conflicts related to flex operations including procurement and dispatch Resolution of ESO DSO conflicts including: *Conflicting price signals, and time of use windows - sub optimal dispatch *Conflicting dispatch signals for multi service provider DERs/FSPs |
| 13 | Complexity of market participation and contractual arrangements | High Score = lower complexity for market participation or ability to overcome potential complexities Including: * Access to market for FSPs * Complexity of contractual arrangements for FSPs *Complexity of contractual arrangements for coordinator(s), (Including Qualification, procurement, dispatch and settlement for all parties) |
| 14 | Market liquidity | High Score = Good Market Liquidity *Ability for flexibility services to be traded, without significant impact on service costs. *differing levels of liquidity across DNO and ESO markets reduces customer benefit initially |

## Qualitative Assessment Responses

The feedback from the project stakeholders has been collated to provide insight into the current opinions of key ESO and NGED representatives on the relative strengths and weaknesses of the two coordination schemes. High scores (Maximum of 5) for a criterion represents strong credentials against this aspect of the scheme, low scores (Minimum of 1) represent perceived weaknesses and issues which need to be addressed. It is of note that the responses do not reflect an agreed company position for either the ESO or NGED, but are provided by staff who are actively engaged in this area of work and are familiar with the Commander project.

### ESO-DSO Feedback and Results for Qualitative Assessment Matrix

The combined criteria scores from the qualitative assessment are shown in Figure 2-3. The total score for the assessment is not intended to be used to select a ‘winner’ from the two schemes but does provide a useful means to visualise the way that the criteria are considered by the assessor. Where there are clear differences between the scoring of the two schemes, this does also provide an indication that a scheme has an overall preference for the assessor.

ESO-DSO Responder 1

Figure 2-3 – ESO-DSO Responder 1, Qualitative Assessment Scores, Shown by Scheme and Phase

The criteria assessment results from the first ESO-DSO representative indicate that, overall, they consider that Scheme 2 provides notable overall benefits in phase 1 and in phase 2, when the schemes are considered to be mature.

Key Discussion Points

The individual Criteria Scores provided by the ESO-DSO are shown in Figure 2-4. The individual criteria scores are shown for the two schemes, for each phase.

Figure 2-4 – ESO-DSO Responder 1, Qualitative Assessment Scores, Shown by Criteria

When considering individual assessment criteria, the responses from the first ESO-DSO assessor indicate that they particularly see scheme 2 being relatively stronger across criteria 01 (Structural and regulatory requirements/changes), and also marginally stronger for criteria 04 (Service availability and reliability), criteria 05 (Whole System Optimisation - Coordination Platform), criteria 06 (Whole System Optimisation - Electricity System Investment), criteria 07 (Clear accountability for technical performance) and criteria 10 (Adaptability and enabler of innovation).

The comments provided for the relative strengths of Scheme 1 were:

Criteria 01: there are significant capability barriers to coordination today.

Criteria 02: If Scheme 2 were to be implemented I have assumed that there would be more clarity on this than there is on Scheme 1 given that it is such a leap from where we are today.

Scheme1, Phase1: Relatively lower level of regulatory and policy change, in particular GDPR concerns over CERs

Scheme2, Phase1:

Criteria 08 – Scheme Delivery Time, Comment Applied to Scheme 2: More work to do and would require extensive consultation.

### ESO-DSO Responder 2 Feedback and Results for Qualitative Assessment Matrix

Chart of Scores

Figure 2-7 – ESO-DSO Responder 2 Qualitative Assessment Scores, Shown by Scheme and Phase

The criteria assessment results from the ESO-DSO Responder 2 representatives indicate that, overall, they have a small preference for Scheme 1 over Scheme 2, over both phases of deployment. The difference in the total scores is reduced for phase 2 of the schemes.

Discussion Points

The individual Criteria Scores provided by the ESO-DSO Responder 2 are shown in Figure 2-8. The individual criteria scores are shown for the two schemes, for each phase.

Figure 2-8 – ESO-DSO Responder 2 Qualitative Assessment Scores, Shown by Criteria

When considering individual assessment criteria, the responses from the ESO-DSO Responder 2 indicate that they particularly see scheme 1 being relatively stronger across criteria 02 (Structural and regulatory requirements/changes), criteria 08 (Resilience and recovery) and criteria 09 (Time required for delivery). Whereas they see scheme 2 being stronger (in phase 2) regarding criteria 03 (Complexity of system operation), criteria 05 (Whole System Optimisation - Coordination Platform) and criteria 13 (Complexity of market participation and contractual arrangements).

The comments provided for the relative strengths of Scheme 1 were:

Criteria 02: This is the evolution of a current process, and should be simpler to implement. We have stakeholder buy in and processes for delivery.

Criteria 07, Comment Applied to Scheme 2: This scheme is scored lower as it moves accountability away from the procurer of the service.

Criteria 08, Comment Applied to Scheme 2: Use of a single system reduces redundancy. However fewer parts reduces the risk of integration issues. (With reference to Scheme 1 having fewer organisations to coordinate)

Criteria 09, Comment Applied to Scheme 1: This is an evolution of the current process.

Comment Applied to Scheme 2: Developing such capabilities would be a significant endeavour.

Questions remain on the feasibility due to the complexity of operations.

The comments provided for the strengths of scheme 2 were:

Criteria 03: Both schemes will require the exchange of significant amounts of data. A single coordinating entity may reduce some flows and centralise some the exchanges.

Criteria 05: A single coordination/optimisation should prove a more optimal output.

Criteria 13: Having a single optimisation will reduce the need to participate in parallel schemes.

### ESO-DSO Responder 3 Feedback and Results for Qualitative Assessment Matrix

Figure 2-5 – ESO-DSO Responder 3, Qualitative Assessment Scores, Shown by Scheme and Phase

The criteria assessment results from the third ESO-DSO representative indicate that, overall, they consider that Scheme 2 provides substantial overall benefits in both phase 1, and phase 2 when the scheme is considered to be mature.

Key Discussion Points

The individual Criteria Scores provided by the ESO-DSO third responder are shown in Figure 2-6. The individual criteria scores are shown for the two schemes, for each phase.

Figure 2-6 – ESO-DSO, Responder 3, Qualitative Assessment Scores, Shown by Criteria

When considering individual assessment criteria, the responses from the third ESO-DSO assessor indicate that they see strong benefits for Scheme 2 in both phase 1 and phase 2. Key areas of perceived advantages for scheme 2, when mature, being in criteria 01, 04, 05, and from 07-10.

The comments provided for areas that need to be addressed for either scheme were:

Criteria 02: Scale of change needed to enable scheme-1 will probably be higher than scheme-2.  Additional risk around pace of change will depend upon DSOs - not all entities will move to the same rate of change.

Criteria 06: Unable to comment.  Investment signals could flow from an efficient market framework.  Need to know more about how this sits alongside existing DNO framework where revenue are tied to connection volumes.

Criteria 14: Unable to comment. Investment signals could flow from an efficient market framework. Unsure how both schemes help however scheme-2 may potentially offer higher liquidity.

The comments provided for the relative strengths of Scheme 2 were:

Criteria 03: Both Schemes add complexity to system operation however a single optimisation process and single optimisation platform provides clear insight into optimisation decisions.

Criteria 04: Both schemes will face challenges around service availability & reliability however scheme-2 will be able to apply learnings more efficiently across board.

Criteria 05: Both schemes will face challenges around service availability & reliability however scheme-2 will be able to apply learnings more efficiently across board.

Criteria 07: Scheme-2 clearly scores higher for me on this account.  Single optimisation owned by a single entity provides clear insight into decisions.

Criteria 08: Scheme-2 potentially offers greater provision for sharing localised risks across all DSOs.

Criteria 09: Although scheme-1 may have a slight head start (DSO legally exist whereas DFC does not), it is not a huge factor.   Scheme-1 is still early stages in maturity so cannot see this as a significant advantage compared to Scheme2.

Criteria 10: Scheme 1 will be slow progress such as ON.  Single DFC able to progress innovation and adapt faster to changing conditions.

Criteria 11: Scheme-2 clearly scores higher for me on this account.  Single optimisation owned by a single entity provides clear insight into decisions.

### WSP Results for Qualitative Assessment Matrix

Chart of Scores

Figure 2-9 - WSP Qualitative Assessment Scores, Shown by Scheme and Phase

The assessment undertaken by WSP has considered the findings from the Commander study, in combination with the key points raised during other similar studies focussed on flex market coordination and the latest feedback from the Ofgem Consultation on TFDF (refer to section 2.6for further information). It is considered to take a neutral perspective with no vested interest in either scheme.

The WSP qualitative analysis indicates the scheme 1 has greater benefits during phase 1, whereas scheme 2 shows greater benefits when mature, represented in phase 2 criteria assessment scores.

Key Discussion Points

Figure 2-10 - WSP Qualitative Assessment Scores, Shown by Criteria

The WSP study team has recognised key benefits for scheme 1 in phase 1 in the following areas:

01 - existing capabilities,

02 - lower requirements for structural, policy and regulatory changes

03 – less complex in terms operational requirements and changes

Whereas the key strengths for scheme 2 are expected in phase 2, when the scheme is mature and are focussed on the following criteria areas:

05 & 06 – Whole System Optimisation, across both the coordination of flexibility services and long-term network planning

11 – The ability to resolve potential conflicts of interest (which may be perceived as unfair market practices) and retain neutrality with respect to procurement of flexibility services and longer-term network planning

12 – Operational conflict management – ensuring that flexibility services procured at different voltage levels or geographical areas of the network do not produce sub-optimal or problematic conflicts on the network.

14 – Maintaining a high degree of market liquidity, by ensuring that the market has access to clear products and pricing which are maintained in the scheme with greater coordination.

### Imperial College Feedback and Results for Qualitative Assessment Matrix

Chart of Scores

Figure 2-11 - ICL Qualitative Assessment Scores, Shown by Scheme and Phase

The assessment undertaken by ICL has particular focus on the findings from IWES modelling analysis, and the associated implications on the coordination schemes, whilst also considering the Imperial team’s wider industry work in this field.

The qualitative assessment by ICL shows an overall preference for scheme 2, both in the initial phase and when the schemes are mature.

.

Key Discussion Points

Figure 2-12 - ICL Qualitative Assessment Scores, Shown by Criteria

The ICL IWES project team has recognised key benefits for scheme 1 in phase 1 in the following areas:

01 - existing capabilities,

‘Benefits of Member from ESO and DSOs are familiar with their roles and understand well their networks; however, ESO only understands the network around the GSP interface at distribution systems while DSO only understands partially the transmission surrounding their operational regions’

Common issues with scheme 2

‘Lack of experiences in dealing with smart emerging flexibility technologies

Harnessing flexibility especially from millions of small/medium-scale sources is challenging, and the technologies are still not mature yet’

02 - lower requirements for structural, policy and regulatory changes

Criteria 03, Phase 1

For scheme 1: The coordination may involve intensive discussions, need time, risk of lack of transparency.

For scheme 2: Huge amount of data need to be processed; High computational cost; No iteration; More complex.

Criteria 03, Phase 2

For scheme 1: More advanced computer equipment will emerge helping large data to be processed in a real time.

For scheme 2: No iteration process makes the decision making process faster and More accurate.

Selected Considerations for both schemes are highlighted below:

Phase 1

‘-Scheme 1 leads to a smaller local network capacity which may constraint the volume of distributed flexibility that can be accessed by ESO

- If the whole-system value of flexibility assets is not recognised, it will disincentivise further deployment of those flexibility technologies

- There is a risk that ESO does not have full access to all distributed flexibility resources

- ESO may prioritise flexibility at transmission where ESO can have a direct control - disincentivising development of distributed flexibility’

Phase 2

‘Scheme 2 may be able to analyse more comprehensively the availability and reliability characteristics of service providers considering it collects all relevant information for the analysis. Hence it can derive more comprehensive strategies to enhance the availability and reliability of services’

Criteria 12:

Scheme 1 phase 1: More likely to have conflicts as the coordination is conducted iteratively by different entities which protect their business interests.

Scheme 2 phase 1: Integrated - less conflict and optimal synergy

Scheme 1 phase 2: Integrated - less conflict and optimal synergy

## Qualitative Assessment Combined Results

The qualitative assessment results from the separate responses have been combined into a single set of responses, to help identify and illustrate where there is common opinion and where there are more diverse views for the two schemes across the different assessment criteria. The combined responses also provide an overall view of the perceived strengths and weaknesses of the two schemes, across both implementation phases.

Figure 2-13 - Qualitative Assessment Scores, Averaged from all Responses, Shown by Scheme and Phase

The scores from all of the qualitative responses have been averaged for each criteria, scheme, and phase and are shown in Figure 2-13 for each scheme and phase. The total scores provide a reasonable indication of the overall preference for a scheme. The combined averaged scores indicate that there is an overall preference for scheme 2, by a fairly narrow margin, in phase 1 and by a larger margin in phase 2 when the schemes are considered to be mature.

Figure 2-14 - Qualitative Assessment Scores, Averaged from all Responses, Shown by Scheme and Phase, by Criteria

The scores from all of the qualitative assessment responses have been averaged for each criteria, scheme, and phase and are shown in Figure 2-14 by criteria. The averaged phase 1 scores (Ph1 S1 and Ph1 S2 scores) show a perceived fairly even mix of strengths and weaknesses across the different criteria for the two schemes. Whereas there is a clear sign of relative strengths for Scheme 2 in phase 2, when it is considered to be mature, with higher averaged scores across twelve of the fourteen criteria, and for one of the two criteria where the score is lower, it is only by a small margin. The only criteria where Scheme 1 is considered to be clearly stronger in phase 2, is for criteria 02 which represents the changes necessary to address structural and regulatory requirements.

Figure 2-15 - Qualitative Assessment, Range of Scores from all Responses, Shown by Scheme and Phase, by Criteria

The range of scores received from all of the qualitative assessment responses are shown in Figure 2-15. These provide a string indciator of how aligned the respondees opinions are across the different criteria, schemes and phases. Criteria 12 (Conflict management – Operational) shows the greatest diversity in applied scores (a range of 4) for scheme 1, phase 1. There is also significant diversity of opinion (a range of 3) across the following criteria, schemes and phases:

Phase 2 of scheme 1 for Criteria 08 (resilience and Recovery) and 09 (time required for delivery)

Phase 1 of scheme 1 for Criteria 10 (Adaptability and enabler of innovation), 11 (Neutrality/resolving conflict of interest) and 14 (Market liquidity)

Phase 1 of scheme 2 for Criteria 09, 11, 12 and 13 (Complexity of market participation and contractual arrangements)

There is a stronger consensus for when both schemes are mature (phase 2), and this is especially the case for Scheme 2 where there are only four criteria with a variation of two in the assessment scoring, eight criteria with a variation of one, and two criteria with no variation in scores (04 and 10 – values of zero were replaced with small positive values to retain the chart structure)

Figure 2-16 - Qualitative Assessment Scores, Showing the Mode from all Responses, Shown by Scheme and Phase, by Criteria

The mode (most frequently occurring values) for the combined qualitative assessment responses are shown in Figure 2-16. Scheme 2, Phase 2 clearly shows the more consistent higher scores, with the mode being at least three across all criteria and at least four across nine criteria.

## Qualitative Assessment Summary

The qualitative assessment has developed a clear set of assessment criteria which are considered critical for the development and operation of either of the coordination schemes. The assessment has then sought to establish opinions from a range of project stakeholders which have experience in this field and are actively engaged in related electricity network operations or analysis. The assessment analysis has shown that there are a range of opinions regarding the near-term benefits and implementation hurdles of each scheme, but that there is much closer consensus in the relative strengths of the mature schemes.

When considering the overall averaged combined scheme criteria scores, Scheme 2 is preferred for both phase 1 and phase 2, however there is much more diverse opinion regarding the relative issues that Scheme 2 may have in phase 1, primarily due to the larger changes required to set up and manage the transition to a new coordination body and the development of a the systems required for a central coordinating body.

Based on the feedback from ESO and NGED representatives and the ICL and WSP project team members, there is clear consensus that Scheme 2 provides notable benefits over Scheme 1 when both schemes are mature. This is evidenced by both the higher criteria scores and also the tightness of the scoring for the mature Scheme 2. It would be beneficial to include additional feedback from the wider industry stakeholders to determine opinion from across the industry.

## Ofgem Consultation on The Future of Distributed Flexibility, Key Stakeholder Feedback

In March 2023, Ofgem opened a consultation of The Future of Distributed Flexibility, with a call for input (CFI). Responses, classed as non-confidential, have been published on the Ofgem website. WSP have reviewed a broad selection of the published responses from across the stakeholder groups to ascertain stated archetype preferences, key concerns, views on enabling factors and benefits that may be realised. Selected response comments and expressed archetype preferences are shown below to highlight some of the views expressed.

### Industry Feedback

Piclo Flex: preference for an alternative archetype: ‘We suggest an alternative approach and architecture is explored that benefits from coordination, enables innovative value propositions and is based on agreed standards and data protocols. However, importantly it also acts as a gatekeeper to ensure all platforms and markets follow these agreed standards- providing the teeth necessary for the benefits Ofgem outlines to exist, without the risks identified above. This would look something like a “Markets Governance Framework” (MGF)’

Innovate UK: No preference explicitly expressed, inference for medium or thick ‘The call for input discusses how ‘thin’ a layer of infrastructure is needed. Political imperatives may dictate that this layer is defined as thinly as possible to allow for market competition to define the best solution as much as possible. While this is desirable in many ways, this requirement should be balanced with the pace of change needed in delivering a digitalized energy system, fit for the future. It is likely that a more significant centralized digital infrastructure will enable a faster pace of change more appropriate to the current situation rather than allowing market evolution through competition and standard development.’

Trade Associations

Energy UK, towards thin initially, but recognising benefits (and risks) of medium and thick: ‘A ‘thin’ archetype (directory of buyers and sellers) could be developed immediately, alongside the work of actively managing the ON programme to ensure that the key enablers are satisfactorily completed, according to the agreed timeline.

Members recommend that work on a medium /thick archetype is paused until this work is complete. This is both because this work should be prioritised and because the outputs will be needed to inform the next stage and ensure that additional spend can be justified in terms of benefits to the consumer. Members generally support an evolutionary approach here (to reduce the risk of procuring assets that may be outdated by the time they are delivered).’

‘Whilst a ‘thick’ archetype with full interoperability would deliver the best benefits to the market, a ten(+) year delivery timeframe is too long. By 2033, either the flex markets will be working effectively without this or alternative flex provision (for example, on the supply side, potentially at higher cost) would have been built/ commissioned to support the system. Members also highlighted the risk that, given the pace of change, any thick archetype platform specific now could be out of date/ redundant before it was complete.’

Community Energy England, no preference expressed, implied ‘towards thick’: ‘Community energy organisations are always looking for new and strategic ways to deliver decarbonisation and community benefit (as the old business models of installing more local generation are made increasingly difficult to execute). Some have tried to engage with flexibility but the general message from our members is that the tender is often not in their area and even if it were, the money offered in the auction is insufficient to build a business case for building flexibility assets. If the value of carbon avoided by the flexibility asset was priced in, rather than just the value of avoided reinforcement, then it is likely that the price would enable flexibility projects to happen. (One organisation told us that installing batteries for flexibility is not financially viable. They do it to store daytime generation and sell at times of peak demand when the price is high, which is ‘flexibility’ but not enabled by the current flexibility market or auctions.)’

‘Additionally, very key problems for community energy organisations that have engaged in flexibility have been interoperability of products, access to data, including smart meter data.

This will require a nationally (and internationally) joined up approach which a single entity with strong links to government is better placed to deliver’

Scottish Renewables, preference for medium, whilst noting potential benefits of thick. ‘While the functionality of ‘Thick’ archetype is compelling, concerns around the task of delivering and operating such a system in the timescales required and for an acceptable cost, may make the ‘Medium’ archetype more achievable in the real world. The Business-as-Usual approach or ‘Thin’ archetype might not deliver the co-ordinated lowest cost distributed flexibility we need for net-zero.’

Power Generators

Sembcorp, preference for Thick archetype, noted that CERs may not easily provide large volumes of flex. ‘We would support a thicker, more centralised model as we believe it is more likely to be successful. The effectiveness of the market – sending accurate signals to the correct parties – is the most important criteria in our opinion. If the solution is otherwise perfect but users are being incentivised to act in a manner that is unhelpful to the system, this will be similar or worse than the status quo.’

Aggregators & FSP Associations

Flexible Power Alliance: No preference expressed: ‘I believe that regulated bodies should really play the role of enabler, creating the right conditions, but there I believe there the responsibility stops. Leave the execution to the market. Market based partners have the skills and capabilities of setting up viable partnerships. They know how to engage with customers; they know to set up attractive, innovative propositions, they know (the psychology) of regular users, customers etc, and how to nudge them into change.

In the Netherlands we have now a Market Facilitation Forum (English website), where regulated parties and market parties can find each other in the common goal of creating the right incentives and environment for the energy system of the future.’

Octopus Energy

Octopus Energy acknowledge the benefits of a centrally coordinated system (thick archetype ), but are concerned that it may be overly complex, expensive and time consuming to develop from scratch, advocating that if selected then it should build on the best of the existing platforms and systems. If this is not possible then they support the medium archetype which is considered more straight forward to implement.

‘If it proves not to be possible to evolve and adapt existing systems, then instead we would favour the medium archetype. While the potential benefits in terms of usability and market access may be slightly lower than the central market platform approach, we agree that this scores more highly from a feasibility perspective and that this outweighs the marginal gains of the monolithic central platform. In addition, we view that the exchange approach may be more able to adapt as distributed flexibility markets and approaches to manage congestion evolve with time.’

Octopus Energy also noted that there are several immediate needs which must be addressed to enable smooth operation and development of the market:

‘● Complete standardisation of current DNO flexibility products – including contracts, pre-qualification processes, data standards and dispatch methods

● Introduction of a central digital asset register by the end of 2023 – to improve visibility and transparency for DNOs, regulators and market participants, to reduce the risk of duplication and conflicts, and to ease entry into new markets

● A standardised approach to baselining - to ensure payments for the provision of services are as accurate as possible, noting this gets more difficult with smaller sample sizes

Whilst there is ongoing work to achieve the above objectives, through the ENA Open Networks (ON) project and Government’s Automatic Asset Register (AAR) programme - progress has been slow. In order to ensure the objectives of the ON project are achieved, we would like to see Ofgem use its regulatory powers to hold DNOs to account and clearly demonstrate progress under ON in Ofgem’s annual DSO Incentive Reports. Ofgem should set stretching targets for the ON ensuring full project deliverability and completion by the end of 2024, at the latest.’

DSOs

Only four DSOs have provided responses*, one of which was as part of a combined response (*which have been published by Ofgem, others may have been received but not published) – main preference for medium archetype, either with some consideration of thin or thick elements.

Elexon, preference for medium, acknowledging benefits of thick but see long time frame required being an issue: ‘We propose that those reform options that can be implemented promptly should be prioritised and considered further. For instance, although Archetype 4 - ‘Thick’ performs well in terms of meeting Ofgem’s three critical functions, we do not believe it is feasible given the time and costs involved in its delivery. On the other hand, Archetype 3 – Medium ‘Exchange’ builds on existing capabilities, can be implemented faster, and performs well against the three critical functions. The earlier we implement the proposed changes, the sooner we can enable the benefits of distributed flexibility, particularly as it will be a key enabler for achieving net zero’

Open Networks, no preference expressed: ‘While we share Ofgem’s view of the problem in terms of a lack of a pace and the need to drive standardisation, we are concerned that Ofgem is too dismissive of the progress that has been made by Open Networks and in particular the Challenge Group see it as vital that momentum is not lost while any longer-term solution is put in place. As Ofgem themselves say “there is no time to lose”. In particular the Group are clear they do not want Open Networks to “down tools” while waiting for an Ofgem decision – and would welcome Ofgem itself reiterating that message.’

### Summary of Ofgem Consultation Responses

The feedback received by Ofgem in their recent consultation shows that there are a diverse range of opinions from across the industry stakeholder groups, there are however some common themes which are highlighted across diverse groups. A summary of key areas of concern or focus follows.

Flexibility Service Providers

From the flexibility providers responses which were reviewed there were similar concerns that a complex centralised system built from scratch would be open to long timelines and risks associated with delivery, inability to adapt (which may make it in partially redundant by the time it is delivered due to other market developments), restraining market innovation and high implementation costs. A support for some of the potential benefits for a ‘thick archetype’ centralised system were acknowledged in terms of facilitation of market mechanisms, with one provider suggesting a medium archetype being more realisable if the thick archetype could not be evolved from current market systems. An alternative approach was advocated by one of the flexibility platform providers, which was more aligned to a ‘Market Governance Framework’.

DNOs

The DNOs, with published responses, showed a general preference for the medium architecture, whilst recognising some short-term benefits for the thin archetype and longer-term benefits of the thick archetype.

Trade Associations

Trade associations cover a wide range of members, with different requirements and concerns. Energy UK emphasised the need for prompt action (initially thin archetype) but recognised benefits of medium and thick, Scottish Renewables expressed a preference for medium, as easier to move towards, but also acknowledged longer term benefits of thick. Community Energy England did not directly express a preference but consider that a more centrally coordinated approach (thick) would provide greater market access for their members.

Power Generators

General preference expressed for thick, due to appreciation of dealing with a more centrally coordinated body.

Flexibility Platforms and Aggregators

Flex platform provider recommendation for an alternative approach, enabling the market to resolve any issues and provide the innovation for development. Expressed some concerns that a thick system may not be fit for purpose in terms of the market requirements moving faster that it can be developed. The aggregator expressed a general preference for medium as seen as evolutionary and easier to implement, but recognised the benefits of thick for the long term net zero agenda.

Elexon

Preference expressed for medium due to the long timescale required to implement thick.

Open Networks

No preference expressed, concerned that Ofgem did not recognise the work already undertaken by the ON programme, and wished for Ofgem to provide a clear supporting message for current and planned activities to be completed, and not delayed due the development of new coordination archetypes.

### Consideration of Ofgem TFDF Consultation Responses for WP3

The responses from the Ofgem TFDF consultation highlight the different views and needs of a broad range of stakeholders. Many of the responses noted the longer-term benefits of the Thick Archetype, which is most aligned with Scheme 2, however there were many concerns raised regarding the time and complexity to implement the Thick Archetype as well as the potential for stranded flexibility supplier assets and coordination platform architecture and IT systems.

The timescale of consideration for the TFDF consultation is more aligned with the here and now and near-term considerations of the stakeholders, whereas this study is largely focussed on the long-term benefits and the preferred scheme when the UK’s energy systems are predominantly decarbonised.

The key considerations of the Ofgem TFDF feedback for this project are:

- That a centrally coordinated approach (Scheme 2 / Thick Archetype) must build on existing best practice and will benefit from transitioning from an approach with improved coordination from existing BAU and will be difficult to move to in the immediate term.

- Acknowledgement of the long-term benefits of a centrally coordinated approach, whilst recognising the need to maintain market innovation and should work with industry facilitators rather than replacing their functionality.

- Clear road mapping of scheme development is critical to ensure that the market continues to develop and to substantially reduce the risk of stranded assets related to delivery or management of flexibility assets.

# Quantitative Assessment of Implementation Costs

The Schemes selected in WS1 have been analysed in the IWES model in WS2. quantitative assessment conducted in WS3 combines the latest IWES flexibility and whole system modelling analysis with platform implementation costs to provide an assessment of overall scheme costs and how these vary under different scenarios, use cases and timelines and compare across the two schemes.

Following an outline assessment of available implementation cost data and subsequent review with the ESO and NGED it was agreed that a full refresh of historic implementation costs, which were prepared within the previous ENA Future Worlds programme by Baringa, was not necessary or feasible within the scope and timeline for this project. Instead, a review of the previous ENA Future World costs has been undertaken, and an assessment of the validity of historic cost data and assumptions has been provided by NGED.

The analysis results from IWES WS3 results and the previous WS2 analysis are combined with the Scheme Implementation analysis to generate insight into a comparison of the two schemes and to identify when the projected flexibility volumes become the dominating factor in driving whole system costs, and therefore help to inform a timeline for critical aspects of the system conversion to improved more efficient coordination platforms.

## ENA Future World Implementation Cost Review

An approach to assessing the implementation costs for alternative ESO-DSO coordination platforms was developed within the ENA Future World programme, in 2018/2019.

Five Future Worlds were proposed within the programme, these were reviewed in WS1 and two worlds were selected to provide an approach starting point for the proposed Scheme 1 and Scheme 2 of this study. The Future World B represents the most aligned characteristics with Scheme 1 and similarly World E is most aligned with Scheme 2. In conjunction with a review of the overall approach taken in the ENA Future Worlds assessment, the review of the prepared Implementation cost details will only consider Worlds B and E.  The ENA Future World costs are split by the system actors: ESO, DSO and for World E a newly formed Flexibility Coordinator (FC).

The ENA’s Future World Implementation Cost analysis includes copies of the spreadsheets developed by Baringa. The spreadsheets detail the cost build up for the alternative Future ESO-DSO Flexibility Services Worlds. The costs are broken down into Capital Expenditure (Capex) and Operational Expenditure (Opex) and consider annualised costs from 2018 to 2050. The timeline for all of the proposed worlds is split into two stages, both of which are deemed to start, for stage 1, in 2018/19, with all associated cost calculations running from this start year. The duration of these stages differs from World B to World E, and are shown below:

Table 3-1 - End date for ENA Future World Stages

| End date for stages | World B | World E |
| --- | --- | --- |
| Stage 1 | 2028 | 2036 |
| Stage 2 | 2050 | 2050 |

The large time discrepancy between the two Worlds is notable, the key reason being the longer duration required to set up the more extensively coordinated World E infrastructure and regulatory bodies.

The Following System Functions are assessed:

- System Coordination

- Network Operation

- Investment Planning

- Connections * Connection Rights

- System Defence and Restoration

- Services/Market Facilitation

- Service Optimisation

- Charging

System function descriptions are shown in the Appendix C. For further details refer to Commander work package one and the ENA website.

Annualised costs are calculated based on spreading the operational costs across the duration of each stage. A summary comparison of the projected ENA Future Worlds implementation costs, by actor and stage, are shown in Figure 3-1 and Figure 3-2 below

Figure 3-1 - ENA Future Worlds Published projected ESO, DSO and FC costs (£m) by Stage and Totals

The ENA Baringa Future Worlds cost forecasts projects a lower total implementation cost for World E (Most Closely Aligned with Scheme 2), with a saving in the order of £130m over the 30 year period. It is notable that the World B (most Closely Aligned with Scheme 1) projects substantial additional implementation costs for the DSOs in both stages.

Figure 3-2 - ENA Future Worlds Published projected ESO, DSO and FC costs (£m) by Stage, Anualised Totals over Stage Durations

The annualised costs, based on the duration of each stage within the ENA’s Future World B and World E scenarios, are shown in Figure 3-2. It is evident that the annualised costs projected for the DSOs under World B are very much higher for the stage 1 of the two coordination scenarios. This is partly due to the longer duration for stage 1 for World E, however, and bearing this in mind, the annualised projected costs for the DSOs is almost three times greater for the DSOs during the 2020-2028 period that stage 1 for World B was set as.

The total averaged annualised costs shown in the table reveal that over the full duration of both stages for both Worlds, the average annualised costs are projected to be a little over 10% greater for World B (at c. £43m/annum) than they are for World E (at c.£38m/annum).

The ENA Future Worlds projected an overall cost saving for World E over World B. To gain greater understanding of where the key projected savings are to be found in World E, which closely aligns with Commander Scheme 2, a review of the differences in expected expenditure, by function, follows.

Figure 3-3 - ENA Future Worlds, Published projected DSO implementation costs (£m) for Worlds B & E, Stage 1 & 2

Service optimisation represents the greatest cost category for the DSOs in World B, Stage 1 and in Stage 2, representing almost 25% of the total projected DSO implementation costs.

Significant cost reductions are observed from World B to World E for all expenditure categories, in particular for system coordination, network operation and service optimisation.

Figure 3-4 - ENA Future Worlds, Published projected ESO implementation costs (£m) for Worlds B & E, Stage 1 & 2

The ENA projected costs for the ESO show the greatest reduction in expenditure from World B to World E are expected to be for system coordination, and lower savings projected across network operations, investment planning, service optimisation and charging. Increased projected costs from World B to World E are seen for connections and service / market facilitation.

Figure 3-5 - ENA Future Worlds, Published projected FC implementation costs (£m) for World E, Stage 1 & 2

The FC only exists within World E. The cost breakdown has been used to show the breakdown across expenditure categories and how this varies from stage 1 to stage 2. The projected FC stage 1 costs are dominated by system coordination, service / marker facilitation and service optimisation. Stage 2 costs show similarly high costs in these categories and additional significant expenditure for connections.

A breakdown of costs by sector shows that a significant component of the projected costs are formed from the required resources to manage either of the two coordination platforms

### Overall Scheme Implementation Costs Summary

As shown in the previous ENA Baringa cost analysis for the Future Worlds projected that World E (Most aligned to Scheme 2) would be an overall lower cost to implement than World B (Most aligned to Scheme 1). The annualised costs for World B (refer to Figure 3-2) show significantly higher expenditure (around 3 times higher) in the projected implementation expenditure for the DNOs in the earlier years (2020-2028) of the programme when compared with World E.

The averaged annualised implementation costs over the full 30 year period are projected to be around 10% lower (at c. £38m/year) for World E than for World B (at c. £43m/year).

## ENA Future World Implementation Cost Comparison for Stage 1 v NGED ED2 Costs Forecasts

NGED have undertaken a review of the projected costs, by overall category, which have been allocated for flexibility related actions and development for RIIO ED2 (2023-2028). The period ends in the same year as the historic ENA Future World B Stage 1 time-line, however the World B timeline began three years earlier. The total costs allocated by NGED for ED2 (c. £102m) are around 10% higher than the costs projected the ENA Future World B (c. £89m) central analysis case. There is considerable variation in the costs attributed to the individual categories of expenditure, although this may be partly due to how the expenditure has been attributed against the cost categories. It is unclear whether the costs provide by NGED have isolated costs associated mainly with coordination or whether they also include general network operations (for example significant costs have been allocated to Network Operation).

Figure 3-6 - ENA Future Worlds projected DSO implementation costs (£m) for World B, Stage 1 (2020-2028) and NGED ED2 Forecast Costs (2023-2028).

# Quantitative Assessment of Schemes 1 and 2

## Overview

This section analyses quantitatively and identifies the system impact differences of three ESO/DSO Coordination Schemes, as defined in WS 2, namely:

- Business-as-Usual (BaU) with the ESO has a central role in procuring and dispatching the flexibility sources for balancing and supporting the operational integrity of the national grid system. In this scheme, the current mechanism will continue with some refinement, and the aggregation of small-scale resources will occur to facilitate access and some control to those small grid service providers.

- Scheme 1 (S1): Enhanced Coordination is motivated to achieve greater operational coordination between the ESO and DSOs than in a single entity-led scheme. It assumes two key optimisation stages:

  - The first stage is for the DSO to use DFR to manage distribution network operation, minimise distribution network reinforcement, aggregate the available DFR resources that ESO can use considering local distribution network constraints and inform that information to the ESO.

  - Based on that information, the ESO will optimise and allocate the DFR services in all DSO regions in coordination with large-scale flexibility resources at transmission in the second stage to support the national transmission system at minimum cost.

- Scheme 2 (S2): Distributed Flexibility Coordinator (DFC) assumes the ESO and DSO have full access to DSR flexibility services, with decisions about access to services determined on an operational basis by a single entity, i.e. DFC. DFC will also provide information on how local and national energy systems should be designed to achieve maximum optimality.

An integrated whole energy systems model (IWES) has been enhanced to quantify the system impacts of different coordination schemes. As a short overview, IWES is a least-cost optimisation model that minimises long-term investment and short-term operating costs across multi-energy systems (electricity, heating, hydrogen) from the supply side and energy network to the end customers while meeting the required carbon targets and system security constraints. IWES also optimises the deployment of flexibility technologies such as energy storage (thermal, electricity, hydrogen), demand response technologies (e.g. smart electric vehicle charging system with and without vehicle-to-grid capability, industrial and commercial sector demand response), interconnection with Europe, electrolysers, and generation flexibility to ensure adequate generation capacity during the peak demand with low renewable outputs.

As the flexibility requirements are system-specific, we analyse two main scenarios of future (2050) energy systems where the heating demand of on-gas grid customers is decarbonised through hydrogen ("H2") as the first scenario and through electrification ("ELEC") using electric heating (a combination of heat pumps and resistive heating) as the second scenario. Details of the energy system backgrounds and assumptions used in the studies can be found in Appendix A in the WS 2 report.

The following sections discuss the key system implication differences between the selected schemes. While some of the analyses were discussed in the WS 2 report, additional analyses have been made to give deeper insights and understanding of the impact of those selected schemes.

The key findings are summarised as follows:

ESO/DSO coordination approach affects the whole energy system development (not only distribution or transmission) and how it should be operated.

The business case to depart from BaU is stronger in the Deep Electrification pathway, where the system requires more distributed flexibility to be deployed than in the Hydrogen pathway. The gross benefits of departing from the BaU to Scheme 1 or 2 are between 0.3–0.4 £bn/year in the Hydrogen pathway and 1.4–2.3 £bn/year in the Deep Electrification pathway. Scheme 2 has the highest savings. The cost of enabling Scheme 1 or 2 is excluded.

Improving ESO/DSO coordination will maximise the value of distributed flexibility technologies, reduce electricity peak demand and distribution network reinforcement costs, and the need for large-scale flexibility sources such as hydrogen storage, which is needed to support sector-coupling flexibility between electricity and hydrogen systems, and the increased ability to export electricity due to more efficient system operation.

Most of the savings are CAPEX-related, which means that the benefits of harnessing flexibility are more tied to avoidable investment costs than operating costs. A suitable market framework should be developed to reflect the value of those flexibility.

The total magnitude of changes in Scheme 2 compared to BaU is less than in Scheme 1. The results suggest that the transition from BaU to Scheme 2 relatively involves fewer system changes than the transition to Scheme 1.

As the distribution system capacity is optimised in Schemes 1 and 2, DSO will operate the system with high loading (80% of peak) for longer hours (up to 10% of a year). Because the distribution capacity in BaU is higher than the other two schemes, the operation hours with high loading are less than 2%.

A large difference between the distribution capacity in BaU and Scheme 1 may indicate substantial potential conflict. The potential conflicts are higher in the Deep Electrification pathway. Scheme 2 provides a trade-off between BaU and Scheme 1.

Load flexibility will be required across all DSO regions driven by electrification. BaU will utilise demand response more than the other schemes but requires a stronger distribution system and generation capacity. Scheme 1 will use less demand response as its application will be more constrained by the local network capacity.

Deep Electrification will require more load flexibility than the Hydrogen pathway.

The spatial allocation of distributed storage is system-specific and less uniform than the demand response. Most storage capacities are located in the North of GB and Wales. Scheme 1 uses more storage than the other two schemes.

In all coordination schemes, the operation pattern is similar, as all distributed or transmission-connected flexibility technologies will be used to maintain the supply-demand balance.

Scheme 1 has the highest total generation capacity and stimulates more solar PV but less wind power development than BaU or Scheme 2.

BaU will drive the highest hydrogen storage requirement. The results imply that the portfolio in BaU (which uses more wind resources) will require more long-term storage to store excess energy during high RES and low demand. There is a correlation between the high electricity storage installed and the less hydrogen storage in Scheme 1. More electricity storage reduces the need for other energy storage technologies.

## Key differences between the selected schemes

### Annual system costs of the ESO/DSO coordination schemes

Figure 4-1 and Figure 4-2 show the detailed and simplified annual system costs of the selected schemes quantified using IWES. The results demonstrate the granularity of the model to capture the system impacts of different schemes across all energy infrastructures and operational costs. Those 32 cost components in Figure 4-1 are then grouped into smaller (12) main categories, as shown in Figure 4-2.

Figure 4-1 - Detailed annual system cost components of three selected ESO/DSO coordination schemes in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

Figure 4-2 - Simplified annual system cost components of three selected ESO/DSO coordination schemes in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

Based on those results, we observe the following:

- The cost performance of the three selected schemes in the Hydrogen pathway is relatively similar, between 83.0–83.4 £bn/year.

- In contrast, the annual system costs in ELEC can be reduced from £89bn/year in BaU to £87.8bn/year using Scheme 1 (Enhanced Coordination) and to £86.8bn/year using Scheme 2 (Distributed Flexibility Coordination).

Hence, it can be concluded that the business case to depart from BaU is stronger in the Deep Electrification pathway, where the system requires more distributed flexibility to be deployed than in the Hydrogen pathway.

### System costs and benefits of departing from the Business-as-Usual approach

Using the BaU's result as the basis for evaluation, the impacts of Scheme 1 and 2 on the annual system cost components can be analysed. The results are shown in  Figure 4-3. The left diagram shows the details of changes in system cost components, while the right diagram shows the aggregated changes based on the 12 main system costs.

Figure 4-3 - Impacts of progressing from BaU to Scheme 1 (EC) and 2 (DFC) on the system costs in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

- Detailed components	                         (b) Main system cost components

The results demonstrate that:

The gross benefits of departing from the BaU to Scheme 1 or 2 are between 0.3–0.4 £bn/year in the Hydrogen pathway and 1.4 £bn/year (Scheme 1) to 2.3 (Scheme 2) £bn/year in the Deep Electrification pathway. The cost of enabling Scheme 1 or 2 is excluded. The benefits of S1 and S2 in H2 are lower than those in deep electrification. Again, this highlights the need for moving to S2, especially in the deep electrification scenario. However, if the future system relies on hydrogen for decarbonising heating, the business case for improving the BaU approach becomes less.

- Departing to Scheme 1 or 2 will require additional system costs for having larger heat pumps to substitute resistive heating, which is less energy efficient and drives a higher electricity peak demand, higher capacity of electricity and thermal storage. The demand for those investments is higher in Scheme 1 than 2, as shown Figure 4-3. In Schemes 1 and 2, the distribution network capacity is lower than in BaU; therefore, additional investment in the above technologies will be needed to limit the increased peak of electricity demand due to electrification.

The main benefits of shifting towards Scheme 1 and 2 are the reduction of distribution network costs due to a lower electricity peak demand, the reduction in hydrogen storage, which is needed to support sector-coupling flexibility between electricity and hydrogen systems, and the increased ability to export electricity due to more efficient system operation.

The total magnitude of changes in Scheme 2 compared to BaU is less than in Scheme 1. The results suggest that the transition from BaU to Scheme 2 relatively involves fewer changes than the transition to S1.

In both schemes, most of the benefits are CAPEX-related. It means the benefits of harnessing flexibility are more tied to avoidable investment costs than operating costs. A suitable market framework should be developed to reflect the value of those flexibility.

The modelling results also demonstrate that moving to Schemes 1 and 2 increases the OPEX of electricity since gas CCS is utilised more to compensate for the reduction in the electricity output from hydrogen-based power generation. Given that the hydrogen production cost is calculated separately in the model, the cost of hydrogen used in the power generation is excluded from the electricity OPEX calculation. Hence, the increased OPEX of electricity should be seen as a whole picture with reduced hydrogen system costs.

### Distribution capacity development under selected schemes

The main difference between Schemes 1 and 2, is that in Scheme 1, DSO has a higher priority to reduce distribution network reinforcement costs due to its 2-stage system optimisation approach. This approach results in the least distribution capacity in Scheme 1 compared to the capacity in the other two schemes, as shown in Figure 4-4. The modelling results also demonstrate that maintaining the Business-as-Usual (BaU) approach will deliver the highest distribution network capacity requirements since ESO will require strong distribution systems, allowing maximum utilisation of distributed flexibility resources for the national system needs. However, the optimal solution lies between those two solutions as the optimal balance between the cost of reinforcing the distribution system is weighted against the value of reinforcing the system to enable more distributed flexibility services to support the broader system. The optimal solution will balance the needs of ESO/DSO and Customers to ensure the security of supply at the lowest cost.

The impact of different schemes on distribution capacity requirements is higher in the Deep Electrification pathway than in the Hydrogen pathway. The results are unsurprising, given that full heat electrification will substantially increase the electricity peak demand by around 35 GW in the BaU scenario compared to the peak in the Hydrogen pathway. Hence, the differences in Scheme 1 and 2 results are also larger. In the Hydrogen pathway, Scheme 1 can save 10 GW distribution capacity compared to the BaU, and Scheme 2 requires 4 GW more than in Scheme 1 but save 6 GW capacity compared to the BaU. In the Deep electrification pathway, Scheme 1 reduces distribution network capacity by 28 GW from the BaU approach. Scheme 2 requires 10 GW more than Scheme 1 but 18 GW less than the BaU approach.

Figure 4-4 - GB's electricity distribution capacity under different schemes

The impact of different coordination schemes on the GB distribution capacity is also observed for the individual distribution network regions, as shown in Figure 4-4The pattern looks consistent, although the magnitudes are different, indicating spatial characteristics of distribution systems and the volume of distributed flexibility resources being deployed. By analysing the results, our analyses suggest the following:

The large difference between the distribution capacity in BaU, Schemes 1 and 2 typically correlates with the volume of flexibility resources in those areas.

However, the large difference may also indicate a high level of possible conflict between the ESO and DSO approaches in utilising the distributed flexibility resources. For example, in the Scotland network, using the substantial distributed storage capacity proposed by the model (discussed in the next section) can have a different impact on the transmission and distribution system. When wind in Scotland blows strongly, the storage can be charged to absorb wind, but it will increase local distribution network capacity requirement. However, if the DSO in Scotland discharges the storage to reduce peak demand and network reinforcement requirement during that time, this action can reduce the system's ability to absorb wind and increase congestion flows between Scotland and England.

The capacity difference between BaU and Scheme 1 is larger than that of Scheme 2; it may indicate that the transition from BaU to Scheme 2 could lead to less conflict than the transition to Scheme 1.

Comparing the results of the Hydrogen and Deep Electrification pathways, the potential conflicts between ESO and DSO will be higher in the second pathway. The results are expected, considering the demand for and value of distributed flexibility are higher when heat demand is fully electrified.

Figure 4-5 - Electricity distribution capacity under different schemes for the 14 distribution network regions

X-axis legends:

| NS: North Scotland | SS: South Scotland | NWE: North West England | NEE: North East England |
| --- | --- | --- | --- |
| NW: North Wales | Y: Yorkshire | SW: South Wales | WM: West Midlands |
| EM : East Midland | SWE: South West England | SE: South England | L: London |
| EE:: East England | SEE: South East England |  |  |

The implementation of different coordination schemes will also affect the electricity load profiles. Figure 4-6 shows the load duration curves of the three schemes evaluated using the Deep Electrification pathway. The loads exclude electricity storage discharge or local distributed generation output.

Figure 4-6 - Load duration curves of the three coordination schemes in the Deep Electrification pathway

The modelling results show:

BaU has the highest electricity peak load (130 GW) compared to the other two schemes (S1: 118GW and S2: 115 GW). Scheme 1 and 2's peak loads are relatively similar. In all schemes, the impact of the peak load on the network capacity requirement will be reduced by using distributed generation such as PV or distributed storage.

The minimum demand is the same in all schemes and is not critical for security.

In BaU, peak load duration is relatively short, with only 12 hours of load above 90% of the maximum load or 130 hours above 80%. However, in Schemes 1 and 2, the duration of high loading is substantially longer. Scheme 1 has the longest duration (872 hours) with loads above 80% max, implying that the DSO must operate with high loading around 10% time in a year.

Normalised load factors in Schemes 1 and 2 are 5%-6% higher than in BaU. The load factor in scheme 2 is similar to scheme 1, only 1% higher. The higher load factor normally indicates better network asset usage.

### Flexibility resources deployed in different schemes

The impact of different coordination schemes on the optimal portfolio of distributed flexibility resources needed by the system was analysed in the WS2 report. The portfolios of distributed flexibility technologies under different schemes are shown in Figure 4-7.

Figure 4-7 - Optimal portfolios of distributed flexibility resources for different coordination schemes in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

The results demonstrate:

Selecting a different scenario will lead to a different portfolio of distributed flexibility requirements.

The total volume of distributed flexibility is relatively similar in the Hydrogen pathway, i.e. around 200 GW comprising 159 GW of heat flexibility. The rest is the electricity flexibility from electricity storage and demand response from electric vehicles, smart appliances and industrial and commercial demand. The first two schemes in Deep Electrification require around 280 GW distributed flexibility capacity. However, scheme 3 requires much less flexibility requirements. It means that the optimal solution does not require the highest distributed flexibility requirements. A similar pattern is also observed in the Hydrogen pathway, although the difference in the total flexibility volume is modest. The hydrogen pathway requires less distributed flexibility since the level of electrification is lower than the other pathway.

The volume of demand response in BaU is the highest compared to the other two pathways.

Scheme 1 always leads to higher electricity storage than scheme 2 but with less demand response capability. While electricity storage has a similar characteristic to demand response, it is more flexible than demand as its availability and operation are not constrained by a demand pattern.

Substantial heat storage requirements prove that heat storage can provide flexibility, especially for electric heating customers. The coordination between heat and electricity flexibility is also important. However, the allocation of thermal storage is the same across different coordination schemes as the volume reaches the maximum level predefined in the analysis.

- Figure 4-8 and Figure 4-9 show the modelling results' regional distribution of demand response capability in GW and the percentage of the regional peak demand. The modelling results demonstrate that:

More than 35% demand response capability will be required in every region across all scenarios. As electrification of transport and heat occurs across GB, the flexibility of electricity demand will be required in all regions to minimise the cost of electrification. The results show the importance of harnessing demand response for facilitating efficient energy system development and operation in GB.

The impact of different coordination schemes on the regional demand response requirements is similar to the pattern observed at the national system level.

BaU requires the highest demand response capacity in most regions, followed by Schemes 2 and 1. The level of demand response requirement is also substantially higher in the Deep Electrification pathway than in the Hydrogen pathway. The modelling results may suggest the potential overuse of demand response in the BaU approach, considering its impact on the local network is not appropriately accounted. On the other hand, Scheme 1 may restrict the use of demand response technologies because of inadequate local network capacity.

Figure 4-8 - Regional-allocation of demand response capability in GW proposed by the model under different schemes in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

Figure 4-9 - Regional-allocation of demand response capability in % of max demand proposed by the model under different schemes in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

- In contrast to the demand response technology, the distribution of electricity storage is not similar. The regional allocation of distributed electricity storage proposed by the model in the studies is shown in Figure 4-10. The results suggest the following:

In the Hydrogen pathway, the requirement for electricity storage is between 4 and 10 GW. The range in the Deep Electrification pathway is 28 GW–50 GW. In both pathways, the storages are mostly distributed in Scotland and North West of England and Wales. We suspect wind power locations mostly drive this allocation as the North has abundant and good wind resources.

Figure 4-10 - Distributed storage capacity under different schemes in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

In several regions, e.g. Scotland, York and South Wales, the distributed storage requirement in Scheme 1 is much higher than in BaU and Scheme 2. This is opposite to its demand response requirement, as discussed previously.

### Utilisation of distributed flexibility resources under different use cases

In the WS 2 report, we identified a set of stressed situations to investigate how the distributed flexibility supports the system to deal with those conditions; these conditions are:

High or low offshore wind energy generation

High heat pump consumption

High demand for transport

High-embedded generation, namely solar PV

- Those conditions are embedded in the hourly system operations being studied using the IWES model. Special attention is given to the condition when the electricity demand is high, driven by high heat pump, resistive heating and EV loads but low RES output for a few days. High heat-led electricity load is driven by high demand for heat during extreme cold weather and when the ambient temperature is low, reducing heat pump efficiency and increasing heat pump's electricity load. These conditions are part of the winter week studied in IWES, shown on days 16-18, illustrated in Figure 4-11. The top diagram shows the power generation output from different technologies and electricity import from the interconnectors while the bottom diagram shows the electricity demand and exports to neighbourhood countries. The graph shows the case without distributed demand flexibility.

Figure 4-11 - A winter week which consists 3-days high electricity demand due to heat pumps and electric vehicles coinciding with very low renewable output Case: no distributed flexibility]

- Even without distributed flexibility, the system can survive, but costs are high since the system needs substantial infrastructure capacity to meet the peak demand. In these three days of extreme events, gas CCS, hydrogen-fire power generation, and electricity import provide system balancing, substantial energy resources and capacity, and nuclear plants, which run flat out.

- The transition from low wind to high wind conditions (from day 18 to 19) will stress the system. In this case, the model uses electrolysers to balance the system and export the excess electricity to Europe. Electrolysers are also being used during the off-peak period on day 17 and 18 to replenish the hydrogen supply that will be used by hydrogen power generation. In that case, it reduces the need for hydrogen storage while maximising the value of electrolyser assets.

- Figure 4-12 illustrates how the electricity load would be modified under different schemes to deal with the extreme events. Diagram A shows the non-modified electricity demand. Diagrams B, C, and D refer to the electricity load in the BaU, Schemes 1 and 2. In (B), the electricity load, particularly from Electric Vehicles (EV) and Smart Appliances (SA), are shifted to off-peak periods. BaU uses resistive heating to meet the heat demand, allowing customers to have a smaller heat pump size but at the expense of a higher system cost.

- In (C), Scheme 1 will encourage the application of heat pumps to reduce the peak demand. EV and SA's loads are still shifted to the off-peak period but less compared to (B). While (D) shows the case between (B) and (C).

(B) BaU

(A) No distributed flexibility

Figure 4-12 - Electricity demand profiles under different coordination schemes (A: No distributed flexibility, B: BaU, C: Scheme 1 (EC), D: Scheme 2 (DFC))

(B) BaU

(C) S1 (EC)

(D) S2 (DFC)

- From the supply side, thermal generation (gas CCS and hydrogen-fired power generation), storage and interconnectors will also provide some flexibility to maintain the supply-demand balance. Figure 4-13 shows the electricity supply for four cases, matched with the demand profile in the previous figure.

(A) No distributed flexibility

(B) BaU

Figure 4-13 - Electricity generation profiles under different coordination schemes (A: No distributed flexibility, B: BaU, C: Scheme 1 (EC), D: Scheme 2 (DFC))

(C) S1 (EC)

(D) S2 (DFC)

- The supply patterns of those three schemes are similar. Gas CCS and nuclear run flat out when the wind output is low; while hydrogen power generation and interconnectors provide balancing actions synchronised with changes in demand profiles due to load shifting.

### Annual Utilisation of flexibility services

The IWES modelling undertakes optimisation at the regional level, and analysis of the use of flexibility assets can provide insight as to how the two schemes may influence the preferred levels of flexibility in an optimised energy system. Figure 4-14 shows the regional variation in flexibility volumes provided by smart appliance (SA) for the different schemes under the deep electrification and hydrogen pathways, split by Rural and Urban areas within the regions. The box plots sow the 25%-75% quartile ranges, where a larger range represents a greater degree of variation across the different regions.

The flexibility ratio represents the variation from the BAU asset profile, divided by the total BAU energy consumption for that asset type.

Figure 4-14 - Regional SA Flex Volume Normalized by total SA Consumption

It can be seen that for Urban SA flexibility, there is a high degree of alignment between the regional flexibility volumes for the deep electrification (Elec) across Scheme 1 and Scheme 2. There is far greater variation for the Rural SA flexibility ratios from Scheme 1 to Scheme 2, with Scheme 1 showing much greater range of SA flexibility usage in rural areas than for Scheme 2. The median value for rural SA flex is quite well aligned across the two schemes.

Figure 4-15 shows the regional variation of flexibility ratios for EVs for the different Schemes and pathways, split by Urban and Rural areas. Scheme 1 shows much greater variation across the regions, for both the Rural and Urban areas, with a substantially higher median in rural areas than for urban areas. For Scheme 2 the spread of EV flexibility ratios is much smaller and is similar for the urban and rural regional areas. The EV flexibility ratio median is also significantly higher for Scheme 2 deep electrification scenario for urban areas than for Scheme 1. This indicates the advantage of the Scheme 2 whole system optimisation, in unlocking additional flexibility from EVs when compared with Scheme 1. For the hydrogen pathway, Scheme 2 also shows notably higher average use of EV flexibility ratios than for Scheme 2, both in Urban and Rural areas.

Figure 4-15 - Regional EV Flex Volume Normalized by total EV Consumption

### Impact of different ESO/DSO coordination schemes on the optimal power generation portfolio

- As reported in the WS 2 report, the system impact of implementing different coordination schemes is beyond distribution network development. It also affects how the optimal power generation should be developed in future. Figure 4-16 shows the optimal power generation portfolios of different cases. The modelling results show:

BaU supports offshore wind development since this technology has lower LCOE than solar PV, as assumed in this study. The LCOE of wind is £35/MWh while PV is £44/MWh;

S1 incentivises the development of more PV and distributed storage to deal with distribution congestion due to increased electrification;

S2 provides a more balanced mix between BaU and S1;

Gas CCS and hydrogen-fired power generation play an important role in meeting peak demand and improving system flexibility and energy resilience against extreme weather events such as Winter-Peak Wind Draught conditions for a few days/weeks. A higher requirement for hydrogen power is observed in BaU than in other Schemes due to higher electricity peak load requirements;

The results also indicate that there must be synergy between the use of flexibility from transmission-connected large-scale resources and distributed flexibility resources.

Figure 4-16 - The optimal power generation portfolio under different schemes in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

- Figure 4-17 shows the spatial distribution of wind power capacity across GB. Major installations are expected in Scotland and East regions of the GB system. As wind will be the main renewable source, wind capacity deployed in most regions will reach regional potential development by 2050, as assumed in this study. It is not affected by the ESO/DSO coordination schemes except in Wales, considering its relative capacity factor.

Figure 4-17 - Spatial distribution of wind power under different schemes in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

Figure 4-18 shows the spatial distribution of solar PV across GB. Most solar PV is expected to be installed in Midlands and South part of GB because of better solar resources.

Figure 4-18 - Spatial distribution of solar power under different schemes in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

The results demonstrate that:

Scheme 1 will facilitate more solar PV development than BaU or Scheme 2.

High solar PV in Scheme 1 correlates with the ability of Scheme 1 to reduce the required distribution network capacity. It demonstrates how distributed generation and flexibility can also be the alternative for network assets.

### Impact on other flexibility technologies

- Different flexibility technologies and power generation portfolios will also affect flexibility requirements in other energy vectors, such as hydrogen. Since hydrogen and electricity systems will be strongly coupled because of the applications of electrolysers and hydrogen power generation, and the coupling between heat and hydrogen system, the modelling results show that different ESO/DSO coordination approaches will also affect the capacity of hydrogen storage required, as shown in Figure 4-19.

Figure 4-19 - Impact of different ESO/DSO schemes on hydrogen storage requirements in the Hydrogen (H2) and Deep Electrification (ELEC) pathways

The modelling results suggest:

BaU will drive the highest hydrogen storage requirement. The results imply that the portfolio in BaU (which uses more wind resources) will require more long-term storage to store excess energy during high RES and low demand.

The hydrogen storage requirements in Scheme 2 lie between the requirement of BaU and Scheme 1.

In the Hydrogen pathway, the need for long-term storage is lessened because of the inclusion of hydrogen demand for heating. While in the Deep Electrification pathway, the need for hydrogen for power generation can be quite seasonal, especially dealing with the long wind draught during winter peak demand.

We observe a correlation between the high electricity storage installed and the less hydrogen storage in Scheme 1. More electricity storage reduces the need for other energy storage technologies.

# Stakeholder Consultation - Workshop

In addition to the qualitative and quantitative assessments undertaken during WP3, a stakeholder consultation was undertaken to share findings from the study, gather key opinions and receive feedback to incorporate into the scheme assessment and subsequent road mapping.

Building on the findings from the WP1 workshop and the subsequent findings of the Commander project, it was clear that a broad spectrum of stakeholders from the operational, regulatory and supplier industry was desirable. It was decided that an in-person workshop would provide the greatest opportunity for the engagement of stakeholders and for the sharing of views on the future of ESO-DSO coordination and the development of coordinated flexibility services and system planning. Online access was also provided to ensure that there was maximum opportunity for attendance.

The workshop was attended by representatives from the Commander project team – WSP and Imperial College London, ESO and the majority of GB DNOs, Ofgem, ENA and Energy UK. Table 5-1 – Summary of stakeholder views captures the key topics raised and discussed by the stakeholders during the workshop.

Table 5-1 – Summary of stakeholder views

| Topic area | Stakeholder views |
| --- | --- |
| Coordination Schemes Selection | Currently, there is minimal conflict risk between the ESO and DNO/DSO(s), but the potential for conflict grows with the increasing presence of DERs and CERs. |
| Schemes enhanced modelling | Importance of considering multiple suppliers and network planning coordinated between ESO and DSO |
| Impact assessment and selection of preferred scheme | Relevance of the timing to realise benefits and gather key elements for selection between schemes |
| Discussion topic 1: Are data and technology facilitators or blockers to the participation of DERs and CERs? | Discussion around enablers and the lack of data governance and one data strategy in the industry. It is important to understand the level of granularity for data, aligned or not with voltage levels. ICL confirmed that the « lack of data » is part of the BAU scenario and its impact has been considered in Commander. It was raised the need for an industry-wide study that identifies a kind of « holistic plan » for enablers. The group highlighted the multifaceted challenges and considerations involved needed for a more sustainable and effective coordination. Requirement of market driven approach and data should be mapped out with one of many activities which will help to look at coordination mechanisms/interfaces. There is a need for increased visibility of the value of flexibility at regional level. There is a need for an industry-wide study that identifies a kind of « holistic plan » for enablers. ICL confirms that the « lack of data » is part of the BAU scenario and its impact has been considered in Commander. There is a significant leap between BAU and either Scheme 1 or 2, namely in terms of data and technology. |
| Discussion topic 2: Transition from BAU to Scheme 1 or Scheme 2: what will be the direction of travel? What may be the obstacles? | Need for clear roles and responsibilities in Scheme 2, as well as the transparency and visibility of DNO/ESO requirements. The primary challenge revolves around data coordination, suggesting the need to take a reverse engineering approach to discern the requirements for Scheme 2 and establish a clear roadmap of steps. It's imperative to pinpoint tipping points, address data accounting, and enhance communication, all while giving due consideration to planning coordination for an effective strategy. In Denmark and in some other European regions, single central data management platforms for the whole industry have been established. |
| Discussion topic 3: Distributed Flexibility Coordinator (DFC) (Scheme 2) format | DFC could play a major role in covering the responsibilities of regional market planners and facilitating market design. The perimeter of a potential DFC needs to be combined (national and regional) to effectively address the evolving energy landscape. A data sharing structure component doesn't necessarily need to be centralized, highlighting the potential within the DFC to facilitate data sharing and management. Need for a flexible and hybrid strategy that can efficiently manage energy resources across different levels while leveraging existing tools and platforms for data management. The data architecture might incorporate a peer-to-peer decentralized system to enhance efficiency and reliability. A market facilitator serves as a means for DNOs and the ESO to access energy markets through established and transparent sets of rules and regulations. There is a risk that the ESO could be considered for too many roles so the level of detail and granularity (data, roles, process etc.) shall be clearly defined. Considerations about planning committees, the role of the FSO, and the need to ensure core areas need to be addressed effectively. DFC could play the flexibility optimiser role, which was included in Commander Scheme 2 modelling). |

# Overall Impact Assessment

This section involves the combination of all results of the qualitative and quantitative assessments, in line with the approach shown in 1.3.

Both schemes are underpinned by a number of factors that are considered as assumptions for the study. For details of comparative strengths and weaknesses of each scheme, refer to Workstream 2 report.

## Impact Assessment Key Findings

The key findings of the impact assessment are presented in the following sections for the combined quantitative and qualitative assessments. These are followed by the recommendations for the preferred scheme. The summary tables utilise a colour indicator to represent concerns/weaknesses and strengths against the listed criteria, the colour key is shown below.

| Lowest Performance / Key Issues Identified | Some Issues Identified | Generally Good Performance, Minimal Issue | Strong Performance, any identified issues expected to be resolved |
| --- | --- | --- | --- |

### Quantitative Assessment

A summary of the quantitative assessment findings is provided in Table 6-2 below.

Table 6-1 - Quantitative Assessment Summary

| Criteria | Scheme 1 | Scheme 2 |
| --- | --- | --- |
| Scheme Projected Implementation Costs (from ENA Future Worlds) | The annual cost (£43m/year) is relatively small compared to the benefits. | The annual cost (£38m/year) is relatively small compared to the benefits. |
| System benefits of departing from BaU to the Schemes | Benefits of 0.3 (H2)–1.4 (ELEC) £bn/year | Benefits of 0.4 (H2)–2.3 (ELEC) £bn/year |
| Distribution capacity development | The scheme leads to a smaller distribution network capacity and may constrain access or hinder further deployment of distributed technology | Sufficient distribution capacity is built to enable optimal access and volume of distributed flexibility resources |
| Flexibility resources deployed | Less volume of flexibility from low-cost demand response and more on higher-cost distributed storage. | Enable optimal mix of different flexibility technologies |
| Annual Utilisation of flexibility services | Highly utilised across all operating snapshots | Highly utilised across all operating snapshots |
| Power generation development | Incentivises more Distributed Generation (DG) to participate in distribution network congestion management. Although, local DG could be more expensive than remote renewable energy sources (e.g. offshore wind) and inhibit development of larger generation capacity. | Enable optimal generation mix and facilitate integration of remote offshore wind farms. |
| Impact on other flexibility technologies | Distributed flexibility will offset the need for transmission-connected flexibility. | Distributed flexibility will offset the need for transmission-connected flexibility. |

### Qualitative Assessment Findings

A summary of the qualitative assessment findings is provided in Table 6-2 below.

Table 6-2 - Qualitative Assessment Summary

| Criteria | Scheme1 Phase1 | Scheme2 Phase1 | Scheme1 Phase2 | Scheme2 Phase2 |
| --- | --- | --- | --- | --- |
| Key Issues Raised with no Mitigating Responses from Any Responders1 | Issues noted with preparatory industry works | Issues noted with preparatory industry works, system design, regulatory changes | Main operational issues expected to be resolved. Some concerns over ability to resolve conflicts and optimise system | Identified issues expected to be resolved |
| Key Benefits Recognised for Implementation Process | Evolutionary approach generally assumed, reducing implementation hurdles | Concerns raised about the depth of change required in a short timescale, digital/ structural/regulatory. Some benefits recognised related to correct long-term alignment of functions | Implementation hurdles expected to be resolved for phase 2 | Implementation hurdles expected to be resolved for phase 2 |
| Key Benefits Recognised for Market Operations | As scheme 1 is more evolutionary from current BAU, it is expected to be able to reap some benefits in phase 1. | Some benefits noted for market operation but coupled with some concerns about how quickly the overall architecture and regulations can be delivered | Key Benefits over BAU recognised for implemented Scheme. Some inabilities to address long term requirements for net zero noted. | Key Benefits over BAU and Scheme1 recognised. In particular for system efficiency, whole system optimisation and stability. |
| Highest Combined Averaged Response Scores | Some responders scored higher overall scores for Scheme 1 | Averaged combined scores were slightly higher for Scheme 2 | One responder scored marginally higher overall scores, all others scored Scheme 1 lower than Scheme 2 | Combined scores for Scheme 2 were notably higher than for Scheme 1, the majority of responders scoring Scheme 2 higher |
| Consistency of Response Scores | Large differences in opinions for scoring different criteria in phase 1 | Fairly large differences in opinions for scoring different criteria in phase 1 | Good alignment for scoring in phase 2 | Very good alignment for scoring in phase 2 |

## Recommendation: preferred Coordination Scheme

The quantitative assessment undertaken with the IWES modelling shows clear long-term benefits for an optimisation approach represented by Scheme 2, with significant annualised whole system cost reductions projected when the scheme is mature. These cost reductions are particularly evident for the deep electrification scenario (electric heat and EV dominated) and less so for the hydrogen heating scenario. There is however a much higher degree of uncertainty regarding the mass deployment of hydrogen for heating, than there is for the large-scale deployment of heat-pumps and advanced resistive heating.

Scheme 1 utilise a two-stage optimisation process which tends to minimise the distribution network reinforcement costs, and this may constrain the use of distributed flexibility to support the national energy system. Whereas Scheme 2 uses a single stage of optimisation leading to a more integrated ESO-DSO system. Therefore, in addition to providing the greatest economic system benefits, Scheme 2 also provides an overall energy network with greater capacity and ability to manage energy flows across the country than Scheme 1, providing increased overall system resilience and flexibility to adapt.

From the previous ENA Future Worlds implementation cost analysis, the total costs for World B (aligned with Scheme 1) are around £1.29B, versus around £1.15B for World E (aligned with Scheme 2), making World E the lower cost platform to implement. When considering the implementation costs on an averaged annual basis, World B (Scheme 1) is around £43m/annum and World E (Scheme 2) is around £38m/annum. When put into the context of the overall system costs and related savings against BAU projected by the IWES whole system modelling, it is evident that the coordination platform costs, and any variation from the selected scheme, are minimal in comparison and only represent in the region of 1% of the total system costs. Therefore, variations in the projections of the ENA Future World costs will have marginal impact on the whole system costs and should not be considered as an influencing factor in the selected coordination Scheme.

The qualitative assessment has shown a strong consensus for a preference for Scheme 2 when it is mature. There are however a range of mixed views and concerns over how quickly Scheme 2 can be implemented and the potential issues related to a sudden transition from current operational and market practices. When also taking into account the wider industry feedback which Ofgem have recently received from their consultation on The Future of Distributed Flexibility, it is considered to be preferable to transition to a Scheme 1 approach to coordination in the near term, whilst ensuring that a clear road map is in place to transition to Scheme 2 within a ten-year timeframe. This should enable the development of the necessary systems, regulation, and market interfaces to be established in an effective and well managed approach for the transition. Clear road mapping will also be vital to enable market investors to develop appropriate solutions without risking the stranding of flexibility assets due to unforeseen market changes.

# Next steps: Work Package 4 - Roadmap for the deployment of the ESO/DSO coordination scheme

Work Package 4 is focused on development of a roadmap for the transition towards the preferred scheme. Some of the progression towards the preferred scheme is expected to be evolutionary, acknowledging and supporting the best aspects of the current market system, whilst identifying opportunities for further improvements and necessary changes.

- Develop a cost-benefit analysis of the feasible solutions identified in WP3 (started in WP3);

- Define the preferred scheme in further detail, including roles and responsibilities and exchanges between system players (including diagrams);

- Identify and define the key activities and initiatives for the deployment of the preferred scheme, time-sequence the activities on the roadmap and seek for stakeholder feedback on the roadmap activities;

- Assess the roadmap in terms of its impact across operational areas of the ESO business and assess the ability of the ESO to manage the implied change via a (high-level) gap analysis;

- Identify the break-even point (investment vs. efficiency savings of preferred scheme);

- Develop a small set of management KPIs to track the delivery of the roadmap.

The quantitative analysis has highlighted the significant benefits of a whole system coordinated approach, which is an inherent feature of Scheme 2, however there is a substantial part of the industry that believes that this will be complex and require a long timescale. In WP3, we have fully acknowledged these concerns and we have addressed these in the conclusion and scheme selection. WP4 will account for these requirements, and where helpful, will take a reverse engineering approach for Scheme 2, determining critical requirements for central system features. These will include data coordination, market access, and regulatory and policy considerations.

IWES is a least-cost optimisation model that can simultaneously minimise long-term investment and short-term operating costs across the whole energy system (electricity, heating, hydrogen) from the supply side, energy network to the end-customers while meeting the required carbon targets and system security constraints. Modelling has been undertaken for the fully net zero compliant energy system, expected to be largely operational by 2045-2050. In WP4, IWES modelling will also be completed for an interim phase towards net zero in 2035. This will help to inform when key transition steps need be completed by, to ensure that there is efficient and effective whole energy system operations, both in terms of flexibility investment, procurement and dispatch, but also in terms of strategic network planning and investment.

## Additional Sensitivity Analysis with IWES

Additional Sensitivity analysis with the IWES model has been identified for WP4. This will help to inform the operational requirements under system stress conditions, which in turn will help to develop the energy system scenarios.

The second step is to define the energy system scenarios used to evaluate the schemes. We plan to use two snapshot years – 2030 or 2035 and 2050. The former is selected to identify the value of the schemes in the short/medium term, especially from an operational point of view, while the latter is used to analyse the impact of the schemes in shaping both investment and operation of the net-zero energy system. We propose to use the net-zero 2050 Leading the Way scenario as an input to the IWES model. Once the scenarios are agreed upon, IWES’ input data will be updated accordingly.

Qualitative Assessment

# Appendix A: Future Worlds Qualitative Impact Assessment Results

Figure A-1 - Summary of world ranking from Future Worlds Impact Assessment

Future of Distributed Flexibility Consultation

Appendix B: The Future of Distributed Flexibility Consultation

This appendix provides additional detail on the Archetypes defined within the Ofgem consultation on The Future of Distributed Flexibility.

Thin Archetype ‘Process Map’

Medium Archetype ‘Process Map’

Thick Archetype ‘Process Map’

ENA Future Worlds Scheme Implementation Cost Review (Baringa, 2018)

Appendix C: ENA Future Worlds Scheme Implementation Cost Review

This appendix details the review of the original ENA-Baringa Future World implementation costs, undertaken by personnel from NGED and the ESO. It was not possible to conduct an extensive evaluation of the implementation costs during this study, however key areas of expenditure have been checked by NGED to establish in the previously estimated implementation costs are within a realistic region when compared with a DNOs anticipated costs for platform development and the necessary enabling actions.

ENA Future Worlds Cost Category Descriptions

WSP House 70 Chancery Lane London WC2A 1AF wsp.com WSP UK Limited makes no warranties or guarantees, actual or implied, in relation to this report, or the ultimate commercial, technical, economic, or financial effect on the project to which it relates, and bears no responsibility or liability related to its use other than as set out in the contract under which it was supplied.

Future World Impact Assessment, 22 February 2019, Baringa LLP

COMMANDER – Workstream 1 Report – Development of Coordination Schemes, March 2023, WSP

Basic schemes for TSO-DSO coordination and ancillary services provision, Dec 2016, https://smartnet-project.eu/wp-content/uploads/2016/12/D1.3_20161202_V1.0.pdf

The Future of Distribution Flexibility, Call for input, Ofgem, March 2023

https://www.ofgem.gov.uk/publications/call-input-future-distributed-flexibility

Call for Input: The Future of Distributed Flexibility | Ofgem

The publicly available data spreadsheet, produced by Baringa for the ENA Future Worlds Report in 2019, show some errors regarding resource cost totals, which may need to be reviewed further and may result in some adjustments to the overall costs.

Even in the Hydrogen pathway, around 40% of customers use electric heating.