## Cover
tRESP Consistent Planning Assumptions (CPAs) Value Workbook
About
The Consistent Planning Assumptions Value Workbook contains default values/ranges for all CPAs and outlines the complete modelling process for deriving demand from electric vehicles and residential heat pumps. It also contains an end-to-end example of applying the electric vehicle and heat pump CPAs.
Version
Version Control

## Contents
Contents: tRESP Consistent Planning Assumptions (CPAs) Value Workbook
Tab Name
Scope | Overview
Tab Name
CPA Lists | EV CPA List
HP CPA List
Tab Name
Process diagrams | EV CPA Process
HP CPA Process
Summary tables and related values/ranges
| Summary Table - Tab Name | CPA Number - Tab Name | CPA
Summary tables and related values/ranges | EV CPA Summary Table | EV01 | Vehicle mileage
|  | EV02 | Distance in EV mode
|  | EV03 | EV efficiency
|  | EV04 | Proportion of charging by charger type
|  | EV05 | Proportion of consumers by behaviour
|  | EV06 | Normalised half-hourly profile
|  | EV07 | Diversity-correction curve
|  | EV08 | Minimum count for full diversification
|  | EV09 | Charge point utilisation
|  | EV10 | Size of chargers
| Domestic HP CPA Summary Table | HP01 | Size of HP
|  | HP02 | Dwelling thermal efficiency factor
|  | HP03 | Efficiency of HP
|  | HP04 | Specific HP heat output
|  | HP05 | Temperature difference
|  | HP06 | Normalised half-hourly profile
|  | HP07 | Proportion of consumers by behaviour
|  | HP08 | Diversity-correction curve
|  | HP09 | Minimum count for full diversification
| Domestic EE CPA Summary Table | EE01 | Residential energy efficiency
Tab Name
CPA Indicative Impact | EV Indicative Impact
HP Indicative Impact
CPA End-to-End Calculation | EV End to End Example
HP End to End Example
| Type | Tab Name
CPA Additional Information | Lists and shorthand mapping used throughout the workbook | Mapping
| CPA IDs | CPA ID info
| tRESP building block for EV and HP | tRESP BB for EV and HP

## Version Control
Version Control
Back to contents
Version | Date | Classification | Changes
1 | 2026-01-30 | Public | Initial Published Version

## Overview
Overview of CPA scope
Back to contents
The modelling process is designed for the assessment of demand during four representative days (peak demand winter day, peak demand summer day, peak demand shoulder season day, overall minimum demand day) within an average weather year, to focus on the assessment of scenarios that drive network planning. There is expected to be little variation in demand between seasons for electric vehicles, so the CPAs provided apply across all representative days. However, heat pump demand is heavily dependent on outside air temperature and so different half-hourly demand profiles and other relevant CPAs are provided for each of the representative days.
For both electric vehicles and heat pumps, CPAs are provided to enable users to account for the impact of diversity, i.e. the reduction in peak demand that is associated with multiple end users, reflecting the fact that not all end users will operate at their maximum capacity simultaneously.
Where the CPAs are provided on an annual basis, the years refer to the period from 1st April to 31st March, in line with the tRESP Pathways definition of years. That is, the baseline year, 2025, refers to the year ending on 31st March 2025.
For electric vehicles, the modelling process is designed to enable consideration of different vehicle types, charger types and behaviours, as well as allowing for regional/national and temporal variation. The scope of vehicle types, charger types and behaviours considered are summarised in Table 1.
| Vehicle types | Charger types | Behaviours (domestic chargers only)
| Electric light vans, cars and motorbikes | Domestic | No flexibility
| Plug in hybrid light vans, cars and motorbikes | Workplace | Static smart charging
| Electric heavy goods vehicles and buses | Public slow/ fast
| Plug in hybrid heavy goods vehicles and buses | Public rapid
HGV depot
Table 1: vehicle types, charger types and charging behaviours considered within the scope of the tRESP CPAs for electric vehicles
For heat pumps, the modelling process is designed to enable consideration of different dwelling categories, representative days in a year and space-heating behaviours, as well as allowing for regional/national and temporal variation. The scope of the variations considered are summarised in Table 2.
| Dwelling categories | Representative days | Space-heating behaviours
| Detached (existing build) | Peak demand winter day | Bimodal
| Semi-detached and end-terraced (existing build) | Peak demand summer day | Daytime
| Mid-terraced (existing build) | Peak demand shoulder season day | Continuous
| Flats (existing build) | Overall minimum demand day
Detached (new build)
Semi-detached and end-terraced (new build)
Mid-terraced (new build)
Flats (new build)
Table 2: dwelling categories, representative days and space-heating behaviours considered within the scope of the tRESP CPAs for residential heat pumps
Whilst the tRESP CPAs focus primarily on electric vehicles and residential heat pumps, a CPA is also provided to drive consistency in the impact of energy efficiency improvements (for lighting and appliances) on residential electricity demand.

## Glossary
Back to contents
Glossary
Term/ Acronym | Definition
BBs | Building Blocks
BRE | Building Research Establishment
COP | Coefficient of Performance
CPA | Consistent Planning Assumptions
DC | Dwelling Category
DESNZ | Department for Energy Security and Net Zero
DfT | Department for Transport
DNO | Any Electricity Distributor in whose electricity distribution licence the requirements of Section B of the standard conditions of that licence have effect (whether in whole or in part).
EE | Energy Efficiency
ESC | Energy Systems Catapult
EVs | Electric vehicles – vehicles wholly driven by an electric motor that is wholly powered through a battery and does not produce any tailpipe emissions
FES | Future Energy Scenarios
GB | Great Britain
HGV | Heavy Goods Vehicles
HPs | Heat pumps
kW | Kilowatt (unit of power)
kWh | Kilowatt hour (unit of energy)
LCT | Low Carbon Technology: LCTs is the collective term for the following technologies: • Heat pumps at existing connections that do not lead to a new or modified connection • Electric vehicle (EV) chargers, both slow and fast charging, at existing connections that do not lead to a new or modified connection • Photovoltaics (PV) connected under Engineering Recommendation G98 • Other renewable Distributed Generation (DG), excluding PV, connected under Engineering Recommendation G98 • Renewable DG not connected under Engineering Recommendation G98
PHEV | Plug-in hybrid electric vehicle
SPF | Seasonal Performance Factor
tRESP | Transitional Regional Energy Strategic Plan

## CPA ID info
The CPAs have unique name IDs depending on technology, scope, representative day, behaviour category, spatial granularity
Back to contents
| CPA technology ID | CPA Number | Technology detail | Representative days | Behaviours | Spatial granularity | Examples
| Identifier for the technology category the CPA applies to: EV=electric vehicle, HP=heat pump, EE=energy efficiency | Identifier for the assumption, numbers restart for each technology category | Identifier for the specific sub-technology (can be one or multiple, separated by a hyphen/technologies or archetype/s the assumption applies to (can be one or multiple, separated by a hyphen). For EVs, these correspond to Building Blocks (BB) or charger types, for HPs, these correspond to the Dwelling Categories (DC). | The representative day for which the assumption applies: WP=winter peak, SP=summer peak, SSP=shoulder season peak, MIN=overall minimum, ALL=applicable to all representative days, NA=not applicable | The consumer behaviour for which the assumption applies. These behaviours can be different for each technology and are indicated by a number or shorthand. BHV1= behaviour type 1 (e.g. bimodal heat pump operation), BHV2= behaviour type 2 (e.g. daytime demand heat pump operation), ALL=applicable to all behaviours, NA=not applicable etc. | The spatial region the assumption applies to: GB=same value/s for all of GB, NorthEast=assumption applies to North East (note: government regions), MersNWales = assumptions applies to the Merseyside and North Wales DNO licence area. | CPA ID | Description
| EV | 01 | BB1 | NA | NA | GB | EV01_BB1-BB2_NA_NA_East | EV assumption 1, applies to building blocks 1 and 2, does not apply to specific representative days or flexibility behaviours, specific assumption for East of England.
| HP | 02 | BB2 | ALL | ALL | NorthEast | EV05_BB10_ALL_FLX2_GB | EV assumption 1, applies to building block 10, applicable for all representative days, flexibility behaviour type 2, applicable to all of GB.
| EE | 03 | BB1-BB2 | WP | BHV1 | NorthWest | HP01_DC1_NA_ALL_GB | HP assumption 1, applies to dwelling category 1, does not apply to specific representative days, applicable to all flexibility behaviours, applicable to all of GB.
|  | 04 | etc. (related to BBs/DCs where applicable) | SP | BHV2 | East | HP05_NA_WP_NA_NorthEast | HP assumption 5, does not apply to specific dwelling categories, applies to winter peak demand day, does not apply for specific flexibility behaviours, specific assumption for the North East.
|  | 05 | DC1 | SSP | BHV3 | etc.
|  | etc. | DC2 | MIN | etc.
ALL
NA

## Mapping
Lists and shorthand mapping used throughout the workbook
Back to contents
| CPA Number | EV CPA | EV BBs | BB shorthand | EV charger type | EV charger type shorthand | EV flexibility behaviours | Flex shorthand | CPA Number | HP CPA | HP BBs | BB shorthand | Dwelling categories | Dwelling categories shorthand | HP behaviours | Behaviour shorthand | CPA number | EE CPA | Representative days | Representative days shorthand | Spatial granularity | Temporal granularity | New build status | New build status shorthand | Government regions | Region shorthand | DNO licence areas | DNO licence areas shorthand | RAG list | Year list | Switch
| EV01 | Vehicle mileage | Lct_BB001 | BB1 | Domestic | domestic | No flexibility | NoFlex | HP01 | Size of heat pump | Lct_BB005 | BB5 | Detached | DC1 | Bimodal (reference only) | BHV1 | EE01 | Residential energy efficiency | Peak demand winter day | WP | GB | None | Existing build | EXIST | Scotland | Scotland | East Midlands | EastMids | 1 | 2024 | ON
| EV02 | Distance in EV mode | Lct_BB002 | BB2 | Workplace | workplace | Flexibility (static TouT) | Smart | HP02 | Dwelling thermal efficiency factor | Lct_BB006 | BB6 | Semi-detached and end-terraced | DC2 | Daytime (reference only) | BHV2 |  |  | Peak demand summer day | SP | Region | Annual | New build | NEW | Wales | Wales | Eastern | East | 2 | 2025 | OFF
| EV03 | EV efficiency | Lct_BB003 | BB3 | Slow/fast public | slowfast | Applicable across all | ALL | HP03 | Efficiency of heat pump (COP/SPF) | N/A | NA | Mid-terraced | DC3 | Continuous (reference only) | BHV3 |  |  | Peak demand shoulder season day | SSP |  | Half-hourly |  |  | East | East | London | London | 3 | 2026
| EV04 | Proportion of charging by charger type | Lct_BB004 | BB4 | Rapid public | rapid | N/A | NA | HP04 | Specific heat pump heat output |  |  | Flats | DC4 | Applicable across all | ALL |  |  | Overall minimum demand day | MIN |  | Half-hourly, annual |  |  | East Midlands | EastMids | Merseyside and North Wales | MersNWales | NA | 2027
| EV05 | Proportion of consumers by flexibility behaviour | N/A | NA | HGV depot | depot |  |  | HP05 | Temperature difference |  |  | Applicable across all | ALL | Weighted average | WA |  |  | Applicable across all | ALL |  |  |  |  | London | London | Midlands | Wmids |  | 2028
| EV06 | Normalised half-hourly profile | Applicable across all | ALL | N/A | N/A |  |  | HP06 | Normalised half-hourly profiles |  |  | N/A | NA | N/A | NA |  |  | N/A | NA |  |  |  |  | North East | NorthEast | North Scotland | NorthScot |  | 2029
| EV07 | Diversity-correction curve |  |  | Applicable across all | ALL |  |  | HP07 | Proportion of consumers with each behaviour pattern | [14 empty] | Yorkshire and The Humber | YorksHumber | North Western | NorthWest |  | 2030
| EV08 | Minimum count for full diversification | [6 empty] | HP08 | Diversity-correction curve | [14 empty] | North West | NorthWest | Northern | North |  | 2031
| EV09 | Charge point utilisation | [6 empty] | HP09 | Minimum count for full diversification | [14 empty] | South West | SouthWest | South Eastern | SouthEast |  | 2032
| EV10 | Size of chargers | [22 empty] | West Midlands | WestMids | South Scotland | SouthScot |  | 2033
[25 empty] | South East | SouthEast | South Wales | SouthWales |  | 2034
[27 empty] | South Western | SouthWest |  | 2035
[27 empty] | Southern | South |  | 2036
[27 empty] | Yorkshire | Yorkshire |  | 2037
2038
2039
2040
2041
2042
2043
2044
2045
2046
2047
2048
2049
2050

## tRESP BB for EV and HP
Back to contents
tRESP Building blocks for Electric Vehicles and Heat Pumps
Technology | FES BB ID Number | Technology detail
Electric Vehicles | Lct_BB001 | Pure Electric (vans, cars and motorbikes)
Electric Vehicles | Lct_BB002 | Plug-in-hybrid (vans, cars and motorbikes)
Electric Vehicles | Lct_BB003 | Pure Electric (buses, coaches and HGV)
Electric Vehicles | Lct_BB004 | Plug-in-hybrid (buses, coaches and HGVs)
Heat Pumps | Lct_BB005 | Domestic - Non-hybrid
Heat Pumps | Lct_BB006 | Domestic – Hybrid

## EV CPA Process
EV CPA Process
Back to contents
Back to EV CPA Summary Table

## EV CPA Summary Table
EV CPA Summary Table
Back to contents
CPA Number | CPA | Description | Scope | Unit | Data source/s | Link/s | Data processing comment | Default values comment | Overall RAG rating | Based on reliable source | RAG | Be relevant | RAG | Be up to date | RAG | Be location specific | RAG | Considers changes through time | RAG | Weather and climate impact | RAG
EV01 | Vehicle mileage | The number of kilometres travelled in one year per vehicle. | Defined for Lct_BB001 and Lct_BB002, Lct_BB003 and Lct_BB004 | km/year | a) DfT TRA0206 table | https://www.gov.uk/government/statistical-data-sets/road-traffic-statistics-tra#traffic-volume-in-kilometres-tra02 | Number of kilometres travelled from TAR0206 and TRA8905 tables divided by number of vehicles from VEH0105 tables to get mileage. Table TRA8905 provides vehicle kilometres for three selected vehicle types at local authority resolution, Cars and Taxis, Light Commercial Vehicles, and Heavy Goods Vehicles. Table TRA0206 provides vehicle kilometres for two additional vehicle types, Motorcycles, and Buses and Coaches by nation and region in GB, i.e. Scotland, Wales and the nine English Government regions. Where local authority data is available, this was used to derive values for the total vehicle kilometres at licence area resolution. For Motorcycles, and Buses and Coaches, the licence area values are a weighted average of the government region data for the regions overlapping each licence area, weighted by vehicle registrations from VEH0105 rather than geographic area. Default values are average over two historic years (2023-2024). | Default values are values for the licence area each network asset sits within. Additional detail can be added by using different vehicle type categories (e.g. defining mileage for cars and light commercial vehicles separately) and/or by defining values at higher geospatial resolution. | 3 | Government published data | 3 | DfT tables log milage and total vehicle stock for Lct_BB001-2 (cars and taxis, light commercial vehicles, motorcycles), and Lct_BB002-3 (heavy goods vehicles, buses and coaches). | 3 | Road traffic data updated annually, vehicle stock data updated quarterly. | 3 | Datasets are GB-specific and are available for Scotland, Wales and the UK Government-defined English regions, with some data available by local authority | 3 | Not considered. | 2 | Not considered. | 2
[5 empty] | b) DfT TRA8905 table | https://www.gov.uk/government/statistical-data-sets/road-traffic-statistics-tra#traffic-volume-in-kilometres-tra89
[5 empty] | c) DfT and DVLA VEH0105 table | https://www.gov.uk/government/statistical-data-sets/vehicle-licensing-statistics-data-tables
EV02 | Distance in EV mode | The proportion of vehicle kilometres travelled that use the electric component of plug-in vehicles (for full battery electric vehicles, this is 100%). | Defined for Lct_BB002, Lct_BB004 | % of mileage | a) Department for Transport, Zero Emission Vehicle Mandate and CO2 Regulations - Vehicle Emissions Trading Scheme Updates: Cost Benefit Analysis, November 2025 | https://www.legislation.gov.uk/uksi/2025/1101/pdfs/uksiod_20251101_en_001.pdf | Lct_BB002 values are derived from DfT analysis underlying amendments to the VETS order (data source a). This is based on analysis conducted by the ICCT (data source b) and internal DfT statistics on vehicle registrations, combined with European data on PHEV electric ranges (data source c). | Default values provided for all trip speeds but the report highlighted that there is a case for making this a variable for trip speeds. | 2 | Based on Department of Transport (DfT) analysis. | 3 | Based on real-world usage study of plug-in-hybrid cars and modelled values for other vehicle types. | 2 | Analysis from 2025 based on data from 2022 and more recent | 3 | UK DfT analysis based on data from both UK and Europe | 2 | Not considered | 2 | Not considered. | 2
[5 empty] | b) ICCT White Paper, Real-World Usage of Plug-in Hybrid Vehicles in Europe: A 2022 Update on Fuel Consumption, Electric Driving, and CO2 Emissions, June 2022 | https://theicct.org/wp-content/uploads/2022/06/real-world-phev-use-jun22-1.pdf
[5 empty] | c) European Environment Agency Datahub, CO2 emissions from new passenger cars, Updated June 2025 | https://co2cars.apps.eea.europa.eu
[5 empty] | d) Ricardo for Department for Transport, Speed-Emission/Energy Consumption Curves for Ultra-Low Emission Vehicles and Non-Fuel Operating Costs for All Vehicles, July 2023 | https://assets.publishing.service.gov.uk/media/6899f224e7be62b4f0643229/speed-emission-energy-consumption-curves-operating-costs.pdf | Lct_BB004 values are weighted average for HGVs, buses, and coaches from Section 2.2.5. Note that these are modelled values as PHEV HGVs, buses, and coaches are not in widespread use in the UK and therefore no trial data available.
EV03 | EV efficiency | The amount of electrical energy an EV consumes to travel one kilometre, with lower values indicating higher efficiency. | Defined for Lct_BB001, Lct_BB002, Lct_BB003 and Lct_BB004 | kWh/km | a) DfT TAG (Transport Analysis Guidance) data book. Table A 1.3.11 | https://www.gov.uk/government/publications/tag-data-book | Lct_BB001 values are weighted average Car and LGV values, from Table A 1.3.11, using weighting factors from FES25 HT. Lct_BB002 values are weighted average Car and LGV values, from DfT supporting information, using weighting factors from FES25 HT Lct_BB003 and Lct_BB004 values are PSV values from Table A 1.3.11. | Additional detail can be added by using different vehicle type categories (e.g. defining efficiency for cars and light commercial vehicles separately). | 3 | Government published data | 3 | TAG data book contains vehicle efficiencies for Lct_BB001/2(cars, light goods vehicles) and public service vehicles. | 3 | Latest version TAG May 25 v2.01 | 3 | Based on GB-specific data | 3 | Data covers years 2010-2089 to account for improvements in vehicle efficiency over time. | 3 | Not considered. | 1
[5 empty] | b) Supporting information for PHEV car and LGV efficiencies, provided to NESO by DfT | N/A
EV04 | Proportion of charging by charger type | The distribution of charging demand to different charger types, defined for each vehicle type. Represented as the proportion of required charging energy (kWh) from each charger type. | Defined for Lct_BB001, Lct_BB002, Lct_BB003, Lct_BB004 as proportion of charging met by domestic, workplace, public slow/fast, public rapid, and HGV depot charging. | % | a) Element Energy for National Grid ESO, Electric Vehicle Charging Behaviour Study, March 2019. | https://www.erm.com/contentassets/553cd40a6def42b196e32e4d70e149a1/ev-charging-behaviour-study.pdf | Table 6-4 from a) used for Lct_BB001 and Lct_BB002 values. Allowable ranges found by assessing the charging distribution at GSP level, using assumptions from Table 5 from c) with Table TS061 from d) to reflect commuter status, and Table TS044 from d) to estimate home charging. Lct_BB003 values from b) assuming no public charging for Lct_BB004. | Default values are provided for the GB-average, additional regionality can be added on a sub-GSP scale. | 2 | Detailed study based on real world data. | 2 | Discusses charging distribution for BEV and PHEV cars into residential, work, slow/fast public charging, and rapid public charging. | 2 | Analysis/reporting in 2019 based on charging data from 2017 and 2018. | 1 | GB-specific study. | 3 | Not considered. | 2 | Not considered. | 2
[5 empty] | b) Element Energy for Transport and Environment, Why Great Britain's long-distance, heavy-duty HGVs can go battery electric - and what needs to be done to achieve this, April 2023 | https://www.erm.com/contentassets/553cd40a6def42b196e32e4d70e149a1/phase-two-report-use-cases-that-do-need-public-charging.pdf
[5 empty] | c) ICCT White Paper, Quantifying the electric vehicle charging infrastructure gap in the United Kingdom, August 2020 | https://theicct.org/wp-content/uploads/2021/06/UK-charging-gap-082020.pdf
[5 empty] | d) Office for National Statistics, 2021 Census of Population | https://www.nomisweb.co.uk/sources/census_2021
EV05 | Proportion of consumers by behaviour | The proportion of domestic charging events that use the flexed charging profile. | Defined as annual % | % | FES 2025, NESO data for Table ED5 (received internally from NESO data team) | https://www.neso.energy/publications/future-energy-scenarios-fes/fes-documents | Values for Holistic Transition used. | Default values are provided for the GB-average. | 3 | Based on NESO FES data, compiled over multiple years with input from stakeholders | 2 | Relates to residentially charging cars, vans and motorbikes. | 3 | Latest version July 2025 | 3 | GB-specific assumption. | 2 | Data covers years 2024-2050. | 3 | Not considered. | 2
EV06 | Normalised half-hourly profile | The half-hourly diversified demand contribution for each charging type, normalised against the annual consumption for that charger type. | Defined for domestic (normal, flexed), workplace, public slow/fast, public rapid, and HGV depot charging. | kW/annual kWh | a) NESO data. From Element Energy for National Grid ESO, Electric Vehicle Charging Behaviour Study, March 2019 (received dataset internally from NESO data team) | https://www.erm.com/contentassets/553cd40a6def42b196e32e4d70e149a1/ev-charging-behaviour-study.pdf | Non-flexible profiles are based on Element Energy processing of NESO data and averaged across the year. See further details in linked study. Flexible profiles are based on results from UKPN Shift,ToU DUoS trial. | Default profiles are provided as applicable to all representative days. | 2 | Detailed study based on real world data. | 2 | Considers charging of BEV and PHEV cars at residential, work slow/fast public and rapid public charging. | 3 | Analysis/reporting in 2019 based on charging data from 2017 and 2018. | 2 | Based on GB-specific study. | 3 | Change through time captured for domestic charging through EV05 and smart charging profile. Changes through time not considered for other charging types. | 2 | Not considered. | 1
[5 empty] | b) UK Power Networks: Shift Innovation Project, 2021. Results from ToU DUoS trial. | https://innovation.ukpowernetworks.co.uk/projects/shift
EV07 | Diversity-correction curve | The ‘un-diversification’ scaling factor to be applied to the fully diversified profile based on the number of electric vehicles on a network asset. | Defined for domestic, workplace, public slow/fast, public rapid, and HGV depot charging. | N/A (scaling factor) | a) Electric Nation trial data (Crowd Charge Transactions and GreenFlux Transactions), National Grid, 2019. | https://connecteddata.nationalgrid.co.uk/dataset/electric-nation | Diversity-correction curve calculated by first creating simulated profiles for individual charging events by charger type. This is done using normalised, diversified profiles from EV06 as the probability distribution for the charging session mid-point, and data from the Electric Nation trial transaction data for charging durations and frequency. For each N (number of EVs in sample), randomly draw subsets of profiles from the simulated profiles and find the ratio between the peak load for the aggregated subset (normalised by N) and the diversified peak. For each N, the random draw was repeated 10000 times and the mean of the top 10% of the ratios (to provide a smooth approximation for the 95th percentile) for each N was set as the diversity-correction factor. | Default values provided for each charger type. | 2 | Based on real-word trial data | 3 | Relates to all different charging types modelled, domestic, workplace, slow/fast public, rapid public, and HGV depot. | 2 | Charging data from 2017 and 2018. | 1 | Based on GB-specific study. | 3 | Change through time captured by relating the diversity correction to the number of electric vehicles at the asset - higher EV adoption leads to higher diversity of demand. | 2 | Not considered. | 2
[5 empty] | b) NESO data. From Element Energy for National Grid ESO, Electric Vehicle Charging Behaviour Study, March 2019 (received dataset internally from NESO data team) | https://www.erm.com/contentassets/553cd40a6def42b196e32e4d70e149a1/ev-charging-behaviour-study.pdf
EV08 | Minimum count for full diversification | The minimum number of electric vehicles at which the profile should be considered fully diversified. | Defined for domestic, workplace, public slow/fast, public rapid, and HGV depot charging. | # of vehicles | Electric Nation trial data (Crowd Charge Transactions and GreenFlux Transactions), National Grid, 2019. | https://connecteddata.nationalgrid.co.uk/dataset/electric-nation | The minimum count for full diversification is the lowest N (number of EVs) that gives a diversity correction of <1.2. | Default values provided for each charger type. | 2 | Based on real-word trial data | 3 | Relates to all different charging types modelled, domestic, workplace, slow/fast public, rapid public, and HGV depot. | 1 | Charging data from 2017 and 2018. | 1 | Based on GB-specific study. | 3 | Change through time captured by relating the diversity correction to the number of electric vehicles at the asset - higher EV adoption leads to higher diversity of demand. | 2 | Not considered. | 2
EV09 | Charge point utilisation | The total time a charging station is actively used to charge electric vehicles, measured in hours per year. | Defined for domestic, workplace, public slow/fast, public rapid, and HGV depot charging. | hours/year | a) Green Finance Institute (based on Zapmap data), | https://www.greenfinanceinstitute.com/wp-content/uploads/2024/09/Demystifying-Utilisation-2024-Update.pdf | Public charge point utilisation from Green Finance Institute report (based on Zapmap data), Domestic and Workplace utilisation based on NESO modelling. Domestic: using tRESP CPAs to find the annual energy demand of vehicles, charging at domestic charge points, assuming one charger per vehicle and capacity of 7kW. | Default values are averages, additional information can be added to the analysis by utilising location-specific data, where available. | 2 | Zapmap tracks public charge point installations in the UK | 2 | Zapmap data only available for public charge points, domestic and workplace utilisation modelled. | 2 | Updated Q1 2024 | 3 | UK specific data | 1 | Not considered | 1 | Not considered. | 2
b) NESO modelling, using tRESP CPAs
EV10 | Size of chargers | The average rated capacity of each charger type or the maximum amount of electrical power that a charger can deliver to an electric vehicle at any given moment. | Defined domestic, workplace, public slow/fast, public rapid, and HGV depot charging. | kW | a) DfT EV public charging infrastructure statistics (July 2025) | https://www.gov.uk/government/collections/electric-vehicle-charging-infrastructure-statistics | Domestic and workplace capacity from British gas article (aligned to industry standard), public charge points from DfT EV public charging infrastructure statistics (Chart 3). HGV depot capacity from ES Catapult report. | Default values and ranges provided. | 2 | Partially based on Government published data | 1 | Data for charge point size in UK but does not relate directly to the categorisation considered here. | 1 | Statistic from 2024. | 3 | UK specific data | 2 | Not considered | 2 | Not considered. | 2
[5 empty] | b) British Gas article | https://www.britishgas.co.uk/electrical/guides/ev-charger-types.html
[5 empty] | c) Energy Systems Catapult, Electric Heavy Goods Vehicles? Industry perspectives on the prospect for their adoption in the UK, 2024 | https://es.catapult.org.uk/report/electric-heavy-goods-vehicles-industry-perspectives-on-the-prospects-for-their-adoption-in-the-uk/

## EV CPA List
Back to contents
Back to EV CPA Summary Table
CPA ID | CPA number | CPA | Unit | BB1 | BB2 (if applicable) | Charger type | Representative day | Flexibility behaviour | Level of spatial granularity | Temporal granularity
EV01_BB1-BB2_NA_NA_Region | EV01 | Vehicle mileage | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | Region | None
EV01_BB3-BB4_NA_NA_Region | EV01 | Vehicle mileage | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | Region | None
EV02_BB2_NA_NA_GB | EV02 | Distance in EV mode | % | Lct_BB002 | N/A | N/A | N/A | N/A | GB | None
EV02_BB4_NA_NA_GB | EV02 | Distance in EV mode | % | Lct_BB004 | N/A | N/A | N/A | N/A | GB | None
EV03_BB1_NA_NA_GB | EV03 | EV efficiency | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | Annual
EV03_BB2_NA_NA_GB | EV03 | EV efficiency | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | Annual
EV03_BB3-BB4_NA_NA_GB | EV03 | EV efficiency | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | Annual
EV04_BB1-domestic_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB001 | N/A | Domestic | N/A | N/A | GB | None
EV04_BB1-workplace_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB001 | N/A | Workplace | N/A | N/A | GB | None
EV04_BB1-slowfast_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB001 | N/A | Slow/fast public | N/A | N/A | GB | None
EV04_BB1-rapid_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB001 | N/A | Rapid public | N/A | N/A | GB | None
EV04_BB1-depot_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB001 | N/A | HGV depot | N/A | N/A | GB | None
EV04_BB2-domestic_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB002 | N/A | Domestic | N/A | N/A | GB | None
EV04_BB2-workplace_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB002 | N/A | Workplace | N/A | N/A | GB | None
EV04_BB2-slowfast_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB002 | N/A | Slow/fast public | N/A | N/A | GB | None
EV04_BB2-rapid_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB002 | N/A | Rapid public | N/A | N/A | GB | None
EV04_BB2-depot_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB002 | N/A | HGV depot | N/A | N/A | GB | None
EV04_BB3-domestic_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB003 | N/A | Domestic | N/A | N/A | GB | None
EV04_BB3-workplace_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB003 | N/A | Workplace | N/A | N/A | GB | None
EV04_BB3-slowfast_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB003 | N/A | Slow/fast public | N/A | N/A | GB | None
EV04_BB3-rapid_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB003 | N/A | Rapid public | N/A | N/A | GB | None
EV04_BB3-depot_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB003 | N/A | HGV depot | N/A | N/A | GB | None
EV04_BB4-domestic_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB004 | N/A | Domestic | N/A | N/A | GB | None
EV04_BB4-workplace_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB004 | N/A | Workplace | N/A | N/A | GB | None
EV04_BB4-slowfast_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB004 | N/A | Slow/fast public | N/A | N/A | GB | None
EV04_BB4-rapid_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB004 | N/A | Rapid public | N/A | N/A | GB | None
EV04_BB4-depot_NA_NA_GB | EV04 | Proportion of charging by charger type | % | Lct_BB004 | N/A | HGV depot | N/A | N/A | GB | None
EV05_domestic_ALL_NoFlex_GB | EV05 | Proportion of consumers by behaviour | % | Applicable across all | N/A | Domestic | Applicable across all | No flexibility | GB | Annual
EV05_domestic_ALL_Smart_GB | EV05 | Proportion of consumers by behaviour | % | Applicable across all | N/A | Domestic | Applicable across all | Flexibility (static TouT) | GB | Annual
EV06_domestic_ALL_NoFlex_GB | EV06 | Normalised half-hourly profile | kW/annual kWh | Applicable across all | N/A | Domestic | Applicable across all | No flexibility | GB | Half-hourly
EV06_domestic_ALL_Smart_GB | EV06 | Normalised half-hourly profile | kW/annual kWh | Applicable across all | N/A | Domestic | Applicable across all | Flexibility (static TouT) | GB | Half-hourly
EV06_workplace_ALL_NoFlex_GB | EV06 | Normalised half-hourly profile | kW/annual kWh | Applicable across all | N/A | Workplace | Applicable across all | No flexibility | GB | Half-hourly
EV06_slowfast_ALL_NoFlex_GB | EV06 | Normalised half-hourly profile | kW/annual kWh | Applicable across all | N/A | Slow/fast public | Applicable across all | No flexibility | GB | Half-hourly
EV06_rapid_ALL_NoFlex_GB | EV06 | Normalised half-hourly profile | kW/annual kWh | Applicable across all | N/A | Rapid public | Applicable across all | No flexibility | GB | Half-hourly
EV06_depot_ALL_NoFlex_GB | EV06 | Normalised half-hourly profile | kW/annual kWh | Applicable across all | N/A | HGV depot | Applicable across all | No flexibility | GB | Half-hourly
EV07_domestic_ALL_ALL_GB | EV07 | Diversity-correction curve | N/A (scaling factor) | Applicable across all | N/A | Domestic | Applicable across all | Applicable across all | GB | None
EV07_workplace_ALL_ALL_GB | EV07 | Diversity-correction curve | N/A (scaling factor) | Applicable across all | N/A | Workplace | Applicable across all | Applicable across all | GB | None
EV07_slowfast_ALL_ALL_GB | EV07 | Diversity-correction curve | N/A (scaling factor) | Applicable across all | N/A | Slow/fast public | Applicable across all | Applicable across all | GB | None
EV07_rapid_ALL_ALL_GB | EV07 | Diversity-correction curve | N/A (scaling factor) | Applicable across all | N/A | Rapid public | Applicable across all | Applicable across all | GB | None
EV07_depot_ALL_ALL_GB | EV07 | Diversity-correction curve | N/A (scaling factor) | Applicable across all | N/A | HGV depot | Applicable across all | Applicable across all | GB | None
EV08_domestic_ALL_ALL_GB | EV08 | Minimum count for full diversification | # of vehicles | Applicable across all | N/A | Domestic | Applicable across all | Applicable across all | GB | None
EV08_workplace_ALL_ALL_GB | EV08 | Minimum count for full diversification | # of vehicles | Applicable across all | N/A | Workplace | Applicable across all | Applicable across all | GB | None
EV08_slowfast_ALL_ALL_GB | EV08 | Minimum count for full diversification | # of vehicles | Applicable across all | N/A | Slow/fast public | Applicable across all | Applicable across all | GB | None
EV08_rapid_ALL_ALL_GB | EV08 | Minimum count for full diversification | # of vehicles | Applicable across all | N/A | Rapid public | Applicable across all | Applicable across all | GB | None
EV08_depot_ALL_ALL_GB | EV08 | Minimum count for full diversification | # of vehicles | Applicable across all | N/A | HGV depot | Applicable across all | Applicable across all | GB | None
EV09_domestic_NA_ALL_GB | EV09 | Charge point utilisation | h/y | N/A | N/A | Domestic | N/A | Applicable across all | GB | None
EV09_workplace_NA_ALL_GB | EV09 | Charge point utilisation | h/y | N/A | N/A | Workplace | N/A | Applicable across all | GB | None
EV09_slowfast_NA_ALL_GB | EV09 | Charge point utilisation | h/y | N/A | N/A | Slow/fast public | N/A | Applicable across all | GB | None
EV09_rapid_NA_ALL_GB | EV09 | Charge point utilisation | h/y | N/A | N/A | Rapid public | N/A | Applicable across all | GB | None
EV09_depot_NA_ALL_GB | EV09 | Charge point utilisation | h/y | N/A | N/A | HGV depot | N/A | Applicable across all | GB | None
EV10_domestic_NA_ALL_GB | EV10 | Size of chargers | kW | N/A | N/A | Domestic | N/A | Applicable across all | GB | None
EV10_workplace_NA_ALL_GB | EV10 | Size of chargers | kW | N/A | N/A | Workplace | N/A | Applicable across all | GB | None
EV10_slowfast_NA_ALL_GB | EV10 | Size of chargers | kW | N/A | N/A | Slow/fast public | N/A | Applicable across all | GB | None
EV10_rapid_NA_ALL_GB | EV10 | Size of chargers | kW | N/A | N/A | Rapid public | N/A | Applicable across all | GB | None
EV10_depot_NA_ALL_GB | EV10 | Size of chargers | kW | N/A | N/A | HGV depot | N/A | Applicable across all | GB | None

## EV01
Back to contents
Back to EV CPA Summary Table
CPA ID | Unit | BB1 | BB2 | Charger type | Representative day | Flexibility behaviour | Licence area | Default value
EV01_BB1-BB2_NA_NA_EastMids | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | East Midlands | 13900
EV01_BB1-BB2_NA_NA_East | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | Eastern | 13700
EV01_BB1-BB2_NA_NA_London | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | London | 9900
EV01_BB1-BB2_NA_NA_MersNWales | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | Merseyside and North Wales | 14100
EV01_BB1-BB2_NA_NA_Wmids | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | Midlands | 13600
EV01_BB1-BB2_NA_NA_NorthScot | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | North Scotland | 16300
EV01_BB1-BB2_NA_NA_NorthWest | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | North Western | 12800
EV01_BB1-BB2_NA_NA_North | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | Northern | 14600
EV01_BB1-BB2_NA_NA_SouthEast | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | South Eastern | 13000
EV01_BB1-BB2_NA_NA_SouthScot | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | South Scotland | 14600
EV01_BB1-BB2_NA_NA_SouthWales | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | South Wales | 14600
EV01_BB1-BB2_NA_NA_SouthWest | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | South Western | 14000
EV01_BB1-BB2_NA_NA_South | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | Southern | 11800
EV01_BB1-BB2_NA_NA_Yorkshire | km/year | Lct_BB001 | Lct_BB002 | N/A | N/A | N/A | Yorkshire | 12800
EV01_BB3-BB4_NA_NA_EastMids | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | East Midlands | 50800
EV01_BB3-BB4_NA_NA_East | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | Eastern | 56000
EV01_BB3-BB4_NA_NA_London | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | London | 33200
EV01_BB3-BB4_NA_NA_MersNWales | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | Merseyside and North Wales | 43000
EV01_BB3-BB4_NA_NA_Wmids | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | Midlands | 46000
EV01_BB3-BB4_NA_NA_NorthScot | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | North Scotland | 60100
EV01_BB3-BB4_NA_NA_NorthWest | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | North Western | 41300
EV01_BB3-BB4_NA_NA_North | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | Northern | 52900
EV01_BB3-BB4_NA_NA_SouthEast | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | South Eastern | 52300
EV01_BB3-BB4_NA_NA_SouthScot | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | South Scotland | 59800
EV01_BB3-BB4_NA_NA_SouthWales | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | South Wales | 40500
EV01_BB3-BB4_NA_NA_SouthWest | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | South Western | 37900
EV01_BB3-BB4_NA_NA_South | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | Southern | 39800
EV01_BB3-BB4_NA_NA_Yorkshire | km/year | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | Yorkshire | 47000

## EV02
Back to contents
Back to EV CPA Summary Table
CPA ID | Unit | BB1 | Charger type | Representative day | Flexibility behaviour | Level of spatial granularity | Default value | Range (lower bound) | Range (upper bound)
EV02_BB2_NA_NA_GB | % | Lct_BB002 | N/A | N/A | N/A | GB | 31.2% | 20% | 50%
EV02_BB4_NA_NA_GB | % | Lct_BB004 | N/A | N/A | N/A | GB | 40% | 30% | 50%

## EV03
Back to contents
Back to EV CPA Summary Table
CPA ID | Unit | BB1 | BB2 | Charger type | Representative day | Flexibility behaviour | Level of spatial granularity | Year | Default value
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2024 | 0.2062
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2025 | 0.2046
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2026 | 0.2025
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2027 | 0.2004
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2028 | 0.1982
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2029 | 0.196
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2030 | 0.1943
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2031 | 0.1936
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2032 | 0.1935
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2033 | 0.1938
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2034 | 0.1942
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2035 | 0.1946
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2036 | 0.1947
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2037 | 0.1946
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2038 | 0.1942
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2039 | 0.1937
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2040 | 0.1934
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2041 | 0.1931
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2042 | 0.1926
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2043 | 0.1921
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2044 | 0.1916
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2045 | 0.1912
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2046 | 0.1907
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2047 | 0.1902
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2048 | 0.1885
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2049 | 0.188
EV03_BB1_NA_NA_GB | kWh/km | Lct_BB001 | N/A | N/A | N/A | N/A | GB | 2050 | 0.1874
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2024 | 0.1908
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2025 | 0.1873
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2026 | 0.1852
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2027 | 0.1837
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2028 | 0.1827
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2029 | 0.1819
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2030 | 0.1812
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2031 | 0.1806
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2032 | 0.1797
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2033 | 0.179
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2034 | 0.1783
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2035 | 0.1775
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2036 | 0.1767
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2037 | 0.1759
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2038 | 0.1751
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2039 | 0.1743
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2040 | 0.1733
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2041 | 0.1722
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2042 | 0.1713
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2043 | 0.1706
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2044 | 0.1699
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2045 | 0.1689
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2046 | 0.1679
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2047 | 0.1672
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2048 | 0.1665
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2049 | 0.1658
EV03_BB2_NA_NA_GB | kWh/km | Lct_BB002 | N/A | N/A | N/A | N/A | GB | 2050 | 0.1651
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2024 | 1.1908
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2025 | 1.191
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2026 | 1.191
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2027 | 1.19
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2028 | 1.1887
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2029 | 1.1872
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2030 | 1.1855
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2031 | 1.184
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2032 | 1.1849
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2033 | 1.1844
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2034 | 1.178
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2035 | 1.1755
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2036 | 1.1752
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2037 | 1.1697
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2038 | 1.1667
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2039 | 1.1665
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2040 | 1.1636
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2041 | 1.1591
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2042 | 1.1549
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2043 | 1.1519
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2044 | 1.1489
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2045 | 1.1455
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2046 | 1.1425
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2047 | 1.1397
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2048 | 1.1365
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2049 | 1.1337
EV03_BB3-NA_NA_NA_GB | kWh/km | Lct_BB003 | Lct_BB004 | N/A | N/A | N/A | GB | 2050 | 1.1308

## EV04
Back to contents
Back to EV CPA Summary Table
CPA ID | Unit | BB1 | Charger type | Representative day | Flexibility behaviour | Level of spatial granularity | Default value | Range (lower bound) | Range (upper bound)
EV04_BB1-domestic_NA_NA_GB | % | Lct_BB001 | Domestic | N/A | N/A | GB | 71% | 63% | 79%
EV04_BB1-workplace_NA_NA_GB | % | Lct_BB001 | Workplace | N/A | N/A | GB | 13.7% | 11% | 16%
EV04_BB1-slowfast_NA_NA_GB | % | Lct_BB001 | Slow/fast public | N/A | N/A | GB | 5.3% | 1% | 10%
EV04_BB1-rapid_NA_NA_GB | % | Lct_BB001 | Rapid public | N/A | N/A | GB | 10% | 3% | 17%
EV04_BB1-depot_NA_NA_GB | % | Lct_BB001 | HGV depot | N/A | N/A | GB | 0% | 0% | 0%
EV04_BB2-domestic_NA_NA_GB | % | Lct_BB002 | Domestic | N/A | N/A | GB | 78.3% | 71% | 86%
EV04_BB2-workplace_NA_NA_GB | % | Lct_BB002 | Workplace | N/A | N/A | GB | 15.7% | 12% | 20%
EV04_BB2-slowfast_NA_NA_GB | % | Lct_BB002 | Slow/fast public | N/A | N/A | GB | 6% | 0% | 17%
EV04_BB2-rapid_NA_NA_GB | % | Lct_BB002 | Rapid public | N/A | N/A | GB | 0% | 0% | 0%
EV04_BB2-depot_NA_NA_GB | % | Lct_BB002 | HGV depot | N/A | N/A | GB | 0% | 0% | 0%
EV04_BB3-domestic_NA_NA_GB | % | Lct_BB003 | Domestic | N/A | N/A | GB | 0% | 0% | 0%
EV04_BB3-workplace_NA_NA_GB | % | Lct_BB003 | Workplace | N/A | N/A | GB | 0% | 0% | 0%
EV04_BB3-slowfast_NA_NA_GB | % | Lct_BB003 | Slow/fast public | N/A | N/A | GB | 0% | 0% | 0%
EV04_BB3-rapid_NA_NA_GB | % | Lct_BB003 | Rapid public | N/A | N/A | GB | 10% | 10% | 10%
EV04_BB3-depot_NA_NA_GB | % | Lct_BB003 | HGV depot | N/A | N/A | GB | 90% | 90% | 90%
EV04_BB4-domestic_NA_NA_GB | % | Lct_BB004 | Domestic | N/A | N/A | GB | 0% | 0% | 0%
EV04_BB4-workplace_NA_NA_GB | % | Lct_BB004 | Workplace | N/A | N/A | GB | 0% | 0% | 0%
EV04_BB4-slowfast_NA_NA_GB | % | Lct_BB004 | Slow/fast public | N/A | N/A | GB | 0% | 0% | 0%
EV04_BB4-rapid_NA_NA_GB | % | Lct_BB004 | Rapid public | N/A | N/A | GB | 0% | 0% | 0%
EV04_BB4-depot_NA_NA_GB | % | Lct_BB004 | HGV depot | N/A | N/A | GB | 100% | 100% | 100%

## EV05
Back to contents
Back to EV CPA Summary Table
CPA ID | Unit | BB1 | Charger type | Representative day | Flexibility behaviour | Level of spatial granularity | Year | Default value
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2024 | 75%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2025 | 67%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2026 | 58%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2027 | 50%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2028 | 42%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2029 | 34%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2030 | 25%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2031 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2032 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2033 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2034 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2035 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2036 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2037 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2038 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2039 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2040 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2041 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2042 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2043 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2044 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2045 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2046 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2047 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2048 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2049 | 17%
EV05_domestic_ALL_NoFlex_GB | % | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2050 | 17%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2024 | 25%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2025 | 33%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2026 | 42%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2027 | 50%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2028 | 58%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2029 | 66%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2030 | 75%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2031 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2032 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2033 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2034 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2035 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2036 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2037 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2038 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2039 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2040 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2041 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2042 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2043 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2044 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2045 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2046 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2047 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2048 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2049 | 83%
EV05_domestic_ALL_Smart_GB | % | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2050 | 83%

## EV06
Back to contents
Back to EV CPA Summary Table
CPA ID | Unit | BB1 | Charger type | Representative day | Flexibility behaviour | Level of spatial granularity | Start of half hour period | Default value
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 0:00 | 0.00011684
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 0:30 | 9.7899e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 1:00 | 7.8957e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 1:30 | 6.4322e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2:00 | 4.9687e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 2:30 | 4.0844e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 3:00 | 3.2001e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 3:30 | 2.7057e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 4:00 | 2.2113e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 4:30 | 1.9747e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 5:00 | 1.7381e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 5:30 | 1.762e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 6:00 | 1.786e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 6:30 | 2.1212e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 7:00 | 2.4564e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 7:30 | 3.1427e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 8:00 | 3.829e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 8:30 | 4.752e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 9:00 | 5.675e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 9:30 | 6.0655e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 10:00 | 6.456e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 10:30 | 6.9604e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 11:00 | 7.4649e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 11:30 | 8.0345e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 12:00 | 8.6042e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 12:30 | 9.0079e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 13:00 | 9.4115e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 13:30 | 9.629e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 14:00 | 9.8465e-05
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 14:30 | 0.00010697
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 15:00 | 0.00011547
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 15:30 | 0.00013637
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 16:00 | 0.00015726
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 16:30 | 0.00018485
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 17:00 | 0.00021243
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 17:30 | 0.00023898
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 18:00 | 0.00026553
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 18:30 | 0.00027015
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 19:00 | 0.00027477
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 19:30 | 0.0002653
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 20:00 | 0.00025583
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 20:30 | 0.00024177
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 21:00 | 0.00022771
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 21:30 | 0.00021337
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 22:00 | 0.00019904
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 22:30 | 0.00017922
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 23:00 | 0.00015941
EV06_domestic_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | No flexibility | GB | 23:30 | 0.00013813
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 0:00 | 0.00023851
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 0:30 | 0.00027227
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 1:00 | 0.00026855
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 1:30 | 0.00025298
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2:00 | 0.00025539
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 2:30 | 0.00024334
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 3:00 | 0.00022646
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 3:30 | 0.00019905
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 4:00 | 0.00016946
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 4:30 | 0.00013438
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 5:00 | 0.00010391
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 5:30 | 8.3743e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 6:00 | 7.0151e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 6:30 | 5.3929e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 7:00 | 5.5244e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 7:30 | 4.779e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 8:00 | 3.5952e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 8:30 | 4.1652e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 9:00 | 4.1214e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 9:30 | 4.2967e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 10:00 | 4.5598e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 10:30 | 4.8667e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 11:00 | 4.9106e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 11:30 | 5.2613e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 12:00 | 5.349e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 12:30 | 5.5244e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 13:00 | 5.5244e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 13:30 | 5.8751e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 14:00 | 5.8751e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 14:30 | 5.5244e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 15:00 | 5.5682e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 15:30 | 5.8313e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 16:00 | 6.9713e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 16:30 | 7.5412e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 17:00 | 8.3304e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 17:30 | 9.2512e-05
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 18:00 | 0.00010084
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 18:30 | 0.0001118
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 19:00 | 0.00011794
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 19:30 | 0.00012233
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 20:00 | 0.00012671
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 20:30 | 0.00014074
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 21:00 | 0.00014469
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 21:30 | 0.00014732
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 22:00 | 0.00014907
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 22:30 | 0.00015433
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 23:00 | 0.00017231
EV06_domestic_ALL_Smart_GB | kW/annual kWh | Applicable across all | Domestic | Applicable across all | Flexibility (static TouT) | GB | 23:30 | 0.00018678
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 0:00 | 2.2105e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 0:30 | 1.9169e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 1:00 | 1.6233e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 1:30 | 1.4636e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 2:00 | 1.304e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 2:30 | 1.2529e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 3:00 | 1.2017e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 3:30 | 1.2361e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 4:00 | 1.2704e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 4:30 | 1.6659e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 5:00 | 2.0613e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 5:30 | 4.8411e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 6:00 | 7.6209e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 6:30 | 0.00015966
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 7:00 | 0.0002431
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 7:30 | 0.00033215
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 8:00 | 0.00042121
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 8:30 | 0.00040129
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 9:00 | 0.00038137
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 9:30 | 0.00031601
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 10:00 | 0.00025065
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 10:30 | 0.0002184
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 11:00 | 0.00018614
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 11:30 | 0.00017882
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 12:00 | 0.00017149
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 12:30 | 0.00017135
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 13:00 | 0.00017121
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 13:30 | 0.00015999
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 14:00 | 0.00014876
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 14:30 | 0.00013754
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 15:00 | 0.00012632
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 15:30 | 0.00011637
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 16:00 | 0.00010642
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 16:30 | 9.6531e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 17:00 | 8.6642e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 17:30 | 7.7456e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 18:00 | 6.827e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 18:30 | 6.198e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 19:00 | 5.569e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 19:30 | 5.0528e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 20:00 | 4.5367e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 20:30 | 4.2372e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 21:00 | 3.9377e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 21:30 | 3.7627e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 22:00 | 3.5877e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 22:30 | 3.2388e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 23:00 | 2.8899e-05
EV06_workplace_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Workplace | Applicable across all | No flexibility | GB | 23:30 | 2.5502e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 0:00 | 3.0067e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 0:30 | 2.7307e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 1:00 | 2.4547e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 1:30 | 2.1889e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 2:00 | 1.923e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 2:30 | 1.7239e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 3:00 | 1.5247e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 3:30 | 1.4751e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 4:00 | 1.4255e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 4:30 | 1.7434e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 5:00 | 2.0613e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 5:30 | 3.1794e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 6:00 | 4.2975e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 6:30 | 7.179e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 7:00 | 0.00010061
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 7:30 | 0.00015017
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 8:00 | 0.00019973
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 8:30 | 0.00023046
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 9:00 | 0.00026119
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 9:30 | 0.00025312
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 10:00 | 0.00024506
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 10:30 | 0.000232
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 11:00 | 0.00021895
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 11:30 | 0.0002137
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 12:00 | 0.00020846
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 12:30 | 0.00020541
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 13:00 | 0.00020237
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 13:30 | 0.00019464
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 14:00 | 0.00018691
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 14:30 | 0.00017571
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 15:00 | 0.00016451
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 15:30 | 0.00015631
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 16:00 | 0.00014811
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 16:30 | 0.00014477
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 17:00 | 0.00014142
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 17:30 | 0.0001401
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 18:00 | 0.00013877
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 18:30 | 0.0001299
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 19:00 | 0.00012103
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 19:30 | 0.00010582
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 20:00 | 9.0622e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 20:30 | 7.6743e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 21:00 | 6.2864e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 21:30 | 5.4334e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 22:00 | 4.5803e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 22:30 | 4.11e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 23:00 | 3.6398e-05
EV06_slowfast_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Slow/fast public | Applicable across all | No flexibility | GB | 23:30 | 3.3232e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 0:00 | 3.4021e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 0:30 | 2.6311e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 1:00 | 2.1532e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 1:30 | 1.6754e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 2:00 | 1.3865e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 2:30 | 1.0976e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 3:00 | 9.693e-06
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 3:30 | 8.41e-06
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 4:00 | 8.718e-06
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 4:30 | 9.027e-06
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 5:00 | 1.2922e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 5:30 | 1.6817e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 6:00 | 3.04e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 6:30 | 4.3983e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 7:00 | 6.1363e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 7:30 | 7.8744e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 8:00 | 9.7966e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 8:30 | 0.00011719
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 9:00 | 0.00013441
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 9:30 | 0.00015162
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 10:00 | 0.0001579
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 10:30 | 0.00016418
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 11:00 | 0.000173
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 11:30 | 0.00018181
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 12:00 | 0.00019324
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 12:30 | 0.00020467
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 13:00 | 0.00020991
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 13:30 | 0.00021515
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 14:00 | 0.00021228
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 14:30 | 0.00020941
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 15:00 | 0.00020642
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 15:30 | 0.00020343
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 16:00 | 0.0002012
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 16:30 | 0.00019897
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 17:00 | 0.00019819
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 17:30 | 0.0001974
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 18:00 | 0.00019522
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 18:30 | 0.00019305
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 19:00 | 0.00017954
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 19:30 | 0.00016603
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 20:00 | 0.00014787
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 20:30 | 0.00012971
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 21:00 | 0.00011128
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 21:30 | 9.2843e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 22:00 | 7.7174e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 22:30 | 6.1505e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 23:00 | 5.1619e-05
EV06_rapid_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | Rapid public | Applicable across all | No flexibility | GB | 23:30 | 4.1732e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 0:00 | 0.00018804
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 0:30 | 0.00017903
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 1:00 | 0.00017948
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 1:30 | 0.00017993
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 2:00 | 0.00018041
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 2:30 | 0.0001809
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 3:00 | 0.0001761
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 3:30 | 0.0001713
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 4:00 | 0.00015844
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 4:30 | 0.00014559
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 5:00 | 0.00012918
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 5:30 | 0.00011277
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 6:00 | 0.00010168
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 6:30 | 9.0598e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 7:00 | 8.1176e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 7:30 | 7.1753e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 8:00 | 6.4773e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 8:30 | 5.7793e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 9:00 | 5.2413e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 9:30 | 4.7033e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 10:00 | 4.3441e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 10:30 | 3.9849e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 11:00 | 3.8006e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 11:30 | 3.6162e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 12:00 | 3.5044e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 12:30 | 3.3927e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 13:00 | 3.3578e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 13:30 | 3.3229e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 14:00 | 3.3868e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 14:30 | 3.4507e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 15:00 | 3.7996e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 15:30 | 4.1485e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 16:00 | 5.0856e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 16:30 | 6.0227e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 17:00 | 7.9237e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 17:30 | 9.8246e-05
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 18:00 | 0.00012581
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 18:30 | 0.00015337
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 19:00 | 0.00016919
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 19:30 | 0.00018501
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 20:00 | 0.0001892
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 20:30 | 0.00019338
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 21:00 | 0.00019624
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 21:30 | 0.00019909
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 22:00 | 0.0001983
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 22:30 | 0.0001975
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 23:00 | 0.00019728
EV06_depot_ALL_NoFlex_GB | kW/annual kWh | Applicable across all | HGV depot | Applicable across all | No flexibility | GB | 23:30 | 0.00019705

## EV07
Back to contents
Back to EV CPA Summary Table
CPA ID | Unit | BB1 | Charger type | Representative day | Flexibility behaviour | Level of spatial granularity | Number of electric vehicles - lower bound | Number of electric vehicles - upper bound | Default value
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 1 | 1 | 15.177
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 2 | 2 | 9.296
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 3 | 3 | 8.621
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 4 | 4 | 7.82
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 5 | 6 | 6.429
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 7 | 8 | 5.306
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 9 | 11 | 4.911
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 12 | 14 | 4.207
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 15 | 17 | 3.831
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 18 | 20 | 3.602
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 21 | 24 | 3.233
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 25 | 29 | 3.134
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 30 | 39 | 2.878
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 40 | 49 | 2.578
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 50 | 74 | 2.384
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 75 | 99 | 2.085
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 100 | 149 | 1.95
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 150 | 199 | 1.731
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 200 | 299 | 1.627
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 300 | 499 | 1.499
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 500 | 749 | 1.368
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 750 | 999 | 1.295
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 1000 | 1249 | 1.25
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 1250 | 1532 | 1.221
EV07_domestic_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 1533 | N/A | 1
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 1 | 1 | 7.951
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 2 | 2 | 5.756
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 3 | 3 | 5.452
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 4 | 4 | 4.385
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 5 | 6 | 3.924
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 7 | 8 | 3.64
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 9 | 11 | 3.112
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 12 | 14 | 2.869
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 15 | 17 | 2.617
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 18 | 20 | 2.47
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 21 | 24 | 2.356
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 25 | 29 | 2.207
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 30 | 39 | 2.088
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 40 | 49 | 1.943
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 50 | 74 | 1.824
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 75 | 99 | 1.658
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 100 | 149 | 1.553
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 150 | 199 | 1.454
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 200 | 299 | 1.388
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 300 | 499 | 1.312
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 500 | 690 | 1.232
EV07_workplace_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 691 | N/A | 1
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 1 | 1 | 5.184
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 2 | 2 | 5.184
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 3 | 3 | 4.239
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 4 | 4 | 3.985
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 5 | 6 | 3.496
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 7 | 8 | 3.147
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 9 | 11 | 2.864
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 12 | 14 | 2.599
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 15 | 17 | 2.387
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 18 | 20 | 2.221
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 21 | 24 | 2.106
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 25 | 29 | 2.018
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 30 | 39 | 1.913
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 40 | 49 | 1.784
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 50 | 74 | 1.69
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 75 | 99 | 1.545
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 100 | 149 | 1.46
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 150 | 199 | 1.366
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 200 | 299 | 1.307
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 300 | 432 | 1.245
EV07_slowfast_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 433 | N/A | 1
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 1 | 1 | 12.887
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 2 | 2 | 11.972
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 3 | 3 | 8.918
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 4 | 4 | 7.287
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 5 | 6 | 6.688
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 7 | 8 | 5.823
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 9 | 11 | 4.963
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 12 | 14 | 4.509
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 15 | 19 | 3.979
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 20 | 24 | 3.499
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 25 | 29 | 3.266
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 30 | 39 | 3.042
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 40 | 49 | 2.696
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 50 | 74 | 2.478
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 75 | 99 | 2.197
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 100 | 149 | 1.989
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 150 | 199 | 1.787
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 200 | 299 | 1.657
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 300 | 499 | 1.522
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 500 | 749 | 1.383
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 750 | 999 | 1.299
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 1000 | 1249 | 1.25
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 1250 | 1417 | 1.216
EV07_rapid_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 1418 | N/A | 1
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 1 | 1 | 13.544
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 2 | 2 | 9.745
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 3 | 3 | 9.192
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 4 | 4 | 7.266
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 5 | 6 | 6.306
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 7 | 8 | 5.776
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 9 | 11 | 4.87
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 12 | 14 | 4.308
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 15 | 17 | 3.934
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 18 | 20 | 3.599
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 21 | 24 | 3.465
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 25 | 29 | 3.16
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 30 | 39 | 2.98
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 40 | 49 | 2.649
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 50 | 74 | 2.474
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 75 | 99 | 2.151
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 100 | 149 | 1.997
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 150 | 199 | 1.779
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 200 | 299 | 1.662
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 300 | 499 | 1.526
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 500 | 749 | 1.391
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 750 | 999 | 1.309
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 1000 | 1249 | 1.264
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 1250 | 1566 | 1.226
EV07_depot_ALL_ALL_GB | N/A (scaling factor) | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 1567 | N/A | 1

## EV08
Back to contents
Back to EV CPA Summary Table
CPA ID | Unit | BB1 | Charger type | Representative day | Flexibility behaviour | Level of spatial granularity | Default value
EV08_domestic_ALL_ALL_GB | # of vehicles | Applicable across all | Domestic | Applicable across all | Applicable across all | GB | 1533
EV08_workplace_ALL_ALL_GB | # of vehicles | Applicable across all | Workplace | Applicable across all | Applicable across all | GB | 691
EV08_slowfast_ALL_ALL_GB | # of vehicles | Applicable across all | Slow/fast public | Applicable across all | Applicable across all | GB | 433
EV08_rapid_ALL_ALL_GB | # of vehicles | Applicable across all | Rapid public | Applicable across all | Applicable across all | GB | 1418
EV08_depot_ALL_ALL_GB | # of vehicles | Applicable across all | HGV depot | Applicable across all | Applicable across all | GB | 1567

## EV09
Back to contents
Back to EV CPA Summary Table
CPA ID | Unit | BB1 | Charger type | Representative day | Flexibility behaviour | Level of spatial granularity | Default value | Corresponding time-based utilisation (%)
EV09_domestic_NA_ALL_GB | h/y | N/A | Domestic | N/A | Applicable across all | GB | 244 | 2.785%
EV09_workplace_NA_ALL_GB | h/y | N/A | Workplace | N/A | Applicable across all | GB | 870 | 9.932%
EV09_slowfast_NA_ALL_GB | h/y | N/A | Slow/fast public | N/A | Applicable across all | GB | 1164 | 13.29%
EV09_rapid_NA_ALL_GB | h/y | N/A | Rapid public | N/A | Applicable across all | GB | 1175 | 13.41%
EV09_depot_NA_ALL_GB | h/y | N/A | HGV depot | N/A | Applicable across all | GB | 1175 | 13.41%

## EV10
Back to contents
Back to EV CPA Summary Table
CPA ID | Unit | BB1 | Charger type | Representative day | Flexibility behaviour | Level of spatial granularity | Default value | Range (lower bound) | Range (upper bound)
EV10_domestic_NA_ALL_GB | kW | N/A | Domestic | N/A | Applicable across all | GB | 7 | 7 | 7
EV10_workplace_NA_ALL_GB | kW | N/A | Workplace | N/A | Applicable across all | GB | 7 | 7 | 22
EV10_slowfast_NA_ALL_GB | kW | N/A | Slow/fast public | N/A | Applicable across all | GB | 22 | 7 | 22
EV10_rapid_NA_ALL_GB | kW | N/A | Rapid public | N/A | Applicable across all | GB | 50 | 50 | 150
EV10_depot_NA_ALL_GB | kW | N/A | HGV depot | N/A | Applicable across all | GB | 150 | 50 | 1000

## EV Indicative Impact
Back to contents
Back to EV CPA Summary Table
Indicative calculation (as presented in the September 2025 tRESP consultation)
| Parameter | Vehicle type | Charger type | Unit | Value
| Number of Battery Electric cars, vans, motorcycles | Lct_BB001 | All | # | 52.6481
| Number of Plug-in hybrid electric cars, vans, motorcycles | Lct_BB002 | All | # | 46.1147
| Number of Battery electric buses and HGVs | Lct_BB003 | All | # | 1.2372
| Number of Plug-in hybrid buses and HGVs | Lct_BB004 | All | # | 0
| Annual energy demand - Battery Electric cars, vans, motorcycles | Lct_BB001 | All | kWh | 140516.5136
| Annual energy demand - Plug-in hybrid electric cars, vans, motorcycles | Lct_BB002 | All | kWh | 35811.6331
| Annual energy demand - Battery electric buses and HGVs | Lct_BB003 | All | kWh | 56253.3415
| Annual energy demand - Plug-in hybrid buses and HGVs | Lct_BB004 | All | kWh | 0
| Annual energy demand - domestic charging | All | Domestic | kWh | 127807.2334
| Annual energy demand - workplace charging | All | Workplace | kWh | 24873.1888
| Annual energy demand - public slow/fast charging | All | Slow/fast public | kWh | 9596.0732
| Annual energy demand - public rapid charging | All | Rapid public | kWh | 19676.9855
| Annual energy demand - HGV depot | All | HGV depot | kWh | 50628.0074
| Peak demand - domestic charging | All | Domestic | kW | 29.227
| workplace charging - at time of domestic peak | All | Workplace | kW | 0.47679
| public slow/fast charging - at time of domestic peak | All | Slow/fast public | kW | 0.26204
| public rapid charging - at time of domestic peak | All | Rapid public | kW | 0.51772
| HGV depot charging - at time of domestic peak | All | HGV depot | kW | 9.0639
| Total EV peak demand |  |  | kW | 39.5474
| Peak demand per EV |  |  | kW | 0.39547
CPAs used for the indicative calculation
| CPA | Vehicle type | Charger type | Selected scope | Unit | Value
| vehicle mileage | Lct_BB001 | N/A | Strict average across regions | km/year | 13736.3636
| vehicle mileage | Lct_BB002 | N/A | Strict average across regions | km/year | 13736.3636
| vehicle mileage | Lct_BB003 | N/A | Strict average across regions | km/year | 38354.5455
| vehicle mileage | Lct_BB004 | N/A | Strict average across regions | km/year | 38354.5455
| distance in EV mode | Lct_BB002 | N/A |  | % | 31.2%
| distance in EV mode | Lct_BB004 | N/A |  | % | 40%
| EV efficiency | Lct_BB001 | N/A | 2030 | kwh/km | 0.1943
| EV efficiency | Lct_BB002 | N/A | 2030 | kwh/km | 0.1812
| EV efficiency | Lct_BB003 | N/A | 2030 | kwh/km | 1.1855
| EV efficiency | Lct_BB004 | N/A | 2030 | kwh/km | 1.1855
| proportion of charging by charger type | Lct_BB001 | Domestic |  | % | 71%
| proportion of charging by charger type | Lct_BB001 | Workplace |  | % | 13.7%
| proportion of charging by charger type | Lct_BB001 | Slow/fast public |  | % | 5.3%
| proportion of charging by charger type | Lct_BB001 | Rapid public |  | % | 10%
| proportion of charging by charger type | Lct_BB001 | HGV depot |  | % | 0%
| proportion of charging by charger type | Lct_BB002 | Domestic |  | % | 78.3%
| proportion of charging by charger type | Lct_BB002 | Workplace |  | % | 15.7%
| proportion of charging by charger type | Lct_BB002 | Slow/fast public |  | % | 6%
| proportion of charging by charger type | Lct_BB002 | Rapid public |  | % | 0%
| proportion of charging by charger type | Lct_BB002 | HGV depot |  | % | 0%
| proportion of charging by charger type | Lct_BB003 | Domestic |  | % | 0%
| proportion of charging by charger type | Lct_BB003 | Workplace |  | % | 0%
| proportion of charging by charger type | Lct_BB003 | Slow/fast public |  | % | 0%
| proportion of charging by charger type | Lct_BB003 | Rapid public |  | % | 10%
| proportion of charging by charger type | Lct_BB003 | HGV depot |  | % | 90%
| proportion of charging by charger type | Lct_BB004 | Domestic |  | % | 0%
| proportion of charging by charger type | Lct_BB004 | Workplace |  | % | 0%
| proportion of charging by charger type | Lct_BB004 | Slow/fast public |  | % | 0%
| proportion of charging by charger type | Lct_BB004 | Rapid public |  | % | 0%
| proportion of charging by charger type | Lct_BB004 | HGV depot |  | % | 100%
| Proportion of consumers by behaviour (non-smart) |  | Domestic | 2030 | % | 25%
| Peak of normalised half-hourly profile | All | Domestic | weighted average across behaviours (smart and non-smart) | kW/ annual kWh | 0.00022868 | time of peak | 0:30
| value of normalised half-hourly profile at time of domestic peak | All | Workplace | Value at domestic charging peak | kW/ annual kWh | 1.9169e-05
| value of normalised half-hourly profile at time of domestic peak | All | Slow/fast public | Value at domestic charging peak | kW/ annual kWh | 2.7307e-05
| value of normalised half-hourly profile at time of domestic peak | All | Rapid public | Value at domestic charging peak | kW/ annual kWh | 2.6311e-05
| value of normalised half-hourly profile at time of domestic peak | All | HGV depot | Value at domestic charging peak | kW/ annual kWh | 0.00017903
Other assumptions used for the indicative calculation
| Assumption | Vehicle type | Charger type | Unit | Value | Source
| Proportion of EV stock that are Battery Electric cars, vans, motorcycles | Lct_BB001 | N/A | % | 52.65% | 9409683 | Totals taken from FES25, 2030 HT, values not important, ratio between values important
| Proportion of EV stock that are Plug-in hybrid electric cars, vans, motorcycles | Lct_BB002 | N/A | % | 46.11% | 8241984 | Totals taken from FES25, 2030 HT, values not important, ratio between values important
| Proportion of EV stock that are Battery electric buses and HGVs | Lct_BB003 | N/A | % | 1.237% | 221117 | Totals taken from FES25, 2030 HT, values not important, ratio between values important
| Proportion of EV stock that are Plug-in hybrid buses and HGVs | Lct_BB004 | N/A | % | 0% | 0 | Totals taken from FES25, 2030 HT, values not important, ratio between values important

## EV End to End Example
CPA Value Selection Tool and End-to-End Calculation: Electric Vehicles
Back to contents
Information
| This sheet is a tool to support users of the CPAs to select the right values for the conditions they wish to model, and create kW per half-hour profiles. | [5 empty] | Key for sheet:
| User inputs: Choose the conditions and technology numbers for the end-end calculation. | [5 empty] | input
| Dashboard: Summarises the results of the end -end calculation based on the user inputs and CPA values, including charts of total and per-EV demand. | [5 empty] | linked input (do not edit)
| CPA values selected: Display of the default, lower range, and upper range CPA values that should be applied in calculations for the user inputs selected. | [5 empty] | linked data (reference to values from CPA tables)
| End-to-end calculation: Example of calculations aligned with the EV CPA process, using the chosen inputs, for default, lower range, and upper range values. | [5 empty] | Calculation
User inputs
Please select the conditions for the value selector and input values for the end-to-end calculation.
| Inputs for CPA selection |  | Value inputs for calculation. Values represent technology numbers on a single network asset.
| DNO licence area |  | Below a count defined per GSP in the tRESP pathways, DNOs to identify the spatial allocation of the technology totals to specific network assets.
| Eastern |  | Please note that in this demonstration, a distinction between the vehicle location and where their demand appears is not made.
Therefore, the calculations reflect all electricity demand from the vehicles below and no other vehicles.
| Representative day |  | Parameter | Vehicle type | Charger type | Unit | Value
| Peak demand winter day |  | Number of Battery Electric cars, vans, motorcycles | Lct_BB001 | All | # | 94
|  |  | Number of Plug-in hybrid electric cars, vans, motorcycles | Lct_BB002 | All | # | 18
| Year |  | Number of Battery electric buses and HGVs | Lct_BB003 | All | # | 8
| 2030 |  | Number of Plug-in hybrid buses and HGVs | Lct_BB004 | All | # | 0
Switch to include/exclude domestic smart charging in response to static time of use tariffs.
Default setting: ON (EV05 assumption applied for proportion of flexibility behaviour). Use OFF (100% no flexibility) for flexibility sensitivity analysis.
|  |  | Domestic smart charging | ON
Dashboard
| Eastern: 2030 Peak demand winter day |  |  |  | Total EV demand - Default value |  |  | Peak demand |  | Peak time |  |  |  |  | Per-EV demand |  | Peak demand |  | Peak time
[8 empty] | 627.5896 | kW | 21:30 |  |  |  |  | Small EVs |  | 0.7772 | kW | 0:30
| Number of small EVs: | 112 | Lct_BB001 + Lct_BB002 | [11 empty] | Lct_BB001, Lct_BB002 |  | 0.66 - 0.91 | kW
| Number of large EVs: | 8 | Lct_BB003 + Lct_BB004
Diversity correction required?
| Domestic | Y
| Workplace | Y
| Slow/fast public | Y
| Rapid public | Y
| HGV depot | Y
[15 empty] | Per-EV demand |  | Peak demand |  | Peak time
[15 empty] | Large EVs |  | 69.9345 | kW | 21:30
[15 empty] | Lct_BB003, Lct_BB004 |  | 69.93 - 69.93 | kW
For reference: Charge points
[7 empty] | Number of charge points |  |  | Installed capacity
[7 empty] | 123 |  |  | 1300.1647 | kW
CPA values selected
This table lists the default, lower range, and upper range values that should be applied in calculations for the conditions listed in the user inputs.
| CPA ID | CPA ID | CPA | Vehicle type | Charger type | Representative day | Flexibility behaviour | Spatial scope | Year | Unit | Value - Default | Lower range | Upper range
| EV01 | EV01 | vehicle mileage | Lct_BB001 | N/A | N/A | N/A | Eastern | All | km/year | 13700 | 13700 | 13700
|  | EV01 | vehicle mileage | Lct_BB002 | N/A | N/A | N/A | Eastern | All | km/year | 13700 | 13700 | 13700
|  | EV01 | vehicle mileage | Lct_BB003 | N/A | N/A | N/A | Eastern | All | km/year | 56000 | 56000 | 56000
|  | EV01 | vehicle mileage | Lct_BB004 | N/A | N/A | N/A | Eastern | All | km/year | 56000 | 56000 | 56000
| EV02 | EV02 | distance in EV mode | Lct_BB002 | N/A | N/A | N/A | GB | All | % | 31.2% | 20% | 50%
|  | EV02 | distance in EV mode | Lct_BB004 | N/A | N/A | N/A | GB | All | % | 40% | 30% | 50%
| EV03 | EV03 | EV efficiency | Lct_BB001 | N/A | N/A | N/A | GB | 2030 | kwh/km | 0.1943 | 0.1943 | 0.1943
|  | EV03 | EV efficiency | Lct_BB002 | N/A | N/A | N/A | GB | 2030 | kwh/km | 0.1812 | 0.1812 | 0.1812
|  | EV03 | EV efficiency | Lct_BB003 | N/A | N/A | N/A | GB | 2030 | kwh/km | 1.1855 | 1.1855 | 1.1855
|  | EV03 | EV efficiency | Lct_BB004 | N/A | N/A | N/A | GB | 2030 | kwh/km | 1.1855 | 1.1855 | 1.1855
| EV04 | EV04 | proportion of charging by charger type | Lct_BB001 | Domestic | N/A | N/A | GB | All | % | 71% | 63% | 79%
|  | EV04 | proportion of charging by charger type | Lct_BB001 | Workplace | N/A | N/A | GB | All | % | 13.7% | 11% | 16%
|  | EV04 | proportion of charging by charger type | Lct_BB001 | Slow/fast public | N/A | N/A | GB | All | % | 5.3% | 1% | 10%
|  | EV04 | proportion of charging by charger type | Lct_BB001 | Rapid public | N/A | N/A | GB | All | % | 10% | 3% | 17%
|  | EV04 | proportion of charging by charger type | Lct_BB001 | HGV depot | N/A | N/A | GB | All | % | 0% | 0% | 0%
|  | EV04 | proportion of charging by charger type | Lct_BB002 | Domestic | N/A | N/A | GB | All | % | 78.3% | 71% | 86%
|  | EV04 | proportion of charging by charger type | Lct_BB002 | Workplace | N/A | N/A | GB | All | % | 15.7% | 12% | 20%
|  | EV04 | proportion of charging by charger type | Lct_BB002 | Slow/fast public | N/A | N/A | GB | All | % | 6% | 0% | 17%
|  | EV04 | proportion of charging by charger type | Lct_BB002 | Rapid public | N/A | N/A | GB | All | % | 0% | 0% | 0%
|  | EV04 | proportion of charging by charger type | Lct_BB002 | HGV depot | N/A | N/A | GB | All | % | 0% | 0% | 0%
|  | EV04 | proportion of charging by charger type | Lct_BB003 | Domestic | N/A | N/A | GB | All | % | 0% | 0% | 0%
|  | EV04 | proportion of charging by charger type | Lct_BB003 | Workplace | N/A | N/A | GB | All | % | 0% | 0% | 0%
|  | EV04 | proportion of charging by charger type | Lct_BB003 | Slow/fast public | N/A | N/A | GB | All | % | 0% | 0% | 0%
|  | EV04 | proportion of charging by charger type | Lct_BB003 | Rapid public | N/A | N/A | GB | All | % | 10% | 10% | 10%
|  | EV04 | proportion of charging by charger type | Lct_BB003 | HGV depot | N/A | N/A | GB | All | % | 90% | 90% | 90%
|  | EV04 | proportion of charging by charger type | Lct_BB004 | Domestic | N/A | N/A | GB | All | % | 0% | 0% | 0%
|  | EV04 | proportion of charging by charger type | Lct_BB004 | Workplace | N/A | N/A | GB | All | % | 0% | 0% | 0%
|  | EV04 | proportion of charging by charger type | Lct_BB004 | Slow/fast public | N/A | N/A | GB | All | % | 0% | 0% | 0%
|  | EV04 | proportion of charging by charger type | Lct_BB004 | Rapid public | N/A | N/A | GB | All | % | 0% | 0% | 0%
|  | EV04 | proportion of charging by charger type | Lct_BB004 | HGV depot | N/A | N/A | GB | All | % | 100% | 100% | 100%
| EV05 | EV05 | Proportion of consumers by behaviour | Applicable across all | Domestic | N/A | No flexibility | GB | 2030 | % | 25% | 25% | 25%
|  | EV05 | Proportion of consumers by behaviour | Applicable across all | Domestic | N/A | Flexibility (static TouT) | GB | 2030 | % | 75% | 75% | 75%
| EV08 | EV08 | Minimum count for full diversification | Applicable across all | Domestic | N/A | N/A | GB | All | # | 1533 | 1533 | 1533
|  | EV08 | Minimum count for full diversification | Applicable across all | Workplace | N/A | N/A | GB | All | # | 691 | 691 | 691
|  | EV08 | Minimum count for full diversification | Applicable across all | Slow/fast public | N/A | N/A | GB | All | # | 433 | 433 | 433
|  | EV08 | Minimum count for full diversification | Applicable across all | Rapid public | N/A | N/A | GB | All | # | 1418 | 1418 | 1418
|  | EV08 | Minimum count for full diversification | Applicable across all | HGV depot | N/A | N/A | GB | All | # | 1567 | 1567 | 1567
| EV07 | EV07 | Diversity correction factor | Applicable across all | Domestic | N/A | N/A | GB | All | N/A (scaling factor) | 1.95 | 1.95 | 1.95
|  | EV07 | Diversity correction factor | Applicable across all | Workplace | N/A | N/A | GB | All | N/A (scaling factor) | 1.553 | 1.553 | 1.553
|  | EV07 | Diversity correction factor | Applicable across all | Slow/fast public | N/A | N/A | GB | All | N/A (scaling factor) | 1.46 | 1.46 | 1.46
|  | EV07 | Diversity correction factor | Applicable across all | Rapid public | N/A | N/A | GB | All | N/A (scaling factor) | 1.989 | 1.989 | 1.989
|  | EV07 | Diversity correction factor | Applicable across all | HGV depot | N/A | N/A | GB | All | N/A (scaling factor) | 5.776 | 5.776 | 5.776
| EV09 | EV09 | Charge point utilisation | Applicable across all | Domestic | N/A | N/A | GB | All | h/year | 244 | 244 | 244
|  | EV09 | Charge point utilisation | Applicable across all | Workplace | N/A | N/A | GB | All | h/year | 870 | 870 | 870
|  | EV09 | Charge point utilisation | Applicable across all | Slow/fast public | N/A | N/A | GB | All | h/year | 1164 | 1164 | 1164
|  | EV09 | Charge point utilisation | Applicable across all | Rapid public | N/A | N/A | GB | All | h/year | 1175 | 1175 | 1175
|  | EV09 | Charge point utilisation | Applicable across all | HGV depot | N/A | N/A | GB | All | h/year | 1175 | 1175 | 1175
| EV10 | EV10 | Size of chargers | Applicable across all | Domestic | N/A | N/A | GB | All | kW | 7 | 7 | 7
|  | EV10 | Size of chargers | Applicable across all | Workplace | N/A | N/A | GB | All | kW | 7 | 7 | 22
|  | EV10 | Size of chargers | Applicable across all | Slow/fast public | N/A | N/A | GB | All | kW | 22 | 7 | 22
|  | EV10 | Size of chargers | Applicable across all | Rapid public | N/A | N/A | GB | All | kW | 50 | 50 | 150
|  | EV10 | Size of chargers | Applicable across all | HGV depot | N/A | N/A | GB | All | kW | 150 | 50 | 1000
| EV06 | [8 empty] | Domestic | Domestic | Domestic
|  | Table unit: kW/annual kWh | Domestic | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot |  | Default | Lower range | Upper range
|  | Half hour start time | No flexibility | Flexibility (static TouT) | No flexibility | No flexibility | No flexibility | No flexibility |  | Weighted average flexibility, no flexibility | Weighted average flexibility, no flexibility | Weighted average flexibility, no flexibility
|  | 0:00 | 0.00011684 | 0.00023851 | 2.2105e-05 | 3.0067e-05 | 3.4021e-05 | 0.00018804 |  | 0.0002081 | 0.0002081 | 0.0002081
|  | 0:30 | 9.7899e-05 | 0.00027227 | 1.9169e-05 | 2.7307e-05 | 2.6311e-05 | 0.00017903 |  | 0.00022868 | 0.00022868 | 0.00022868
|  | 1:00 | 7.8957e-05 | 0.00026855 | 1.6233e-05 | 2.4547e-05 | 2.1532e-05 | 0.00017948 |  | 0.00022115 | 0.00022115 | 0.00022115
|  | 1:30 | 6.4322e-05 | 0.00025298 | 1.4636e-05 | 2.1889e-05 | 1.6754e-05 | 0.00017993 |  | 0.00020582 | 0.00020582 | 0.00020582
|  | 2:00 | 4.9687e-05 | 0.00025539 | 1.304e-05 | 1.923e-05 | 1.3865e-05 | 0.00018041 |  | 0.00020397 | 0.00020397 | 0.00020397
|  | 2:30 | 4.0844e-05 | 0.00024334 | 1.2529e-05 | 1.7239e-05 | 1.0976e-05 | 0.0001809 |  | 0.00019271 | 0.00019271 | 0.00019271
|  | 3:00 | 3.2001e-05 | 0.00022646 | 1.2017e-05 | 1.5247e-05 | 9.693e-06 | 0.0001761 |  | 0.00017784 | 0.00017784 | 0.00017784
|  | 3:30 | 2.7057e-05 | 0.00019905 | 1.2361e-05 | 1.4751e-05 | 8.41e-06 | 0.0001713 |  | 0.00015605 | 0.00015605 | 0.00015605
|  | 4:00 | 2.2113e-05 | 0.00016946 | 1.2704e-05 | 1.4255e-05 | 8.718e-06 | 0.00015844 |  | 0.00013262 | 0.00013262 | 0.00013262
|  | 4:30 | 1.9747e-05 | 0.00013438 | 1.6659e-05 | 1.7434e-05 | 9.027e-06 | 0.00014559 |  | 0.00010572 | 0.00010572 | 0.00010572
|  | 5:00 | 1.7381e-05 | 0.00010391 | 2.0613e-05 | 2.0613e-05 | 1.2922e-05 | 0.00012918 |  | 8.2279e-05 | 8.2279e-05 | 8.2279e-05
|  | 5:30 | 1.762e-05 | 8.3743e-05 | 4.8411e-05 | 3.1794e-05 | 1.6817e-05 | 0.00011277 |  | 6.7212e-05 | 6.7212e-05 | 6.7212e-05
|  | 6:00 | 1.786e-05 | 7.0151e-05 | 7.6209e-05 | 4.2975e-05 | 3.04e-05 | 0.00010168 |  | 5.7078e-05 | 5.7078e-05 | 5.7078e-05
|  | 6:30 | 2.1212e-05 | 5.3929e-05 | 0.00015966 | 7.179e-05 | 4.3983e-05 | 9.0598e-05 |  | 4.5749e-05 | 4.5749e-05 | 4.5749e-05
|  | 7:00 | 2.4564e-05 | 5.5244e-05 | 0.0002431 | 0.00010061 | 6.1363e-05 | 8.1176e-05 |  | 4.7574e-05 | 4.7574e-05 | 4.7574e-05
|  | 7:30 | 3.1427e-05 | 4.779e-05 | 0.00033215 | 0.00015017 | 7.8744e-05 | 7.1753e-05 |  | 4.37e-05 | 4.37e-05 | 4.37e-05
|  | 8:00 | 3.829e-05 | 3.5952e-05 | 0.00042121 | 0.00019973 | 9.7966e-05 | 6.4773e-05 |  | 3.6537e-05 | 3.6537e-05 | 3.6537e-05
|  | 8:30 | 4.752e-05 | 4.1652e-05 | 0.00040129 | 0.00023046 | 0.00011719 | 5.7793e-05 |  | 4.3119e-05 | 4.3119e-05 | 4.3119e-05
|  | 9:00 | 5.675e-05 | 4.1214e-05 | 0.00038137 | 0.00026119 | 0.00013441 | 5.2413e-05 |  | 4.5098e-05 | 4.5098e-05 | 4.5098e-05
|  | 9:30 | 6.0655e-05 | 4.2967e-05 | 0.00031601 | 0.00025312 | 0.00015162 | 4.7033e-05 |  | 4.7389e-05 | 4.7389e-05 | 4.7389e-05
|  | 10:00 | 6.456e-05 | 4.5598e-05 | 0.00025065 | 0.00024506 | 0.0001579 | 4.3441e-05 |  | 5.0339e-05 | 5.0339e-05 | 5.0339e-05
|  | 10:30 | 6.9604e-05 | 4.8667e-05 | 0.0002184 | 0.000232 | 0.00016418 | 3.9849e-05 |  | 5.3901e-05 | 5.3901e-05 | 5.3901e-05
|  | 11:00 | 7.4649e-05 | 4.9106e-05 | 0.00018614 | 0.00021895 | 0.000173 | 3.8006e-05 |  | 5.5492e-05 | 5.5492e-05 | 5.5492e-05
|  | 11:30 | 8.0345e-05 | 5.2613e-05 | 0.00017882 | 0.0002137 | 0.00018181 | 3.6162e-05 |  | 5.9546e-05 | 5.9546e-05 | 5.9546e-05
|  | 12:00 | 8.6042e-05 | 5.349e-05 | 0.00017149 | 0.00020846 | 0.00019324 | 3.5044e-05 |  | 6.1628e-05 | 6.1628e-05 | 6.1628e-05
|  | 12:30 | 9.0079e-05 | 5.5244e-05 | 0.00017135 | 0.00020541 | 0.00020467 | 3.3927e-05 |  | 6.3953e-05 | 6.3953e-05 | 6.3953e-05
|  | 13:00 | 9.4115e-05 | 5.5244e-05 | 0.00017121 | 0.00020237 | 0.00020991 | 3.3578e-05 |  | 6.4962e-05 | 6.4962e-05 | 6.4962e-05
|  | 13:30 | 9.629e-05 | 5.8751e-05 | 0.00015999 | 0.00019464 | 0.00021515 | 3.3229e-05 |  | 6.8136e-05 | 6.8136e-05 | 6.8136e-05
|  | 14:00 | 9.8465e-05 | 5.8751e-05 | 0.00014876 | 0.00018691 | 0.00021228 | 3.3868e-05 |  | 6.868e-05 | 6.868e-05 | 6.868e-05
|  | 14:30 | 0.00010697 | 5.5244e-05 | 0.00013754 | 0.00017571 | 0.00020941 | 3.4507e-05 |  | 6.8175e-05 | 6.8175e-05 | 6.8175e-05
|  | 15:00 | 0.00011547 | 5.5682e-05 | 0.00012632 | 0.00016451 | 0.00020642 | 3.7996e-05 |  | 7.0629e-05 | 7.0629e-05 | 7.0629e-05
|  | 15:30 | 0.00013637 | 5.8313e-05 | 0.00011637 | 0.00015631 | 0.00020343 | 4.1485e-05 |  | 7.7826e-05 | 7.7826e-05 | 7.7826e-05
|  | 16:00 | 0.00015726 | 6.9713e-05 | 0.00010642 | 0.00014811 | 0.0002012 | 5.0856e-05 |  | 9.16e-05 | 9.16e-05 | 9.16e-05
|  | 16:30 | 0.00018485 | 7.5412e-05 | 9.6531e-05 | 0.00014477 | 0.00019897 | 6.0227e-05 |  | 0.00010277 | 0.00010277 | 0.00010277
|  | 17:00 | 0.00021243 | 8.3304e-05 | 8.6642e-05 | 0.00014142 | 0.00019819 | 7.9237e-05 |  | 0.00011559 | 0.00011559 | 0.00011559
|  | 17:30 | 0.00023898 | 9.2512e-05 | 7.7456e-05 | 0.0001401 | 0.0001974 | 9.8246e-05 |  | 0.00012913 | 0.00012913 | 0.00012913
|  | 18:00 | 0.00026553 | 0.00010084 | 6.827e-05 | 0.00013877 | 0.00019522 | 0.00012581 |  | 0.00014201 | 0.00014201 | 0.00014201
|  | 18:30 | 0.00027015 | 0.0001118 | 6.198e-05 | 0.0001299 | 0.00019305 | 0.00015337 |  | 0.00015139 | 0.00015139 | 0.00015139
|  | 19:00 | 0.00027477 | 0.00011794 | 5.569e-05 | 0.00012103 | 0.00017954 | 0.00016919 |  | 0.00015715 | 0.00015715 | 0.00015715
|  | 19:30 | 0.0002653 | 0.00012233 | 5.0528e-05 | 0.00010582 | 0.00016603 | 0.00018501 |  | 0.00015807 | 0.00015807 | 0.00015807
|  | 20:00 | 0.00025583 | 0.00012671 | 4.5367e-05 | 9.0622e-05 | 0.00014787 | 0.0001892 |  | 0.00015899 | 0.00015899 | 0.00015899
|  | 20:30 | 0.00024177 | 0.00014074 | 4.2372e-05 | 7.6743e-05 | 0.00012971 | 0.00019338 |  | 0.000166 | 0.000166 | 0.000166
|  | 21:00 | 0.00022771 | 0.00014469 | 3.9377e-05 | 6.2864e-05 | 0.00011128 | 0.00019624 |  | 0.00016544 | 0.00016544 | 0.00016544
|  | 21:30 | 0.00021337 | 0.00014732 | 3.7627e-05 | 5.4334e-05 | 9.2843e-05 | 0.00019909 |  | 0.00016383 | 0.00016383 | 0.00016383
|  | 22:00 | 0.00019904 | 0.00014907 | 3.5877e-05 | 4.5803e-05 | 7.7174e-05 | 0.0001983 |  | 0.00016156 | 0.00016156 | 0.00016156
|  | 22:30 | 0.00017922 | 0.00015433 | 3.2388e-05 | 4.11e-05 | 6.1505e-05 | 0.0001975 |  | 0.00016056 | 0.00016056 | 0.00016056
|  | 23:00 | 0.00015941 | 0.00017231 | 2.8899e-05 | 3.6398e-05 | 5.1619e-05 | 0.00019728 |  | 0.00016908 | 0.00016908 | 0.00016908
|  | 23:30 | 0.00013813 | 0.00018678 | 2.5502e-05 | 3.3232e-05 | 4.1732e-05 | 0.00019705 |  | 0.00017461 | 0.00017461 | 0.00017461
End-to-end calculation
|  |  | Parameter | Detail | Vehicle type | Charger type | Unit | Value - Default | Lower range | Upper range | [5 empty] | Parameter | Detail | Vehicle type | Charger type | Unit | Value - Default | Lower range | Upper range
| 1. Check if diversity correction is required |  | Diversity correction check | Domestic charging |  | Domestic | Y/N | Y | Y | Y |  | 5. Find installed capacity of chargers by type |  |  |  | Installed capacity of chargers | Domestic charging capacity | All | Domestic | Y/N | 772.836 | 672.0632 | 888.8833
|  |  | Diversity correction check | Workplace charging |  | Workplace | Y/N | Y | Y | Y | [5 empty] | Installed capacity of chargers | Workplace charging capacity | All | Workplace | Y/N | 41.9182 | 32.8696 | 51.1535
|  |  | Diversity correction check | Public slow/fast charging |  | Slow/fast public | Y/N | Y | Y | Y | [5 empty] | Installed capacity of chargers | Slow/fast public charging capacity | All | Slow/fast public | Y/N | 12.1118 | 2.1497 | 24.7595
|  |  | Diversity correction check | Public rapid charging |  | Rapid public | Y/N | Y | Y | Y | [5 empty] | Installed capacity of chargers | Rapid public charging capacity | All | Rapid public | Y/N | 66.4956 | 51.5889 | 81.4023
|  |  | Diversity correction check | HGV depot |  | HGV depot | Y/N | Y | Y | Y | [5 empty] | Installed capacity of chargers | HGV depot charging capacity | All | HGV depot | Y/N | 406.8031 | 406.8031 | 406.8031
| 2. Calculate annual electricity demand by vehicle type |  | Annual energy demand | Battery electric cars, vans, motorcycles | Lct_BB001 | All | kWh | 250219.54 | 250219.54 | 250219.54 |  | 6. Convert charger capacity to number of charge points |  |  |  | Number of charge points | Number of domestic charge points | All | Domestic | Y/N | 110.4051 | 96.009 | 126.9833
|  |  | Annual energy demand | Plug-in hybrid electric cars, vans, motorcycles | Lct_BB002 | All | kWh | 13941.383 | 8936.784 | 22341.96 | [5 empty] | Number of charge points | Number of workplace charge points | All | Workplace | Y/N | 5.9883 | 1.4941 | 7.3076
|  |  | Annual energy demand | Battery electric buses and HGVs | Lct_BB003 | All | kWh | 531104 | 531104 | 531104 | [5 empty] | Number of charge points | Number of slow/fast public charge points | All | Slow/fast public | Y/N | 0.55054 | 0.097711 | 3.5371
|  |  | Annual energy demand | Plug-in hybrid buses and HGVs | Lct_BB004 | All | kWh | 0 | 0 | 0 | [5 empty] | Number of charge points | Number of rapid public charge points | All | Rapid public | Y/N | 1.3299 | 0.34393 | 1.628
[16 empty] | Number of charge points | Number of HGV depot charge points | All | HGV depot | Y/N | 2.712 | 0.4068 | 8.1361
| 3. Calculate annual electricity demand by charger type |  | Annual energy demand | Domestic charging | All | Domestic | kWh | 188571.9763 | 163983.4268 | 216887.5222
|  |  | Annual energy demand | Workplace charging | All | Workplace | kWh | 36468.8741 | 28596.5635 | 44503.5184 |  | 7. (Optional) Round Number of charge points to integer |  |  |  | Number of charge points (rounded) | Number of domestic charge points (rounded) | All | Domestic | Y/N | 111 | 97 | 127
|  |  | Annual energy demand | Public slow/fast charging | All | Slow/fast public | kWh | 14098.1186 | 2502.1954 | 28820.0872 |  | Note: rounds all values up |  |  |  | Number of charge points (rounded) | Number of workplace charge points (rounded) | All | Workplace | Y/N | 6 | 2 | 8
|  |  | Annual energy demand | Public rapid charging | All | Rapid public | kWh | 78132.354 | 60616.9862 | 95647.7218 | [5 empty] | Number of charge points (rounded) | Number of slow/fast public charge points (rounded) | All | Slow/fast public | Y/N | 1 | 1 | 4
|  |  | Annual energy demand | HGV depot | All | HGV depot | kWh | 477993.6 | 477993.6 | 477993.6 | [5 empty] | Number of charge points (rounded) | Number of rapid public charge points (rounded) | All | Rapid public | Y/N | 2 | 1 | 2
[16 empty] | Number of charge points (rounded) | Number of HGV depot charge points (rounded) | All | HGV depot | Y/N | 3 | 1 | 9
| 3.1 (Alternative step for graphs) Calculate annual electricity demand by charger type for small EVs only |  | Small EVs only:
|  |  | Annual energy demand | Domestic charging | Lct_BB001, Lct_BB002 | Domestic | kWh | 188571.9763 | 163983.4268 | 216887.5222
|  |  | Annual energy demand | Workplace charging | Lct_BB001, Lct_BB002 | Workplace | kWh | 36468.8741 | 28596.5635 | 44503.5184
|  |  | Annual energy demand | Public slow/fast charging | Lct_BB001, Lct_BB002 | Slow/fast public | kWh | 14098.1186 | 2502.1954 | 28820.0872
|  |  | Annual energy demand | Public rapid charging | Lct_BB001, Lct_BB002 | Rapid public | kWh | 25021.954 | 7506.5862 | 42537.3218
|  |  | Annual energy demand | HGV depot | Lct_BB001, Lct_BB002 | HGV depot | kWh | 0 | 0 | 0
| 3.2 (Alternative step for graphs) Calculate annual electricity demand by charger type for large EVs only |  | Large EVs only:
|  |  | Annual energy demand | Domestic charging | Lct_BB003, Lct_BB004 | Domestic | kWh | 0 | 0 | 0
|  |  | Annual energy demand | Workplace charging | Lct_BB003, Lct_BB004 | Workplace | kWh | 0 | 0 | 0
|  |  | Annual energy demand | Public slow/fast charging | Lct_BB003, Lct_BB004 | Slow/fast public | kWh | 0 | 0 | 0
|  |  | Annual energy demand | Public rapid charging | Lct_BB003, Lct_BB004 | Rapid public | kWh | 53110.4 | 53110.4 | 53110.4
|  |  | Annual energy demand | HGV depot | Lct_BB003, Lct_BB004 | HGV depot | kWh | 477993.6 | 477993.6 | 477993.6
4. Apply half-hourly profiles and find peak demand values in the day and its time. This is done for each charger type for default values, lower range values, and upper range values.
| All EVs - Default values | [9 empty] | All EVs - Lower range values | [9 empty] | All EVs - Upper range values
|  |  | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  |  | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  |  | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV
| Parameter | Unit | Default | Default | Default | Default | Default | Default | Default |  | Parameter | Unit | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range |  | Parameter | Unit | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range
| Peak demand | kW | 84.0891 | 23.8554 | 5.3761 | 33.4354 | 549.6686 | 627.5896 | 5.2299 |  | Peak demand | kW | 73.1245 | 18.7059 | 0.95417 | 25.94 | 549.6686 | 615.1199 | 5.126 |  | Peak demand | kW | 96.7158 | 29.1111 | 10.99 | 40.9309 | 549.6686 | 641.5074 | 5.3459
| Time of peak demand | Half hour start time | 0:30 | 8:00 | 9:00 | 13:30 | 21:30 | 21:30 | 21:30 |  | Time of peak demand | Half hour start time | 0:30 | 8:00 | 9:00 | 13:30 | 21:30 | 21:30 | 21:30 |  | Time of peak demand | Half hour start time | 0:30 | 8:00 | 9:00 | 13:30 | 21:30 | 21:30 | 21:30
|  | Table unit: kW | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  | Table unit: kW | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  | Table unit: kW | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV
|  | Half hour start time | Default | Default | Default | Default | Default | Default | Default |  |  | Half hour start time | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range |  |  | Half hour start time | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range
| 1 | 0:00 | 76.5199 | 1.2519 | 0.61887 | 5.287 | 519.1607 | 602.8385 | 5.0237 |  |  | 0:00 | 66.5422 | 0.98169 | 0.10984 | 4.1018 | 519.1607 | 590.8963 | 4.9241 |  |  | 0:00 | 88.01 | 1.5278 | 1.2651 | 6.4723 | 519.1607 | 616.4359 | 5.137
| 2 | 0:30 | 84.0891 | 1.0857 | 0.56207 | 4.0889 | 494.2823 | 584.1081 | 4.8676 |  |  | 0:30 | 73.1245 | 0.8513 | 0.099758 | 3.1722 | 494.2823 | 571.5301 | 4.7628 |  |  | 0:30 | 96.7158 | 1.3248 | 1.149 | 5.0055 | 494.2823 | 598.4774 | 4.9873
| 3 | 1:00 | 81.32 | 0.91937 | 0.50526 | 3.3462 | 495.5247 | 581.6156 | 4.8468 |  |  | 1:00 | 70.7164 | 0.72092 | 0.089677 | 2.5961 | 495.5247 | 569.6478 | 4.7471 |  |  | 1:00 | 93.5309 | 1.1219 | 1.0329 | 4.0963 | 495.5247 | 595.3067 | 4.9609
| 4 | 1:30 | 75.6821 | 0.82893 | 0.45054 | 2.6037 | 496.7671 | 576.3324 | 4.8028 |  |  | 1:30 | 65.8136 | 0.64999 | 0.079965 | 2.02 | 496.7671 | 565.3307 | 4.7111 |  |  | 1:30 | 87.0464 | 1.0116 | 0.92103 | 3.1873 | 496.7671 | 588.9334 | 4.9078
| 5 | 2:00 | 75.0018 | 0.73854 | 0.39582 | 2.1547 | 498.1034 | 576.3942 | 4.8033 |  |  | 2:00 | 65.222 | 0.57911 | 0.070253 | 1.6717 | 498.1034 | 565.6464 | 4.7137 |  |  | 2:00 | 86.2639 | 0.90125 | 0.80916 | 2.6377 | 498.1034 | 588.7154 | 4.906
| 6 | 2:30 | 70.8636 | 0.70959 | 0.35483 | 1.7057 | 499.4397 | 573.0734 | 4.7756 |  |  | 2:30 | 61.6235 | 0.55642 | 0.062977 | 1.3233 | 499.4397 | 563.0059 | 4.6917 |  |  | 2:30 | 81.5043 | 0.86593 | 0.72537 | 2.0881 | 499.4397 | 584.6234 | 4.8719
| 7 | 3:00 | 65.3954 | 0.6806 | 0.31384 | 1.5063 | 486.1846 | 554.0808 | 4.6173 |  |  | 3:00 | 56.8683 | 0.53368 | 0.055702 | 1.1687 | 486.1846 | 544.8109 | 4.5401 |  |  | 3:00 | 75.215 | 0.83054 | 0.64157 | 1.844 | 486.1846 | 564.7158 | 4.706
| 8 | 3:30 | 57.3836 | 0.70008 | 0.30363 | 1.307 | 472.9324 | 532.6266 | 4.4386 |  |  | 3:30 | 49.9011 | 0.54896 | 0.053889 | 1.014 | 472.9324 | 524.4503 | 4.3704 |  |  | 3:30 | 66.0002 | 0.85432 | 0.62069 | 1.5999 | 472.9324 | 542.0075 | 4.5167
| 9 | 4:00 | 48.7672 | 0.71951 | 0.29341 | 1.3548 | 437.4439 | 488.5788 | 4.0715 |  |  | 4:00 | 42.4083 | 0.56419 | 0.052076 | 1.0511 | 437.4439 | 481.5195 | 4.0127 |  |  | 4:00 | 56.09 | 0.87802 | 0.59981 | 1.6585 | 437.4439 | 496.6702 | 4.1389
| 10 | 4:30 | 38.8763 | 0.9435 | 0.35885 | 1.4028 | 401.9554 | 443.5369 | 3.6961 |  |  | 4:30 | 33.8071 | 0.73983 | 0.06369 | 1.0884 | 401.9554 | 437.6544 | 3.6471 |  |  | 4:30 | 44.7139 | 1.1514 | 0.73357 | 1.7173 | 401.9554 | 450.2716 | 3.7523
| 11 | 5:00 | 30.2551 | 1.1674 | 0.42428 | 2.0081 | 356.6491 | 390.5041 | 3.2542 |  |  | 5:00 | 26.3101 | 0.91543 | 0.075303 | 1.558 | 356.6491 | 385.5079 | 3.2126 |  |  | 5:00 | 34.7982 | 1.4246 | 0.86734 | 2.4583 | 356.6491 | 396.1976 | 3.3016
| 12 | 5:30 | 24.7149 | 2.7418 | 0.65442 | 2.6135 | 311.3457 | 342.0703 | 2.8506 |  |  | 5:30 | 21.4923 | 2.15 | 0.11615 | 2.0276 | 311.3457 | 337.1316 | 2.8094 |  |  | 5:30 | 28.4261 | 3.3459 | 1.3378 | 3.1993 | 311.3457 | 347.6547 | 2.8971
| 13 | 6:00 | 20.9886 | 4.3162 | 0.88457 | 4.7243 | 280.7384 | 311.6521 | 2.5971 |  |  | 6:00 | 18.2518 | 3.3845 | 0.157 | 3.6652 | 280.7384 | 306.1969 | 2.5516 |  |  | 6:00 | 24.1401 | 5.2671 | 1.8083 | 5.7834 | 280.7384 | 317.7374 | 2.6478
| 14 | 6:30 | 16.8228 | 9.0424 | 1.4777 | 6.8352 | 250.1312 | 284.3092 | 2.3692 |  |  | 6:30 | 14.6292 | 7.0904 | 0.26227 | 5.3029 | 250.1312 | 277.416 | 2.3118 |  |  | 6:30 | 19.3488 | 11.0345 | 3.0208 | 8.3675 | 250.1312 | 291.9028 | 2.4325
| 15 | 7:00 | 17.4937 | 13.7685 | 2.0708 | 9.5361 | 224.1181 | 266.9872 | 2.2249 |  |  | 7:00 | 15.2126 | 10.7964 | 0.36753 | 7.3984 | 224.1181 | 257.893 | 2.1491 |  |  | 7:00 | 20.1205 | 16.8019 | 4.2332 | 11.6739 | 224.1181 | 276.9476 | 2.3079
| 16 | 7:30 | 16.069 | 18.8119 | 3.0909 | 12.2372 | 198.1022 | 248.3113 | 2.0693 |  |  | 7:30 | 13.9737 | 14.7511 | 0.54859 | 9.4939 | 198.1022 | 236.8696 | 1.9739 |  |  | 7:30 | 18.4819 | 22.9565 | 6.3186 | 14.9805 | 198.1022 | 260.8397 | 2.1737
| 17 | 8:00 | 13.4351 | 23.8554 | 4.111 | 15.2244 | 178.8312 | 235.4572 | 1.9621 |  |  | 8:00 | 11.6833 | 18.7059 | 0.72965 | 11.8115 | 178.8312 | 221.7615 | 1.848 |  |  | 8:00 | 15.4525 | 29.1111 | 8.404 | 18.6374 | 178.8312 | 250.4363 | 2.087
| 18 | 8:30 | 15.8556 | 22.7274 | 4.7436 | 18.2116 | 159.5602 | 221.0983 | 1.8425 |  |  | 8:30 | 13.7881 | 17.8213 | 0.84191 | 14.129 | 159.5602 | 206.1406 | 1.7178 |  |  | 8:30 | 18.2364 | 27.7345 | 9.697 | 22.2942 | 159.5602 | 237.5224 | 1.9794
| 19 | 9:00 | 16.5832 | 21.5993 | 5.3761 | 20.8874 | 144.7066 | 209.1525 | 1.7429 |  |  | 9:00 | 14.4208 | 16.9368 | 0.95417 | 16.205 | 144.7066 | 193.2233 | 1.6102 |  |  | 9:00 | 19.0732 | 26.3579 | 10.99 | 25.5698 | 144.7066 | 226.6976 | 1.8891
| 20 | 9:30 | 17.4258 | 17.8977 | 5.2101 | 23.5632 | 129.853 | 193.9497 | 1.6162 |  |  | 9:30 | 15.1536 | 14.0342 | 0.92471 | 18.2809 | 129.853 | 178.2464 | 1.4854 |  |  | 9:30 | 20.0424 | 21.8408 | 10.6508 | 28.8455 | 129.853 | 211.2324 | 1.7603
| 21 | 10:00 | 18.5103 | 14.196 | 5.0442 | 24.5385 | 119.9359 | 182.2248 | 1.5185 |  |  | 10:00 | 16.0967 | 11.1316 | 0.89526 | 19.0376 | 119.9359 | 167.097 | 1.3925 |  |  | 10:00 | 21.2897 | 17.3236 | 10.3115 | 30.0394 | 119.9359 | 198.9002 | 1.6575
| 22 | 10:30 | 19.8204 | 12.3693 | 4.7754 | 25.5138 | 110.0187 | 172.4976 | 1.4375 |  |  | 10:30 | 17.2359 | 9.6992 | 0.84756 | 19.7942 | 110.0187 | 157.5957 | 1.3133 |  |  | 10:30 | 22.7966 | 15.0944 | 9.7621 | 31.2334 | 110.0187 | 188.9052 | 1.5742
| 23 | 11:00 | 20.4051 | 10.5425 | 4.5066 | 26.8845 | 104.9304 | 167.2691 | 1.3939 |  |  | 11:00 | 17.7444 | 8.2667 | 0.79986 | 20.8576 | 104.9304 | 152.5991 | 1.2717 |  |  | 11:00 | 23.4691 | 12.8651 | 9.2127 | 32.9113 | 104.9304 | 183.3886 | 1.5282
| 24 | 11:30 | 21.8961 | 10.1276 | 4.3987 | 28.255 | 99.8393 | 164.5167 | 1.371 |  |  | 11:30 | 19.0409 | 7.9414 | 0.7807 | 21.9209 | 99.8393 | 149.5233 | 1.246 |  |  | 11:30 | 25.1839 | 12.3589 | 8.992 | 34.5891 | 99.8393 | 180.9633 | 1.508
| 25 | 12:00 | 22.6616 | 9.7127 | 4.2908 | 30.0307 | 96.7527 | 163.4484 | 1.3621 |  |  | 12:00 | 19.7067 | 7.6161 | 0.76154 | 23.2985 | 96.7527 | 148.1355 | 1.2345 |  |  | 12:00 | 26.0644 | 11.8526 | 8.7714 | 36.7628 | 96.7527 | 180.2038 | 1.5017
| 26 | 12:30 | 23.5164 | 9.7047 | 4.228 | 31.8065 | 93.6688 | 162.9244 | 1.3577 |  |  | 12:30 | 20.45 | 7.6098 | 0.75041 | 24.6762 | 93.6688 | 147.1552 | 1.2263 |  |  | 12:30 | 27.0476 | 11.8428 | 8.6432 | 38.9367 | 93.6688 | 180.139 | 1.5012
| 27 | 13:00 | 23.8874 | 9.6967 | 4.1653 | 32.621 | 92.7052 | 163.0756 | 1.359 |  |  | 13:00 | 20.7727 | 7.6036 | 0.73928 | 25.3081 | 92.7052 | 147.1288 | 1.2261 |  |  | 13:00 | 27.4743 | 11.8331 | 8.515 | 39.9338 | 92.7052 | 180.4613 | 1.5038
| 28 | 13:30 | 25.0547 | 9.061 | 4.0063 | 33.4354 | 91.7416 | 163.2991 | 1.3608 |  |  | 13:30 | 21.7877 | 7.1051 | 0.71106 | 25.94 | 91.7416 | 147.2856 | 1.2274 |  |  | 13:30 | 28.8168 | 11.0573 | 8.1899 | 40.9309 | 91.7416 | 180.7366 | 1.5061
| 29 | 14:00 | 25.2546 | 8.4254 | 3.8473 | 32.9894 | 93.5059 | 164.0226 | 1.3669 |  |  | 14:00 | 21.9616 | 6.6067 | 0.68284 | 25.594 | 93.5059 | 148.351 | 1.2363 |  |  | 14:00 | 29.0468 | 10.2817 | 7.8648 | 40.3849 | 93.5059 | 181.084 | 1.509
| 30 | 14:30 | 25.0689 | 7.7899 | 3.6167 | 32.5434 | 95.2701 | 164.2889 | 1.3691 |  |  | 14:30 | 21.8001 | 6.1083 | 0.6419 | 25.248 | 95.2701 | 149.0683 | 1.2422 |  |  | 14:30 | 28.8332 | 9.5061 | 7.3934 | 39.8389 | 95.2701 | 180.8416 | 1.507
| 31 | 15:00 | 25.9714 | 7.1543 | 3.3861 | 32.0791 | 104.9028 | 173.4937 | 1.4458 |  |  | 15:00 | 22.5849 | 5.61 | 0.60097 | 24.8877 | 104.9028 | 158.5864 | 1.3216 |  |  | 15:00 | 29.8712 | 8.7305 | 6.922 | 39.2704 | 104.9028 | 189.6969 | 1.5808
| 32 | 15:30 | 28.6179 | 6.5908 | 3.2173 | 31.6147 | 114.5356 | 184.5763 | 1.5381 |  |  | 15:30 | 24.8863 | 5.168 | 0.57103 | 24.5275 | 114.5356 | 169.6884 | 1.4141 |  |  | 15:30 | 32.9151 | 8.0428 | 6.5771 | 38.702 | 114.5356 | 200.7725 | 1.6731
| 33 | 16:00 | 33.6828 | 6.0272 | 3.0486 | 31.2675 | 140.4079 | 214.4341 | 1.787 |  |  | 16:00 | 29.2908 | 4.7262 | 0.54108 | 24.2581 | 140.4079 | 199.224 | 1.6602 |  |  | 16:00 | 38.7405 | 7.3551 | 6.2322 | 38.277 | 140.4079 | 231.0126 | 1.9251
| 34 | 16:30 | 37.7904 | 5.4671 | 2.9798 | 30.9205 | 166.2802 | 243.438 | 2.0287 |  |  | 16:30 | 32.8628 | 4.287 | 0.52887 | 23.9889 | 166.2802 | 227.9477 | 1.8996 |  |  | 16:30 | 43.4649 | 6.6716 | 6.0915 | 37.8521 | 166.2802 | 260.3603 | 2.1697
| 35 | 17:00 | 42.5026 | 4.9071 | 2.911 | 30.799 | 218.7647 | 299.8843 | 2.499 |  |  | 17:00 | 36.9605 | 3.8478 | 0.51665 | 23.8946 | 218.7647 | 283.9843 | 2.3665 |  |  | 17:00 | 48.8847 | 5.9882 | 5.9508 | 37.7034 | 218.7647 | 317.2917 | 2.6441
| 36 | 17:30 | 47.4826 | 4.3868 | 2.8837 | 30.6775 | 271.2465 | 356.6771 | 2.9723 |  |  | 17:30 | 41.2912 | 3.4399 | 0.51181 | 23.8003 | 271.2465 | 340.2897 | 2.8357 |  |  | 17:30 | 54.6125 | 5.3533 | 5.8949 | 37.5546 | 271.2465 | 374.6618 | 3.1222
| 37 | 18:00 | 52.2209 | 3.8666 | 2.8564 | 30.339 | 347.3394 | 436.6223 | 3.6385 |  |  | 18:00 | 45.4117 | 3.0319 | 0.50696 | 23.5377 | 347.3394 | 419.8277 | 3.4986 |  |  | 18:00 | 60.0623 | 4.7184 | 5.8391 | 37.1403 | 347.3394 | 455.0995 | 3.7925
| 38 | 18:30 | 55.6687 | 3.5103 | 2.6737 | 30.0004 | 423.4323 | 515.2854 | 4.294 |  |  | 18:30 | 48.4098 | 2.7526 | 0.47454 | 23.275 | 423.4323 | 498.3443 | 4.1529 |  |  | 18:30 | 64.0277 | 4.2837 | 5.4658 | 36.7257 | 423.4323 | 533.9352 | 4.4495
| 39 | 19:00 | 57.7862 | 3.1541 | 2.4911 | 27.9015 | 467.1152 | 558.448 | 4.6537 |  |  | 19:00 | 50.2513 | 2.4732 | 0.44213 | 21.6466 | 467.1152 | 541.9284 | 4.5161 |  |  | 19:00 | 66.4633 | 3.849 | 5.0924 | 34.1563 | 467.1152 | 576.6761 | 4.8056
| 40 | 19:30 | 58.1245 | 2.8617 | 2.1782 | 25.8026 | 510.798 | 599.765 | 4.998 |  |  | 19:30 | 50.5455 | 2.244 | 0.3866 | 20.0183 | 510.798 | 583.9923 | 4.8666 |  |  | 19:30 | 66.8524 | 3.4922 | 4.4528 | 31.5869 | 510.798 | 617.1822 | 5.1432
| 41 | 20:00 | 58.4628 | 2.5694 | 1.8653 | 22.9801 | 522.3495 | 608.2271 | 5.0686 |  |  | 20:00 | 50.8396 | 2.0148 | 0.33106 | 17.8285 | 522.3495 | 593.3635 | 4.9447 |  |  | 20:00 | 67.2414 | 3.1355 | 3.8131 | 28.1317 | 522.3495 | 624.6712 | 5.2056
| 42 | 20:30 | 61.0399 | 2.3998 | 1.5796 | 20.1575 | 533.8983 | 619.0751 | 5.159 |  |  | 20:30 | 53.0807 | 1.8818 | 0.28036 | 15.6386 | 533.8983 | 604.7798 | 5.0398 |  |  | 20:30 | 70.2055 | 2.9285 | 3.2291 | 24.6763 | 533.8983 | 634.9377 | 5.2911
| 43 | 21:00 | 60.8358 | 2.2302 | 1.2939 | 17.2929 | 541.7835 | 623.4362 | 5.1953 |  |  | 21:00 | 52.9032 | 1.7488 | 0.22965 | 13.4162 | 541.7835 | 610.0813 | 5.084 |  |  | 21:00 | 69.9708 | 2.7215 | 2.6451 | 21.1695 | 541.7835 | 638.2904 | 5.3191
| 44 | 21:30 | 60.2433 | 2.131 | 1.1184 | 14.4283 | 549.6686 | 627.5896 | 5.2299 |  |  | 21:30 | 52.388 | 1.671 | 0.19849 | 11.1938 | 549.6686 | 615.1199 | 5.126 |  |  | 21:30 | 69.2893 | 2.6006 | 2.2862 | 17.6628 | 549.6686 | 641.5074 | 5.3459
| 45 | 22:00 | 59.409 | 2.0319 | 0.94278 | 11.9932 | 547.4736 | 621.8506 | 5.1821 |  |  | 22:00 | 51.6624 | 1.5933 | 0.16733 | 9.3047 | 547.4736 | 610.2014 | 5.085 |  |  | 22:00 | 68.3297 | 2.4796 | 1.9273 | 14.6818 | 547.4736 | 634.8921 | 5.2908
| 46 | 22:30 | 59.0386 | 1.8343 | 0.84598 | 9.5582 | 545.2787 | 616.5559 | 5.138 |  |  | 22:30 | 51.3404 | 1.4384 | 0.15015 | 7.4155 | 545.2787 | 605.6231 | 5.0469 |  |  | 22:30 | 67.9037 | 2.2385 | 1.7294 | 11.7009 | 545.2787 | 628.8512 | 5.2404
| 47 | 23:00 | 62.1748 | 1.6367 | 0.74918 | 8.0219 | 544.6575 | 617.2401 | 5.1437 |  |  | 23:00 | 54.0676 | 1.2834 | 0.13297 | 6.2236 | 544.6575 | 606.3651 | 5.053 |  |  | 23:00 | 71.5108 | 1.9973 | 1.5315 | 9.8202 | 544.6575 | 629.5174 | 5.246
| 48 | 23:30 | 64.2084 | 1.4443 | 0.68403 | 6.4854 | 544.0391 | 616.8612 | 5.1405 |  |  | 23:30 | 55.836 | 1.1326 | 0.1214 | 5.0315 | 544.0391 | 606.1606 | 5.0513 |  |  | 23:30 | 73.8497 | 1.7625 | 1.3983 | 7.9392 | 544.0391 | 628.9889 | 5.2416
4.1 (Alternative step for graphs) Apply half-hourly profiles and find peak demand values and times for small EVs only.
| Small EVs only - Default values | [10 empty] | Small EVs only - Lower range values | [9 empty] | Small EVs only - Upper range values
|  |  | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  |  | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  |  | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV
| Parameter | Unit | Default | Default | Default | Default | Default | Default | Default |  | Parameter | Unit | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range |  | Parameter | Unit | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range
| Peak demand | kW | 84.0891 | 23.8554 | 5.3761 | 10.7077 | 0 | 87.0463 | 0.7772 |  | Peak demand | kW | 73.1245 | 18.7059 | 0.95417 | 3.2123 | 0 | 74.4684 | 0.6649 |  | Peak demand | kW | 96.7158 | 29.1111 | 10.99 | 18.2031 | 0 | 101.4157 | 0.9055
| Time of peak demand | Half hour start time | 0:30 | 8:00 | 9:00 | 13:30 | 0:00 | 0:30 | 0:30 |  | Time of peak demand | Half hour start time | 0:30 | 8:00 | 9:00 | 13:30 | 0:00 | 0:30 | 0:30 |  | Time of peak demand | Half hour start time | 0:30 | 8:00 | 9:00 | 13:30 | 0:00 | 0:30 | 0:30
|  | Table unit: kW | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  | Table unit: kW | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  | Table unit: kW | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV
|  | Half hour start time | Default | Default | Default | Default | Default | Default | Default |  |  | Half hour start time | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range |  |  | Half hour start time | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range
| 1 | 0:00 | 76.5199 | 1.2519 | 0.61887 | 1.6932 | 0 | 80.0839 | 0.71504 |  |  | 0:00 | 66.5422 | 0.98169 | 0.10984 | 0.50795 | 0 | 68.1417 | 0.60841 |  |  | 0:00 | 88.01 | 1.5278 | 1.2651 | 2.8784 | 0 | 93.6813 | 0.83644
| 2 | 0:30 | 84.0891 | 1.0857 | 0.56207 | 1.3095 | 0 | 87.0463 | 0.7772 |  |  | 0:30 | 73.1245 | 0.8513 | 0.099758 | 0.39284 | 0 | 74.4684 | 0.6649 |  |  | 0:30 | 96.7158 | 1.3248 | 1.149 | 2.2261 | 0 | 101.4157 | 0.9055
| 3 | 1:00 | 81.32 | 0.91937 | 0.50526 | 1.0716 | 0 | 83.8163 | 0.74836 |  |  | 1:00 | 70.7164 | 0.72092 | 0.089677 | 0.32149 | 0 | 71.8485 | 0.6415 |  |  | 1:00 | 93.5309 | 1.1219 | 1.0329 | 1.8218 | 0 | 97.5074 | 0.8706
| 4 | 1:30 | 75.6821 | 0.82893 | 0.45054 | 0.83382 | 0 | 77.7954 | 0.6946 |  |  | 1:30 | 65.8136 | 0.64999 | 0.079965 | 0.25015 | 0 | 66.7938 | 0.59637 |  |  | 1:30 | 87.0464 | 1.0116 | 0.92103 | 1.4175 | 0 | 90.3964 | 0.80711
| 5 | 2:00 | 75.0018 | 0.73854 | 0.39582 | 0.69004 | 0 | 76.8262 | 0.68595 |  |  | 2:00 | 65.222 | 0.57911 | 0.070253 | 0.20701 | 0 | 66.0784 | 0.58999 |  |  | 2:00 | 86.2639 | 0.90125 | 0.80916 | 1.1731 | 0 | 89.1473 | 0.79596
| 6 | 2:30 | 70.8636 | 0.70959 | 0.35483 | 0.54626 | 0 | 72.4743 | 0.64709 |  |  | 2:30 | 61.6235 | 0.55642 | 0.062977 | 0.16388 | 0 | 62.4067 | 0.5572 |  |  | 2:30 | 81.5043 | 0.86593 | 0.72537 | 0.92864 | 0 | 84.0243 | 0.75022
| 7 | 3:00 | 65.3954 | 0.6806 | 0.31384 | 0.48241 | 0 | 66.8722 | 0.59707 |  |  | 3:00 | 56.8683 | 0.53368 | 0.055702 | 0.14472 | 0 | 57.6024 | 0.51431 |  |  | 3:00 | 75.215 | 0.83054 | 0.64157 | 0.82009 | 0 | 77.5072 | 0.69203
| 8 | 3:30 | 57.3836 | 0.70008 | 0.30363 | 0.41855 | 0 | 58.8059 | 0.52505 |  |  | 3:30 | 49.9011 | 0.54896 | 0.053889 | 0.12557 | 0 | 50.6296 | 0.45205 |  |  | 3:30 | 66.0002 | 0.85432 | 0.62069 | 0.71154 | 0 | 68.1867 | 0.60881
| 9 | 4:00 | 48.7672 | 0.71951 | 0.29341 | 0.43388 | 0 | 50.214 | 0.44834 |  |  | 4:00 | 42.4083 | 0.56419 | 0.052076 | 0.13016 | 0 | 43.1547 | 0.38531 |  |  | 4:00 | 56.09 | 0.87802 | 0.59981 | 0.7376 | 0 | 58.3054 | 0.52058
| 10 | 4:30 | 38.8763 | 0.9435 | 0.35885 | 0.44926 | 0 | 40.628 | 0.36275 |  |  | 4:30 | 33.8071 | 0.73983 | 0.06369 | 0.13478 | 0 | 34.7454 | 0.31023 |  |  | 4:30 | 44.7139 | 1.1514 | 0.73357 | 0.76374 | 0 | 47.3626 | 0.42288
| 11 | 5:00 | 30.2551 | 1.1674 | 0.42428 | 0.64311 | 0 | 32.49 | 0.29009 |  |  | 5:00 | 26.3101 | 0.91543 | 0.075303 | 0.19293 | 0 | 27.4937 | 0.24548 |  |  | 5:00 | 34.7982 | 1.4246 | 0.86734 | 1.0933 | 0 | 38.1834 | 0.34092
| 12 | 5:30 | 24.7149 | 2.7418 | 0.65442 | 0.83696 | 0 | 28.9481 | 0.25847 |  |  | 5:30 | 21.4923 | 2.15 | 0.11615 | 0.25109 | 0 | 24.0094 | 0.21437 |  |  | 5:30 | 28.4261 | 3.3459 | 1.3378 | 1.4228 | 0 | 34.5326 | 0.30833
| 13 | 6:00 | 20.9886 | 4.3162 | 0.88457 | 1.513 | 0 | 27.7023 | 0.24734 |  |  | 6:00 | 18.2518 | 3.3845 | 0.157 | 0.45389 | 0 | 22.2471 | 0.19864 |  |  | 6:00 | 24.1401 | 5.2671 | 1.8083 | 2.572 | 0 | 33.7876 | 0.30167
| 14 | 6:30 | 16.8228 | 9.0424 | 1.4777 | 2.189 | 0 | 29.5318 | 0.26368 |  |  | 6:30 | 14.6292 | 7.0904 | 0.26227 | 0.65669 | 0 | 22.6386 | 0.20213 |  |  | 6:30 | 19.3488 | 11.0345 | 3.0208 | 3.7213 | 0 | 37.1254 | 0.33148
| 15 | 7:00 | 17.4937 | 13.7685 | 2.0708 | 3.054 | 0 | 36.3869 | 0.32488 |  |  | 7:00 | 15.2126 | 10.7964 | 0.36753 | 0.91619 | 0 | 27.2927 | 0.24368 |  |  | 7:00 | 20.1205 | 16.8019 | 4.2332 | 5.1917 | 0 | 46.3473 | 0.41382
| 16 | 7:30 | 16.069 | 18.8119 | 3.0909 | 3.919 | 0 | 41.8908 | 0.37403 |  |  | 7:30 | 13.9737 | 14.7511 | 0.54859 | 1.1757 | 0 | 30.4491 | 0.27187 |  |  | 7:30 | 18.4819 | 22.9565 | 6.3186 | 6.6623 | 0 | 54.4192 | 0.48589
| 17 | 8:00 | 13.4351 | 23.8554 | 4.111 | 4.8756 | 0 | 46.2773 | 0.41319 |  |  | 8:00 | 11.6833 | 18.7059 | 0.72965 | 1.4627 | 0 | 32.5815 | 0.29091 |  |  | 8:00 | 15.4525 | 29.1111 | 8.404 | 8.2886 | 0 | 61.2563 | 0.54693
| 18 | 8:30 | 15.8556 | 22.7274 | 4.7436 | 5.8323 | 0 | 49.1588 | 0.43892 |  |  | 8:30 | 13.7881 | 17.8213 | 0.84191 | 1.7497 | 0 | 34.201 | 0.30537 |  |  | 8:30 | 18.2364 | 27.7345 | 9.697 | 9.9149 | 0 | 65.5829 | 0.58556
| 19 | 9:00 | 16.5832 | 21.5993 | 5.3761 | 6.6892 | 0 | 50.2477 | 0.44864 |  |  | 9:00 | 14.4208 | 16.9368 | 0.95417 | 2.0068 | 0 | 34.3185 | 0.30642 |  |  | 9:00 | 19.0732 | 26.3579 | 10.99 | 11.3717 | 0 | 67.7929 | 0.60529
| 20 | 9:30 | 17.4258 | 17.8977 | 5.2101 | 7.5461 | 0 | 48.0797 | 0.42928 |  |  | 9:30 | 15.1536 | 14.0342 | 0.92471 | 2.2638 | 0 | 32.3763 | 0.28907 |  |  | 9:30 | 20.0424 | 21.8408 | 10.6508 | 12.8284 | 0 | 65.3624 | 0.58359
| 21 | 10:00 | 18.5103 | 14.196 | 5.0442 | 7.8585 | 0 | 45.6089 | 0.40722 |  |  | 10:00 | 16.0967 | 11.1316 | 0.89526 | 2.3575 | 0 | 30.4811 | 0.27215 |  |  | 10:00 | 21.2897 | 17.3236 | 10.3115 | 13.3594 | 0 | 62.2843 | 0.55611
| 22 | 10:30 | 19.8204 | 12.3693 | 4.7754 | 8.1708 | 0 | 45.1359 | 0.403 |  |  | 10:30 | 17.2359 | 9.6992 | 0.84756 | 2.4512 | 0 | 30.2339 | 0.26995 |  |  | 10:30 | 22.7966 | 15.0944 | 9.7621 | 13.8904 | 0 | 61.5435 | 0.5495
| 23 | 11:00 | 20.4051 | 10.5425 | 4.5066 | 8.6098 | 0 | 44.064 | 0.39343 |  |  | 11:00 | 17.7444 | 8.2667 | 0.79986 | 2.5829 | 0 | 29.3939 | 0.26245 |  |  | 11:00 | 23.4691 | 12.8651 | 9.2127 | 14.6366 | 0 | 60.1835 | 0.53735
| 24 | 11:30 | 21.8961 | 10.1276 | 4.3987 | 9.0487 | 0 | 45.4711 | 0.40599 |  |  | 11:30 | 19.0409 | 7.9414 | 0.7807 | 2.7146 | 0 | 30.4777 | 0.27212 |  |  | 11:30 | 25.1839 | 12.3589 | 8.992 | 15.3828 | 0 | 61.9176 | 0.55284
| 25 | 12:00 | 22.6616 | 9.7127 | 4.2908 | 9.6173 | 0 | 46.2824 | 0.41324 |  |  | 12:00 | 19.7067 | 7.6161 | 0.76154 | 2.8852 | 0 | 30.9695 | 0.27651 |  |  | 12:00 | 26.0644 | 11.8526 | 8.7714 | 16.3495 | 0 | 63.0379 | 0.56284
| 26 | 12:30 | 23.5164 | 9.7047 | 4.228 | 10.1861 | 0 | 47.6352 | 0.42531 |  |  | 12:30 | 20.45 | 7.6098 | 0.75041 | 3.0558 | 0 | 31.8661 | 0.28452 |  |  | 12:30 | 27.0476 | 11.8428 | 8.6432 | 17.3163 | 0 | 64.8498 | 0.57902
| 27 | 13:00 | 23.8874 | 9.6967 | 4.1653 | 10.4469 | 0 | 48.1964 | 0.43032 |  |  | 13:00 | 20.7727 | 7.6036 | 0.73928 | 3.1341 | 0 | 32.2496 | 0.28794 |  |  | 13:00 | 27.4743 | 11.8331 | 8.515 | 17.7597 | 0 | 65.5821 | 0.58555
| 28 | 13:30 | 25.0547 | 9.061 | 4.0063 | 10.7077 | 0 | 48.8298 | 0.43598 |  |  | 13:30 | 21.7877 | 7.1051 | 0.71106 | 3.2123 | 0 | 32.8162 | 0.293 |  |  | 13:30 | 28.8168 | 11.0573 | 8.1899 | 18.2031 | 0 | 66.2672 | 0.59167
| 29 | 14:00 | 25.2546 | 8.4254 | 3.8473 | 10.5649 | 0 | 48.0923 | 0.4294 |  |  | 14:00 | 21.9616 | 6.6067 | 0.68284 | 3.1695 | 0 | 32.4206 | 0.28947 |  |  | 14:00 | 29.0468 | 10.2817 | 7.8648 | 17.9603 | 0 | 65.1536 | 0.58173
| 30 | 14:30 | 25.0689 | 7.7899 | 3.6167 | 10.4221 | 0 | 46.8975 | 0.41873 |  |  | 14:30 | 21.8001 | 6.1083 | 0.6419 | 3.1266 | 0 | 31.6769 | 0.28283 |  |  | 14:30 | 28.8332 | 9.5061 | 7.3934 | 17.7175 | 0 | 63.4501 | 0.56652
| 31 | 15:00 | 25.9714 | 7.1543 | 3.3861 | 10.2733 | 0 | 46.7851 | 0.41772 |  |  | 15:00 | 22.5849 | 5.61 | 0.60097 | 3.082 | 0 | 31.8778 | 0.28462 |  |  | 15:00 | 29.8712 | 8.7305 | 6.922 | 17.4647 | 0 | 62.9884 | 0.5624
| 32 | 15:30 | 28.6179 | 6.5908 | 3.2173 | 10.1246 | 0 | 48.5507 | 0.43349 |  |  | 15:30 | 24.8863 | 5.168 | 0.57103 | 3.0374 | 0 | 33.6628 | 0.30056 |  |  | 15:30 | 32.9151 | 8.0428 | 6.5771 | 17.2119 | 0 | 64.7469 | 0.5781
| 33 | 16:00 | 33.6828 | 6.0272 | 3.0486 | 10.0135 | 0 | 52.7721 | 0.47118 |  |  | 16:00 | 29.2908 | 4.7262 | 0.54108 | 3.004 | 0 | 37.5621 | 0.33538 |  |  | 16:00 | 38.7405 | 7.3551 | 6.2322 | 17.0229 | 0 | 69.3507 | 0.6192
| 34 | 16:30 | 37.7904 | 5.4671 | 2.9798 | 9.9023 | 0 | 56.1397 | 0.50125 |  |  | 16:30 | 32.8628 | 4.287 | 0.52887 | 2.9707 | 0 | 40.6493 | 0.36294 |  |  | 16:30 | 43.4649 | 6.6716 | 6.0915 | 16.8339 | 0 | 73.062 | 0.65234
| 35 | 17:00 | 42.5026 | 4.9071 | 2.911 | 9.8634 | 0 | 60.184 | 0.53736 |  |  | 17:00 | 36.9605 | 3.8478 | 0.51665 | 2.959 | 0 | 44.284 | 0.39539 |  |  | 17:00 | 48.8847 | 5.9882 | 5.9508 | 16.7678 | 0 | 77.5914 | 0.69278
| 36 | 17:30 | 47.4826 | 4.3868 | 2.8837 | 9.8245 | 0 | 64.5776 | 0.57659 |  |  | 17:30 | 41.2912 | 3.4399 | 0.51181 | 2.9473 | 0 | 48.1902 | 0.43027 |  |  | 17:30 | 54.6125 | 5.3533 | 5.8949 | 16.7016 | 0 | 82.5624 | 0.73716
| 37 | 18:00 | 52.2209 | 3.8666 | 2.8564 | 9.7161 | 0 | 68.6599 | 0.61304 |  |  | 18:00 | 45.4117 | 3.0319 | 0.50696 | 2.9148 | 0 | 51.8654 | 0.46308 |  |  | 18:00 | 60.0623 | 4.7184 | 5.8391 | 16.5173 | 0 | 87.1372 | 0.77801
| 38 | 18:30 | 55.6687 | 3.5103 | 2.6737 | 9.6076 | 0 | 71.4603 | 0.63804 |  |  | 18:30 | 48.4098 | 2.7526 | 0.47454 | 2.8823 | 0 | 54.5192 | 0.48678 |  |  | 18:30 | 64.0277 | 4.2837 | 5.4658 | 16.333 | 0 | 90.1102 | 0.80456
| 39 | 19:00 | 57.7862 | 3.1541 | 2.4911 | 8.9355 | 0 | 72.3668 | 0.64613 |  |  | 19:00 | 50.2513 | 2.4732 | 0.44213 | 2.6806 | 0 | 55.8473 | 0.49864 |  |  | 19:00 | 66.4633 | 3.849 | 5.0924 | 15.1903 | 0 | 90.5949 | 0.80888
| 40 | 19:30 | 58.1245 | 2.8617 | 2.1782 | 8.2633 | 0 | 71.4277 | 0.63775 |  |  | 19:30 | 50.5455 | 2.244 | 0.3866 | 2.479 | 0 | 55.655 | 0.49692 |  |  | 19:30 | 66.8524 | 3.4922 | 4.4528 | 14.0476 | 0 | 88.8449 | 0.79326
| 41 | 20:00 | 58.4628 | 2.5694 | 1.8653 | 7.3594 | 0 | 70.2569 | 0.62729 |  |  | 20:00 | 50.8396 | 2.0148 | 0.33106 | 2.2078 | 0 | 55.3933 | 0.49458 |  |  | 20:00 | 67.2414 | 3.1355 | 3.8131 | 12.511 | 0 | 86.701 | 0.77412
| 42 | 20:30 | 61.0399 | 2.3998 | 1.5796 | 6.4554 | 0 | 71.4747 | 0.63817 |  |  | 20:30 | 53.0807 | 1.8818 | 0.28036 | 1.9366 | 0 | 57.1794 | 0.51053 |  |  | 20:30 | 70.2055 | 2.9285 | 3.2291 | 10.9743 | 0 | 87.3374 | 0.7798
| 43 | 21:00 | 60.8358 | 2.2302 | 1.2939 | 5.5381 | 0 | 69.8979 | 0.62409 |  |  | 21:00 | 52.9032 | 1.7488 | 0.22965 | 1.6614 | 0 | 56.543 | 0.50485 |  |  | 21:00 | 69.9708 | 2.7215 | 2.6451 | 9.4147 | 0 | 84.7521 | 0.75672
| 44 | 21:30 | 60.2433 | 2.131 | 1.1184 | 4.6207 | 0 | 68.1134 | 0.60816 |  |  | 21:30 | 52.388 | 1.671 | 0.19849 | 1.3862 | 0 | 55.6437 | 0.49682 |  |  | 21:30 | 69.2893 | 2.6006 | 2.2862 | 7.8551 | 0 | 82.0312 | 0.73242
| 45 | 22:00 | 59.409 | 2.0319 | 0.94278 | 3.8408 | 0 | 66.2245 | 0.59129 |  |  | 22:00 | 51.6624 | 1.5933 | 0.16733 | 1.1523 | 0 | 54.5753 | 0.48728 |  |  | 22:00 | 68.3297 | 2.4796 | 1.9273 | 6.5294 | 0 | 79.266 | 0.70773
| 46 | 22:30 | 59.0386 | 1.8343 | 0.84598 | 3.061 | 0 | 64.7799 | 0.57839 |  |  | 22:30 | 51.3404 | 1.4384 | 0.15015 | 0.91831 | 0 | 53.8472 | 0.48078 |  |  | 22:30 | 67.9037 | 2.2385 | 1.7294 | 5.2037 | 0 | 77.0753 | 0.68817
| 47 | 23:00 | 62.1748 | 1.6367 | 0.74918 | 2.569 | 0 | 67.1297 | 0.59937 |  |  | 23:00 | 54.0676 | 1.2834 | 0.13297 | 0.7707 | 0 | 56.2547 | 0.50227 |  |  | 23:00 | 71.5108 | 1.9973 | 1.5315 | 4.3673 | 0 | 79.407 | 0.70899
| 48 | 23:30 | 64.2084 | 1.4443 | 0.68403 | 2.0769 | 0 | 68.4137 | 0.61084 |  |  | 23:30 | 55.836 | 1.1326 | 0.1214 | 0.62308 | 0 | 57.7131 | 0.5153 |  |  | 23:30 | 73.8497 | 1.7625 | 1.3983 | 3.5308 | 0 | 80.5414 | 0.71912
4.2 (Alternative step for graphs) Apply half-hourly profiles and find peak demand values and times for large EVs only.
| Large EVs only - Default values | [10 empty] | Large EVs only - Lower range values | [9 empty] | Large EVs only - Upper range values
|  |  | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  |  | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  |  | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV
| Parameter | Unit | Default | Default | Default | Default | Default | Default | Default |  | Parameter | Unit | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range |  | Parameter | Unit | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range
| Peak demand | kW | 0 | 0 | 0 | 22.7277 | 549.6686 | 559.4762 | 69.9345 |  | Peak demand | kW | 0 | 0 | 0 | 22.7277 | 549.6686 | 559.4762 | 69.9345 |  | Peak demand | kW | 0 | 0 | 0 | 22.7277 | 549.6686 | 559.4762 | 69.9345
| Time of peak demand | Half hour start time | 0:00 | 0:00 | 0:00 | 13:30 | 21:30 | 21:30 | 21:30 |  | Time of peak demand | Half hour start time | 0:00 | 0:00 | 0:00 | 13:30 | 21:30 | 21:30 | 21:30 |  | Time of peak demand | Half hour start time | 0:00 | 0:00 | 0:00 | 13:30 | 21:30 | 21:30 | 21:30
|  | Table unit: kW | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  | Table unit: kW | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV |  |  | Table unit: kW | Domestic | Workplace | Slow/fast public | Rapid public | HGV depot | Total | Total - per EV
|  | Half hour start time | Default | Default | Default | Default | Default | Default | Default |  |  | Half hour start time | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range | Lower range |  |  | Half hour start time | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range | Upper range
| 1 | 0:00 | 0 | 0 | 0 | 3.5939 | 519.1607 | 522.7546 | 65.3443 |  |  | 0:00 | 0 | 0 | 0 | 3.5939 | 519.1607 | 522.7546 | 65.3443 |  |  | 0:00 | 0 | 0 | 0 | 3.5939 | 519.1607 | 522.7546 | 65.3443
| 2 | 0:30 | 0 | 0 | 0 | 2.7794 | 494.2823 | 497.0617 | 62.1327 |  |  | 0:30 | 0 | 0 | 0 | 2.7794 | 494.2823 | 497.0617 | 62.1327 |  |  | 0:30 | 0 | 0 | 0 | 2.7794 | 494.2823 | 497.0617 | 62.1327
| 3 | 1:00 | 0 | 0 | 0 | 2.2746 | 495.5247 | 497.7993 | 62.2249 |  |  | 1:00 | 0 | 0 | 0 | 2.2746 | 495.5247 | 497.7993 | 62.2249 |  |  | 1:00 | 0 | 0 | 0 | 2.2746 | 495.5247 | 497.7993 | 62.2249
| 4 | 1:30 | 0 | 0 | 0 | 1.7698 | 496.7671 | 498.537 | 62.3171 |  |  | 1:30 | 0 | 0 | 0 | 1.7698 | 496.7671 | 498.537 | 62.3171 |  |  | 1:30 | 0 | 0 | 0 | 1.7698 | 496.7671 | 498.537 | 62.3171
| 5 | 2:00 | 0 | 0 | 0 | 1.4647 | 498.1034 | 499.568 | 62.446 |  |  | 2:00 | 0 | 0 | 0 | 1.4647 | 498.1034 | 499.568 | 62.446 |  |  | 2:00 | 0 | 0 | 0 | 1.4647 | 498.1034 | 499.568 | 62.446
| 6 | 2:30 | 0 | 0 | 0 | 1.1595 | 499.4397 | 500.5991 | 62.5749 |  |  | 2:30 | 0 | 0 | 0 | 1.1595 | 499.4397 | 500.5991 | 62.5749 |  |  | 2:30 | 0 | 0 | 0 | 1.1595 | 499.4397 | 500.5991 | 62.5749
| 7 | 3:00 | 0 | 0 | 0 | 1.0239 | 486.1846 | 487.2086 | 60.9011 |  |  | 3:00 | 0 | 0 | 0 | 1.0239 | 486.1846 | 487.2086 | 60.9011 |  |  | 3:00 | 0 | 0 | 0 | 1.0239 | 486.1846 | 487.2086 | 60.9011
| 8 | 3:30 | 0 | 0 | 0 | 0.8884 | 472.9324 | 473.8208 | 59.2276 |  |  | 3:30 | 0 | 0 | 0 | 0.8884 | 472.9324 | 473.8208 | 59.2276 |  |  | 3:30 | 0 | 0 | 0 | 0.8884 | 472.9324 | 473.8208 | 59.2276
| 9 | 4:00 | 0 | 0 | 0 | 0.92094 | 437.4439 | 438.3648 | 54.7956 |  |  | 4:00 | 0 | 0 | 0 | 0.92094 | 437.4439 | 438.3648 | 54.7956 |  |  | 4:00 | 0 | 0 | 0 | 0.92094 | 437.4439 | 438.3648 | 54.7956
| 10 | 4:30 | 0 | 0 | 0 | 0.95358 | 401.9554 | 402.9089 | 50.3636 |  |  | 4:30 | 0 | 0 | 0 | 0.95358 | 401.9554 | 402.9089 | 50.3636 |  |  | 4:30 | 0 | 0 | 0 | 0.95358 | 401.9554 | 402.9089 | 50.3636
| 11 | 5:00 | 0 | 0 | 0 | 1.365 | 356.6491 | 358.0142 | 44.7518 |  |  | 5:00 | 0 | 0 | 0 | 1.365 | 356.6491 | 358.0142 | 44.7518 |  |  | 5:00 | 0 | 0 | 0 | 1.365 | 356.6491 | 358.0142 | 44.7518
| 12 | 5:30 | 0 | 0 | 0 | 1.7765 | 311.3457 | 313.1222 | 39.1403 |  |  | 5:30 | 0 | 0 | 0 | 1.7765 | 311.3457 | 313.1222 | 39.1403 |  |  | 5:30 | 0 | 0 | 0 | 1.7765 | 311.3457 | 313.1222 | 39.1403
| 13 | 6:00 | 0 | 0 | 0 | 3.2114 | 280.7384 | 283.9498 | 35.4937 |  |  | 6:00 | 0 | 0 | 0 | 3.2114 | 280.7384 | 283.9498 | 35.4937 |  |  | 6:00 | 0 | 0 | 0 | 3.2114 | 280.7384 | 283.9498 | 35.4937
| 14 | 6:30 | 0 | 0 | 0 | 4.6462 | 250.1312 | 254.7774 | 31.8472 |  |  | 6:30 | 0 | 0 | 0 | 4.6462 | 250.1312 | 254.7774 | 31.8472 |  |  | 6:30 | 0 | 0 | 0 | 4.6462 | 250.1312 | 254.7774 | 31.8472
| 15 | 7:00 | 0 | 0 | 0 | 6.4822 | 224.1181 | 230.6003 | 28.825 |  |  | 7:00 | 0 | 0 | 0 | 6.4822 | 224.1181 | 230.6003 | 28.825 |  |  | 7:00 | 0 | 0 | 0 | 6.4822 | 224.1181 | 230.6003 | 28.825
| 16 | 7:30 | 0 | 0 | 0 | 8.3182 | 198.1022 | 206.4205 | 25.8026 |  |  | 7:30 | 0 | 0 | 0 | 8.3182 | 198.1022 | 206.4205 | 25.8026 |  |  | 7:30 | 0 | 0 | 0 | 8.3182 | 198.1022 | 206.4205 | 25.8026
| 17 | 8:00 | 0 | 0 | 0 | 10.3488 | 178.8312 | 189.18 | 23.6475 |  |  | 8:00 | 0 | 0 | 0 | 10.3488 | 178.8312 | 189.18 | 23.6475 |  |  | 8:00 | 0 | 0 | 0 | 10.3488 | 178.8312 | 189.18 | 23.6475
| 18 | 8:30 | 0 | 0 | 0 | 12.3793 | 159.5602 | 171.9395 | 21.4924 |  |  | 8:30 | 0 | 0 | 0 | 12.3793 | 159.5602 | 171.9395 | 21.4924 |  |  | 8:30 | 0 | 0 | 0 | 12.3793 | 159.5602 | 171.9395 | 21.4924
| 19 | 9:00 | 0 | 0 | 0 | 14.1982 | 144.7066 | 158.9048 | 19.8631 |  |  | 9:00 | 0 | 0 | 0 | 14.1982 | 144.7066 | 158.9048 | 19.8631 |  |  | 9:00 | 0 | 0 | 0 | 14.1982 | 144.7066 | 158.9048 | 19.8631
| 20 | 9:30 | 0 | 0 | 0 | 16.017 | 129.853 | 145.87 | 18.2338 |  |  | 9:30 | 0 | 0 | 0 | 16.017 | 129.853 | 145.87 | 18.2338 |  |  | 9:30 | 0 | 0 | 0 | 16.017 | 129.853 | 145.87 | 18.2338
| 21 | 10:00 | 0 | 0 | 0 | 16.68 | 119.9359 | 136.6159 | 17.077 |  |  | 10:00 | 0 | 0 | 0 | 16.68 | 119.9359 | 136.6159 | 17.077 |  |  | 10:00 | 0 | 0 | 0 | 16.68 | 119.9359 | 136.6159 | 17.077
| 22 | 10:30 | 0 | 0 | 0 | 17.343 | 110.0187 | 127.3617 | 15.9202 |  |  | 10:30 | 0 | 0 | 0 | 17.343 | 110.0187 | 127.3617 | 15.9202 |  |  | 10:30 | 0 | 0 | 0 | 17.343 | 110.0187 | 127.3617 | 15.9202
| 23 | 11:00 | 0 | 0 | 0 | 18.2747 | 104.9304 | 123.2051 | 15.4006 |  |  | 11:00 | 0 | 0 | 0 | 18.2747 | 104.9304 | 123.2051 | 15.4006 |  |  | 11:00 | 0 | 0 | 0 | 18.2747 | 104.9304 | 123.2051 | 15.4006
| 24 | 11:30 | 0 | 0 | 0 | 19.2063 | 99.8393 | 119.0457 | 14.8807 |  |  | 11:30 | 0 | 0 | 0 | 19.2063 | 99.8393 | 119.0457 | 14.8807 |  |  | 11:30 | 0 | 0 | 0 | 19.2063 | 99.8393 | 119.0457 | 14.8807
| 25 | 12:00 | 0 | 0 | 0 | 20.4133 | 96.7527 | 117.166 | 14.6457 |  |  | 12:00 | 0 | 0 | 0 | 20.4133 | 96.7527 | 117.166 | 14.6457 |  |  | 12:00 | 0 | 0 | 0 | 20.4133 | 96.7527 | 117.166 | 14.6457
| 26 | 12:30 | 0 | 0 | 0 | 21.6204 | 93.6688 | 115.2892 | 14.4111 |  |  | 12:30 | 0 | 0 | 0 | 21.6204 | 93.6688 | 115.2892 | 14.4111 |  |  | 12:30 | 0 | 0 | 0 | 21.6204 | 93.6688 | 115.2892 | 14.4111
| 27 | 13:00 | 0 | 0 | 0 | 22.1741 | 92.7052 | 114.8793 | 14.3599 |  |  | 13:00 | 0 | 0 | 0 | 22.1741 | 92.7052 | 114.8793 | 14.3599 |  |  | 13:00 | 0 | 0 | 0 | 22.1741 | 92.7052 | 114.8793 | 14.3599
| 28 | 13:30 | 0 | 0 | 0 | 22.7277 | 91.7416 | 114.4694 | 14.3087 |  |  | 13:30 | 0 | 0 | 0 | 22.7277 | 91.7416 | 114.4694 | 14.3087 |  |  | 13:30 | 0 | 0 | 0 | 22.7277 | 91.7416 | 114.4694 | 14.3087
| 29 | 14:00 | 0 | 0 | 0 | 22.4245 | 93.5059 | 115.9304 | 14.4913 |  |  | 14:00 | 0 | 0 | 0 | 22.4245 | 93.5059 | 115.9304 | 14.4913 |  |  | 14:00 | 0 | 0 | 0 | 22.4245 | 93.5059 | 115.9304 | 14.4913
| 30 | 14:30 | 0 | 0 | 0 | 22.1214 | 95.2701 | 117.3914 | 14.6739 |  |  | 14:30 | 0 | 0 | 0 | 22.1214 | 95.2701 | 117.3914 | 14.6739 |  |  | 14:30 | 0 | 0 | 0 | 22.1214 | 95.2701 | 117.3914 | 14.6739
| 31 | 15:00 | 0 | 0 | 0 | 21.8057 | 104.9028 | 126.7085 | 15.8386 |  |  | 15:00 | 0 | 0 | 0 | 21.8057 | 104.9028 | 126.7085 | 15.8386 |  |  | 15:00 | 0 | 0 | 0 | 21.8057 | 104.9028 | 126.7085 | 15.8386
| 32 | 15:30 | 0 | 0 | 0 | 21.4901 | 114.5356 | 136.0256 | 17.0032 |  |  | 15:30 | 0 | 0 | 0 | 21.4901 | 114.5356 | 136.0256 | 17.0032 |  |  | 15:30 | 0 | 0 | 0 | 21.4901 | 114.5356 | 136.0256 | 17.0032
| 33 | 16:00 | 0 | 0 | 0 | 21.2541 | 140.4079 | 161.662 | 20.2077 |  |  | 16:00 | 0 | 0 | 0 | 21.2541 | 140.4079 | 161.662 | 20.2077 |  |  | 16:00 | 0 | 0 | 0 | 21.2541 | 140.4079 | 161.662 | 20.2077
| 34 | 16:30 | 0 | 0 | 0 | 21.0182 | 166.2802 | 187.2984 | 23.4123 |  |  | 16:30 | 0 | 0 | 0 | 21.0182 | 166.2802 | 187.2984 | 23.4123 |  |  | 16:30 | 0 | 0 | 0 | 21.0182 | 166.2802 | 187.2984 | 23.4123
| 35 | 17:00 | 0 | 0 | 0 | 20.9356 | 218.7647 | 239.7003 | 29.9625 |  |  | 17:00 | 0 | 0 | 0 | 20.9356 | 218.7647 | 239.7003 | 29.9625 |  |  | 17:00 | 0 | 0 | 0 | 20.9356 | 218.7647 | 239.7003 | 29.9625
| 36 | 17:30 | 0 | 0 | 0 | 20.853 | 271.2465 | 292.0995 | 36.5124 |  |  | 17:30 | 0 | 0 | 0 | 20.853 | 271.2465 | 292.0995 | 36.5124 |  |  | 17:30 | 0 | 0 | 0 | 20.853 | 271.2465 | 292.0995 | 36.5124
| 37 | 18:00 | 0 | 0 | 0 | 20.6229 | 347.3394 | 367.9623 | 45.9953 |  |  | 18:00 | 0 | 0 | 0 | 20.6229 | 347.3394 | 367.9623 | 45.9953 |  |  | 18:00 | 0 | 0 | 0 | 20.6229 | 347.3394 | 367.9623 | 45.9953
| 38 | 18:30 | 0 | 0 | 0 | 20.3927 | 423.4323 | 443.8251 | 55.4781 |  |  | 18:30 | 0 | 0 | 0 | 20.3927 | 423.4323 | 443.8251 | 55.4781 |  |  | 18:30 | 0 | 0 | 0 | 20.3927 | 423.4323 | 443.8251 | 55.4781
| 39 | 19:00 | 0 | 0 | 0 | 18.966 | 467.1152 | 486.0811 | 60.7601 |  |  | 19:00 | 0 | 0 | 0 | 18.966 | 467.1152 | 486.0811 | 60.7601 |  |  | 19:00 | 0 | 0 | 0 | 18.966 | 467.1152 | 486.0811 | 60.7601
| 40 | 19:30 | 0 | 0 | 0 | 17.5393 | 510.798 | 528.3372 | 66.0422 |  |  | 19:30 | 0 | 0 | 0 | 17.5393 | 510.798 | 528.3372 | 66.0422 |  |  | 19:30 | 0 | 0 | 0 | 17.5393 | 510.798 | 528.3372 | 66.0422
| 41 | 20:00 | 0 | 0 | 0 | 15.6207 | 522.3495 | 537.9702 | 67.2463 |  |  | 20:00 | 0 | 0 | 0 | 15.6207 | 522.3495 | 537.9702 | 67.2463 |  |  | 20:00 | 0 | 0 | 0 | 15.6207 | 522.3495 | 537.9702 | 67.2463
| 42 | 20:30 | 0 | 0 | 0 | 13.702 | 533.8983 | 547.6004 | 68.45 |  |  | 20:30 | 0 | 0 | 0 | 13.702 | 533.8983 | 547.6004 | 68.45 |  |  | 20:30 | 0 | 0 | 0 | 13.702 | 533.8983 | 547.6004 | 68.45
| 43 | 21:00 | 0 | 0 | 0 | 11.7548 | 541.7835 | 553.5383 | 69.1923 |  |  | 21:00 | 0 | 0 | 0 | 11.7548 | 541.7835 | 553.5383 | 69.1923 |  |  | 21:00 | 0 | 0 | 0 | 11.7548 | 541.7835 | 553.5383 | 69.1923
| 44 | 21:30 | 0 | 0 | 0 | 9.8076 | 549.6686 | 559.4762 | 69.9345 |  |  | 21:30 | 0 | 0 | 0 | 9.8076 | 549.6686 | 559.4762 | 69.9345 |  |  | 21:30 | 0 | 0 | 0 | 9.8076 | 549.6686 | 559.4762 | 69.9345
| 45 | 22:00 | 0 | 0 | 0 | 8.1524 | 547.4736 | 555.626 | 69.4533 |  |  | 22:00 | 0 | 0 | 0 | 8.1524 | 547.4736 | 555.626 | 69.4533 |  |  | 22:00 | 0 | 0 | 0 | 8.1524 | 547.4736 | 555.626 | 69.4533
| 46 | 22:30 | 0 | 0 | 0 | 6.4972 | 545.2787 | 551.7759 | 68.972 |  |  | 22:30 | 0 | 0 | 0 | 6.4972 | 545.2787 | 551.7759 | 68.972 |  |  | 22:30 | 0 | 0 | 0 | 6.4972 | 545.2787 | 551.7759 | 68.972
| 47 | 23:00 | 0 | 0 | 0 | 5.4529 | 544.6575 | 550.1104 | 68.7638 |  |  | 23:00 | 0 | 0 | 0 | 5.4529 | 544.6575 | 550.1104 | 68.7638 |  |  | 23:00 | 0 | 0 | 0 | 5.4529 | 544.6575 | 550.1104 | 68.7638
| 48 | 23:30 | 0 | 0 | 0 | 4.4084 | 544.0391 | 548.4475 | 68.5559 |  |  | 23:30 | 0 | 0 | 0 | 4.4084 | 544.0391 | 548.4475 | 68.5559 |  |  | 23:30 | 0 | 0 | 0 | 4.4084 | 544.0391 | 548.4475 | 68.5559
User inputs:
Dashboard:
CPA values selected:
End-to-end calculation:
EV CPA process

## HP CPA Summary Table
Domestic HP CPA Summary Table
Back to contents
CPA Number | CPA | Description | Scope | Unit | Data source/s | Link/s | Data processing comment | Default values comment | Overall RAG rating | Based on reliable source | RAG | Be relevant | RAG | Be up to date | RAG | Be location specific | RAG | Considers changes through time | RAG | Weather and climate impact | RAG
HP01 | Size of HP | The heat pump installation size. | Defined for four dwelling categories (Detached, semi-detached and end-terraced, mid-terraced, flats), and for existing stock and new builds | kW_th | a) Building Research Establishment (BRE): Dwelling heat loss | https://tools.bregroup.com/heatpumpefficiency/dwelling-heat-loss | BRE source provides an estimate of dwelling design heat losses in the UK, which can serve as a proxy for the heat pump size required. BRE estimates are provided for different dwelling age categories. For existing builds, the heat pump size is based on the weighted average dwelling design heat loss across all dwelling age categories, using government council tax stock data to provide the proportions of dwelling stock by dwelling age. For new builds, the dwelling design heat loss for 2007 onwards from the BRE source is used. | Default values are provided based on the average age of dwellings in England and Wales. Additional regionality can be added by calculating an adjusted weighted average of the BRE data for the distribution of dwelling stock ages in a particular region. | 3 | Based on English Housing Survey Data using the Building Research Establishment Standard Assessment Procedure (the UK's National Calculation Methodology for energy rating of dwellings), and published government data. | 2 | Developed as part of the Domestic Annual Heat Pump System Efficiency (DAHPSE) Estimator, data provided by dwelling category. | 3 | Analysis conducted within last 10 years. | 2 | UK-based analysis based on English Housing Survey data. Dwelling age data from council tax data for England and Wales. Data has not been disaggregated by region. | 3 | Captured through HP02 instead (although separate values provided for new builds). | NA | Not considered (captured through other CPAs). | NA
[5 empty] | b) GOV.UK Council Tax: stock of properties, 2024 (Table CTSOP 4.0) | https://www.gov.uk/government/statistics/council-tax-stock-of-properties-2024
HP02 | Dwelling thermal efficiency factor | A factor to account for improvements in building fabric efficiency, defined as a proportion of the baseline efficiency (i.e. the factor is 1 at baseline and less than 1 in future years). | Defined as a global assumption across dwelling categories (but projected improvements are not applicable for new builds) | % | FES Data Workbook 2025 (National Energy System Operator) Table ED7 | https://www.neso.energy/publications/future-energy-scenarios-fes/fes-documents | Approximated from FES based on savings from insulation as a proportion of total heat pump energy consumption in 2050. The pace of efficiency improvements depends on a range of complex factors, so the data has been simplified by assuming that improvements are linear on an annual basis up until 2035, then the efficiency factor relative to the baseline remains constant from 2035. | Default value provided across all dwelling categories at a GB-level. Note that this improvement in building fabric efficiency does not apply to new builds, as the higher fabric efficiency is already reflected in the lower values for HP01 for new builds. | 2 | Based on interpretation of FES data. FES modelling is very granular so the interpreted data may include the impact of other factors. | 2 | Relies on interpretation of FES data which may include the impact of other factors. | 1 | FES data published in 2025. | 3 | Not considered | NA | Based on FES projection in 2050. Intermediate years interpolated. | 2 | Not considered. | NA
HP03 | Efficiency of HP | A measure of efficiency of the heat pump that indicates how much heat energy is produced for every unit of electrical energy consumed. | Defined for each representative day | N/A | Energy Systems Catapult "Electrification of Heat" data, Analysis 2 (combined with HP05, see below for sources) | https://github.com/ES-Catapult/electrification_of_heat/blob/main/notebooks/Analysis%202%20-%20COP%20%26%20Energy%20vs%20Temperature.ipynb | COP provided as a function of outside air temperature in the "Electrification of Heat" data. Outside air temperature for each region is based on HP05. For the overall minimum demand day and peak demand summer day, the COP for an outside air temperature of 18˚C has been used (offering a conservative approach for peak demand summer day, as the analysis by ESC shows a slight decrease in COP once the outside air temperature increases above 10˚C). | Default values are provided by government region, aligned with HP05. | 3 | Based on the Electrification of Heat trial project funded by DESNZ. | 3 | This trial project was focused on ca. 700 homes equipped with heat pumps. | 3 | The data was recorded between December 2020 and September 2023. | 3 | The efficiency of Air Source Heat Pumps is linked to the outside air temperature. Hence, the temperature difference is an input to the choice of the COP for the region to be modelled. | 3 | This data does not account for potential improvements in the quality of installation, controls, etc. as it is based on metered data. | NA | The default value is based on the coldest day recorded during the project period. The impact of climate change could result in more extreme scenarios which would impact the value used. More data would be needed for extreme weather. | 2
HP04 | Specific HP heat output | Defined as the daily thermal output of the heat pump (kWh_th) relative to the installed capacity (kW_th) and the temperature difference between target inside air temperature and the outdoor air temperature (˚C). | Defined as a global assumption | kWh_th/kW/temp_diff (for peak demand winter day and peak demand shoulder season day) or kWh_th/kW (for peak demand summer day and overall minimum demand day) | a) Energy Systems Catapult "Electrification of Heat" data cleansed 30 min interval dataset | https://beta.ukdataservice.ac.uk/datacatalogue/studies/study?id=9209 | The "Electrification of Heat" cleansed 30min data was combined with information about the heating system (size and type of heat-pumps). The data was then aggregated at daily resolution and only Air Source Heat Pumps were kept for this analysis. For peak demand winter day and peak demand shoulder season day, it is the median value of the ratio between heat output, size of heat pump and temperature difference between the average daily temperature and the indoor air temperature of 21˚C from all daily records with a daily temperature between -2˚C to 9˚C after removing the records falling above the 95th percentiles and below the 5th percentiles. For peak demand summer day and overall minimum demand day, it is the median value of the ratio between heat output and size of heat pump from all daily records with a daily temperature above 20˚C after removing the records falling above the 95th percentiles and below the 5th percentiles. | Default value provided across all dwelling categories at a GB-level (regional variation and dwelling-type variation captured through other CPAs). | 3 | Based on the Electrification of Heat trial project funded by DESNZ. | 3 | This trial project was focused on ca. 700 homes equipped with heat pumps. | 3 | The data was recorded between December 2020 and September 2023. | 3 | The data is from UK homes and include information about location but this information was not used as this CPA is not expected to differ between regions. | 3 | This data does not account for potential improvements in the quality of installation, controls, etc. as it is based on metered data. | 1 | The default value is based on the coldest day recorded during the project period. The impact of climate change could result in more extreme scenarios which would impact the value used. | 2
[5 empty] | b) Energy Systems Catapult "DESNZ Electrification of Heat Project - Heat Pump Performance Data Summary | https://usmart.io/org/esc/discovery/discovery-view-detail/6a5e5753-aaff-455e-8b3b-8ee282010261
HP05 | Temperature difference | Temperature difference between target inside air temperature (assumed to be 21˚C) and the calculated representative outdoor air temperature. | Defined for each representative day | ˚C | a) Met Office HadUK-Grid dataset (Gridded Climate Observations on a 12km grid over the UK, v1.3.1.ceda) | https://catalogue.ceda.ac.uk/uuid/3302df4f8d174999bfbc5d0b86d93dce/?jump=related-docs-anchor | For peak demand winter and peak demand shoulder season: To find the temperature difference CPAs, we first find representative minimum outdoor air temperatures for each month (using source a), based on the day within each month when the minimum temperature occurs. The representative temperature provided is the ‘daily midrange temperature’ for this day (i.e. the midpoint between the maximum and minimum temperature on the day), averaged across all 12 km squares that fall within each DNO licence area, averaged over 2015 to 2024. For peak demand winter day, the month with the lowest representative minimum temperature is used (coldest minimum temperature). For peak demand shoulder season day, first the month with the highest representative minimum temperature is identified (warmest minimum temperature), then the minimum temperature in the shoulder month is identified by taking the average between this temperature and the peak demand winter day temperature, and the converting it to a daily midrange temperature. To find the range of allowable temperature differences for each DNO licence area, the same calculation is performed as above, but instead finding the 12 km square within each licence area with the lowest and highest representative minimum outdoor air temperatures (as opposed to the average across all squares), but continuing to average across 2015 to 2024. In all cases, the CPA is presented as the temperature difference between the calculated representative outdoor air temperature and a target indoor air temperature of 21˚C (source b). For peak demand summer day and minimum overall day: temperature difference is N/A, assuming that HP usage for these representative days is dominated by hot water demand, with no significant space heating (noting that the scope of tRESP includes only residential, not commercial heat pumps). | Default values are provided by DNO licence area. Note that the use of temperature difference in the calculation of daily electricity consumption is only applicable for the peak demand winter day and peak demand shoulder season day. | 3 | Government published data. | 3 | Measured temperature data across all relevant regions. Other data processing approaches (e.g. average daily temperature rather than minimum daily temperature) could also be considered. | 2 | Data is from 2015 to 2024 inclusive. | 3 | Data provided for the whole of the UK, at a high spatial granularity (12 km squares). | 3 | Temperature averaged across 10 years. Future changes in temperature (as a result of climate change) are not considered. | 2 | Weather impacts inherently captured. Future changes in temperature (as a result of climate change) are not considered. | 2
[5 empty] | b) Microgeneration Certification Scheme, Heat Pump: Design Standard (2025), Table 1 | https://mcscertified.com/wp-content/uploads/2025/02/MIS-3005-D-2025-V1.0.pdf
HP06 | Normalised half-hourly profile | The half-hourly diversified demand contribution from heat pumps, normalised against the daily electricity consumption for that heat pump type and consumer behaviour. | Defined for each representative day and type of consumer behaviour | kW/daily kWh_e | a) Energy Systems Catapult Electrification of heat data, Cleansed 30-minute interval dataset | https://beta.ukdataservice.ac.uk/datacatalogue/studies/study?id=9209 | For peak demand winter day and peak demand shoulder season day, the cleansed 30-minute data from the electrification of heat dataset is used. For peak demand winter day, a subset of recorded daily profiles with a daily average temperature between -2˚C to 1 ˚C is found. For peak demand shoulder season day, a daily average temperature range of 4.5˚C to 8.5˚C is used. Both temperature ranges are in line with HP05. The profiles are normalised, converting to kW/daily kWh_e. To offer visibility of the expected patterns of usage that make up the overall profile, k-means clustering is used to identify 3 behavioural clusters, using the bimodal, daytime and continuous profiles from Watson (2021) for the relevant temperature range to initialise clusters. For peak demand summer day and overall minimum demand day, the domestic hot water profile from Watson (2021) is used (which in turn is drawn from the Energy Demand Research Project). Again, this is normalised to convert to kW/daily kWh_e. | Default value provided across all dwelling categories at a GB-level. | 3 | Based on the Electrification of Heat trial project funded by DESNZ. | 3 | This trial project was focused on ca. 700 homes equipped with heat pumps. | 3 | The data was recorded between December 2020 and September 2023. | 3 | The data is from UK homes and include information about location but this information was not used as regional differences are instead captured through the temperature difference CPA. | 3 | This data does not account for potential improvements in the quality of installation, controls, etc. as it is based on metered data. | 1 | Weather impacts captured by considering relevant temperature ranges. Future changes in temperature (as a result of climate change) are not considered. | 2
[5 empty] | b) S.D. Watson, K.J. Lomas, R.A. Buswell, "How will heat pumps alter national half-hourly heat demands? Empirical modelling based on GB field trials" Energy and Buildings | https://www.sciencedirect.com/science/article/pii/S037877882100061X
HP07 | Proportion of consumers by behaviour | Percentage of consumers exhibiting each behaviour pattern | Defined as a proportional split between types of consumer behaviour | % | a) Energy Systems Catapult Electrification of heat data, Cleansed 30-minute interval dataset | https://beta.ukdataservice.ac.uk/datacatalogue/studies/study?id=9209 | For the peak demand winter day and peak demand shoulder season day, the counts of profiles in each of the three clusters (as described under HP06) are used to provide the proportions of each behaviour type. Separate behavioural profiles are not provided for peak demand summer day and overall minimum demand day. Note that this CPA is provided for reference only, to support understanding of the separate behavioural profiles provided in HP06, but is not required for use in DNO analysis as the provided weighted average profiles shall be used directly by DNOs. | Default value provided across all dwelling categories at a GB-level. | 2 | Based on the Electrification of Heat trial project funded by DESNZ. | 3 | This trial project was focused on ca. 700 homes equipped with heat pumps. | 3 | The data was recorded between December 2020 and September 2023. | 3 | The data is from UK homes and include information about location but this information was not used as regional differences are instead captured through the temperature difference CPA. More nuanced consideration of how behaviour might vary between regions, decoupled from temperature, was not considered. | 2 | This data does not account for changes in consumer behaviour, as it is based on metered data. | 1 | Weather impacts captured by considering relevant temperature ranges. Future changes in temperature (as a result of climate change) are not considered. | 2
[5 empty] | b) S.D. Watson, K.J. Lomas, R.A. Buswell, How will heat pumps alter national half-hourly heat demands? Empirical modelling based on GB field trials, Energy and Buildings | https://www.sciencedirect.com/science/article/pii/S037877882100061X
HP08 | Diversity-correction curve | The ‘un-diversification’ scaling factor to be applied to the fully diversified profile based on the number of heat pumps on a network asset. | Defined for each representative day | N/A (scaling factor) | Energy Systems Catapult Electrification of heat data, Cleansed 30-minute interval dataset | https://beta.ukdataservice.ac.uk/datacatalogue/studies/study?id=9209 | Diversity-correction curves calculated using the cleansed 30-minute data from the "Electrification of Heat" dataset. For peak demand winter day, a set of recorded daily profiles with a daily average temperature between -2˚C to 1 ˚C is found. For peak demand shoulder season day, a daily average temperature range of 4.5˚C to 8.5˚C is used, and for peak demand summer day and overall minimum demand day a temperature range of 20˚C to 30˚C is used. The fully diversified profile was calculated by finding the mean half-hourly values for each representative day's set. For each N (number of HPs in a sample), subsets of profiles from the full representative day profiles subset were drawn. The ratio between the peak load and the peak of the fully-diversified profile was found. For each N, the random draw was repeated 1000 times and the 95th percentile of the calculated ratios for each N was set as the diversity-correction factor. | Default value provided across all dwelling categories at a GB-level, across all behaviour types (based on weighted average profile). | 3 | Based on the Electrification of Heat trial project funded by DESNZ. | 3 | This trial project was focused on ca. 700 homes equipped with heat pumps. | 3 | The data was recorded between December 2020 and September 2023. | 3 | The data is from UK homes and include information about location but this information was not used as regional differences are instead captured through the temperature difference CPA. | 3 | This data does not account for potential improvements in the quality of installation, controls, etc. as it is based on metered data. | 1 | Weather impacts captured by considering relevant temperature ranges. Future changes in temperature (as a result of climate change) are not considered. | 2
HP09 | Minimum count for full diversification | The minimum number of heat pumps at which the profile should be considered fully diversified. | Defined for each representative day | # of heat pumps | Energy Systems Catapult Electrification of heat data, Cleansed 30-minute interval dataset | https://beta.ukdataservice.ac.uk/datacatalogue/studies/study?id=9209 | Set by finding the minimum count for full diversification is the lowest count of heat pumps that gives a diversity correction of <1.2, using the HP08 curves. | Default value provided across all dwelling categories at a GB-level, for each representative day. | 2 | Based on the Electrification of Heat trial project funded by DESNZ. | 3 | This trial project was focused on ca. 700 homes equipped with heat pumps. | 3 | The data was recorded between December 2020 and September 2023. | 3 | The data is from UK homes and include information about location but this information was not used as regional differences are instead captured through the temperature difference CPA. | 2 | This data does not account for changes in consumer behaviour, as it is based on metered data. | 1 | Weather impacts captured by considering relevant temperature ranges. Future changes in temperature (as a result of climate change) are not considered. | 2

## HP CPA list
Back to contents
Back to HP CPA Summary Table
CPA ID | CPA number | CPA | Unit | BB1 | BB2 (if applicable) | Dwelling Category | Representative day | Behaviour | Level of spatial granularity | Temporal granularity | New build status
HP01_DC1_NA_ALL_GB_EXIST | HP01 | Size of HP | kW_th | Lct_BB005 | Lct_BB006 | Detached | N/A | Applicable across all | GB | None | Existing build
HP01_DC2_NA_ALL_GB_EXIST | HP01 | Size of HP | kW_th | Lct_BB005 | Lct_BB006 | Semi-detached and end-terraced | N/A | Applicable across all | GB | None | Existing build
HP01_DC3_NA_ALL_GB_EXIST | HP01 | Size of HP | kW_th | Lct_BB005 | Lct_BB006 | Mid-terraced | N/A | Applicable across all | GB | None | Existing build
HP01_DC4_NA_ALL_GB_EXIST | HP01 | Size of HP | kW_th | Lct_BB005 | Lct_BB006 | Flats | N/A | Applicable across all | GB | None | Existing build
HP01_DC1_NA_ALL_GB_NEW | HP01 | Size of HP | kW_th | Lct_BB005 | Lct_BB006 | Detached | N/A | Applicable across all | GB | None | New build
HP01_DC2_NA_ALL_GB_NEW | HP01 | Size of HP | kW_th | Lct_BB005 | Lct_BB006 | Semi-detached and end-terraced | N/A | Applicable across all | GB | None | New build
HP01_DC3_NA_ALL_GB_NEW | HP01 | Size of HP | kW_th | Lct_BB005 | Lct_BB006 | Mid-terraced | N/A | Applicable across all | GB | None | New build
HP01_DC4_NA_ALL_GB_NEW | HP01 | Size of HP | kW_th | Lct_BB005 | Lct_BB006 | Flats | N/A | Applicable across all | GB | None | New build
HP02_ALL_NA_ALL_GB_EXIST | HP02 | Dwelling thermal efficiency factor | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Annual | Existing build
HP02_ALL_NA_ALL_GB_NEW | HP02 | Dwelling thermal efficiency factor | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | None | New build
HP03_ALL_WP_ALL_Region | HP03 | Efficiency of HP | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | Region | None
HP03_ALL_SP_ALL_Region | HP03 | Efficiency of HP | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | Region | None
HP03_ALL_SSP_ALL_Region | HP03 | Efficiency of HP | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | Region | None
HP03_ALL_MIN_ALL_Region | HP03 | Efficiency of HP | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | Region | None
HP04_ALL_WP_ALL_GB | HP04 | Specific HP heat output | daily kWh_th/ kW_th/ °C | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | None
HP04_ALL_SP_ALL_GB | HP04 | Specific HP heat output | daily kWh_th/ kW_th | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | None
HP04_ALL_SSP_ALL_GB | HP04 | Specific HP heat output | daily kWh_th/ kW_th/ °C | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | None
HP04_ALL_MIN_ALL_GB | HP04 | Specific HP heat output | daily kWh_th/ kW_th | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | None
HP05_NA_WP_NA_Region | HP05 | Temperature difference | °C | N/A | N/A | N/A | Peak demand winter day | N/A | Region | None
HP05_NA_SP_NA_Region | HP05 | Temperature difference | °C | N/A | N/A | N/A | Peak demand summer day | N/A | Region | None
HP05_NA_SSP_NA_Region | HP05 | Temperature difference | °C | N/A | N/A | N/A | Peak demand shoulder season day | N/A | Region | None
HP05_NA_MIN_NA_Region | HP05 | Temperature difference | °C | N/A | N/A | N/A | Overall minimum demand day | N/A | Region | None
HP05_ALL_WP_WA_GB | HP05 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | Half-hourly
HP06_ALL_WP_BHV1_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | Half-hourly
HP06_ALL_WP_BHV2_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | Half-hourly
HP06_ALL_WP_BHV3_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | Half-hourly
HP07_ALL_SP_WA_GB | HP07 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Weighted average | GB | Half-hourly
HP06_ALL_SP_BHV1_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Bimodal (reference only) | GB | Half-hourly
HP06_ALL_SP_BHV2_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Daytime (reference only) | GB | Half-hourly
HP06_ALL_SP_BHV3_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Continuous (reference only) | GB | Half-hourly
HP07_ALL_SSP_WA_GB | HP07 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | Half-hourly
HP06_ALL_SSP_BHV1_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | Half-hourly
HP06_ALL_SSP_BHV2_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | Half-hourly
HP06_ALL_SSP_BHV3_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | Half-hourly
HP07_ALL_MIN_WA_GB | HP07 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Weighted average | GB | Half-hourly
HP06_ALL_MIN_BHV1_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Bimodal (reference only) | GB | Half-hourly
HP06_ALL_MIN_BHV2_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Daytime (reference only) | GB | Half-hourly
HP06_ALL_MIN_BHV3_GB | HP06 | Normalised half-hourly profile | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Continuous (reference only) | GB | Half-hourly
HP07_ALL_ALL_BHV1_GB | HP07 | Proportion of consumers by behaviour | % | Lct_BB005 | Lct_BB006 | Applicable across all | Applicable across all | Bimodal (reference only) | GB | None
HP07_ALL_ALL_BHV2_GB | HP07 | Proportion of consumers by behaviour | % | Lct_BB005 | Lct_BB006 | Applicable across all | Applicable across all | Daytime (reference only) | GB | None
HP07_ALL_ALL_BHV3_GB | HP07 | Proportion of consumers by behaviour | % | Lct_BB005 | Lct_BB006 | Applicable across all | Applicable across all | Continuous (reference only) | GB | None
HP08_ALL_WP_ALL_GB | HP08 | Diversity-correction curve | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | None
HP08_ALL_SP_ALL_GB | HP08 | Diversity-correction curve | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | None
HP08_ALL_SSP_ALL_GB | HP08 | Diversity-correction curve | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | None
HP08_ALL_MIN_ALL_GB | HP08 | Diversity-correction curve | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | None
HP09_ALL_WP_ALL_GB | HP09 | Minimum count for full diversification | # of heat pumps | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | None
HP09_ALL_SP_ALL_GB | HP09 | Minimum count for full diversification | # of heat pumps | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | None
HP09_ALL_SSP_ALL_GB | HP09 | Minimum count for full diversification | # of heat pumps | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | None
HP09_ALL_MIN_ALL_GB | HP09 | Minimum count for full diversification | # of heat pumps | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | None

## HP CPA Process
HP CPA Process
Back to contents
Back to HP CPA Summary Table

## HP01
Back to contents
Back to HP CPA Summary Table
CPA ID | Unit | BB1 | BB2 | Dwelling Category | Representative day | Behaviour | Level of spatial granularity | New build status | Default value | Range (lower bound) | Range (upper bound)
HP01_DC1_NA_ALL_GB_EXIST | kW_th | Lct_BB005 | Lct_BB006 | Detached | N/A | Applicable across all | GB | Existing build | 13.6 | 12.6 | 14.6
HP01_DC2_NA_ALL_GB_EXIST | kW_th | Lct_BB005 | Lct_BB006 | Semi-detached and end-terraced | N/A | Applicable across all | GB | Existing build | 8.7 | 7.9 | 9.5
HP01_DC3_NA_ALL_GB_EXIST | kW_th | Lct_BB005 | Lct_BB006 | Mid-terraced | N/A | Applicable across all | GB | Existing build | 6.3 | 5.9 | 6.7
HP01_DC4_NA_ALL_GB_EXIST | kW_th | Lct_BB005 | Lct_BB006 | Flats | N/A | Applicable across all | GB | Existing build | 4.4 | 4 | 4.8
HP01_DC1_NA_ALL_GB_NEW | kW_th | Lct_BB005 | Lct_BB006 | Detached | N/A | Applicable across all | GB | New build | 9.9 | N/A | N/A
HP01_DC2_NA_ALL_GB_NEW | kW_th | Lct_BB005 | Lct_BB006 | Semi-detached and end-terraced | N/A | Applicable across all | GB | New build | 4.2 | N/A | N/A
HP01_DC3_NA_ALL_GB_NEW | kW_th | Lct_BB005 | Lct_BB006 | Mid-terraced | N/A | Applicable across all | GB | New build | 4 | N/A | N/A
HP01_DC4_NA_ALL_GB_NEW | kW_th | Lct_BB005 | Lct_BB006 | Flats | N/A | Applicable across all | GB | New build | 2.1 | N/A | N/A

## HP02
Back to contents
Back to HP CPA Summary Table
CPA ID | Unit | BB1 | BB2 | Dwelling Category | Representative day | Behaviour | Level of spatial granularity | New build status | Year | Default value
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2024 | 101%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2025 | 100%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2026 | 99.05%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2027 | 98.09%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2028 | 97.14%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2029 | 96.18%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2030 | 95.23%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2031 | 94.27%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2032 | 93.32%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2033 | 92.36%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2034 | 91.41%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2035 | 90.45%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2036 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2037 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2038 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2039 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2040 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2041 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2042 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2043 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2044 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2045 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2046 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2047 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2048 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2049 | 89.5%
HP02_ALL_NA_ALL_GB_EXIST | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | Existing build | 2050 | 89.5%
HP02_ALL_NA_ALL_GB_NEW | % | Lct_BB005 | Lct_BB006 | Applicable across all | N/A | Applicable across all | GB | New build | all years | 100%

## HP03
Back to contents
Back to HP CPA Summary Table
CPA ID | Unit | BB1 | BB2 | Dwelling Category | Representative day | Behaviour | Licence area | Default value
HP03_ALL_WP_ALL_EastMids | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | East Midlands | 2.57
HP03_ALL_WP_ALL_East | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | Eastern | 2.58
HP03_ALL_WP_ALL_London | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | London | 2.66
HP03_ALL_WP_ALL_MersNWales | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | Merseyside and North Wales | 2.59
HP03_ALL_WP_ALL_Wmids | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | Midlands | 2.55
HP03_ALL_WP_ALL_NorthScot | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | North Scotland | 2.48
HP03_ALL_WP_ALL_NorthWest | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | North Western | 2.51
HP03_ALL_WP_ALL_North | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | Northern | 2.49
HP03_ALL_WP_ALL_SouthEast | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | South Eastern | 2.61
HP03_ALL_WP_ALL_SouthScot | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | South Scotland | 2.48
HP03_ALL_WP_ALL_SouthWales | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | South Wales | 2.56
HP03_ALL_WP_ALL_SouthWest | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | South Western | 2.69
HP03_ALL_WP_ALL_South | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | Southern | 2.59
HP03_ALL_WP_ALL_Yorkshire | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | Yorkshire | 2.57
HP03_ALL_SP_ALL_EastMids | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | East Midlands | 2.83
HP03_ALL_SP_ALL_East | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | Eastern | 2.83
HP03_ALL_SP_ALL_London | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | London | 2.83
HP03_ALL_SP_ALL_MersNWales | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | Merseyside and North Wales | 2.83
HP03_ALL_SP_ALL_Wmids | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | Midlands | 2.83
HP03_ALL_SP_ALL_NorthScot | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | North Scotland | 2.83
HP03_ALL_SP_ALL_NorthWest | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | North Western | 2.83
HP03_ALL_SP_ALL_North | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | Northern | 2.83
HP03_ALL_SP_ALL_SouthEast | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | South Eastern | 2.83
HP03_ALL_SP_ALL_SouthScot | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | South Scotland | 2.83
HP03_ALL_SP_ALL_SouthWales | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | South Wales | 2.83
HP03_ALL_SP_ALL_SouthWest | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | South Western | 2.83
HP03_ALL_SP_ALL_South | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | Southern | 2.83
HP03_ALL_SP_ALL_Yorkshire | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | Yorkshire | 2.83
HP03_ALL_SSP_ALL_EastMids | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | East Midlands | 3.23
HP03_ALL_SSP_ALL_East | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | Eastern | 3.25
HP03_ALL_SSP_ALL_London | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | London | 3.32
HP03_ALL_SSP_ALL_MersNWales | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | Merseyside and North Wales | 3.18
HP03_ALL_SSP_ALL_Wmids | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | Midlands | 3.2
HP03_ALL_SSP_ALL_NorthScot | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | North Scotland | 2.97
HP03_ALL_SSP_ALL_NorthWest | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | North Western | 3.1
HP03_ALL_SSP_ALL_North | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | Northern | 3.08
HP03_ALL_SSP_ALL_SouthEast | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | South Eastern | 3.27
HP03_ALL_SSP_ALL_SouthScot | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | South Scotland | 3.03
HP03_ALL_SSP_ALL_SouthWales | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | South Wales | 3.16
HP03_ALL_SSP_ALL_SouthWest | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | South Western | 3.27
HP03_ALL_SSP_ALL_South | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | Southern | 3.23
HP03_ALL_SSP_ALL_Yorkshire | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | Yorkshire | 3.21
HP03_ALL_MIN_ALL_EastMids | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | East Midlands | 2.83
HP03_ALL_MIN_ALL_East | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | Eastern | 2.83
HP03_ALL_MIN_ALL_London | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | London | 2.83
HP03_ALL_MIN_ALL_MersNWales | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | Merseyside and North Wales | 2.83
HP03_ALL_MIN_ALL_Wmids | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | Midlands | 2.83
HP03_ALL_MIN_ALL_NorthScot | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | North Scotland | 2.83
HP03_ALL_MIN_ALL_NorthWest | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | North Western | 2.83
HP03_ALL_MIN_ALL_North | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | Northern | 2.83
HP03_ALL_MIN_ALL_SouthEast | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | South Eastern | 2.83
HP03_ALL_MIN_ALL_SouthScot | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | South Scotland | 2.83
HP03_ALL_MIN_ALL_SouthWales | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | South Wales | 2.83
HP03_ALL_MIN_ALL_SouthWest | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | South Western | 2.83
HP03_ALL_MIN_ALL_South | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | Southern | 2.83
HP03_ALL_MIN_ALL_Yorkshire | heat:power | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | Yorkshire | 2.83

## HP04
Back to contents
Back to HP CPA Summary Table
CPA ID | Unit | BB1 | BB2 | Dwelling Category | Representative day | Behaviour | Level of spatial granularity | Default value
HP04_ALL_WP_ALL_GB | daily kWh_th/ kW_th/ °C | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 0.34
HP04_ALL_SP_ALL_GB | daily kWh_th/ kW_th | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 0.45
HP04_ALL_SSP_ALL_GB | daily kWh_th/ kW_th/ °C | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 0.34
HP04_ALL_MIN_ALL_GB | daily kWh_th/ kW_th | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 0.45

## HP05
Back to contents
Back to HP CPA Summary Table
CPA ID | Unit | BB | Dwelling Category | Representative day | Behaviour | Licence Area | Default value | Range (lower bound) | Range (upper bound)
HP05_NA_WP_NA_EastMids | °C | N/A | N/A | Peak demand winter day | N/A | East Midlands | 21 | 20.2 | 21.8
HP05_NA_WP_NA_East | °C | N/A | N/A | Peak demand winter day | N/A | Eastern | 20.9 | 19.9 | 21.6
HP05_NA_WP_NA_London | °C | N/A | N/A | Peak demand winter day | N/A | London | 19.9 | 19.5 | 20.2
HP05_NA_WP_NA_MersNWales | °C | N/A | N/A | Peak demand winter day | N/A | Merseyside and North Wales | 20.8 | 18.3 | 22.7
HP05_NA_WP_NA_Wmids | °C | N/A | N/A | Peak demand winter day | N/A | Midlands | 21.3 | 20.3 | 22.5
HP05_NA_WP_NA_NorthScot | °C | N/A | N/A | Peak demand winter day | N/A | North Scotland | 22.3 | 18.9 | 26.1
HP05_NA_WP_NA_NorthWest | °C | N/A | N/A | Peak demand winter day | N/A | North Western | 21.9 | 20 | 23.9
HP05_NA_WP_NA_North | °C | N/A | N/A | Peak demand winter day | N/A | Northern | 22.2 | 20.6 | 24.6
HP05_NA_WP_NA_SouthEast | °C | N/A | N/A | Peak demand winter day | N/A | South Eastern | 20.5 | 19.1 | 21.2
HP05_NA_WP_NA_SouthScot | °C | N/A | N/A | Peak demand winter day | N/A | South Scotland | 22.3 | 19.7 | 24.2
HP05_NA_WP_NA_SouthWales | °C | N/A | N/A | Peak demand winter day | N/A | South Wales | 21.1 | 18.2 | 22.8
HP05_NA_WP_NA_SouthWest | °C | N/A | N/A | Peak demand winter day | N/A | South Western | 19.5 | 17.5 | 20.9
HP05_NA_WP_NA_South | °C | N/A | N/A | Peak demand winter day | N/A | Southern | 20.7 | 19 | 21.8
HP05_NA_WP_NA_Yorkshire | °C | N/A | N/A | Peak demand winter day | N/A | Yorkshire | 21 | 20.1 | 23
HP05_NA_SP_NA_EastMids | °C | N/A | N/A | Peak demand summer day | N/A | East Midlands | N/A
HP05_NA_SP_NA_East | °C | N/A | N/A | Peak demand summer day | N/A | Eastern | N/A
HP05_NA_SP_NA_London | °C | N/A | N/A | Peak demand summer day | N/A | London | N/A
HP05_NA_SP_NA_MersNWales | °C | N/A | N/A | Peak demand summer day | N/A | Merseyside and North Wales | N/A
HP05_NA_SP_NA_Wmids | °C | N/A | N/A | Peak demand summer day | N/A | Midlands | N/A
HP05_NA_SP_NA_NorthScot | °C | N/A | N/A | Peak demand summer day | N/A | North Scotland | N/A
HP05_NA_SP_NA_NorthWest | °C | N/A | N/A | Peak demand summer day | N/A | North Western | N/A
HP05_NA_SP_NA_North | °C | N/A | N/A | Peak demand summer day | N/A | Northern | N/A
HP05_NA_SP_NA_SouthEast | °C | N/A | N/A | Peak demand summer day | N/A | South Eastern | N/A
HP05_NA_SP_NA_SouthScot | °C | N/A | N/A | Peak demand summer day | N/A | South Scotland | N/A
HP05_NA_SP_NA_SouthWales | °C | N/A | N/A | Peak demand summer day | N/A | South Wales | N/A
HP05_NA_SP_NA_SouthWest | °C | N/A | N/A | Peak demand summer day | N/A | South Western | N/A
HP05_NA_SP_NA_South | °C | N/A | N/A | Peak demand summer day | N/A | Southern | N/A
HP05_NA_SP_NA_Yorkshire | °C | N/A | N/A | Peak demand summer day | N/A | Yorkshire | N/A
HP05_NA_SSP_NA_EastMids | °C | N/A | N/A | Peak demand shoulder season day | N/A | East Midlands | 13.7 | 12.9 | 15
HP05_NA_SSP_NA_East | °C | N/A | N/A | Peak demand shoulder season day | N/A | Eastern | 13.5 | 12.4 | 14.3
HP05_NA_SSP_NA_London | °C | N/A | N/A | Peak demand shoulder season day | N/A | London | 12.3 | 12 | 12.6
HP05_NA_SSP_NA_MersNWales | °C | N/A | N/A | Peak demand shoulder season day | N/A | Merseyside and North Wales | 14.3 | 11.8 | 16.6
HP05_NA_SSP_NA_Wmids | °C | N/A | N/A | Peak demand shoulder season day | N/A | Midlands | 14.1 | 13.1 | 15.6
HP05_NA_SSP_NA_NorthScot | °C | N/A | N/A | Peak demand shoulder season day | N/A | North Scotland | 16.3 | 13.5 | 20.1
HP05_NA_SSP_NA_NorthWest | °C | N/A | N/A | Peak demand shoulder season day | N/A | North Western | 15.2 | 13.1 | 17.5
HP05_NA_SSP_NA_North | °C | N/A | N/A | Peak demand shoulder season day | N/A | Northern | 15.4 | 13.5 | 18.4
HP05_NA_SSP_NA_SouthEast | °C | N/A | N/A | Peak demand shoulder season day | N/A | South Eastern | 13.3 | 12 | 14
HP05_NA_SSP_NA_SouthScot | °C | N/A | N/A | Peak demand shoulder season day | N/A | South Scotland | 15.8 | 13.7 | 18
HP05_NA_SSP_NA_SouthWales | °C | N/A | N/A | Peak demand shoulder season day | N/A | South Wales | 14.6 | 12.3 | 16.7
HP05_NA_SSP_NA_SouthWest | °C | N/A | N/A | Peak demand shoulder season day | N/A | South Western | 13.3 | 11.7 | 15.1
HP05_NA_SSP_NA_South | °C | N/A | N/A | Peak demand shoulder season day | N/A | Southern | 13.7 | 11.8 | 14.7
HP05_NA_SSP_NA_Yorkshire | °C | N/A | N/A | Peak demand shoulder season day | N/A | Yorkshire | 14 | 13.1 | 16.5
HP05_NA_MIN_NA_EastMids | °C | N/A | N/A | Overall minimum demand day | N/A | East Midlands | N/A
HP05_NA_MIN_NA_East | °C | N/A | N/A | Overall minimum demand day | N/A | Eastern | N/A
HP05_NA_MIN_NA_London | °C | N/A | N/A | Overall minimum demand day | N/A | London | N/A
HP05_NA_MIN_NA_MersNWales | °C | N/A | N/A | Overall minimum demand day | N/A | Merseyside and North Wales | N/A
HP05_NA_MIN_NA_Wmids | °C | N/A | N/A | Overall minimum demand day | N/A | Midlands | N/A
HP05_NA_MIN_NA_NorthScot | °C | N/A | N/A | Overall minimum demand day | N/A | North Scotland | N/A
HP05_NA_MIN_NA_NorthWest | °C | N/A | N/A | Overall minimum demand day | N/A | North Western | N/A
HP05_NA_MIN_NA_North | °C | N/A | N/A | Overall minimum demand day | N/A | Northern | N/A
HP05_NA_MIN_NA_SouthEast | °C | N/A | N/A | Overall minimum demand day | N/A | South Eastern | N/A
HP05_NA_MIN_NA_SouthScot | °C | N/A | N/A | Overall minimum demand day | N/A | South Scotland | N/A
HP05_NA_MIN_NA_SouthWales | °C | N/A | N/A | Overall minimum demand day | N/A | South Wales | N/A
HP05_NA_MIN_NA_SouthWest | °C | N/A | N/A | Overall minimum demand day | N/A | South Western | N/A
HP05_NA_MIN_NA_South | °C | N/A | N/A | Overall minimum demand day | N/A | Southern | N/A
HP05_NA_MIN_NA_Yorkshire | °C | N/A | N/A | Overall minimum demand day | N/A | Yorkshire | N/A

## HP06
Back to contents
Back to HP CPA Summary Table
CPA ID | Unit | BB1 | BB2 | Dwelling Category | Representative day | Behaviour | Level of spatial granularity | Start of half hour period | Default value
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 0:00 | 0.0274
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 0:30 | 0.0283
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 1:00 | 0.0298
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 1:30 | 0.0314
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 2:00 | 0.0328
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 2:30 | 0.0344
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 3:00 | 0.0354
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 3:30 | 0.0366
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 4:00 | 0.038
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 4:30 | 0.0403
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 5:00 | 0.0433
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 5:30 | 0.0481
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 6:00 | 0.0529
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 6:30 | 0.0574
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 7:00 | 0.0591
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 7:30 | 0.0587
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 8:00 | 0.0567
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 8:30 | 0.054
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 9:00 | 0.0507
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 9:30 | 0.0477
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 10:00 | 0.0449
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 10:30 | 0.043
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 11:00 | 0.041
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 11:30 | 0.0398
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 12:00 | 0.0388
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 12:30 | 0.0383
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 13:00 | 0.0376
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 13:30 | 0.0373
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 14:00 | 0.0375
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 14:30 | 0.0389
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 15:00 | 0.0407
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 15:30 | 0.0429
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 16:00 | 0.0448
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 16:30 | 0.0466
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 17:00 | 0.0476
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 17:30 | 0.0481
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 18:00 | 0.048
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 18:30 | 0.0481
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 19:00 | 0.0478
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 19:30 | 0.0472
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 20:00 | 0.0458
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 20:30 | 0.0435
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 21:00 | 0.0405
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 21:30 | 0.036
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 22:00 | 0.0317
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 22:30 | 0.0281
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 23:00 | 0.0266
HP06_ALL_WP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Weighted average | GB | 23:30 | 0.0261
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 0:00 | 0.0184
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 0:30 | 0.0193
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 1:00 | 0.0206
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 1:30 | 0.0226
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 2:00 | 0.0242
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 2:30 | 0.0264
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 3:00 | 0.0277
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 3:30 | 0.0292
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 4:00 | 0.0309
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 4:30 | 0.0342
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 5:00 | 0.0385
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 5:30 | 0.0454
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 6:00 | 0.0527
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 6:30 | 0.0601
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 7:00 | 0.0646
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 7:30 | 0.067
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 8:00 | 0.0674
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 8:30 | 0.067
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 9:00 | 0.0652
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 9:30 | 0.0626
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 10:00 | 0.0596
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 10:30 | 0.0567
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 11:00 | 0.0537
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 11:30 | 0.051
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 12:00 | 0.0486
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 12:30 | 0.0472
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 13:00 | 0.0458
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 13:30 | 0.0447
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 14:00 | 0.0438
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 14:30 | 0.0439
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 15:00 | 0.0445
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 15:30 | 0.045
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 16:00 | 0.0451
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 16:30 | 0.045
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 17:00 | 0.0446
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 17:30 | 0.0438
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 18:00 | 0.0427
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 18:30 | 0.0422
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 19:00 | 0.0421
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 19:30 | 0.0418
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 20:00 | 0.0405
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 20:30 | 0.0384
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 21:00 | 0.0352
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 21:30 | 0.03
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 22:00 | 0.0244
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 22:30 | 0.0198
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 23:00 | 0.0181
HP06_ALL_WP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 23:30 | 0.0176
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 0:00 | 0.0313
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 0:30 | 0.0327
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 1:00 | 0.0348
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 1:30 | 0.0367
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 2:00 | 0.0379
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 2:30 | 0.0391
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 3:00 | 0.0399
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 3:30 | 0.0411
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 4:00 | 0.0426
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 4:30 | 0.0447
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 5:00 | 0.0472
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 5:30 | 0.051
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 6:00 | 0.0545
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 6:30 | 0.0572
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 7:00 | 0.0566
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 7:30 | 0.0532
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 8:00 | 0.0477
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 8:30 | 0.0417
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 9:00 | 0.0362
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 9:30 | 0.0321
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 10:00 | 0.0293
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 10:30 | 0.028
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 11:00 | 0.0273
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 11:30 | 0.028
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 12:00 | 0.0286
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 12:30 | 0.0291
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 13:00 | 0.0293
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 13:30 | 0.0301
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 14:00 | 0.0316
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 14:30 | 0.0346
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 15:00 | 0.0382
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 15:30 | 0.0427
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 16:00 | 0.0472
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 16:30 | 0.0515
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 17:00 | 0.0547
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 17:30 | 0.0567
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 18:00 | 0.0577
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 18:30 | 0.0582
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 19:00 | 0.0576
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 19:30 | 0.0561
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 20:00 | 0.054
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 20:30 | 0.0506
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 21:00 | 0.0468
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 21:30 | 0.0414
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 22:00 | 0.0372
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 22:30 | 0.0333
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 23:00 | 0.0315
HP06_ALL_WP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 23:30 | 0.0307
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 0:00 | 0.0464
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 0:30 | 0.0459
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 1:00 | 0.046
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 1:30 | 0.0459
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 2:00 | 0.0466
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 2:30 | 0.0474
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 3:00 | 0.0479
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 3:30 | 0.0482
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 4:00 | 0.0481
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 4:30 | 0.0478
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 5:00 | 0.048
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 5:30 | 0.0486
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 6:00 | 0.0491
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 6:30 | 0.0485
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 7:00 | 0.0478
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 7:30 | 0.0471
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 8:00 | 0.0473
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 8:30 | 0.0466
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 9:00 | 0.0449
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 9:30 | 0.0434
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 10:00 | 0.042
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 10:30 | 0.041
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 11:00 | 0.0389
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 11:30 | 0.0374
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 12:00 | 0.0359
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 12:30 | 0.0352
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 13:00 | 0.0342
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 13:30 | 0.0339
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 14:00 | 0.0338
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 14:30 | 0.0345
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 15:00 | 0.0352
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 15:30 | 0.0361
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 16:00 | 0.0365
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 16:30 | 0.0368
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 17:00 | 0.0368
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 17:30 | 0.037
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 18:00 | 0.0372
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 18:30 | 0.0378
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 19:00 | 0.0382
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 19:30 | 0.0389
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 20:00 | 0.0392
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 20:30 | 0.0396
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 21:00 | 0.0397
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 21:30 | 0.04
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 22:00 | 0.0401
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 22:30 | 0.0403
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 23:00 | 0.041
HP06_ALL_WP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 23:30 | 0.0413
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 0:00 | 0.0141
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 0:30 | 0.0129
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 1:00 | 0.0119
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 1:30 | 0.0116
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 2:00 | 0.0114
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 2:30 | 0.0113
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 3:00 | 0.0117
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 3:30 | 0.0124
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 4:00 | 0.014
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 4:30 | 0.017
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 5:00 | 0.0252
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 5:30 | 0.0373
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 6:00 | 0.0577
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 6:30 | 0.0798
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 7:00 | 0.0896
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 7:30 | 0.0852
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 8:00 | 0.0752
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 8:30 | 0.0626
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 9:00 | 0.0538
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 9:30 | 0.0466
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 10:00 | 0.0411
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 10:30 | 0.0372
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 11:00 | 0.0351
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 11:30 | 0.0354
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 12:00 | 0.0374
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 12:30 | 0.0361
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 13:00 | 0.0339
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 13:30 | 0.0315
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 14:00 | 0.0298
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 14:30 | 0.0302
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 15:00 | 0.0318
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 15:30 | 0.0398
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 16:00 | 0.0547
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 16:30 | 0.0729
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 17:00 | 0.0828
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 17:30 | 0.0796
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 18:00 | 0.0788
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 18:30 | 0.073
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 19:00 | 0.066
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 19:30 | 0.0579
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 20:00 | 0.0518
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 20:30 | 0.0465
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 21:00 | 0.0411
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 21:30 | 0.0363
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 22:00 | 0.0327
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 22:30 | 0.0268
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 23:00 | 0.0212
HP06_ALL_SP_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 23:30 | 0.0172
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 0:00 | 0.0264
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 0:30 | 0.0275
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 1:00 | 0.0289
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 1:30 | 0.0306
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 2:00 | 0.0321
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 2:30 | 0.0344
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 3:00 | 0.0357
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 3:30 | 0.0376
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 4:00 | 0.039
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 4:30 | 0.0433
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 5:00 | 0.0476
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 5:30 | 0.0549
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 6:00 | 0.0598
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 6:30 | 0.0639
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 7:00 | 0.0637
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 7:30 | 0.0618
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 8:00 | 0.0578
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 8:30 | 0.053
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 9:00 | 0.0481
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 9:30 | 0.0441
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 10:00 | 0.041
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 10:30 | 0.0389
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 11:00 | 0.0373
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 11:30 | 0.0365
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 12:00 | 0.0357
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 12:30 | 0.0355
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 13:00 | 0.035
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 13:30 | 0.0352
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 14:00 | 0.0358
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 14:30 | 0.038
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 15:00 | 0.0399
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 15:30 | 0.0426
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 16:00 | 0.0447
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 16:30 | 0.0475
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 17:00 | 0.0491
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 17:30 | 0.0502
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 18:00 | 0.0502
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 18:30 | 0.0501
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 19:00 | 0.0493
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 19:30 | 0.0479
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 20:00 | 0.046
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 20:30 | 0.0431
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 21:00 | 0.0396
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 21:30 | 0.0348
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 22:00 | 0.0304
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 22:30 | 0.0266
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 23:00 | 0.0247
HP06_ALL_SSP_WA_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Weighted average | GB | 23:30 | 0.0241
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 0:00 | 0.0194
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 0:30 | 0.0199
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 1:00 | 0.021
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 1:30 | 0.0223
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 2:00 | 0.0235
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 2:30 | 0.0257
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 3:00 | 0.0273
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 3:30 | 0.0298
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 4:00 | 0.0314
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 4:30 | 0.036
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 5:00 | 0.041
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 5:30 | 0.0507
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 6:00 | 0.0588
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 6:30 | 0.0674
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 7:00 | 0.0715
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 7:30 | 0.0742
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 8:00 | 0.0735
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 8:30 | 0.071
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 9:00 | 0.0668
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 9:30 | 0.0628
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 10:00 | 0.0587
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 10:30 | 0.0554
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 11:00 | 0.0524
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 11:30 | 0.0506
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 12:00 | 0.0488
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 12:30 | 0.0475
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 13:00 | 0.0457
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 13:30 | 0.0444
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 14:00 | 0.0432
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 14:30 | 0.043
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 15:00 | 0.0426
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 15:30 | 0.0427
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 16:00 | 0.042
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 16:30 | 0.0418
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 17:00 | 0.0407
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 17:30 | 0.0397
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 18:00 | 0.0384
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 18:30 | 0.0381
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 19:00 | 0.0378
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 19:30 | 0.0377
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 20:00 | 0.0371
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 20:30 | 0.0356
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 21:00 | 0.0331
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 21:30 | 0.0289
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 22:00 | 0.0245
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 22:30 | 0.0203
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 23:00 | 0.0182
HP06_ALL_SSP_BHV2_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 23:30 | 0.0175
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 0:00 | 0.029
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 0:30 | 0.0305
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 1:00 | 0.0324
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 1:30 | 0.0347
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 2:00 | 0.0366
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 2:30 | 0.0395
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 3:00 | 0.0406
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 3:30 | 0.0423
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 4:00 | 0.0439
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 4:30 | 0.0486
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 5:00 | 0.0532
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 5:30 | 0.0596
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 6:00 | 0.0625
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 6:30 | 0.0631
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 7:00 | 0.0589
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 7:30 | 0.0524
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 8:00 | 0.0447
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 8:30 | 0.0371
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 9:00 | 0.0308
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 9:30 | 0.0263
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 10:00 | 0.0239
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 10:30 | 0.023
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 11:00 | 0.0227
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 11:30 | 0.023
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 12:00 | 0.0233
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 12:30 | 0.0243
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 13:00 | 0.0249
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 13:30 | 0.0269
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 14:00 | 0.0292
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 14:30 | 0.0341
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 15:00 | 0.0385
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 15:30 | 0.0443
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 16:00 | 0.0495
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 16:30 | 0.0556
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 17:00 | 0.0601
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 17:30 | 0.0632
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 18:00 | 0.0645
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 18:30 | 0.0646
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 19:00 | 0.063
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 19:30 | 0.06
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 20:00 | 0.0563
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 20:30 | 0.0514
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 21:00 | 0.0461
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 21:30 | 0.0398
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 22:00 | 0.0344
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 22:30 | 0.0303
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 23:00 | 0.0283
HP06_ALL_SSP_BHV1_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 23:30 | 0.0278
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 0:00 | 0.0479
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 0:30 | 0.0488
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 1:00 | 0.0498
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 1:30 | 0.0507
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 2:00 | 0.0512
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 2:30 | 0.0519
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 3:00 | 0.0519
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 3:30 | 0.0521
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 4:00 | 0.0519
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 4:30 | 0.0523
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 5:00 | 0.0523
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 5:30 | 0.0524
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 6:00 | 0.0516
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 6:30 | 0.0506
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 7:00 | 0.0493
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 7:30 | 0.0481
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 8:00 | 0.0467
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 8:30 | 0.0452
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 9:00 | 0.0436
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 9:30 | 0.0416
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 10:00 | 0.0399
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 10:30 | 0.0383
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 11:00 | 0.0368
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 11:30 | 0.0355
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 12:00 | 0.0342
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 12:30 | 0.0335
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 13:00 | 0.0327
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 13:30 | 0.0323
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 14:00 | 0.0324
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 14:30 | 0.0329
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 15:00 | 0.0333
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 15:30 | 0.0337
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 16:00 | 0.034
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 16:30 | 0.0349
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 17:00 | 0.0354
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 17:30 | 0.036
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 18:00 | 0.0361
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 18:30 | 0.0366
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 19:00 | 0.0371
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 19:30 | 0.0376
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 20:00 | 0.0379
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 20:30 | 0.038
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 21:00 | 0.0381
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 21:30 | 0.0383
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 22:00 | 0.0385
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 22:30 | 0.0387
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 23:00 | 0.0387
HP06_ALL_SSP_BHV3_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 23:30 | 0.0385
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 0:00 | 0.0141
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 0:30 | 0.0129
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 1:00 | 0.0119
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 1:30 | 0.0116
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 2:00 | 0.0114
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 2:30 | 0.0113
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 3:00 | 0.0117
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 3:30 | 0.0124
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 4:00 | 0.014
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 4:30 | 0.017
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 5:00 | 0.0252
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 5:30 | 0.0373
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 6:00 | 0.0577
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 6:30 | 0.0798
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 7:00 | 0.0896
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 7:30 | 0.0852
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 8:00 | 0.0752
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 8:30 | 0.0626
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 9:00 | 0.0538
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 9:30 | 0.0466
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 10:00 | 0.0411
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 10:30 | 0.0372
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 11:00 | 0.0351
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 11:30 | 0.0354
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 12:00 | 0.0374
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 12:30 | 0.0361
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 13:00 | 0.0339
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 13:30 | 0.0315
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 14:00 | 0.0298
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 14:30 | 0.0302
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 15:00 | 0.0318
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 15:30 | 0.0398
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 16:00 | 0.0547
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 16:30 | 0.0729
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 17:00 | 0.0828
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 17:30 | 0.0796
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 18:00 | 0.0788
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 18:30 | 0.073
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 19:00 | 0.066
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 19:30 | 0.0579
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 20:00 | 0.0518
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 20:30 | 0.0465
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 21:00 | 0.0411
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 21:30 | 0.0363
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 22:00 | 0.0327
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 22:30 | 0.0268
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 23:00 | 0.0212
HP06_ALL_MIN_ALL_GB | kW/daily kWh | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 23:30 | 0.0172

## HP07
Back to contents
Back to HP CPA Summary Table
CPA ID | Unit | BB1 | BB2 | Dwelling Category | Representative day | Behaviour | Level of spatial granularity | Default value
HP07_ALL_WP_BHV2_GB | % | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Daytime (reference only) | GB | 46%
HP07_ALL_WP_BHV1_GB | % | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Bimodal (reference only) | GB | 40.5%
HP07_ALL_WP_BHV3_GB | % | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Continuous (reference only) | GB | 13.5%
HP07_ALL_SP_ALL_GB | % | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 100%
HP07_ALL_SSP_BHV2_GB | % | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Daytime (reference only) | GB | 44.8%
HP07_ALL_SSP_BHV1_GB | % | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Bimodal (reference only) | GB | 46%
HP07_ALL_SSP_BHV3_GB | % | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Continuous (reference only) | GB | 9.2%
HP07_ALL_MIN_ALL_GB | % | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 100%

## HP08
Back to contents
Back to HP CPA Summary Table
CPA ID | Unit | BB1 | BB2 | Dwelling Category | Representative day | Behaviour | Level of spatial granularity | Number of heat pumps - lower bound | Number of heat pumps - upper bound | Default value
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 1 | 1 | 3.172
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 2 | 2 | 2.505
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 3 | 3 | 2.172
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 4 | 4 | 1.966
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 5 | 5 | 1.812
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 6 | 6 | 1.748
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 7 | 9 | 1.668
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 10 | 12 | 1.525
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 13 | 15 | 1.484
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 16 | 19 | 1.421
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 20 | 24 | 1.359
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 25 | 29 | 1.322
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 30 | 39 | 1.284
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 40 | 54 | 1.235
HP08_ALL_WP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 55 | N/A | 1
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 1 | 1 | 19.304
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 2 | 2 | 10.95
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 3 | 3 | 9.157
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 4 | 4 | 7.584
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 5 | 5 | 6.552
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 6 | 6 | 5.868
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 7 | 7 | 5.313
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 8 | 8 | 4.706
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 9 | 9 | 4.588
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 10 | 10 | 4.315
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 11 | 11 | 4.044
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 12 | 13 | 4.009
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 14 | 15 | 3.619
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 16 | 17 | 3.392
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 18 | 19 | 3.23
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 20 | 24 | 3.038
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 25 | 29 | 2.726
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 30 | 34 | 2.561
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 35 | 39 | 2.429
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 40 | 49 | 2.235
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 50 | 59 | 2.085
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 60 | 89 | 1.953
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 90 | 149 | 1.729
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 150 | 299 | 1.523
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 300 | 499 | 1.333
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 500 | 638 | 1.236
HP08_ALL_SP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 639 | N/A | 1
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 1 | 1 | 4.678
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 2 | 2 | 3.257
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 3 | 3 | 2.695
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 4 | 4 | 2.422
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 5 | 5 | 2.211
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 6 | 7 | 2.08
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 8 | 9 | 1.888
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 10 | 12 | 1.771
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 13 | 15 | 1.673
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 16 | 19 | 1.558
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 20 | 24 | 1.5
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 25 | 29 | 1.458
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 30 | 39 | 1.401
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 40 | 49 | 1.349
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 50 | 59 | 1.307
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 60 | 79 | 1.274
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 80 | 105 | 1.234
HP08_ALL_SSP_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 106 | N/A | 1
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 1 | 1 | 19.304
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 2 | 2 | 10.95
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 3 | 3 | 9.157
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 4 | 4 | 7.584
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 5 | 5 | 6.552
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 6 | 6 | 5.868
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 7 | 7 | 5.313
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 8 | 8 | 4.706
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 9 | 9 | 4.588
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 10 | 10 | 4.315
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 11 | 11 | 4.044
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 12 | 13 | 4.009
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 14 | 15 | 3.619
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 16 | 17 | 3.392
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 18 | 19 | 3.23
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 20 | 24 | 3.038
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 25 | 29 | 2.726
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 30 | 34 | 2.561
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 35 | 39 | 2.429
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 40 | 49 | 2.235
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 50 | 59 | 2.085
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 60 | 89 | 1.953
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 90 | 149 | 1.729
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 150 | 299 | 1.523
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 300 | 499 | 1.333
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 500 | 638 | 1.236
HP08_ALL_MIN_ALL_GB | N/A (scaling factor) | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 639 | N/A | 1

## HP09
Back to contents
Back to HP CPA Summary Table
CPA ID | Unit | BB1 | BB2 | Dwelling Category | Representative day | Behaviour | Level of spatial granularity | Default value
HP09_ALL_WP_ALL_GB | # of heat pumps | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand winter day | Applicable across all | GB | 55
HP09_ALL_SP_ALL_GB | # of heat pumps | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand summer day | Applicable across all | GB | 639
HP09_ALL_SSP_ALL_GB | # of heat pumps | Lct_BB005 | Lct_BB006 | Applicable across all | Peak demand shoulder season day | Applicable across all | GB | 106
HP09_ALL_MIN_ALL_GB | # of heat pumps | Lct_BB005 | Lct_BB006 | Applicable across all | Overall minimum demand day | Applicable across all | GB | 639

## HP indicative impact
Back to contents
Back to HP CPA Summary Table
Indicative calculation (as presented in the September 2025 tRESP consultation)
| Parameter | Scope | Unit | Value
| Total installed capacity | Weighted average across dwelling categories | kW_th/ heat pump | 8.2065
| Daily electricity consumption |  | kWh_e/ heat pump | 22.9397
| HP demand profile peak per HP |  | kW/ heat pump | 1.3556 | Winter peak, fully-diversified, across dwelling types at 2030 efficiency
CPAs used for the indicative calculation
| CPA | Selected scope | Unit | Value
| Dwelling thermal efficiency factor | 2030 | % | 95.23%
| Size of HP | Detached | kW_th | 13.6
| Size of HP | Semi-detached | kW_th | 8.7
| Size of HP | Terraced | kW_th | 6.3
| Size of HP | Flats | kW_th | 4.4
| Specific HP heat output | Peak demand winter day | daily kWh_th/ kW_th/ °C | 0.34
| Efficiency of HP | Peak demand winter day GB-average | heat:power | 2.5664
| Temperature difference | Peak demand winter day GB-average | °C | 21.1
| Peak of normalised half-hourly profile | Peak demand winter day (weighted average across behaviours) | kW/daily kWh | 0.059092
Other assumptions used for the indicative calculation
| Assumption | Scope | Unit | Value | Source | Source link
| Proportion of HPs by dwelling category | Detached | % | 25.79% | From census data (2021), averaged across England and Wales and excluding caravans | https://www.ons.gov.uk/peoplepopulationandcommunity/housing/bulletins/housingenglandandwales/census2021
| Proportion of HPs by dwelling category | Semi-detached | % | 31.91% | As above | As above
| Proportion of HPs by dwelling category | Terraced | % | 24.89% | As above | As above
| Proportion of HPs by dwelling category | Flat | % | 17.41% | As above | As above
100%

## HP End to End Example
CPA Value Selection Tool and End-to-End Calculation: Heat Pumps
Back to contents
Information
| This sheet is a tool to support users of the CPAs to select the right values for the conditions they wish to model, and create kW per half-hour profiles. | [5 empty] | Key for sheet:
| User inputs: Choose the conditions and technology numbers for the end-end calculation. | [5 empty] | input
| Dashboard: Summarises the results of the end -end calculation based on the user inputs and CPA values, including charts of total and per-HP demand. | [5 empty] | linked input (do not edit)
| CPA values selected: Display of the default, lower range, and upper range CPA values that should be applied in calculations for the user inputs selected. | [5 empty] | linked data (reference to values from CPA tables)
| End-to-end calculation: Example of calculations aligned with the HP CPA process, using the chosen inputs, for default, lower range, and upper range values. | [5 empty] | Calculation
User inputs
Please select the conditions for the value selector and input values for the end-to-end calculation.
| Inputs for CPA selection |  | Value inputs for calculation.
| DNO licence area |  | Parameter | Heat pump type | Dwelling type | New build status | Unit | Value
| Northern |  | Values represent technology numbers on a single network asset. Below a count defined per GSP in the tRESP pathways, DNOs to identify the spatial allocation of the technology totals to specific network assets.
|  |  | Number of non-hybrid heat pumps | Lct_BB005 | All | All | # | 500
| Representative day |  | Number of hybrid heat pumps | Lct_BB006 | All | All | # | 10
Peak demand winter day
|  |  | Values represent the distribution of heat pumps to building archetypes. | [5 empty] | Reference values | Data source
| Year |  | Proportion heat pumps in existing detached homes | All | Detached | Existing | % | 25.6% | 25.79%
| 2050 |  | Proportion heat pumps in existing semi-detached homes | All | Semi-detached and end-terraced | Existing | % | 31.9% | 31.91%
|  |  | Proportion heat pumps in existing terraced homes | All | Mid-terraced | Existing | % | 25% | 24.89%
|  |  | Proportion heat pumps in existing flats | All | Flats | Existing | % | 17.4% | 17.41%
|  |  | Proportion heat pumps in new detached homes | All | Detached | New | % | 0% | 0%
|  |  | Proportion heat pumps in new semi-detached homes | All | Semi-detached and end-terraced | New | % | 0% | 0%
|  |  | Proportion heat pumps in new terraced homes | All | Mid-terraced | New | % | 0% | 0%
|  |  | Proportion heat pumps in new flats | All | Flats | New | % | 0% | 0%
|  |  | Check sum | All | All | All | % | 99.9%
Dashboard
| Northern: 2050 Peak demand winter day |  |  |  | Total HP demand |  | Peak demand |  | Peak time |  |  | Per-HP demand |  | Peak demand |  | Peak time |  |  | For reference: | Peak demand |  | Peak time
[7 empty] | 703.0487 | kW | 7:00 |  |  |  |  | 1.3785 | kW | 7:00 |  |  | Total HP demand by behaviour | 703.0487 | kW | 7:00
| Number of non-hybrid heat pumps | 500 | Lct_BB005 |  |  |  | 652.38 - 779.05 | kW | [5 empty] | 1.28 - 1.53 | kW |  |  |  | Default value
| Number of hybrid heat pumps | 10 | Lct_BB006
| Outside air temperature | -1.2 | ˚C
| Temperature range | -3.6˚C | 0.4˚C
| Diversity correction required? | N
[21 empty] | TRUE |  | Hot water
[21 empty] | FALSE |  | Continuous
[21 empty] | FALSE |  | Daytime
[21 empty] | FALSE |  | Bimodal
CPA values selected
This table lists the default, lower range, and upper range values that should be applied in calculations for the conditions listed in the inputs.
| CPA ID | CPA ID | CPA | Heat pump type 1 | Heat pump type 2 | Dwelling category | New build status | Representative day | Behaviour | Spatial scope | Year | Unit | Value - Default | Lower range | Upper range
| HP01 | HP01 | Size of HP | Lct_BB005 | Lct_BB006 | Detached | Existing | N/A | Applicable across all | Northern | All | kW_th | 13.6 | 13.6 | 13.6
|  | HP01 | Size of HP | Lct_BB005 | Lct_BB006 | Semi-detached and end-terraced | Existing | N/A | Applicable across all | Northern | All | kW_th | 8.7 | 8.7 | 8.7
|  | HP01 | Size of HP | Lct_BB005 | Lct_BB006 | Mid-terraced | Existing | N/A | Applicable across all | Northern | All | kW_th | 6.3 | 6.3 | 6.3
|  | HP01 | Size of HP | Lct_BB005 | Lct_BB006 | Flats | Existing | N/A | Applicable across all | Northern | All | kW_th | 4.4 | 4.4 | 4.4
|  | HP01 | Size of HP | Lct_BB005 | Lct_BB006 | Detached | New | N/A | Applicable across all | Northern | All | kW_th | 9.9 | 9.9 | 9.9
|  | HP01 | Size of HP | Lct_BB005 | Lct_BB006 | Semi-detached and end-terraced | New | N/A | Applicable across all | Northern | All | kW_th | 4.2 | 4.2 | 4.2
|  | HP01 | Size of HP | Lct_BB005 | Lct_BB006 | Mid-terraced | New | N/A | Applicable across all | Northern | All | kW_th | 4 | 4 | 4
|  | HP01 | Size of HP | Lct_BB005 | Lct_BB006 | Flats | New | N/A | Applicable across all | Northern | All | kW_th | 2.1 | 2.1 | 2.1
| HP02 | HP02 | Dwelling thermal efficiency factor | Lct_BB005 | Lct_BB006 | Applicable across all | Existing | N/A | Applicable across all | GB | 2050 | % | 89.5% | 89.5% | 89.5%
|  | HP02 | Dwelling thermal efficiency factor | Lct_BB005 | Lct_BB006 | Applicable across all | New | N/A | Applicable across all | GB | 2050 | % | 100% | 100% | 100%
| HP03 | HP03 | Efficiency of HP | Lct_BB005 | Lct_BB006 | Applicable across all | All | Peak demand winter day | Applicable across all | Northern | All | heat:power | 2.49 | 2.49 | 2.49
| HP04 | HP04 | Specific HP heat output | Lct_BB005 | Lct_BB006 | Applicable across all | All | Peak demand winter day | Applicable across all | GB | All | daily kWh_th/ kW_th/ °C | 0.34 | 0.34 | 0.34
| HP05 | HP05 | Temperature difference | Lct_BB005 | Lct_BB006 | N/A | All | Peak demand winter day | N/A | Northern | All | °C | 22.2 | 20.6 | 24.6
| HP07 | HP07 | Proportion of consumers by behaviour | Lct_BB005 | Lct_BB006 | Applicable across all | All | Peak demand winter day | Daytime (reference only) | GB | All | % | 46% | 46% | 46%
|  | HP07 | Proportion of consumers by behaviour | Lct_BB005 | Lct_BB006 | Applicable across all | All | Peak demand winter day | Bimodal (reference only) | GB | All | % | 40.5% | 40.5% | 40.5%
|  | HP07 | Proportion of consumers by behaviour | Lct_BB005 | Lct_BB006 | Applicable across all | All | Peak demand winter day | Continuous (reference only) | GB | All | % | 13.5% | 13.5% | 13.5%
|  | HP07 | Proportion of consumers by behaviour | Lct_BB005 | Lct_BB006 | Applicable across all | All | Peak demand winter day | Applicable across all | GB | All | %
| HP09 | HP09 | Minimum count for full diversification | Lct_BB005 | Lct_BB006 | Applicable across all | All | Peak demand winter day | Applicable across all | GB | All | # | 55 | 55 | 55
| HP08 | HP08 | Diversity correction factor | Lct_BB005 | Lct_BB006 | Applicable across all | All | Peak demand winter day | Applicable across all | GB | All | N/A (scaling factor) | 1 | 1 | 1
| HP06 |  | Weighted average | Weighted average | Weighted average |  | For reference: Behavioural breakdown
|  | Table unit: kW/daily kWh_e | Default | Lower range | Upper range |  | Bimodal (reference only) | Daytime (reference only) | Continuous (reference only) | N/A (summer and minimum)
|  | Time | Peak demand winter day | Peak demand winter day | Peak demand winter day |  | Peak demand winter day | Peak demand winter day | Peak demand winter day | Peak demand winter day
|  | 0:00 | 0.0274 | 0.0274 | 0.0274 |  | 0.0313 | 0.0184 | 0.0464
|  | 0:30 | 0.0283 | 0.0283 | 0.0283 |  | 0.0327 | 0.0193 | 0.0459
|  | 1:00 | 0.0298 | 0.0298 | 0.0298 |  | 0.0348 | 0.0206 | 0.046
|  | 1:30 | 0.0314 | 0.0314 | 0.0314 |  | 0.0367 | 0.0226 | 0.0459
|  | 2:00 | 0.0328 | 0.0328 | 0.0328 |  | 0.0379 | 0.0242 | 0.0466
|  | 2:30 | 0.0344 | 0.0344 | 0.0344 |  | 0.0391 | 0.0264 | 0.0474
|  | 3:00 | 0.0354 | 0.0354 | 0.0354 |  | 0.0399 | 0.0277 | 0.0479
|  | 3:30 | 0.0366 | 0.0366 | 0.0366 |  | 0.0411 | 0.0292 | 0.0482
|  | 4:00 | 0.038 | 0.038 | 0.038 |  | 0.0426 | 0.0309 | 0.0481
|  | 4:30 | 0.0403 | 0.0403 | 0.0403 |  | 0.0447 | 0.0342 | 0.0478
|  | 5:00 | 0.0433 | 0.0433 | 0.0433 |  | 0.0472 | 0.0385 | 0.048
|  | 5:30 | 0.0481 | 0.0481 | 0.0481 |  | 0.051 | 0.0454 | 0.0486
|  | 6:00 | 0.0529 | 0.0529 | 0.0529 |  | 0.0545 | 0.0527 | 0.0491
|  | 6:30 | 0.0574 | 0.0574 | 0.0574 |  | 0.0572 | 0.0601 | 0.0485
|  | 7:00 | 0.0591 | 0.0591 | 0.0591 |  | 0.0566 | 0.0646 | 0.0478
|  | 7:30 | 0.0587 | 0.0587 | 0.0587 |  | 0.0532 | 0.067 | 0.0471
|  | 8:00 | 0.0567 | 0.0567 | 0.0567 |  | 0.0477 | 0.0674 | 0.0473
|  | 8:30 | 0.054 | 0.054 | 0.054 |  | 0.0417 | 0.067 | 0.0466
|  | 9:00 | 0.0507 | 0.0507 | 0.0507 |  | 0.0362 | 0.0652 | 0.0449
|  | 9:30 | 0.0477 | 0.0477 | 0.0477 |  | 0.0321 | 0.0626 | 0.0434
|  | 10:00 | 0.0449 | 0.0449 | 0.0449 |  | 0.0293 | 0.0596 | 0.042
|  | 10:30 | 0.043 | 0.043 | 0.043 |  | 0.028 | 0.0567 | 0.041
|  | 11:00 | 0.041 | 0.041 | 0.041 |  | 0.0273 | 0.0537 | 0.0389
|  | 11:30 | 0.0398 | 0.0398 | 0.0398 |  | 0.028 | 0.051 | 0.0374
|  | 12:00 | 0.0388 | 0.0388 | 0.0388 |  | 0.0286 | 0.0486 | 0.0359
|  | 12:30 | 0.0383 | 0.0383 | 0.0383 |  | 0.0291 | 0.0472 | 0.0352
|  | 13:00 | 0.0376 | 0.0376 | 0.0376 |  | 0.0293 | 0.0458 | 0.0342
|  | 13:30 | 0.0373 | 0.0373 | 0.0373 |  | 0.0301 | 0.0447 | 0.0339
|  | 14:00 | 0.0375 | 0.0375 | 0.0375 |  | 0.0316 | 0.0438 | 0.0338
|  | 14:30 | 0.0389 | 0.0389 | 0.0389 |  | 0.0346 | 0.0439 | 0.0345
|  | 15:00 | 0.0407 | 0.0407 | 0.0407 |  | 0.0382 | 0.0445 | 0.0352
|  | 15:30 | 0.0429 | 0.0429 | 0.0429 |  | 0.0427 | 0.045 | 0.0361
|  | 16:00 | 0.0448 | 0.0448 | 0.0448 |  | 0.0472 | 0.0451 | 0.0365
|  | 16:30 | 0.0466 | 0.0466 | 0.0466 |  | 0.0515 | 0.045 | 0.0368
|  | 17:00 | 0.0476 | 0.0476 | 0.0476 |  | 0.0547 | 0.0446 | 0.0368
|  | 17:30 | 0.0481 | 0.0481 | 0.0481 |  | 0.0567 | 0.0438 | 0.037
|  | 18:00 | 0.048 | 0.048 | 0.048 |  | 0.0577 | 0.0427 | 0.0372
|  | 18:30 | 0.0481 | 0.0481 | 0.0481 |  | 0.0582 | 0.0422 | 0.0378
|  | 19:00 | 0.0478 | 0.0478 | 0.0478 |  | 0.0576 | 0.0421 | 0.0382
|  | 19:30 | 0.0472 | 0.0472 | 0.0472 |  | 0.0561 | 0.0418 | 0.0389
|  | 20:00 | 0.0458 | 0.0458 | 0.0458 |  | 0.054 | 0.0405 | 0.0392
|  | 20:30 | 0.0435 | 0.0435 | 0.0435 |  | 0.0506 | 0.0384 | 0.0396
|  | 21:00 | 0.0405 | 0.0405 | 0.0405 |  | 0.0468 | 0.0352 | 0.0397
|  | 21:30 | 0.036 | 0.036 | 0.036 |  | 0.0414 | 0.03 | 0.04
|  | 22:00 | 0.0317 | 0.0317 | 0.0317 |  | 0.0372 | 0.0244 | 0.0401
|  | 22:30 | 0.0281 | 0.0281 | 0.0281 |  | 0.0333 | 0.0198 | 0.0403
|  | 23:00 | 0.0266 | 0.0266 | 0.0266 |  | 0.0315 | 0.0181 | 0.041
|  | 23:30 | 0.0261 | 0.0261 | 0.0261 |  | 0.0307 | 0.0176 | 0.0413
End-to-end calculation
|  |  | Parameter | Heat pump type 1 | Heat pump type 2 | Dwelling category | Unit | Value - Default | Lower range | Upper range
| 1. Check if diversity correction is required |  | Diversity correction check | Lct_BB005 | Lct_BB006 | All | Y/N | N | N | N
| 2. Calculate total installed heat pump capacity |  | Total installed capacity | Lct_BB005 | Lct_BB006 | All | kW_th | 3924.3289 | 3924.3289 | 3924.3289
| 3. Calculate daily electricity consumption |  | Daily electricity consumption | Lct_BB005 | Lct_BB006 | All | KWh_e | 11895.9174 | 11038.554 | 13181.9625
4. Apply half-hourly profiles and find peak demand values in the day and its time. Calculations by behaviour (bimodal, daytime, continuous) provided for reference.
| Total heat pump demand for all behavioural types, default, lower range, and upper range values. | [5 empty] | Per-heat pump demand for all behavioural types, default, lower range, and upper range values. | [5 empty] | For reference: default values by behaviour. Note that for peak demand summer day and overall minimum day, there is only a requirement for hot water and not space heating and a split to behaviours is not applicable.
|  |  | Total HP demand | Total HP demand | Total HP demand |  |  |  | Per HP demand | Per HP demand | Per HP demand |  |  |  | Bimodal | Daytime | Continuous | Hot water (summer and minimum)
| Parameter | Unit | Default | Lower range | Upper range |  | Parameter | Unit | Default | Lower range | Upper range |  | Parameter | Unit | Default | Default | Default | Default
| Peak demand | kW | 703.0487 | 652.3785 | 779.054 |  | Peak demand | kW | 1.3785 | 1.2792 | 1.5276 |  | Peak demand | kW | 692.3424 | 801.7848 | 584.0895
| Time of peak demand | Half hour start time | 7:00 | 7:00 | 7:00 |  | Time of peak demand | Half hour start time | 7:00 | 7:00 | 7:00 |  | Time of peak demand | Half hour start time | 18:30 | 8:00 | 6:00
|  |  | Total HP demand | Total HP demand | Total HP demand |  |  |  | Per HP demand | Per HP demand | Per HP demand |  |  |  | Bimodal | Daytime | Continuous | Hot water (summer and minimum)
|  | Table unit: kW | Default | Lower range | Upper range |  |  | Table unit: kW | Default | Lower range | Upper range |  |  | Table unit: kW | Default | Default | Default | Default
|  | Half hour start time | Peak demand winter day | Peak demand winter day | Peak demand winter day |  |  | Half hour start time | Peak demand winter day | Peak demand winter day | Peak demand winter day |  |  | Half hour start time | Peak demand shoulder season day | Peak demand winter day | Peak demand winter day | Peak demand winter day
|  | 0:00 | 325.9481 | 302.4564 | 361.1858 |  |  | 0:00 | 0.63911 | 0.59305 | 0.70821 |  | 1 | 0:00 | 372.3422 | 218.8849 | 551.9706
|  | 0:30 | 336.6545 | 312.3911 | 373.0495 |  |  | 0:30 | 0.66011 | 0.61253 | 0.73147 |  | 2 | 0:30 | 388.9965 | 229.5912 | 546.0226
|  | 1:00 | 354.4983 | 328.9489 | 392.8225 |  |  | 1:00 | 0.69509 | 0.645 | 0.77024 |  | 3 | 1:00 | 413.9779 | 245.0559 | 547.2122
|  | 1:30 | 373.5318 | 346.6106 | 413.9136 |  |  | 1:30 | 0.73242 | 0.67963 | 0.8116 |  | 4 | 1:30 | 436.5802 | 268.8477 | 546.0226
|  | 2:00 | 390.1861 | 362.0646 | 432.3684 |  |  | 2:00 | 0.76507 | 0.70993 | 0.84778 |  | 5 | 2:00 | 450.8553 | 287.8812 | 554.3498
|  | 2:30 | 409.2196 | 379.7263 | 453.4595 |  |  | 2:30 | 0.80239 | 0.74456 | 0.88914 |  | 6 | 2:30 | 465.1304 | 314.0522 | 563.8665
|  | 3:00 | 421.1155 | 390.7648 | 466.6415 |  |  | 3:00 | 0.82572 | 0.76621 | 0.91498 |  | 7 | 3:00 | 474.6471 | 329.5169 | 569.8144
|  | 3:30 | 435.3906 | 404.0111 | 482.4598 |  |  | 3:30 | 0.85371 | 0.79218 | 0.946 |  | 8 | 3:30 | 488.9222 | 347.3608 | 573.3832
|  | 4:00 | 452.0449 | 419.4651 | 500.9146 |  |  | 4:00 | 0.88636 | 0.82248 | 0.98219 |  | 9 | 4:00 | 506.7661 | 367.5838 | 572.1936
|  | 4:30 | 479.4055 | 444.8537 | 531.2331 |  |  | 4:30 | 0.94001 | 0.87226 | 1.0416 |  | 10 | 4:30 | 531.7475 | 406.8404 | 568.6249
|  | 5:00 | 515.0932 | 477.9694 | 570.779 |  |  | 5:00 | 1.01 | 0.93719 | 1.1192 |  | 11 | 5:00 | 561.4873 | 457.9928 | 571.004
|  | 5:30 | 572.1936 | 530.9544 | 634.0524 |  |  | 5:30 | 1.1219 | 1.0411 | 1.2432 |  | 12 | 5:30 | 606.6918 | 540.0747 | 578.1416
|  | 6:00 | 629.294 | 583.9395 | 697.3258 |  |  | 6:00 | 1.2339 | 1.145 | 1.3673 |  | 13 | 6:00 | 648.3275 | 626.9148 | 584.0895
|  | 6:30 | 682.8257 | 633.613 | 756.6446 |  |  | 6:30 | 1.3389 | 1.2424 | 1.4836 |  | 14 | 6:30 | 680.4465 | 714.9446 | 576.952
|  | 7:00 | 703.0487 | 652.3785 | 779.054 |  |  | 7:00 | 1.3785 | 1.2792 | 1.5276 |  | 15 | 7:00 | 673.3089 | 768.4763 | 568.6249
|  | 7:30 | 698.2904 | 647.9631 | 773.7812 |  |  | 7:30 | 1.3692 | 1.2705 | 1.5172 |  | 16 | 7:30 | 632.8628 | 797.0265 | 560.2977
|  | 8:00 | 674.4985 | 625.886 | 747.4173 |  |  | 8:00 | 1.3225 | 1.2272 | 1.4655 |  | 17 | 8:00 | 567.4353 | 801.7848 | 562.6769
|  | 8:30 | 642.3795 | 596.0819 | 711.826 |  |  | 8:30 | 1.2596 | 1.1688 | 1.3957 |  | 18 | 8:30 | 496.0598 | 797.0265 | 554.3498
|  | 9:00 | 603.123 | 559.6547 | 668.3255 |  |  | 9:00 | 1.1826 | 1.0974 | 1.3104 |  | 19 | 9:00 | 430.6322 | 775.6138 | 534.1267
|  | 9:30 | 567.4353 | 526.539 | 628.7796 |  |  | 9:30 | 1.1126 | 1.0324 | 1.2329 |  | 20 | 9:30 | 381.8589 | 744.6844 | 516.2828
|  | 10:00 | 534.1267 | 495.6311 | 591.8701 |  |  | 10:00 | 1.0473 | 0.97183 | 1.1605 |  | 21 | 10:00 | 348.5504 | 708.9967 | 499.6285
|  | 10:30 | 511.5244 | 474.6578 | 566.8244 |  |  | 10:30 | 1.003 | 0.9307 | 1.1114 |  | 22 | 10:30 | 333.0857 | 674.4985 | 487.7326
|  | 11:00 | 487.7326 | 452.5807 | 540.4605 |  |  | 11:00 | 0.95634 | 0.88741 | 1.0597 |  | 23 | 11:00 | 324.7585 | 638.8108 | 462.7512
|  | 11:30 | 473.4575 | 439.3344 | 524.6421 |  |  | 11:30 | 0.92835 | 0.86144 | 1.0287 |  | 24 | 11:30 | 333.0857 | 606.6918 | 444.9073
|  | 12:00 | 461.5616 | 428.2959 | 511.4601 |  |  | 12:00 | 0.90502 | 0.8398 | 1.0029 |  | 25 | 12:00 | 340.2232 | 578.1416 | 427.0634
|  | 12:30 | 455.6136 | 422.7766 | 504.8692 |  |  | 12:30 | 0.89336 | 0.82897 | 0.98994 |  | 26 | 12:30 | 346.1712 | 561.4873 | 418.7363
|  | 13:00 | 447.2865 | 415.0496 | 495.6418 |  |  | 13:00 | 0.87703 | 0.81382 | 0.97185 |  | 27 | 13:00 | 348.5504 | 544.833 | 406.8404
|  | 13:30 | 443.7177 | 411.7381 | 491.6872 |  |  | 13:30 | 0.87003 | 0.80733 | 0.96409 |  | 28 | 13:30 | 358.0671 | 531.7475 | 403.2716
|  | 14:00 | 446.0969 | 413.9458 | 494.3236 |  |  | 14:00 | 0.8747 | 0.81166 | 0.96926 |  | 29 | 14:00 | 375.911 | 521.0412 | 402.082
|  | 14:30 | 462.7512 | 429.3998 | 512.7783 |  |  | 14:30 | 0.90736 | 0.84196 | 1.0054 |  | 30 | 14:30 | 411.5987 | 522.2308 | 410.4092
|  | 15:00 | 484.1638 | 449.2691 | 536.5059 |  |  | 15:00 | 0.94934 | 0.88092 | 1.052 |  | 31 | 15:00 | 454.424 | 529.3683 | 418.7363
|  | 15:30 | 510.3349 | 473.554 | 565.5062 |  |  | 15:30 | 1.0007 | 0.92854 | 1.1088 |  | 32 | 15:30 | 507.9557 | 535.3163 | 429.4426
|  | 16:00 | 532.9371 | 494.5272 | 590.5519 |  |  | 16:00 | 1.045 | 0.96966 | 1.1579 |  | 33 | 16:00 | 561.4873 | 536.5059 | 434.201
|  | 16:30 | 554.3498 | 514.3966 | 614.2795 |  |  | 16:30 | 1.087 | 1.0086 | 1.2045 |  | 34 | 16:30 | 612.6397 | 535.3163 | 437.7698
|  | 17:00 | 566.2457 | 525.4352 | 627.4614 |  |  | 17:00 | 1.1103 | 1.0303 | 1.2303 |  | 35 | 17:00 | 650.7067 | 530.5579 | 437.7698
|  | 17:30 | 572.1936 | 530.9544 | 634.0524 |  |  | 17:30 | 1.1219 | 1.0411 | 1.2432 |  | 36 | 17:30 | 674.4985 | 521.0412 | 440.1489
|  | 18:00 | 571.004 | 529.8506 | 632.7342 |  |  | 18:00 | 1.1196 | 1.0389 | 1.2407 |  | 37 | 18:00 | 686.3944 | 507.9557 | 442.5281
|  | 18:30 | 572.1936 | 530.9544 | 634.0524 |  |  | 18:30 | 1.1219 | 1.0411 | 1.2432 |  | 38 | 18:30 | 692.3424 | 502.0077 | 449.6657
|  | 19:00 | 568.6249 | 527.6429 | 630.0978 |  |  | 19:00 | 1.115 | 1.0346 | 1.2355 |  | 39 | 19:00 | 685.2048 | 500.8181 | 454.424
|  | 19:30 | 561.4873 | 521.0197 | 622.1886 |  |  | 19:30 | 1.101 | 1.0216 | 1.22 |  | 40 | 19:30 | 667.361 | 497.2493 | 462.7512
|  | 20:00 | 544.833 | 505.5658 | 603.7339 |  |  | 20:00 | 1.0683 | 0.99131 | 1.1838 |  | 41 | 20:00 | 642.3795 | 481.7847 | 466.32
|  | 20:30 | 517.4724 | 480.1771 | 573.4154 |  |  | 20:30 | 1.0147 | 0.94152 | 1.1243 |  | 42 | 20:30 | 601.9334 | 456.8032 | 471.0783
|  | 21:00 | 481.7847 | 447.0614 | 533.8695 |  |  | 21:00 | 0.94468 | 0.87659 | 1.0468 |  | 43 | 21:00 | 556.7289 | 418.7363 | 472.2679
|  | 21:30 | 428.253 | 397.3879 | 474.5507 |  |  | 21:30 | 0.83971 | 0.77919 | 0.93049 |  | 44 | 21:30 | 492.491 | 356.8775 | 475.8367
|  | 22:00 | 377.1006 | 349.9222 | 417.8682 |  |  | 22:00 | 0.73941 | 0.68612 | 0.81935 |  | 45 | 22:00 | 442.5281 | 290.2604 | 477.0263
|  | 22:30 | 334.2753 | 310.1834 | 370.4131 |  |  | 22:30 | 0.65544 | 0.6082 | 0.7263 |  | 46 | 22:30 | 396.134 | 235.5392 | 479.4055
|  | 23:00 | 316.4314 | 293.6255 | 350.6402 |  |  | 23:00 | 0.62045 | 0.57574 | 0.68753 |  | 47 | 23:00 | 374.7214 | 215.3161 | 487.7326
|  | 23:30 | 310.4834 | 288.1063 | 344.0492 |  |  | 23:30 | 0.60879 | 0.56491 | 0.67461 |  | 48 | 23:30 | 365.2047 | 209.3681 | 491.3014
User inputs:
Dashboard:
CPA values selected:
End-to-end calculation:
HP CPA process
Note on K21: Arna Sigurdardottir (NESO): Distribution of existing homes to dwelling types. From census data (2021), averaged across England and Wales and excluding caravans.

## EE CPA Summary Table
Domestic EE CPA Summary Table
Back to contents
CPA Number | CPA | Description | Scope | Unit | Data source/s | Link/s | Data processing comment | Default values comment | Overall RAG rating | Based on reliable source | RAG | Be relevant | RAG | Be up to date | RAG | Be location specific | RAG | Considers changes through time | RAG | Weather and climate impact | RAG
EE01 | Residential energy efficiency | Residential appliance and lighting electricity consumption (kWh/household) compared to the base year. | GB | % | FES 2025 (With adjustments, see comment. Received NESO data models from FES team internally) | https://www.neso.energy/publications/future-energy-scenarios-fes | The initial data is the residential electricity demand for lights and appliances for Holistic Transition for years 2024-2050. The FES projections are based on Energy Consumption in the UK (ECUK) data and consider how demand per appliance and appliance ownership change through time. Adjustment are made to the FES models to (a) update the baseline values for lighting and efficiency based on the most up-to-date data from ECUK, and (b) remove the impact of population growth, such that the trends represent changes to existing stock only. This approach recognises that new build growth rates vary by location and therefore by removing the impact of stock growth, the assumption can be applied across regions. This is then converted to percentage change compared to baseline year value (2025, representing year ending 31 March 2025). | The default values are based on the Holistic Transition pathways. They are average values for the entire existing GB dwelling stock and cover the years 2024 to 2050. Additional detail can be added by splitting the building stock by dwelling categories and regions. They start at 100% meaning no improvement to the demand and decrease to reach 60% by 2050 (which is equivalent to a 40% decrease in demand). | 3 | Based on FES 25 Holistic Transition data. | 2 | This is based on data on electricity demand for residential lights and appliances. | 3 | This is based on FES 25 which was published in July 2025. | 3 | This is based on GB data. More regionalisation could be done. | 2 | The data covers years from 2024 to 2050. | 3 | Not considered | 2

## EE01
Back to contents
Back to EE CPA Summary Table
CPA ID | Unit | Representative day | Level of spatial granularity | Year | Default value
EE01_NA_NA_NA_GB | % | N/A | GB | 2024 | 103.4%
EE01_NA_NA_NA_GB | % | N/A | GB | 2025 | 100%
EE01_NA_NA_NA_GB | % | N/A | GB | 2026 | 96%
EE01_NA_NA_NA_GB | % | N/A | GB | 2027 | 92.81%
EE01_NA_NA_NA_GB | % | N/A | GB | 2028 | 89.94%
EE01_NA_NA_NA_GB | % | N/A | GB | 2029 | 87.45%
EE01_NA_NA_NA_GB | % | N/A | GB | 2030 | 85.3%
EE01_NA_NA_NA_GB | % | N/A | GB | 2031 | 83.38%
EE01_NA_NA_NA_GB | % | N/A | GB | 2032 | 81.82%
EE01_NA_NA_NA_GB | % | N/A | GB | 2033 | 80.35%
EE01_NA_NA_NA_GB | % | N/A | GB | 2034 | 78.95%
EE01_NA_NA_NA_GB | % | N/A | GB | 2035 | 77.56%
EE01_NA_NA_NA_GB | % | N/A | GB | 2036 | 76.11%
EE01_NA_NA_NA_GB | % | N/A | GB | 2037 | 74.69%
EE01_NA_NA_NA_GB | % | N/A | GB | 2038 | 73.35%
EE01_NA_NA_NA_GB | % | N/A | GB | 2039 | 72.12%
EE01_NA_NA_NA_GB | % | N/A | GB | 2040 | 70.94%
EE01_NA_NA_NA_GB | % | N/A | GB | 2041 | 70.22%
EE01_NA_NA_NA_GB | % | N/A | GB | 2042 | 69.74%
EE01_NA_NA_NA_GB | % | N/A | GB | 2043 | 69.28%
EE01_NA_NA_NA_GB | % | N/A | GB | 2044 | 68.83%
EE01_NA_NA_NA_GB | % | N/A | GB | 2045 | 68.39%
EE01_NA_NA_NA_GB | % | N/A | GB | 2046 | 67.97%
EE01_NA_NA_NA_GB | % | N/A | GB | 2047 | 67.57%
EE01_NA_NA_NA_GB | % | N/A | GB | 2048 | 67.21%
EE01_NA_NA_NA_GB | % | N/A | GB | 2049 | 66.86%
EE01_NA_NA_NA_GB | % | N/A | GB | 2050 | 66.52%