## Legal Text Change Record
LEGAL TEXT CHANGES IN GC AS IDENTIFIED
AREA OF GC | SECTION | SUGGESTED CHANGE | LEGAL TEXT
Glossary & Definitions | GD. 1 'Active Control Based Droop Power' | Insert “through the instruction of Primary Response or Dynamic Low and Secondary Response or Dynamic Regulation Low” | The Active Control Based Power output supplied by a Grid Forming Plant through controlled means (be it manual or automatic). For GBGF-I this is equivalent to a Synchronous Generating Unit with a traditional governor coupled to its prime mover. Active Control Based Droop Power is used by The Company to control System Frequency changes through the instruction of Primary Response and Secondary Response or Dynamic Regulation Low.
Glossary & Definitions | GD. 1 'Active Frequency Response Power' | Insert “to Primary Response or Dynamic Regulation Low" | The injection or absorption of Active Power by a Grid Forming Plant to or from the Total System during a deviation of the System Frequency away from the Target Frequency. For a GBGF-I this is very similar to Primary Response or Dynamic Regulation Low but with a response time to achieve the declared service capability (which could be the Maximum Capacity or Registered Capacity) within 1 second. For GBGF-I this can rapidly inject or absorb Active Power in addition to the phase-based Active Inertia Power to provide a system with desirable NFP plot characteristics. Active Frequency Response Power can be produced by any viable control technology.
Glossary & Definitions | “Frequency Sensitive Mode” |  | “Frequency Sensitive Mode” includes references to Primary Response, Secondary Response and High Frequency Response but has not been amended to include the new DR definitions.
Glossary & Definitions | “Limited Frequency Sensitive Mode” |  | refers to the provision of Limited High Frequency Response, without including the new DRHigh definition, despite it has been inserted in some instances where Limited High Frequency Response is used in the GC (e.g. CC.6.3.7). I’m not certain which approach is correct, particularly if “Limited High Frequency Response” is not an ancillary service (see ECC.6.3.7.1.1).
Glossary & Definitions | GD. 1 'Primary Response' (pg 64) | Insert “through the instruction of Primary Response or Dynamic Regulation Low (don't think need to change heading?) | The automatic increase in Active Power output of a Genset or, as the case may be, the decrease in Active Power Demand in response to a System Frequency fall. This increase in Active Power output or, as the case may be, the decrease in Active Power Demand must be in accordance with the provisions of the relevant Ancillary Services Agreement which will provide that it will be released increasingly with time over the period 0 to 10 seconds from the time of the start of the Frequency fall on the basis set out in the Ancillary Services Agreement and fully available by the latter, and sustainable for at least a further 20 seconds. The interpretation of the Primary Response or Dynamic Regulation Low to a – 0.5 Hz frequency change is shown diagrammatically in Figure CC.A.3.2 and Figure ECC.A.3.2
Glossary & Definitions | GD. 1 'Secondary Response' (pg 72) | Insert “the interpretation of Secondary Response or Dynamic Regulation Low” (don't think need to change heading?) | The automatic increase in Active Power output of a Genset or, as the case may be, the decrease in Active Power Demand in response to a System Frequency fall. This increase in Active Power output or, as the case may be, the decrease in Active Power Demand must be in accordance with the provisions of the relevant Ancillary Services Agreement which will provide that it will be fully available by 30 seconds from the time of the start of the Frequency fall and be sustainable for at least a further 30 minutes. The interpretation of the Secondary Response or Dynamic Regulation Low to a -0.5 Hz frequency change is shown diagrammatically in Figure CC.A.3.2 or Figure ECC.A.3.2.
Glossary & Definitions | Designed Minimum Operating Level (pg20) | High frequency Response - change? | The output (in whole MW) below which a Genset or a DC Converter at a DC Converter Station (in any of its operating configurations) has no High Frequency Response or Dynamic Regulation High capability.
Glossary & Definitions | “Unit Load Controller Response Time Constant” |  | “Unit Load Controller Response Time Constant” refers to Secondary Response but there is no amendment to include the new DRLow definition.
Glossary & Definitions | New definition | New definition: Dynamic Regulation Low | Dynamic Regulation Low: A pre-fault service designed to continuously correct deviations of greater than or equal to -0.2Hz in System Frequency, below the target System Frequency of 50Hz.
Glossary & Definitions | New definition | New definition: Dynamic Regulation High | Dynamic Regulation High A pre-fault service designed to continuously correct deviations of greater than or equal to +0.2Hz in System Frequency, above the target System Frequency of 50Hz..
Connection Conditions | CC.6.3.7 | Insert “or Dynamic Regulation High” in (c) (iii) | (c) (iii) in the case of all Generating Units, DC Converter or Power Park Module other than the Steam Unit within a CCGT Module the Frequency control device (or speed governor) deadband should be no greater than 0.03Hz (for the avoidance of doubt, ±0.015Hz). In the case of the Steam Unit within a CCGT Module, the speed Governor Deadband should be set to an appropriate value consistent with the requirements of CC.6.3.7(c)(i) and the requirements of BC3.7.2 for the provision of Limited High Frequency Response or Dynamic Regulation High;
Connection Conditions | APPENDIX 3 - MINIMUM FREQUENCY RESPONSE REQUIREMENT PROFILE AND OPERATING RANGE FOR NEW POWER STATIONS AND DC CONVERTER STATIONS CC A.3.1​ | Insert in CCA.3.1 “Primary Response or Dynamic Regulation Low, Secondary Response or Dynamic Regulation Low, and High Frequency Response or Dynamic Regulation High” | Scope The Frequency response capability is defined in terms of Primary Response, Secondary Response or Dynamic Regulation Low and High Frequency Response or Dynamic Regulation High. This appendix defines the minimum Frequency response requirement profile for:
Connection Conditions | Insert in CCA.3.1 (viii) | Insert in CCA.3.1 (viii) “Primary Response or Dynamic Regulation Low, Secondary Response or Dynamic Regulation Low, and High Frequency Response or Dynamic Regulation High” | …... The minimum Frequency response requirement profile is shown diagrammatically in Figure CC.A.3.1. The capability profile specifies the minimum required levels of Primary Response, Secondary Response or Dynamic Regulation Low and High Frequency Response or Dynamic Regulation High throughout the normal plant operating range. The definitions of these Frequency response capabilities are illustrated diagrammatically in Figures CC.A.3.2 & CC.A.3.3.
Connection Conditions | Insert in CCA.3.2 | Insert “Primary and Secondary Response or Dynamic Regulation Low” | Plant Operating Range The upper limit of the operating range is the Registered Capacity of the Generating Unit or CCGT Module or DC Converter or Power Park Module. The Minimum Generation level may be less than, but must not be more than, 65% of the Registered Capacity. Each Generating Unit and/or CCGT Module and/or Power Park Module and/or DC Converter must be capable of operating satisfactorily down to the Designed Minimum Operating Level as dictated by System operating conditions, although it will not be instructed to below its Minimum Generation level. If a Generating Unit or CCGT Module or Power Park Module or DC Converter is operating below Minimum Generation because of high System Frequency, it should recover adequately to its Minimum Generation level as the System Frequency returns to Target Frequency so that it can provide Primary and Secondary Response or Dynamic Regulation Low from Minimum Generation if the System Frequency continues to fall. For the avoidance of doubt, under normal operating conditions steady state operation below Minimum Generation is not expected. The Designed Minimum Operating Level must not be more than 55% of Registered Capacity.
Connection Conditions | Insert in CCA.3.3 | Insert “High Frequency Response or Dynamic Regulation High” | The Designed Minimum Operating Level is the output at which a Generating Unit and/or CCGT Module and/or Power Park Module and/or DC Converter has no High Frequency Response or Dynamic Regulation High capability. It may be less than, but must not be more than, 55% of the Registered Capacity. This implies that a Generating Unit or CCGT Module or Power Park Module or DC Converter is not obliged to reduce its output to below this level unless the Frequency is at or above 50.5 Hz (cf BC3.7).
Connection Conditions | Insert in CCA.3.4 | Insert “High Frequency Response or Dynamic Regulation Low” | The Primary Response or Dynamic Regulation Low capability (P) of a Generating Unit or a CCGT Module or Power Park Module or DC Converter is the minimum increase in Active Power output between 10 and 30 seconds after the start of the ramp injection as illustrated diagrammatically in Figure CC.A.3.2. This increase in Active Power output should be released increasingly with time over the period 0 to 10 seconds from the time of the start of the Frequency fall as illustrated by the response from Figure CC.A.3.2.
Connection Conditions | Insert in CCA.3.4 | Insert “High Frequency Response or Dynamic Regulation Low” | The Secondary Response or Dynamic Regulation Low capability (S) of a Generating Unit or a CCGT Module or Power Park Module or DC Converter is the minimum increase in Active Power output between 30 seconds and 30 minutes after the start of the ramp injection as illustrated diagrammatically in Figure CC.A.3.2.
Connection Conditions | Insert in CCA.3.4 | Insert “High Frequency Response or Dynamic Regulation High” | The High Frequency Response or Dynamic Regulation High capability (H) of a Generating Unit or a CCGT Module or Power Park Module or DC Converter is the decrease in Active Power output provided 10 seconds after the start of the ramp injection and sustained thereafter as illustrated diagrammatically in Figure CC.A.3.3. This reduction in Active Power output should be released increasingly with time over the period 0 to 10 seconds from the time of the start of the Frequency rise as illustrated by the response in Figure CC.A.3.2.
ECC | ECC A.3.1​ | Insert “Primary Response or Dynamic Regulation Low, Secondary Response or Dynamic Regulation Low and High Frequency Response or Dynamic Regulation High” | Scope The frequency response capability is defined in terms of Primary Response, Secondary Response or Dynamic Regulation Low and High Frequency Response or Dynamic Regulation High. In addition to the requirements defined in ECC.6.3.7 this appendix defines the minimum frequency response requirements for:- (a) each Type C and Type D Power Generating Module (b) each DC Connected Power Park Module (c) each HVDC System
ECC | ECC A.3.2 | Insert “Primary Response or Dynamic Regulation Low, Secondary Response or Dynamic Regulation Low” | Plant Operating Range The upper limit of the operating range is the Maximum Capacity of the Power Generating Module or Generating Unit or CCGT Module or HVDC Equipment. The Minimum Stable Operating Level may be less than, but must not be more than, 65% of the Maximum Capacity. Each Power Generating Module and/or Generating Unit and/or CCGT Module and/or Power Park Module or HVDC Equipment must be capable of operating satisfactorily down to the Minimum Regulating Level as dictated by System operating conditions, although it will not be instructed to below its Minimum Stable Operating Level . If a Power Generating Module or Generating Unit or CCGT Module or Power Park Module, or HVDC Equipment is operating below Minimum Stable Operating Level because of high System Frequency, it should recover adequately to its Minimum Stable Operating Level as the System Frequency returns to Target Frequency so that it can provide Primary and Secondary Response or Dynamic Regulation Low from its Minimum Stable Operating Level if the System Frequency continues to fall. For the avoidance of doubt, under normal operating conditions steady state operation below the Minimum Stable Operating Level is not expected. The Minimum Regulating Level must not be more than 55% of Maximum Capacity.
ECC | ECC A.3.3 | Insert “High Frequency Response or Dynamic Frequency High” | The Minimum Regulating Level is the output at which a Power Generating Module and/or CCGT Module and/or Power Park Module and/or HVDC Equipment has no High Frequency Response or Dynamic Regulation High capability. It may be less than, but must not be more than, 55% of the Maximum Capacity. This implies that a Power Generating Module or CCGT Module or Power Park Module ) or HVDC Equipment is not obliged to reduce its output to below this level unless the Frequency is at or above 50.5 Hz (cf BC3.7).
ECC | ECC A.3.4 | Insert “Primary Response or Dynamic Regulation Low” | The Primary Response or Dynamic Regulation Low capability (P) of a Power Generating Module or a CCGT Module or Power Park Module or HVDC Equipment is the minimum increase in Active Power output between 10 and 30 seconds after the start of the ramp injection as illustrated diagrammatically in Figure ECC.A.3.2. This increase in Active Power output should be released increasingly with time over the period 0 to 10 seconds from the time of the start of the Frequency fall as illustrated by the response from Figure ECC.A.3.2.
ECC | ECC A.3.4 | Insert “Secondary Response or Dynamic Regulation Low” | The Secondary Response or Dynamic Regulation Low capability (S) of a Power Generating Module or a CCGT Module or Power Park Module or HVDC Equipment is the minimum increase in Active Power output between 30 seconds and 30 minutes after the start of the ramp injection as illustrated diagrammatically in Figure ECC.A.3.2.
ECC | ECC A.3.4 | Insert “High Frequency Response or Dynamic Regulation High” | The High Frequency Response or Dynamic Regulation High capability (H) of a Generating Unit or a CCGT Module or Power Park Module or DC Converter is the decrease in Active Power output provided 10 seconds after the start of the ramp injection and sustained thereafter as illustrated diagrammatically in Figure CC.A.3.3. This reduction in Active Power output should be released increasingly with time over the period 0 to 10 seconds from the time of the start of the Frequency rise as illustrated by the response in Figure CC.A.3.2.
ECC | Figure CC.A.3.2 | Insert "or Dynamic Regulation Low" | Figure CC.A.3.2 - Interpretation of Primary and Secondary Response or Dynamic Regulation Low Values
ECC | Figure CC.A.3.3 | Insert "or Dynamic Regulation High" | Figure CC.A.3.3 - Interpretation of High Frequency Response or Dynamic Regulation High Values
ECC | ECC 6.3.7 | Insert "or Dynamic Regulation High" Also a number of diagrams/tables which may need amending - see column E | ECC.6.3.7.3.3(iv) refers to “Active Power Primary Frequency response” without amendment to include DRLow.
Planning Code (PC)​ | PC A.5.5​ | Insert "or Dynamic Regulation High" | PC.A.5.5.3 High Frequency Response or Dynamic Regulation High To Frequency Rise High Frequency Response or Dynamic Regulation High values for a +0.5Hz ramp are required at six MW loading points (MLP1 to MLP6) as detailed above.
Planning Code (PC)​ | APPENDIX D - DATA NOT DISCLOSED TO A RELEVANT TRANSMISSION LICENSEE PC.A.5.3.2 (d) Option 1 (iii) | Insert "or Dynamic Regulation Low" and "or Dynamic Regulation High" | GOVERNOR AND ASSOCIATED PRIME MOVER PARAMETERS Option 1 BOILER & STEAM TURBINE DATA Boiler time constant (Stored Active Energy) HP turbine response ratio: (Proportion of Primary Response or Dynamic Regulation Low arising from HP turbine) HP turbine response ratio: (Proportion of High Frequency Response or Dynamic Regulation High arising from HP turbine)
Planning Code (PC)​ | PART 2 - DETAILED PLANNING DATA PC.A.5.3.2 | Insert "or Dynamic Regulation High" | The following data items need only be supplied for Large Power Stations: (iii) Boiler & Steam Turbine Data Boiler Time Constant (Stored Active Energy) s HP turbine response ratio: proportion of Primary Response or Dynamic Regulation Low arising from HP turbine % HP turbine response ratio: proportion of High Frequency Response or Dynamic Regulation High arising from HP turbine % [End of Option 1]
Planning Code (PC)​ | PC A.9.3.2​ | Insert "or Dynamic Regulation Low" | PC.A.9.3.2 The RMS models shall include all electrical and mechanical phenomena that impact on the Active Power and/or Reactive Power of the User’s Plant and Apparatus for sub-transient, transient and synchronous dynamics within the context of an RMS study assumptions up to and including Primary and Secondary Response or Dynamic Regulation Low timeframes or when post-event steady state conditions have been achieved.
Planning Code (PC)​ | PC.A.5.5.1 MW Loading Points At Which Data Is Require | Insert "or Dynamic Regulation Low" | PC.A.5.5.1 MW Loading Points At Which Data Is Required Response values are required at six MW loading points (MLP1 to MLP6) for each Genset. Primary and Secondary Response or Dynamic Regulation Low values need not be provided for MW loading points which are below Minimum Generation or Minimum Stable Operating Level. MLP1 to MLP6 must be provided to the nearest MW.
Planning Code (PC)​ | PC.A.5.5.2 Primary And Secondary Response or Dynamic Regulation Low To Frequency Fall | Insert "or Dynamic Regulation Low" | PC.A.5.5.2 Primary And Secondary Response or Dynamic Regulation Low To Frequency Fall Primary and Secondary Response or Dynamic Regulation Low values for a -0.5Hz ramp are required at six MW loading points (MLP1 to MLP6) as detailed above
Data Registration Code (DRC)​ | DRC 6.1.4​ | Insert in DRC.6.1.4 “Primary Response or Dynamic Regulation Low, Secondary Response or Dynamic Regulation Low, and High Frequency Response or Dynamic Regulation High” | DRC.6.1.4 Schedule 4 - Large Power Station Droop and Response Data. Comprising data on governor Droop settings and Dynamic Regulation Low and High data for Large Power Stations.
Data Registration Code (DRC)​ | Schedule 1, pg 8 Data Description | Insert "or Dynamic Regulation Low" | HP turbine response ratio: (Proportion of Dynamic Regulation Low arising from HP turbine)
Data Registration Code (DRC)​ | Schedule 1, pg 8 Data Description | Insert "or Dynamic Regulation High" | HP turbine response ratio: (Proportion of Dynamic Regulation High arising from HP turbine)
Data Registration Code (DRC)​ | Schedule 4, Note 4 | Insert in DRC Schedule 4 Note 4 “Primary Response or Dynamic Regulation Low, Secondary Response or Dynamic Regulation Low, and High Frequency Response or Dynamic Regulation High” | Primary, Secondary and High Frequency Response are defined in CC.A.3.2 or ECC.A.3.2 and are based on a frequency ramp of 0.5Hz over 10 seconds. Primary Response is the minimum value of response between 10s and 30s after the frequency ramp starts, Secondary Response between 30s and 30 minutes, and High Frequency Response is the minimum value after 10s on an indefinite basis. For MFR (mandatory Frequency Response) refer to "Prevailing version of the Response Services -Service Terms".
Post Gate Closure Process (BC2)​ | BC2.9.5.1​ | Insert "or Dynamic Regulation Low" Insert "or Dynamic Regulation High" | If, post Gate Closure, The Company determines, in its reasonable opinion, from the information then available to it (including information relating to a Generating Unit (as defined in the Glossary and Definitions and not limited by BC2.2) breakdown) that the number of, and level of Primary or Dynamic Regulation Low, Secondary or Dynamic Regulation Low and High Frequency Response or Dynamic Regulation Low available from Gensets (other than those units within Existing Gas Cooled Reactor Plant, which are permitted to operate in Limited Frequency Sensitive Mode at all times under BC3.5.3) available to operate in Frequency Sensitive Mode, is such that it is not possible to avoid De-Synchronising Existing Gas Cooled Reactor Plant then provided that:
Post Gate Closure Process (BC2)​ | BC2.A.2.1​ | Insert "or Dynamic Regulation Low" Insert "or Dynamic Regulation High" | (b) Frequency Control by means of Frequency sensitive generation. Gensets may be required to move to or from Frequency Sensitive Mode in the combinations agreed in the relevant Ancillary Services Agreement. They will be specifically requested to operate so as to provide Primary Response or Dynamic Regulation Low and/or Secondary Response or Dynamic Regulation Low and/or High Frequency Response or Dynamic Regulation High.
Post Gate Closure Process (BC2)​ | BC2.A.2.5​ | Insert "or Dynamic Regulation Low" Insert "or Dynamic Regulation High" | BC2.A.2.5 Instructions given by Telephone (a) Ancillary Service instructions for Frequency Control will normally follow the form: (i) an exchange of operator names; (ii) BM Unit Name; (iii) Time of instruction; (iv) Type of instruction; (v) Start Time. The times required in the instruction are expressed in London time. For example, for BM Unit ABCD-1 instructed at 1400 hours to provide Primary or Dynamic Regulation Low and High Frequency or Dynamic Regulation High response starting at 1415 hours: “BM Unit ABCD-1 message timed at 1400 hours. Unit to Primary or Dynamic Regulation Low and High Frequency Response or Dynamic Regulation High at 1415 hours”
Frequency Control Process (BC3)​ | BC3.5.4​ (a) | Insert "or Dynamic Regulation Low" Insert "or Dynamic Regulation High" | The Company may issue an instruction to a Genset (or DC Converter at a DC Converter Station or HVDC System if agreed as described in BC3.1.3) to operate so as to provide Primary Response and/or Secondary Response and/or High Frequency Response and/or Dynamic Regulation Low and/or Dynamic egulation High (in the combinations agreed in the relevant Ancillary Services Agreement). When so instructed, the Genset or DC Converter at a DC Converter Station or HVDC System must operate in accordance with the instruction and will no longer be operating in Limited Frequency Sensitive Mode, but by being so instructed will be operating in Frequency Sensitive Mode.
Frequency Control Process (BC3)​ | BC3.5.4​ (b) | Insert "or Dynamic Regulation Low" Insert "or Dynamic Regulation High" | Frequency Sensitive Mode is the generic description for a Genset (or DC Converter at a DC Converter Station or HVDC System) operating in accordance with an instruction to operate so as to provide Primary Response and/or Secondary Response and/or High Frequency Response and/or Dynamic Regulation Low and/or Dynamic Regulation High (in the combinations agreed in the relevant Ancillary Services Agreement)
Frequency Control Process (BC3)​ | BC.3.7 |  | BC.3.7 – contents page of BC No. 3 needs to be updated to include DR High.
Frequency Control Process (BC3)​ | BC3.7.1​ (a) | Insert "or Dynamic Regulation High" | Each Synchronised Genset (or each DC Converter at a DC Converter Station or HVDC System) in respect of which the Generator or DC Converter Station owner or HVDC System Owner and/or EISO has been instructed to operate so as to provide High Frequency Response and/or Dynamic Regulation High, which is producing Active Power and which is operating above the Designed Minimum Operating Level, is required to reduce Active Power output in response to an increase in System Frequency above the Target Frequency (or such other level of Frequency as may have been agreed in an Ancillary Services Agreement). The Target Frequency is normally 50.00 Hz except where modified as specified under BC3.4.2.
Frequency Control Process (BC3)​ | BC3.7.1​ (b)(i) | Insert "or Dynamic Regulation High" | The rate of change of Active Power output with respect to Frequency up to 50.5 Hz shall be in accordance with the provisions of the relevant Ancillary Services Agreement with each Generator or DC Converter Station owner or HVDC System Owner. If more than one rate is provided for in the Ancillary Services Agreement, The Company will instruct the rate when the instruction to operate to provide High Frequency Response and/or Dynamic Regulation High is given.
Frequency Control Process (BC3)​ | BC3.7.1​ (c) | Insert "or Dynamic Regulation High" | In addition to the High Frequency Response and/or Dynamic Regulation High provided, the Genset (or DC Converter at a DC Converter Station or HVDC System) must continue to reduce Active Power output in response to an increase in System Frequency above 50.5 Hz at a minimum rate of 2 per cent of output per 0.1 Hz deviation of System Frequency above that level, such reduction to be achieved within five minutes of the rise to or above 50.5 Hz. For a Power Station with a Completion Date after 1st January 2009, this reduction in Active Power should be delivered in accordance with in (i) to (iv) below. For the avoidance of doubt, the provision of this reduction in Active Power output is not an Ancillary Service.
Frequency Control Process (BC3)​ | BC3.7.2.1 (a) | Insert "or Dynamic Regulation High" | Each Synchronised Genset (or DC Converter at a DC Converter Station) operating in a Limited Frequency Sensitive Mode which is producing Active Power is also required to reduce Active Power output in response to System Frequency when this rises above 50.4 Hz. In the case of DC Converters at DC Converter Stations, the provisions of BC3.7.7 are also applicable. For the avoidance of doubt, the provision of this reduction in Active Power output is not an Ancillary Service. Such provision is known as "Limited High Frequency Response" and/or "Dynamic Regulation High".
Frequency Control Process (BC3)​ | BC3.7.2.1 (c) | Insert "or Dynamic Regulation High" | Each GB Code User in respect of a Genset (or DC Converter at a DC Converter Station) which is providing Limited High Frequency Response and/or Dynamic Regulation High in accordance with BC3.7.2 must continue to provide it until the Frequency has returned to or below 50.4 Hz or until otherwise instructed by The Company.
Operational Planning & Data Provision (OC2)​ | OC2.4.6.2​ | Insert "or Dynamic Regulation High" | This Operational Planning Margin requirements indication will also note the possible level of High Frequency Response and/or Dynamic Regulation High to be utilised by The Company in connection with the operation of the Balancing Mechanism in the week beginning with the Operational Day commencing during the subsequent Monday, which level shall be purely indicative
​
​
​
​
​