Some Potential Case studies

Introduction.

Preliminary research shows that, one case study where this could be implemented is the greater flexibility on securing against thermal overload for a double circuit fault during a planned outage. In this case 9x Electricity Ten Year Statement (ETYS) constraints boundaries were assessed to determine if cascade tripping following a double circuit fault during a planned outage could be secured against the SQSS. As a result, it was identified that on two constraint boundaries this could be implemented and the increase in the constraint capacity was between 150MW and 600MW.

Our analysis across nine key Electricity Ten Year Statement indicates that none of the boundaries can be assessed under a single-circuit fault criterion without risking widespread system disturbance. This demonstrates that the double-circuit fault criterion remains the only applicable standard, as confirmed by our research, which shows that reliability can be maintained only when considering double-circuit faults.

CASE STUDY 1:

### Scenario/Constraint Overview

In this scenario the study is modelled to have North to South flows from Humber region which is typically the case when we have high winds from Scotland. In the scenario, we take an example in 2024, with an outage on a circuit connected to substation X and high wind in the Humber region, high flows are observed making their way between other available circuits.

### Worst Trip and Overload

The worst trip is DC fault close to substation X, which overloads circuit A into its 10-minute ratings, internal assessment has determined that this is a thermal constraint. The post-fault-action that returns the circuit to post fault continuous rating (PFC) is tapping QB at substation Y by 6 taps and taking approximately 900MW drops at substation Z. By ignoring the DC trip, it is possible to increase the limit by approximately 1500MW. Increasing the limit beyond this results in study non-convergence, which indicates voltage collapse.

Observations and Conclusions

By choosing to disregard the DC fault, which has low probability occurrence, it is possible to achieve significant savings for consumers on constraint costs. If these outages are not allowed to take place, it might result in transmission work required for CP2030 being delayed, therefore missing the objectives set.

CASE STUDY 2

### Scenario/Constraint Overview

This scenario examines the potential for limit improvement by incorporating the SQSS relaxation method utilised in Scotland, specifically the approach of disregarding busbar trips. The study is structured to assess East to West power flows, which typically occur during periods of low wind generation in Scotland and can result in certain constraints becoming active. For this analysis, an example from 2024 has been used.

### Worst Trip and Overload

Within this scenario, the most severe event is a fault at substation X busbar, which leads to the overloading of multiple circuits beyond their 20-minute ratings. Generator effectiveness in this context points to a thermal constraint. The recommended post-fault action involves reducing the QB taps by six positions at substation Y and implementing an approximate 400MW reduction of generation at substation X, with additional balancing provided by plants located on the other end of the transmission network. These measures are intended to restore the three overloaded circuits to their post-fault continuous rating.

### Observations and Conclusions

After the analysis in this case study the post fault measures applied indicate that the busbar fault at substation X becomes the most critical, causing overloads on the surrounding circuit when the machine A is offline. Conversely, if the machine A is operational, a fault on the double circuit in the proximity to substation X results in a comparable worst-case scenario. Therefore, when the machine A is not running, higher operational limits can be achieved by ignoring busbar trips.

For this scenario, the application of the Scottish approach—ignoring busbar trips—results in an estimated improvement of approximately 500MW in system limits, with a further benefit of removing the requirement to bid-off 400MW of generation. The fault rate of a busbar/mesh corner occurring on the network is 0.29% per year (FRCR Report 2025).

# References:

Frequency Risk and Control Report (FRCR) | National Energy System Operator

NESO, National Access Policies, Case Study Repository, NAP Team, Case Study 2, Ignoring Bar Trips on a Specific Location, July 2024, Confidential, consulted for the purposes of this proposal only.

NESO, National Access Policies, Case Study Repository, NAP Team, Case Study 1, Ignoring DC Trips on a Specific Location, July 2024, Confidential, consulted for the purposes of this proposal only.

Security and Quality of Supply Standard (SQSS) | National Energy System Operator

Transmission Acceleration Action Plan. Consultation Report, page 29 op cit.

Scottish approach. In the SQSS, Section 4.6 odes page,

FRCR 2025 report https://www.neso.energy/document/360876/download

Page 25