Public

17 February 2026 – Issue 1

Guidance Note - Metering Polarity Standard for Power Flow Data

Public

Contents

1.	Foreword	3

2.	Acronyms and Definitions	4

3.	Introduction	5

4.	Metering Polarity Standard for Power Flow Data	6

5.	Explanation of Metering Polarity Standard	7

Document Record	9

Public

# Foreword

NESO needs to operate the GB electricity network securely and safely in real-time using the Supervisory Control and Data Acquisition (SCADA) tool. The NESO SCADA system constantly receives power flow measurement data from external parties including Generators, Transmission Owners (TOs) and Network Operators (NOs) to show NESO Control Room engineers the most up-to-date network status and assist them to take operational actions if necessary.

In order to help the power flow measurement data received by NESO be consistent with the convention used by the NESO SCADA system, this guidance note has been created for use when setting up operational metering polarity. The convention used in this guidance is not currently enforced, however, it indicates the best practice approach and will be beneficial for all to ensure correct and efficient operation of the network.

Grid Code modification GC0182 and STC Code Modification CM0105 are currently underway to finalise this standard and implement the convention into both the Grid Code and STC. Please note, there is currently no known date of when this convention may be accepted into the Grid Code and STC and there is no guarantee that it will be accepted.

For any queries regarding this Guidance Note, please contact the NESO Operational Metering team via opsmetering@neso.energy

Public

| Aux Tx | Auxiliary Transformer |
| --- | --- |
| CT | Current Transformer |
| DRC | Dynamic Reactive Compensation |
| GB | Great Britain |
| HVDC | High Voltage Direct Current |
| IEMS | Integrated Energy Management System which is NESO’s SCADA system |
| KV | Kilo Volt |
| LV | Low Voltage |
| MVAR | Mega Volt Ampere Reactive |
| MW | Mega Watt |
| NESO | National Energy System Operator |
| NO | Network Operator |
| OFTO | Offshore Transmission Owner |
| S/S | Substation |
| SCADA | Supervisory Control and Data Acquisition |
| SVC | Static VAR Compensator |
| The Company | NESO |
| TO | Transmission Owner |
| VT | Voltage Transformer |

# Acronyms and Definitions

Public

# Introduction

Power flow polarity (assigning positive or negative direction) is of critical importance to ensure all parties can understand and interpret the direction of flow reported by the metering. Therefore, extreme care must be taken when configuring power flow meters.

The polarity of the power flow on NESO’s IEMS should align with that of the user’s systems sending the data, to ensure there is no confusion when comparing power flow values at the two locations.

Where it is required to assign directional flow to a quantity (e.g. MW and MVAR), “positive” (+) and “negative” (-) signs should be used in accordance with the diagram in Section 4. The diagram details the application of this sign convention for most types of Feeders, Transformers, Shunt Connected Reactive Compensation, Series Connected Reactive Compensation and Generator Connections. The arrows denote the direction of active and reactive power flow at the CT and VT.

The operational metering shown in the diagram is asset specific and does not include the bay metering in the TOs and NOs system. Bay metering in these areas is considered to always follow the convention of:

- “positive” (+) assigned to power flow out of the bay

- “negative” (-) assigned to power flow into the bay

In order to more clearly distinguish the asset specific metering, virtual bus nodes (highlighted in red) have been denoted in the diagram. These virtual bus nodes represent the connection points between each individual asset, where there is no physical bus present.

Additionally, connection point nodes (highlighted in green) have been indicated in the diagram to clearly define the boundary between Generator operational metering and the Onshore/Offshore Transmission and Distribution operational metering.

Not all operational metering seen in the diagram is required to be provided to NESO, however, the operational metering that is provided will be required to follow the convention shown.

It is important to note that the diagram is an example of the most common equipment found on the network and is not suggesting that each substation or voltage level be required to contain the equipment represented. Equally, it is not suggesting that each substation or voltage level be limited to the equipment represented.

Public

# Metering Polarity Standard for Power Flow Data

Public

# Explanation of Metering Polarity Standard

The diagram denotes the convention:

- Connections between GB substations are positive when leaving the substation and negative when entering the substation

- Shunt Connected Reactive Compensation is positive when leaving the plant and negative when entering the plant

- Series Connected Reactive Compensation and connections within a substation (e.g. a cable section) are represented by positive flow into the device and negative flow out of the device, on both sides

Public

- Generator and Demand Connections include all assets from the User up to the connection point. All metering associated with User Connections is positive towards the Connection Point and negative away from the Connection Point

- International Interconnectors are positive at the converter station when power is being supplied into a GB substation and negative at the converter station when power is being supplied from a GB substation (effectively they are treated like generators on the GB system)

For any equipment not represented in the diagram, the convention used should be that of the category to which the equipment belongs (as mentioned above):

- Connections between GB substations:

  - positive when leaving the substation and negative when entering the substation

- Shunt Connected Reactive Compensation:

  - positive when leaving the plant and negative when entering the plant

- Series Connected Reactive Compensation and connections within a substation:

  - positive into the device and negative out of the device (on both sides)

- Generator and Demand Connections (including all assets from the User up to the connection point):

  - positive towards the Connection Point and negative away from the Connection Point

- International Interconnectors:

  - positive at the converter station when power is being supplied into a GB substation and negative at the converter station when power is being supplied from a GB substation (effectively they are treated like generators on the GB system)

Public

# Document Record

| Issue | Draft | Date | Author | Description of changes |
| --- | --- | --- | --- | --- |
| 1 |  | 17/02/2026 |  | First Issue. |

— End of Document —