| Workgroup Consultation |  |  |  |
| --- | --- | --- | --- |
| GC0182: Standardisation of Power Flow Metering Polarity Overview: This modification aims to provide a unified standard for Power Flow Metering Polarity when data is sent to NESO. The standard will be in the format of a diagram and explanatory description. |  | Modification process & timetable Workgroup Report 16 September 2026 13 May 2026 Code Administrator Consultation 06 October 2026 - 06 November 2026 29 May 2026 - 29 June 2026 Draft Final Modification Report 18 November 2026 22 July 2026 Final Modification Report 01 December 2026 11 August 2026 Implementation TBC 1 2 3 4 5 6 7 Proposal Form 07 July 2025 Workgroup Consultation 02 March 2026 - 20 March 2026 |  |
| Have 2 minutes? Read our Executive summary Have 60 minutes? Read the full Workgroup Consultation Have 120 minutes? Read the full Workgroup Consultation and Annexes. |  |  |  |
| Status summary: The Workgroup are seeking your views on the work completed to date to form the final solution to the issue raised. |  |  |  |
| This modification is expected to have a: Medium impact on: CUSC parties (BCA, BEGA, BELLA) and LEEMPS Low impact on: NESO and Transmission Licensees |  |  |  |
| Modification drivers: This modification is driven by the need for cross-code consistency, improved efficiency, GB regulatory compliance, harmonisation of standards, and enhancements to system operability, planning, and security. |  |  |  |
| Governance route | Standard Governance modification with assessment by a Workgroup |  |  |
| Who can I talk to about the change? | Proposer: Thomas Goss, NESO Thomas.Goss2@neso.energy |  | Code Administrator Chair: Prisca Evans prisca.evans@neso.energy |
| How do I respond? | Send your response proforma to grid.code@neso.energy by 5pm on 20 March 2026 |  |  |

Contents

Executive Summary	3

What is the issue?	4

What is the defect the Proposer believes this modification will  address?	4

Why change?	4

What is the solution?	4

Proposer’s Original solution	4

Workgroup considerations	4

Alternative Requests	5

Workgroup Alternative 1 solution	7

Workgroup Alternative 2 solution	7

What is the impact of this change?	8

Original and Workgroup Alternative Proposer’s assessment against Code Objectives	8

When will this change take place?	8

Interactions	9

How to respond	9

Acronyms, key terms and reference material	10

Annexes	11

# Executive Summary

Inconsistent power flow polarity can impact situational awareness, system security, and operational efficiency for NESO Control Room engineers, leading to potential Security and Quality of Supply Standard (SQSS) breaches, higher balancing costs, and delays in metering setup. Current challenges include the absence of a unified power flow metering polarity standard, lack of code or licence obligations mandating adherence to a standard or correction where that is not complied with and having different conventions across parties.

What is the issue?

NESO relies on Supervisory Control and Data Acquisition (SCADA) to operate the GB electricity network securely in real time, using power flow data mainly from Generators, Transmission Owners (TOs) and Offshore Transmission Owner (OFTOs). NESO also receive power flow data from    Network Operators (NOs) in some cases, for example the Bolney 132KV substation. There is currently no clear and unified standard in Grid Code or STC for power flow data being sent to NESO and no clauses in Grid Code, STC or licence obligation requesting parties to follow a power flow polarity standard. Thus, parties may choose their own convention which could be inconsistent with other parts of the network. Inconsistent polarity has been identified in over 800 metering points feeding errors into NESO’s SCADA and downstream systems, leading to suboptimal transmission operation, higher operating costs, and increased costs for consumers. Whilst NESO endeavour to minimise the impact of these 800 metering points with incorrect polarity by applying temporary workarounds, it is necessary to prevent the issue of inconsistent meter polarity from getting worse by introducing a mandatory polarity standard through this Grid Code Modification and corresponding STC Modification for the newly installed or upgraded meters whose power flow data will be submitted to NESO.

What is the solution and when will it come into effect?

Proposer’s solution: NESO proposes to introduce and publish an Electrical Standard (Annex 05) defining the polarity convention for operational metering data submitted to NESO. The Standard will comprise a diagram and supporting explanatory notes and will be referenced in the Grid Code and the GC.A.A Annex to the General Conditions.

The Standard will apply to:

- New connections with a Completion Date on or after 540 days following the implementation of GC0182 (10 Working Days after the Authority’s decision); and

- Existing connections where operational metering is newly installed or upgraded on or after 540 days following the implementation of GC0182.

This approach aims to ensure consistent polarity across operational metering and prevent further divergence in practice.

Implementation date: 10 Working days after Authority decision. However, the standard is proposed to become applicable to code users 540 days after the Implementation date.

What is the impact if this change is made?

The Proposed standard will significantly improve system operability and security by ensuring consistent power flow polarity and enhancing situational awareness for NESO. In addition, NESO has been relying on historical metering data to conduct the forecast for generation, demand and interconnectors in long-term and short-term periods. Therefore, improvement in the quality and accuracy of the metering data can significantly improve the forecasting accuracy for NESO. It will also benefit consumers indirectly through reduced operating costs and improved system efficiency.

Interactions

Grid Code Modification interacts with GC0103 (The introduction of harmonised Applicable Electrical Standards in GB to ensure compliance with the EU Connection Codes). As Grid Code modification GC0103 is expected to be approved before GC0182, the legal text developed in GC0182 will be based on the GC0103 text. More specifically, GC0103 will add Part II – Applicable Electrical Standards to the ANNEX to the GENERAL CONDITIONS and specify that the Applicable Electrical Standards are applicable for NGET’s, SPT’s and SHETL’s Transmission System. GC0182 will add the reference to the proposed Metering Polarity Standard for Power Flow to the new Part II (b) added by GC0103. The legal text proposed by GC0182 will also use the term Applicable Electrical Standard introduced by GC0103. This will ensure the Metering Polarity Standard is correctly integrated and consistent with the revised Applicable Electrical Standards introduced through Grid Code modification GC0103 so that the Metering Polarity Standard will be applicable in all Transmission Areas.

This Grid Code Modification also interacts with STC and STCP Modification CM0105 on Power Flow Metering Polarity to ensure consistency across Grid Code and STC.

What is the issue?

## What is the defect the Proposer believes this modification will address?

NESO must operate the GB electricity network securely and safely in real time using the SCADA tool. The NESO SCADA system continuously receives power flow data from external parties — such as Generators, Transmission Owners (TOs), and Network Operators (NOs) — to provide Control Room engineers with up-to-date network status and support operational decisions. However, sometimes power flow metering data with polarity inconsistent with NESO conventions (e.g., negative instead of positive flow) is fed into the system due to the lack of a unified meter polarity standard. Over 800 meters have been identified with incorrect polarity as of February 2025 and NESO has been liaising with corresponding stakeholders to request the polarity of these meters be corrected where possible. Whilst waiting for stakeholders’ response, or if it has been confirmed by the stakeholder that those incorrect polarity issues will not be fixed, NESO applies temporary workarounds such as changing the software configuration for each received metering points on NESO SCADA system so that they are “virtually” consistent with the established NESO convention. These workarounds become difficult to manage and are not sustainable if the number of metering points with incorrect polarity increases. Since NESO SCADA data feeds multiple internal downstream systems, errors in operational metering can lead to suboptimal transmission system operation, increasing operating costs and ultimately raising costs for consumers. Therefore, the major intention and benefit of this proposal will be that the issue of incorrect meter polarity can be prevented from getting worse, once a unified standard is in place for power flow data sent to NESO, and the control engineers will have access to the correct data without having to proactively check the polarity and run it through the process to align it with the established conventions, reducing the probability of errors in decision-making. This will be a gradual resolution as we are not intending to force already active meters to be changed, rather ensure that new connections are adhering to the correct polarity terms, as will any replacement meters at existing sites.

## Why change?

Receiving power flow metering data with inconsistent polarity compared to NESO’s convention can undermine situational awareness for NESO Control Room engineers, reduce system security, and lead to suboptimal performance, potential SQSS breaches, and higher balancing costs. For other stakeholders, it can delay operational metering setup for new connections and increase workload due to the need for corrections, as well as adding the potential for errors to appear in the data and any decisions made as a result. Industry stakeholders may also face delays in NESO’s decision making on approving the outage plan. NESO has worked with industry parties to address these issues, but challenges remain:

- No clear, unified standard for power flow polarity in data sent to NESO.

- No industry code or licence clause requiring parties to follow a polarity standard, allowing inconsistent conventions.

- No obligation for parties to correct inconsistent polarity in operational metering data.

The Original Proposal form can be found in Annex 01.

What is the solution?

## Proposer’s solution

The Proposer suggests publishing a diagram and accompanying explanatory notes as an Electrical Standard (Annex 05), to define a Power Flow Metering Polarity convention to be adhered to when sending operational metering data to NESO. This standard will be referenced in the Grid Code and the GC.A.A Annex to the General Conditions.

The Standard will apply to:

- New connections with a Completion Date on or after 540 days following the implementation of GC0182 (10 Working Days after the Authority’s decision); and

- Existing connections where operational metering is newly installed or upgraded on or after 540 days following the implementation of GC0182.

This Proposal has been refined over many months following discussions at the GCDF (October 2024 and July 2025), in addition to discussion and consultation through the GC0182 Governance Process.

Workgroup considerations

The Workgroup convened 5 times to; discuss the issue as identified by the Proposer within the scope of the defect, develop potential solutions, and evaluate the proposal in relation to the Applicable Code Objectives.

Workgroup Discussions ahead of the Workgroup Consultation

Workgroup 1:

The NESO representative proposed the high-level plan where a unified power flow polarity standard, in the form of a diagram with an explanatory description, would be published as an Electrical Standard (Annex 05) which would be referred in the relevant Grid Code clauses. It was noted that the proposed power flow polarity standard would not apply retroactively. Workgroup members were generally supportive, however, they requested NESO to clarify when the implementation date would be. A Workgroup Member also sought clarity on whether the modification applies to TOs, OFTOs, and large demand users, and the need for potential changes to the STC.

Workgroup 2:

The NESO Representative took the Workgroup through the proposed changes to the Legal Text. The changes consisted of adding a new Electrical Standard (Annex 05) to the General Conditions. The Code User would be directed to the Electrical Standard (Annex 05) via the proposed new clauses CC 6.5.6 (f) and ECC 6.5.6.4 (f).

CC6.5.6.(f): Where a GB Code User changes its operational metering on or after 1st November 2026, the User shall be required to satisfy the requirements of the Meter Polarity Standard for Power Flow. The detailed specifications for this standard are listed as an Electrical Standard in Annex (b) of the General Conditions. The GB Code User shall provide the list of metering points to The Company during the planning stage prior to replacement of the operational metering. These metering points will be checked and validated by The Company and agreed with the GB Code User prior to issue of Limited Operational Notification.

ECC6.5.6.4(f):	Where an EU Code User installs or changes its operational metering on or after 1st November 2026, the User shall be required to satisfy the requirements of the Meter Polarity Standard for Power Flow. The detailed specifications for this standard are listed as an Electrical Standard in Annex (b) of the General Conditions. The EU Code User shall provide the list of metering points to The Company during the planning stage prior to replacement of the operational metering. These metering points will be checked and validated by The Company and agreed with the EU Code User prior to issue of Limited Operational Notification.

The Workgroup discussed whether changes to metering standards should be implemented solely via the Bilateral Connection Agreement (BCA) referencing the General Conditions, or if changes to Connection Conditions (CCs)/European Connection Conditions (ECCs) were necessary. Some members advocated for a streamlined approach using only the BCA and General Conditions, to avoid confusion and conflicting obligations. However, another member suggested that implementing solely via the BCA may miss connections already signed and queued to connect in the future. This member suggested adding clauses to CCs/ECCs, with compliance for new connections determined by the Completion Date. It was agreed by all parties the date of 01/11/2026 was not achievable and would need to be amended in the next draft of legal text.

Workgroup 3:

Based on the workgroup feedback, the NESO Representative outlined a plan for incorporating the metering polarity requirements into the BCA Appendix F5 (Appendix E for LEEMPS) template so that all new offers would need to comply. Following OFGEM approval, the new standard would be formalised as an Electrical Standard (Annex 05) and referenced in the Grid Code, creating new clauses CC 6.5.6 (f) and ECC 6.5.6.4 (f).

CC6.5.6 (f): Where a GB Code User installs or upgrades its operational metering on or after DD/MM/YYYY, the User shall be required to satisfy the requirements of the Metering Polarity Standard for Power Flow Data. The detailed specifications for this standard are listed as an Electrical Standard in Annex (b) of the General Conditions. The GB Code User shall provide the list of metering points being installed or upgraded to The Company and these metering points will be checked and validated by The Company and agreed with the GB Code User.

ECC6.5.6.4 (f): Where an EU Code User whose Completion Date is on or after DD/MM/YYYY the EU Code User shall be required to satisfy the requirements of the Metering Polarity Standard for Power Flow Data. The detailed specifications for this standard are listed as an Electrical Standard in Annex (b) of the General Conditions. The EU Code User shall provide the list of metering points being installed or upgraded to The Company. In the event of a new connection, the metering points will be 	checked and validated by The Company and agreed with the EU Code User prior to issue of Interim Operation Notification.

Once implemented into the Grid Code, the connection agreements would be updated to refer to the Grid Code.

Several Workgroup Members raised concerns over modifying agreements and questioned the appropriateness of introducing a new standard into connection agreements before Grid Code approval, highlighting the need for proper governance and the risk of creating confusion or inconsistency, especially if the standard is considered a CUSC Exhibit.

NESO provided context for the interim use of BCAs, providing examples such as the first storage and wind farm connections to the system. They explained that such measures were sometimes necessary due to lengthy Grid Code modification processes, while acknowledging the associated risks and the need for consensus. One Workgroup member highlighted that if OFGEM were to reject GC0182, any interim requirements added to BCAs would need to be removed from all affected contracts. The Workgroup member added that time, resource, and money may have been spent to comply, which would now be considered unnecessary and wasteful. The Workgroup agreed the preferred approach was not implementing the standard into the BCA before OFGEM’s decision. It was also noted that any interim arrangements required more consideration and possibly further consultation with the panel and industry stakeholders.

One Workgroup Member highlighted the missing scenario of EU Code Users upgrading metering. NESO agreed an additional ECC clause could be required.

Some Workgroup Members voiced concerns around the unknown applicable compliance date. NESO said this was to be determined by OFGEM approval and would likely be chosen to align with the implementation of 10 days after the authority decision. NESO representatives gave their reasoning for choosing Completion Date, explaining there can be long delays between application submission and connection. For NESO to prevent the issue of inconsistent polarity getting worse, they wish to capture connections who are already in the queue.

Workgroup 4:

The NESO Representative revised the implementation plan and presented the intention to publish a Guidance Note (Annex 04) on the NESO website, adding the link to the Guidance Note (Annex 04) in new Connection Agreements, before GC0182 is approved. The Workgroup members voiced their preference for not including the link in the Connection Agreements, due to there being no governance process for changing a guidance note.

The updated implementation plan proposed the following clause additions to the Grid Code:

CC6.5.6 (f) Where a GB Code User installs or upgrades its operational metering on or after DD/MM/YYYY [this being the GC0182 implementation date], the GB Code User shall ensure the operational metering conforms to the Metering Polarity Standard for Power Flow Data as provided in the Applicable Electrical Standards. The GB Code User shall provide the list of metering points being installed or upgraded to The Company and these metering points will be checked and validated by The Company and agreed with the GB Code User.

ECC6.5.6.4 (f) Where an EU Code User installs or upgrades its operational metering on or after DD/MM/YYYY [this being the GC0182 implementation date], the EU Code User shall ensure the operational metering conforms to the Metering Polarity Standard for Power Flow Data as provided in the Applicable Electrical Standards. The EU Code User shall provide the list of metering points being installed or upgraded to The Company and these metering points will be checked and validated by The Company and agreed with the EU Code User.

Some workgroup members questioned the clarity of the clauses, specifically the details of ECC 6.5.6.4. The Workgroup discussed the previously proposed Completion Date and how this was absent from the clauses. Workgroup members also felt the wording was not strong enough to correctly convey who is required to comply and under which scenarios. NESO representatives agreed to reconsider the inclusion of Completion Date and to refine the clauses to clearly state the different scenarios of new connections, and existing connection upgrades.

A Workgroup member also raised concern regarding the amount of time (post OFGEM decision) for connections to comply with the Electrical Standard (Annex 05), requesting that there be a longer period between decision and compliance.

A Workgroup member queried whether the implementation of the metering polarity standard is as simple as choosing which way to connect two wires and asked about the difficulty of making such changes during a project. The NESO Representative responded that it is generally straightforward to implement when installing or replacing the meter, however, making changes after commissioning is much more challenging and costly. Workgroup members discussed offshore sites, as changing connections after commissioning could cost tens or hundreds of thousands of pounds, highlighting the significant impact of late changes. Costs arise because once a site is commissioned and operational, modifying the outflow contract and physical setup becomes expensive. The NESO Representative also explained the option of complying with the Electrical Standard (Annex 05) via software updates, rather than physical re-wiring.

Ahead of Workgroup 5:

The NESO Representatives considered the comments from Workgroup members on how the power flow meter polarity standard can be effectively implemented and refined the proposed approach.

The final draft of the implementation plan, to be agreed by the workgroup members, is detailed below:

- Step 1: Before approval of GC0182, publish a Guidance Note (Annex 04) covering the Metering Polarity Standard on the NESO Website to notify and educate as many industry stakeholders as possible, as early as possible, on the best practice when setting up operational metering points and make them aware of the ongoing Grid Code change GC0182 and STC change CM0105. The Guidance Note (Annex 04) will also state that the principles outlined are not mandatory and corresponding Grid Code and STC Modifications may not be approved.

- Step 2: Before approval of GC0182, add the following statement into the Bilateral Agreement templates to notify as many industry stakeholders as possible, as early as possible, on the best practice when setting up operational metering points:

“Grid Code Modification GC0182 is currently underway to create a unified metering polarity standard for power flow data submitted to NESO. The operational metering of the GB Code User and EU Code User will need to follow the standard, if GC0182 is approved. A guidance note has been published on the NESO website highlighting the key principles of the proposed metering polarity standard. Please note that the key principles are not mandatory unless the GC0182 is approved and implemented”

- Step 3(A): If GC0182 is approved by OFGEM, on the Implementation Date:

- Publish the Metering Polarity Standard for Power Flow Data as a new Electrical Standard (Annex 05) and add reference in Part II (b) of Annex to Grid Code General Conditions.

- Add new clauses to Grid Code CC.6.5.6 and ECC.6.5.6.4 to specify that GB Code Users and EU Code Users will need to follow the Metering Polarity Standard for Power Flow Data 540 days after the Implementation Date of GC0182.

- Remove the Guidance Note (Annex 04) from NESO website.

- Update the Bilateral Agreement templates by adding the link to the newly published Electrical Standard and changing statement added in Step 2 to request all meters shall conform to the Metering Polarity Standard for Power Flow Data in accordance with ECC.6.5.6.

- NESO Compliance team will also send out a letter and memo to inform the industry of the new requirement for the Metering Polarity Standard for Power Flow Data and update the ONCC checklist (used during Compliance process) to capture this new requirement.

- Step 3(B): If GC0182 is rejected by OFGEM:

- Keep the Guidance Note (Annex 04) on NESO website and remove the statement related to ongoing GC0182 and CM0105.

- Update the Bilateral Agreement templates by changing the statement added in Step 2 to “In order to help the power flow measurement data received by NESO be consistent with the convention used by the NESO SCADA system, a guidance note has been published on NESO website for use when setting up operational metering polarity. The convention used in this guidance is not mandatory, however, it indicates the best practice approach and will be beneficial for all to ensure correct and efficient operation of the network.”

Draft legal text

The draft legal text for this change can be found in Annex 03.

What is the impact of this change?

The proposed change will impact NESO, GB Code Users and EU Code Users. GB Code Users and EU Code Users will need to adopt the new standard for new connections during commissioning and when new metering points are installed or upgraded in existing sites, requiring some process updates. The standard has been developed to align with existing unofficial conventions to minimise disruption; however, there may be instances where work is required to conform to the proposed standard such as wiring changes for equipment or software reconfiguration.

This modification is expected to have low impact on NESO as the provided metering will be correctly interpreted by NESO’s systems without the need for manipulation. NESO may, however, require additional checks and tests to ensure compliance.

For NESO, it will improve situational awareness and decision-making by ensuring consistent polarity in power flow data, reducing errors and enhancing system security.

Positive impacts include improved operability, forecasting accuracy, cost efficiency, and alignment with existing conventions, while negative impacts involve implementation effort, transitional challenges, and limited initial scope as the change applies only to new connections and new metering points in existing sites but not legacy metering points.

Forecasting inaccuracies are being addressed by focusing on the accuracy of the SCADA operational metering. Specifically, if the metering has incorrect polarity, it directly impacts the National Demand calculation, leading to inaccuracies in forecasting models. By preventing incorrect polarity in operational metering, the modification aims to enhance the accuracy of National Demand calculations, thereby improving demand forecasting going forward.

Proposer’s assessment against Code Objectives

| Original Proposer’s assessment against Grid Code Objectives |  |
| --- | --- |
| Relevant Applicable Objective | Identified impact |
| (i) To permit the development, maintenance and operation of an efficient, coordinated and economical system for the transmission of electricity; | ​​Positive​ The change will improve situational awareness and system security in general, as well as allowing for better forecasting and reducing balancing costs. Reduce and/or mitigate iterations and delay for setting up new connections and approval for outage and commissioning. Improved coordination, efficiency and transparency between NESO and other parties following unified polarity standard and standardised process. Eliminate situations where some stakeholders (i.e. batteries) are unable to use the current system. |
| (ii) Facilitating effective competition in the generation and supply of electricity (and without limiting the foregoing, to facilitate the national electricity transmission system being made available to persons authorised to supply or generate electricity on terms which neither prevent nor restrict competition in the supply or generation of electricity); | Neutral This Modification will not directly impact on the generation and supply of electricity, however it will instead allow for better overall system management that will be more cost-effective and ensure that no stakeholders are left outside of the system. |
| (iii) Subject to sub-paragraphs (i) and (ii), to promote the security and efficiency of the electricity generation, transmission and distribution systems in the national electricity transmission system operator area taken as a whole; | ​​Positive​ Improved situational awareness, system security, better forecast and reduced balancing cost. Reduce and/or mitigate iterations and delay for setting up new connections and approval for outage and commissioning. Improved coordination, efficiency and transparency between NESO and other parties following unified polarity standard and standardised process. |
| (iv) To efficiently discharge the obligations imposed upon the licensee by this license* and to comply with the Electricity Regulation and any relevant legally binding decisions of the European Commission and/or the Agency; and | Neutral. This Modification is in line with our license and regulatory obligations, which is facilitating a change to a new Frequency Regulation system as mandated by Ofgem. |
| (v) To promote efficiency in the implementation and administration of the Grid Code arrangements | Positive: The data from the meters is used more and more widely by NESO in multiple aspects, and the current methodology is increasingly unviable as the temporary fixes for the meter polarity issues decline in effectiveness. The changes we are proposing will ensure that the Gris Code is much more clear regarding the obligations or all parties, and make significant improvements to the administration resulting in time and cost savings. |

When will this change take place?

Implementation date

10 Working days after Authority decision

Date decision required by

31/12/2025

Interactions

| ​​☐CUSC | ​​☐​BSC | ​​☒​STC | ☐SQSS |
| --- | --- | --- | --- |
| ​​☐European Network Codes | ​​☐​ EBR Article 18 T&Cs1 | ​​☒​Other modifications | ​​☐​Other |
| ☐NCER Article 4 |  |  |  |

How to respond

Standard Workgroup Consultation questions

- Do you believe that the Proposal better facilitate the Applicable Objectives versus the current baseline?

- Do you support the proposed implementation approach?

- Do you have any other comments?

- Do you wish to raise a Workgroup Consultation Alternative request for the Workgroup to consider?

- Does the draft legal text satisfy the intent of the modification?

- Do you agree with the Workgroup’s assessment that the modification does/does not impact the European Electricity Balancing Regulation (EBR) Article 18 terms and conditions held within the Code?

Specific Workgroup Consultation questions

- Do you believe it is appropriate to include the metering polarity requirements as an Electrical Standard? If not, please state your rationale.

- Do you have any specific comments on the draft Metering Polarity Electrical Standard?

The Workgroup is seeking the views of Grid Code Users and other interested parties in relation to the issues noted in this document and specifically in response to the questions above.

Please send your response to grid.code@neso.energy using the response pro-forma which can be found on the GC0182 modification page.

In accordance with Governance Rules if you wish to raise a Workgroup Consultation Alternative Request, please fill in the form which you can find at the above link.

If you wish to submit a confidential response, mark the relevant box on your consultation proforma. Confidential responses will be disclosed to the Authority in full but, unless agreed otherwise, will not be shared with the Panel, Workgroup or the industry and may therefore not influence the debate to the same extent as a non-confidential response.

Acronyms, key terms and reference material

| Acronym / key term | Meaning |
| --- | --- |
| BSC | Balancing and Settlement Code |
| BCA | Bilateral Connection Agreement |
| BEGA | Bilateral Embedded Generation Agreement |
| BELLA | Bilateral Exemptible Large License-exempt Generator Agreement |
| CCs | Connection Conditions |
| CUSC | Connection and Use of System Code |
| ECCs | European Connection Conditions |
| EBR | Electricity Balancing Guideline |
| GCDF | Grid Code Development Forum |
| LEEMPS | License Exemptible Embedded Medium Power Station |
| NO | Network Operator |
| OFTO | Offshore Transmission Owner |
| SCADA | Supervisory Control and Data Acquisition |
| STC | System Operator Transmission Owner Code |
| SQSS | Security and Quality of Supply Standards |
| T&Cs | Terms and Conditions |
| TO | Transmission Owner |

Reference material

- Add links to the main reference material here. Put the title of the document and hyperlink the text

Annexes

| Annex | Information |
| --- | --- |
| Annex 01 | GC0182 Proposal Form |
| Annex 02 | GC0182 Terms of Reference |
| Annex 03 | GC0182 Draft Legal Text |
| Annex 04 | GC0182 Guidance Note |
| Annex 05 | GC0182 New Electrical Standard |