## Totals
Final Sums |  | Liability £m
| Stage 1 | 28
| Stage 2 | 49.5
| Stage 3 | 0
| Total | 77.5
CMP417 |  | Attributable £m | Wider £m*
| Stage 1 | 4.4561 | 0.69302
| Stage 2 | 0.75 | 0.60639
| Stage 3 | 0 | 0
| Total | 5.2061 | 1.2994 | 6.5055
*Calculated on the basis of the additional capacity at each stage

## User input - Stage 1
|  | User input | Calculated
User connection details
| Demand Capacity (MW) | 80
| ETYS zone | A6
| ETYS zonal charge (£/MW) | 8662.75
Transmission connection asset works - Stage 1
CMP417
| Work element | Cost (£m) | Capacity (MW) | Beyond nearest MITS node? (See explainer worksheet) | SIF | LARF* | Attributable Works Cancellation amount (£m)
| 2x 132kV bays (2000A) on switchboard extn | 5.5 | 457.25 | No | 0.17496 | 0.2 | 0.76982
| Spare |  |  | Yes | N/A |  | N/A
| Spare |  |  | Yes | N/A |  | N/A
| Spare |  |  | Yes | N/A |  | N/A
| Spare |  |  | Yes | N/A |  | N/A
| Spare |  |  | Yes | N/A |  | N/A
| Total | 5.5 |  |  |  |  | 0.76982
*See 'LARF examples' worksheet for example figures
Transmission reinforcement works - Stage 1
CMP417
| Work element | Cost (£m) | Capacity (MW) | Beyond nearest MITS node? (See explainer worksheet) | SIF | LARF* | Attributable Works Cancellation amount (£m)
| 132kV switchboard extn, inc bus-section | 7.5 | 457.25 | No | 0.17496 | 0.3 | 0.91853
| 1x new 240MVA SGT | 10 | 240 | No | 0.33333 | 0.2 | 2.6667
| 1x400kV SGT bay (4000A) | 5 | 2771.2 | No | 0.028868 | 0.3 | 0.10104
| Spare |  |  | Yes | N/A |  | N/A
| Spare |  |  | Yes | N/A |  | N/A
| Spare |  |  | Yes | N/A |  | N/A
| Spare |  |  | Yes | N/A |  | N/A
| Total | 22.5 |  |  |  |  | 3.6862
*See 'LARF examples' worksheet for example figures
Final sums
| Category | £m
| Total liability | 28
CMP417
| Category | £m
| Total Attributable liability | 4.4561
| Wider liability | 0.69302
| Total | 5.1491

## User input - Stage 2
|  | User input | Calculated
User connection details
| Total Demand Capacity (MW) | 150
| Additional Demand Capacity (MW) | 70 | Additional capacity added in this stage
| ETYS zone | A6
| ETYS zonal charge (£/MW) | 8662.75
Transmission connection asset works - Stage 2
CMP417
| Work element | Cost (£m) | Capacity (MW) | Beyond nearest MITS node? (See explainer worksheet) | SIF based on Total or Additional capacity? | SIF | LARF* | Attributable Works Cancellation amount (£m)
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Total | 0 | [5 empty] | 0
*See 'LARF examples' worksheet for example figures
Transmission reinforcement works - Stage 2
CMP417
| Work element | Cost (£m) | Capacity (MW) | Beyond nearest MITS node? (See explainer worksheet) | SIF based on Total or Additional capacity? | SIF | LARF* | Attributable Works Cancellation amount (£m)
| SGT 132kV tails upgrade to 240MVA | 1.5 | 240 | No | Total | 0.625 | 0.2 | 0.75
| 400kV OHL double circuit reconductoring | 48 | 2490 | Yes | Total | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Total | 49.5 | [5 empty] | 0.75
*See 'LARF examples' worksheet for example figures
Final sums
| Category | £m
| Total liability | 49.5
CMP417
| Category | £m
| Total Attributable liability | 0.75
| Wider liability | 0.60639
| Total | 1.3564

## User input - Stage 3
|  | User input | Calculated
User connection details
Total Demand Capacity (MW)
Additional Demand Capacity (MW)
| ETYS zone | A1
| ETYS zonal charge (£/MW) | 8662.75
Transmission connection asset works - Stage 2
CMP417
| Work element | Cost (£m) | Capacity (MW) | Beyond nearest MITS node? (See explainer worksheet) | SIF based on Total or Additional capacity? | SIF | LARF* | Attributable Works Cancellation amount (£m)
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Total | 0 | [5 empty] | 0
*See 'LARF examples' worksheet for example figures
Transmission reinforcement works - Stage 2
CMP417
| Work element | Cost (£m) | Capacity (MW) | Beyond nearest MITS node? (See explainer worksheet) | SIF based on Total or Additional capacity? | SIF | LARF* | Attributable Works Cancellation amount (£m)
| Spare |  |  | Yes | Total | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Spare |  |  | Yes |  | N/A |  | N/A
| Total | 0 | [5 empty] | 0
*See 'LARF examples' worksheet for example figures
Final sums
| Category | £m
| Total liability | 0
CMP417
| Category | £m
| Total Attributable liability | 0
| Wider liability | 0
| Total | 0

## Zonal charges
From the 2024/25 Wider Cancellation Charge Statement, effective from 1st April 2024 |  |  | https://www.neso.energy/document/301936/download
| Zone | Tariff (£/MW)
| A1 | 8662.75
| A2 | 0
| A3 | 8662.75
| A4 | 0
| A5 | 0
| A6 | 8662.75
| A7 | 8662.75
| A8 | 8662.75
| A9 | 8662.75
| B1 | 5704.42
| B2 | 838.62
| B3 | 838.62
| B4 | 788.1
| C1 | 4865.8
| C2 | 4865.8
| C3 | 2117.23
| C4 | 6983.03
| C5 | 4865.8
| C6 | 4865.8
| C7 | 6983.03
| C9 | 6983.03
| D4 | 778.1
| D5 | 778.1
| D6 | 778.1
| E1 | 2519.15
| E6 | 0
| E7 | 1680.53
| E8 | 2519.15
| F6 | 2519.15
| G1 | 778.1
| G5 | 778.1
| G6 | 778.1
| G7 | 778.1
| H1 | 0
| H2 | 778.1
| H6 | 778.1
| J1 | 778.1
| J2 | 2076.94
| J3 | 2076.94
| J4 | 778.1
| J5 | 2076.94
| J6 | 778.1
| J7 | 778.1
| J8 | 778.1
| K1 | 778.1
| K2 | 778.1
| K4 | 778.1
| K5 | 778.1
| K6 | 778.1
| L1 | 0
| L2 | 778.1
| L3 | 778.1
| L5 | 778.1
| L7 | 778.1
| L8 | 778.1
| M4 | 1361.62
| M5 | 1361.62
| M6 | 1361.62
| M7 | 1361.62
| M8 | 1361.62
| N1 | 1361.62
| N2 | 1361.62
| N3 | 1361.62
| N4 | 1361.62
| N5 | 1361.62
| N6 | 0
| N7 | 0
| N8 | 1361.62
| P1 | 1361.62
| P2 | 0
| P3 | 1361.62
| P4 | 1361.62
| P5 | 1361.62
| P6 | 1361.62
| P7 | 1361.62
| P8 | 1361.62
| Q2 | 5062.16
| Q4 | 5062.16
| Q5 | 0
| Q6 | 5062.16
| Q7 | 5062.16
| Q8 | 5062.16
| R4 | 3185.76
| R5 | 3185.76
| R6 | 3185.76
| S5 | 7134.88
| S6 | 6977.31
| T1 | 9899.85
| T2 | 8347.98
| T3 | 7502.3
| T4 | 7502.3
| T5 | 15677.41
| T6 | 9899.85

## LARF examples
Type of Asset/Reinforcement Scheme | Typical LARF | SIF
Cable circuit to site (sole use) | 10-35% | ~100% | Only applicable in Scotland
OHL circuit to site (sole use) | 20-35% | ~100% | Only applicable in Scotland
New Substation on site (sole use) | ~5-25%1 | ~100% | Only applicable in Scotland.
New substation - H1 (not sole use) | ~5-40%2 | Varies depending on substation type and works - would normally be based on either busbar capability OR transformer capability. See two rows below.
Bay Extension at existing substation | 20-40% | TEC (MW) / Busbar rating | 400kV or 275kV busbars would usually be rated to 4000A or 5000A
kA x kV x ³√
Transformer upgrade at existing substation | >20%2 | (TEC (MW))/(New Transformer capacity(MVA)) | SIF will usually be based on new N-1 transformer capacity (i.e. if replacing 2 x 240MVA SGTs with 2 x 380MVA firm capacity the SIF would be based on 380MVA)
Wider network upgrade - OHL Reconductoring | Scheme specific - depends on works required, hard to challenge. | (TEC (MW))/(New OHL Rating (MVA)) | If double circuit, SIF will usually be based on new N-1 capacity (i.e. capacity of a single circuit)
Wider network upgrade - new OHL circuit | >20% | (TEC (MW))/(New OHL Rating (MVA))
Notes:
Each TO is responsible for determining their own LARF and SIF values. LARF values are particularly opaque and differ significantly between TOs for similar types of Asset. The main differences are noted below:
1 SSEN typically have higher LARF values than SPT for this component.
2 NGET also typically have higher LARF values for new substation assets - could be up to 80% in the event of upgrades at exisitng substations.
Important: The LARF should be consistent for a specific reinforcement scheme for ALL customers who have that scheme in their attributable works.