#### OPERATING CODE NO.2

#### (OC2)

### OPERATIONAL PLANNING AND DATA PROVISION

### CONTENTS

(This contents page does not form part of the Grid Code)

OPERATIONAL PLANNING AND DATA PROVISION	1

CONTENTS	1

OC2.1 INTRODUCTION	2

OC2.2 SCOPE	3

OC2.3 PROCEDURE	3

OC2.3.1 Co-ordination of Outages	3

OC2.3.2 Data Requirements	17

OC2.3.3 Negative Reserve Active Power Margins	20

OC2.3.4 Frequency Sensitive Operation	22

OC2.4 SPACE WEATHER EVENTS ...……………………………………………………………………………26

OC2 APPENDIX 1– GENERATION PLANNING PARAMETERS	29

OC2 APPENDIX 2 – PLANNING MATRIX FOR GENERATING UNITS	30

OC2 APPENDIX 3 – POWER PARK MODULE PLANNING MATRIX	31

# OC2.1 INTRODUCTION

OC2.1.1	The objectives of OC2 are:

- To facilitate the co-ordination of Planned Outages of the NETS and Users’ Plant and Apparatus.

- To enable The Company to:

  - publish the NETS Surplus;

  - establish the level of System Negative Reserve Active Power Margin (NRAPM);

  - plan the deployment of Frequency Sensitive Mode;

  - establish Operating Margin parameters; and

  - agree for release of Existing Gas Cooled Reactor Plant for outages in certain circumstances.

- To enable the co-ordination of outages on Plant and Apparatus necessary for the operation of the System Restoration Plan.

OC2.1.2		Operational Planning considers matching generation output with forecast NETS Demand and Interconnector flows in order to maintain a reserve of generation output to provide margin, taking into account outages on the NETS together with outages of Users’ Plant and Apparatus over various timescales as described below, in addition to the ability to restore the Total System, in accordance with the requirements of the Electricity System Restoration Standard, following a Total Shutdown or Partial Shutdown.

OC2.1.3	Restoration Contractors should separately identify data which shall be provided in respect of Plant and Apparatus for which they have Restoration Contracts. Restoration Contractors with Embedded Plant and Apparatus need only provide data to the relevant Network Operator should they be required to do so by the Distribution Code, i.e., there is no need to provide identical data to The Company.

OC2.1.4		Generators and Interconnector Owners who have a CUSC Contract and who are also Restoration Contractors, need only submit the data once in respect of their Plant and Apparatus. Generators and Interconnector Owners who are Restoration Contractors are required to state for which Plant they have a Restoration Contract.

OC2.1.5		References in OC2 to a Generator's, Interconnector Owner’s and Restoration Contractor’s best estimate shall mean that Generator's, Interconnector Owner’s or Restoration Contractor’s best estimate acting as a reasonable and prudent Generator or Interconnector Owner.

OC2.1.6		In Scotland, it may be possible, with the agreement of The Company, to reduce the administrative burden for Users in producing planning information where either the active power output from a Power Station is small or the import of a demand User is small.

OC2.1.7		Where in OC2 there is a requirement to submit data or provide information on a particular day that falls on a non-Business Day, that data or information must be submitted by the next Business Day unless otherwise agreed in advance with The Company.

OC2.1.8		In OC2, for the purpose of Generator, Interconnector Owner and Restoration Contractor outage co-ordination, Year 0 means the current calendar year at any time, Year 1 means the next calendar year at any time, Year 2 means the calendar year after Year 1, etc. For the purpose of Transmission outage planning, Year 0 means the current Financial Year at any time, Year 1 means the next Financial Year at any time, Year 2 means the Financial Year after Year 1, etc. References to ‘weeks’ in OC2 are to calendar weeks as defined in ISO 8601.

OC2.1.

9		Network Operators who have a Distribution Restoration Zone Plan in place shall notify The Company whenever an outage of Restoration Contractor’s Plant or Apparatus which contributes to a Distribution Restoration Zone Plan is unavailable or a circuit forming part of that Distribution Restoration Zone Plan is unavailable, making the operation of that Distribution Restoration Zone Plan unviable.

# OC2.2	 SCOPE

OC2.2.1	OC2 applies to The Company and to the following Users:

  - Generators in respect of their generating Plant which is directly connected to the NETS and to any generating Plant in Embedded Large Power Stations;

#### Network Operators;

#### Non-Embedded Customers;

#### HVDC System Owners and DC Converter Station owners;

#### Interconnector Owners in respect of their External Interconnections; and

  - Restoration Contractors who are party to a Local Joint Restoration Zone Plan and who have a CUSC Contract where such data has not already been provided under their User role in OC2.2.1(a), (c), (d) or (e).

The Company may provide to the Relevant Transmission Licensees any data which has been submitted to The Company by any Users in respect of Relevant Units pursuant to the following paragraphs of OC2: OC2.3.1.2, OC2.3.1.3.2 (a), OC2.3.1.3.2 (b), OC2.3.1.3, OC2.3.2.1 (a).

OC2.

3

# PROCEDURE

OC2.3.1	 Co-ordination of Outages

OC2.3.1.1	OC2 makes provision for information exchange between the following parties:

| - Each Generator and each Interconnector Owner and The Company |  |  | In respect of outages of generating Plant, External Interconnection Circuits, and/or Apparatus directly connected to the NETS; |  |
| --- | --- | --- | --- | --- |
| - The Company and each Generator and each Interconnector Owner |  |  | In respect of NETS outages relevant to the Generator and/or Interconnector Owner; |  |
| - The Company and each Network Operator |  |  | In respect of outages of all Embedded Large Power Stations and related Plant and Apparatus; |  |
| - The Company and each Network Operator and each Non-Embedded Customer |  |  | In respect of NETS outages relevant to that Network Operator or Non-Embedded Customer; |  |
| Each Network Operator and each Non-Embedded Customer and The Company |  |  | In respect of outages on the User’s System relevant to The Company. For Network Operators only, outages of the Network Operator’s System that may have an impact on: - an Offshore Transmission System connected to that Network Operator’s System. - that Network Operator’s ability to operate a Local Joint Restoration Plan or - Distribution Restoration Zone Plan. |  |

OC2.3.1.2		Provision of Output Usable data of generating Plant and External Interconnection Circuits, and the publication of Surplus.

OC2.3.1.2.1

If a Generator, Interconnector Owner, or Restoration Contractor referred to in OC2.2.1 (f) where applicable:

- experiences any unplanned change to the availability of generating Plant, or an External Interconnection Circuit and which is expected to last one Settlement Period or longer and up to three years ahead, the Generator and/or Interconnector Owner shall provide The Company with the best estimate of the revised Output Usable;

- makes a plan which would affect the availability of generating Plant or an External Interconnection Circuit and which is expected to last one Settlement Period or longer and up to three years ahead, resulting in a change of level in the Output Usable of that generating Plant or External Interconnection Circuit to a level below or above its previously notified availability, the Generator and/or Interconnector Owner shall provide The Company with the best estimate of the revised Output Usable;

- experiences any unplanned change to the availability of generating Plant or External Interconnection Circuits or makes a future plan which would

- affect the availability of that generating Plant or External Interconnection Circuits, to contribute to a Local Joint Restoration Plan for which the Generator and/or Interconnector Owner is a Restoration Contractor, the Generator and/or Interconnector Owner shall provide The Company with the best estimate of the revised Output Usable.

OC2.3.1.2.2		Generators, Interconnector Owners and/or Restoration Contractors shall provide the revised

data within 24 hours of the unplanned unavailability occurring, or of the change in planned availability

. For

multi-shaft generating Plant the individual shaft availability must also be provided at the same time. For those Generators, Interconnector Owners and/or Restoration Contractors subject to Assimilated Law the revised data must be provided within 1 hour of planning the availability change.

OC2.3.1.2.3		In the case of an External Interconnection Circuit, the details of the individual pole-capacity levels that have been summed to produce the Output Usable should also be defined within 24 hours.

OC2.3.1.2.4		Restoration Contractors referred to in OC2.2.1 (f) which have Plant and Apparatus subject to either a planned or an unplanned change in availability, shall provide the data within 1 hour of planning the availability change, or of the unplanned change in availability.

OC2.3.1.2.5		The Company may, as appropriate, contact each Generator, each Interconnector Owner and each Restoration Contractor referred to in OC2.2.1 (f) who has supplied information to seek clarification on their Output Usable submissions.

OC2.3.1.2.	6     At a regular time interval, at least once per day (by 1600 hours) up to every hour

The Company will:

(a)	having taken into account the information notified to it by Generators,  Interconnector Owners and Restoration Contractors as provided for in OC2.2.1(f) via the process defined in OC2.3.1.2.1 and taking into account:

- Demand forecasts and details of proposed use of Demand Control received under OC1, and an Operational Planning Margin requirement set by The Company;

- NETS constraints and outages;

- Network Operator System constraints and outages, known to The Company and;

- the Output Usable required, in its view, to meet daily total MW requirements;

provide each Generator, each Interconnector Owner and each Restoration Contractor as provided for in OC2.2.1 (f) (where required by The Company) in writing with any suggested amendments to the provisional Output Usable supplied by the Generator,  Interconnector Owner and Restoration Contractor as provided for in OC2.2.1 (f) which The Company believes necessary, and shall advise Generators with Large Power Stations of the Surpluses for the National Electricity Transmission System and potential export limitations, which would occur without such amendments;

(b)	calculate and submit to BMRA:

- total generating Output Usable from Generating Units assumed to be available to the Total System (National Output Usable);

- generating Output Usable by fuel type from Generating Units assumed to be available to the Total System (Output Usable by fuel type);

- generating Output Usable by individual Generating Units assumed to be available to the Total System (Output Useable by Generating Unit);

- total Generating Plant Demand Margin assumed to be available to the Total System (This is sometimes referred to as the National Margin);

- total generating Surplus assumed to be available to the Total System (this is sometimes referred to as the National Surplus);

with daily resolution, for at least the peak Demand of each day for 2 day-ahead to 14 day-ahead time scope, and

with weekly resolution, for at least peak Demand of each week for 2 week-ahead up to 3 year-ahead time scope.

Information from the calculations referred to in OC2.3.1.2.6 (b) shall effectively define the envelope of opportunity for outages of Power Generating Modules (including DC Connected Power Park Modules), Synchronous Generating Units and Power Park Modules covering both Embedded and directly connected Large Power Stations.

The Company may, as appropriate, contact each Generator, each Interconnector Owner and Restoration Contractor (as provided for in OC2.2.1 (f)) who has supplied information to seek clarification on outages and suggest amendments.

(c)	Where a Generator, Interconnector Owner, Network Operator or Restoration Contractor (as provided for in OC2.2.1 (f)) has concerns with  the suggested amendments to its provisional outage programme (in the case of a Generator, Interconnector Owner or a Restoration Contractor  as provided for in OC2.2.1 (f)) or such potential outages (in the case of a Network Operator) it may contact The Company to explain its concerns and The Company and that Generator,  Interconnector Owner, Restoration Contractor (as provided for in OC2.2.1 (f)) or Network Operator shall then discuss the problem and seek to resolve it;

(d)	The possible resolution of the problem may require The Company or a User to contact other Generators, Interconnector Owners, Restoration Contractors (as provided for in OC2.2.1 (f)) or Network Operators, and joint meetings of all parties may, if any User feels it would be helpful, be convened by The Company.  The need for further discussions shall be determined at the time;

Each Generator shall provide The Company with updated Output Usable as per OC2.3.1 resulting from the above for Generating Unit, Power Generating Module, and Power Park Module outage programme covering both Embedded and non-Embedded Large Power Stations;

The Company shall then consider the updated Output Usable and take this into account in the next calculation and submission to BMRA.

OC2.3.1.2.	7   The Company retains the right to contact Generators with Large Power Stations, Interconnector Owners and Network Operators in reference to planned outages of their assets in timescales beyond the European Requirements (3 years) up to the 5 year ahead period to assist in the operational planning of NETS outages.

OC2.3.1.2.8	Where The Company has issued a Space Weather Prepare Notification or a Space Weather Imminent Notification, the Generator, Interconnector Owner, or Restoration Contractor shall follow OC2.4 Space Weather Events.

OC2.3.1.3 	Planning of NETS Outages

The outage planning process is undertaken annually for each of Years 0-5 with each iteration making the plan more certain. The Company shall take into account NETS outages required for maintenance, construction or refurbishment works.

OC2.3.1.3.1	Operational Planning Phase - Planning for Years 2 to 5 inclusive ahead

The Company shall take into account NETS outages required for construction or refurbishment works. Maintenance is taken into account in Years 0-1 outage planning.

The Company shall plan the NETS outage programme on the basis of the previous year's Final Generation Outage Programme. If a Generator's, Interconnector Owner’s or Network Operator's planned outages differ from those contained in the Final Generation Outage Programme, or in the case of Network Operators, they differ from those known to The Company, or in any way conflict with the NETS outage programme, The Company is not obliged to alter the NETS outage programme. Users should bear this in mind.

OC2.3.1.3.2	The timescales within which a User shall provide the required information to The Company is tabulated below. Users may identify their obligations in the relevant clauses using the tables in figures 1, 3, 7, 9, 13, and 15 below. These figures are intended for guidance and to assist Users to identify their requirements easily; however, the obligations as described in the text prevail.

|  | By the end of week |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Party | 8 | 13 |  | 28 | 30 | 34 |
| Generator and/or Interconnector Owner | Do nothing | Provides info | Receives info | Do nothing |  | Receives info |
| The Company | Receives info |  | Provides info |  |  |  |  |
| Non-Embedded Customer | Do nothing |  |  |  |  |  |  |
| Network Operator | Provides info | Receives info |  |  |  |  |  |
| Restoration Contractor as provided for in OC2.2.1(f) | Same as Generator and/or Interconnector Owner obligations |  |  |  |  |  |  |

Figure 1: Overview of Information Exchange by Party – NETS Outage Planning Process from Week 8 to Week 34.

Figure 2: OverviewIn each calendar year:

of the NETS Outage Planning Process from Week 8 to Week 34.

In each calendar year:

- By the end of week 8

Where the items i, ii and iii below may affect the performance of the Total System (which includes, but not limited to, outages of User System Apparatus at Grid Supply Points) each Network Operator shall provide to The Company:

  - all proposed outages in Years 2-5 in its User System which may affect the performance of the Total System (which includes but is not limited to outages of User System Apparatus at Grid Supply Points and outages which constrain the output of Power Generating Modules (including DC Connected Power Park Modules) and/or Synchronous Generating Units and/or Power Park Modules Embedded within that User System);

  - in relation to Offshore Transmission Systems all proposed outages in Years 2- 5 in its User System which may affect the declared values of Maximum Export Capacity and/or Maximum Import Capacity for each Interface Point together with the Network Operator’s revised best estimate of the Maximum Export Capacity and/or Maximum Import Capacity during such outages and any automatic and/or manual post fault actions that it intends to use or plans to use during such outages;

  - any outages of its Apparatus that may affect the ability to activate and/or operate a Distributed Restoration Zone Plan;

- By the end of week 13

- Each Generator shall inform The Company of proposed outages of Generator-owned Apparatus (e.g., substation Apparatus not generating Plant) in Years 2 -5, at each Grid Entry Point;

- The Company shall provide each Network Operator, Generator, and Interconnector Owner a copy of the information given to The Company under paragraph a) above (other than the information given by that Network Operator). In relation to a Network Operator, the data must only be used by that User in planning and operating that Network Operator’s User System and must not be used for any other purpose or passed on to, or used by, any other business of that User or to, or by, any person within any other such business or elsewhere;

- By the end of week 28

The Company shall provide each Network Operator with details of proposed outages in Years 2 - 5 which may affect the performance of that Network Operator’s User System;

- By the end of week 30

Where The Company or a Network Operator has concerns with the proposed outages notified to it under (a), (b) or (c) above, the affected party should discuss their concerns with the notifying party; in this event the provisions set out in OC2.3.1.2.6 (c) and (d) shall apply;

- By the end of week 34

The Company shall draw up a draft NETS outage plan for Years 2-5 and notify each User of those aspects of the plan which may affect that User. The Company shall also indicate where a need may exist to issue other relevant operational instructions or notifications (including but not limited to the requirement for the arming of an Operational Intertripping scheme) or Emergency Instructions to Users in accordance with BC2 to retain the necessary security of the NETS.

OC2.3.1.4	Operational Planning Phase - Planning for Year 1 Ahead

Each calendar year, The Company shall update the draft NETS outage plan prepared under OC2.3.1.3 taking into account outages required for maintenance work.

| By the end of Week |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Party | 13 | 28 | 32 |  | 34 | 36 |  | 49 |
| Generator and /or Interconnector Owner | Provides info | Do nothing |  |  | Receives info | Provides info | Do nothing | Receives info |
| The Company | Receives info | Provides info | Receives info | Provides info |  | Receives info | Provides info |  |
| Non-Embedded Customer | Provides info | Receives info | Do nothing |  |  |  |  | Receives info |
| Network Operator | Do nothing |  | Provides info | Do nothing | Receives info | Provides info | Do nothing |  |
| Restoration Contractor as provided for in OC2.2.1(f) | Same as Generator and/or Interconnector Owner obligations |  |  |  |  |  |  |  |

Figure 3:  Overview of Operational Planning Phase – Planning for Financial Year 1 Ahead.

Figure 4: Overview of the Operational Planning Phase from end of Week 13 to end of Week 34.

In each calendar year:

- By the end of week 13

Each Generator shall inform The Company of proposed outages for Year 1 of Generator-owned Apparatus (e.g., busbar selectors) at each Grid Entry Point. Each Non-Embedded Customer shall inform The Company of proposed outages for Year 1 of Non-Embedded Customer owned Apparatus, at each Grid Supply Point;

- By the end of week 28

The Company shall provide each Network Operator and each Non-Embedded Customer with details of proposed outages in Year 1 which might affect the performance of their User System at the Grid Supply Point;

- By the end of week 32

Each Network Operator shall notify The Company of:

  - proposed outages in Year 1 in its System which may affect the performance of the Total System (which includes but is not limited to outages of User System Apparatus at Grid Supply Points and outages which constrain the output of Power Generating Modules (including DC Connected Power Park Modules) and/or Synchronous Generating Units and/or Power Park Modules Embedded within that User System);

  - in relation to Offshore Transmission Systems, proposed outages in Year 1 in its System which may affect the declared values of Maximum Export Capacity and/or Maximum Import Capacity for each Interface Point within its System together with the Network Operator’s revised best estimate of the Maximum Export Capacity and/or Maximum Import Capacity during such outages and any automatic and/or manual post fault actions that it intends to use or plans to use during such outages;

  - any revisions to Interface Point Target Voltage/Power Factor data submitted pursuant to PC.A.2.5.4.2;

  - any outages of its Plant and Apparatus that may affect the ability to activate and/or operate a Distributed Restoration Zone Plan;

- Between the end of week 32 and the end of week 34

The Company shall draw up a revised NETS outage plan, which will include Transmission Apparatus at Connection Points;

- By the end of week 34

Figure 5: Overview of Obligations in Operational Planning Phase from end of Week 34 to end of Week 49.

The Company shall:

  - notify each Generator, Interconnector Owner, Restoration Contractor (as provided for in OC2.2.1(f) and Network Operator of those aspects of the NETS outage programme which may operationally affect them and in particular, proposed start dates and end dates of relevant NETS outages;

  - provide each User with a copy of the information given to The Company under paragraph (c) above (other than the information given by that Network Operator). In relation to a Network Operator, the data must only be used by that User in planning and operating that Network Operator’s User System and must not be used for any other purpose or passed on to, or used by, any other business of that User or to, or by, any person within any other such business or elsewhere;

- By the end of week 36

Where a User has concerns with the proposed aspects notified to it under (e) above, equivalent provisions to those set out in OC2.3.1.2.6 (c) and (d) shall apply;

- Between the end of week 34 and the end of week 49

The Company shall draw up a final NETS outage plan covering Year 1;

Figure 6:  Overview of Obligations in Operational Planning Phase by the end of Week 49.

- By the end of week 49

- The Company shall complete the final NETS outage plan for Year 1. The plan for Year 1 becomes the final plan for Year 0 when by the passage of time Year 1 becomes Year 0;

- The Company shall notify each User of those aspects of the plan:

  - which may operationally affect such Generator, Interconnector Owner, Restoration Contractor (as provided for in OC2.2.1(f)) and Network Operator including proposed start dates and end dates of relevant NETS outages;

  - where a need may exist to issue other operational instructions or notifications (including but not limited to the requirement for the arming of an Operational Intertripping scheme) or Emergency Instructions to Users in accordance with BC2 to retain the necessary security of the NETS;

- In addition, The Company shall provide to each Generator and each Interconnector Owner a copy of the final NETS outage plan for that year. OC2.3.2.1.5 contains provisions whereby updates of the final NETS outage plan are provided. Note that the final NETS outage plan for Year 1 and any updates will not give a complete understanding of how the NETS will operate in real time, as the NETS operation may be affected by other factors which may not be known at the time of the plan and the updates. Therefore, Users should be advised that unforeseen System conditions in real time may have an impact on the plan;

- Information Release or Exchange

This paragraph i) contains requirements on The Company, paragraph (z) being an alternative to a combination of paragraphs (x) and (y). Paragraph (z) shall only apply in relation to a particular User if The Company and that User agree that paragraph (z) rather that paragraphs (x) and (y) apply. Without any such agreement The Company shall only be required to comply with paragraphs (x) and (y) in the section below.

Information Provision to Each Network Operator and Non-Embedded Customer

Between the end of week 34 and the end of week 49 The Company shall upon written request:

- for radial Systems, provide each Network Operator and Non-Embedded Customer with data to allow the calculation by the Network Operator, and each Non-Embedded Customer, of symmetrical and asymmetrical fault levels; and

- for interconnected Systems, provide to each Network Operator an equivalent network, sufficient to allow the identification of symmetrical and asymmetrical fault levels, and power flows across interconnecting User Systems directly connected to the NETS; or

- as part of a process to facilitate understanding of the operation of the Total System:

    - The Company shall make available to each Network Operator, the NETS Study Network Data Files covering Year 1 which are of relevance to that User's System;

    - where The Company and a User have agreed to the use of data links between them, the User may take a copy of the NETS Study Network Data Files once during that period. The access shall be in a manner agreed by The Company and may be subject to separate agreement. In the absence of agreement, the copy of the NETS Study Network Data Files shall be given to the User in hard copy or by other appropriate means;

the data contained in the NETS Study Network Data Files represents The Company's view of operating conditions although the actual conditions may be different

    - . Data Files received by each Network Operator must only be used by that User in planning and operating that Network Operator’s User System and must not be used for any other purpose or passed on to, or used by, any other business of that User or to, or by, any person within any other such business or elsewhere.

    - The Company shall notify each Network Operator, as soon as reasonably practicable after it has updated the NETS Study Network Data Files covering Year 1 that it has done so, when this update falls before the next annual update under this OC2.3.	1.4 (i). The Company shall then make available to each Network Operator who has received an earlier version, the updated NETS Study Network Files covering the balance of Years 1 and 2 which remain given the passage of time, and which are of relevance to that User's System. The provisions of paragraphs 2. and 3. above shall apply to the making available of these updates.

OC2.3.1.5 Operational Planning Phase - Planning in Year 0 down to the Programming Phase (and in the Case of Load Transfer Capability, also during the Programming Phase)

|  | Year 0 |  |  |
| --- | --- | --- | --- |
| Party | Anytime but not less than 8 weeks from requested change | 14 days from date of request | Where necessary 8-52 weeks ahead |
| Generator and/or Interconnector Owner | Provides info | Receives info |  |
| The Company | Receives info |  | Provides info |
| Non-Embedded Customer | Provides info | Receives info |  |
| Network Operator |  | Do nothing | Receives info |
| Restoration Contractor as provided for in OC2.2.1(f) | Same as Generator and/or Interconnector Owner obligations |  |  |

Figure 7: Overview of Operational Planning Phase - Planning in Year 0 down to the NETS Programming Phase.

Figure 8: Overview of Obligations in Operational Planning Phase Year 0.

- The NETS outage plan for Year 1 issued under OC2 3.1.4 shall become the plan for Year 0 when by the passage of time Year 1 becomes Year 0;

- Each User may, at any time during Year 0, request The Company for changes to the outages requested by them under OC2.3.1.4 In relation to that part of Year 0, excluding the period 1-7 weeks from the date of request, The Company shall determine whether the changes are possible and shall notify the User in question whether this is the case as soon as possible, and in any event within 14 days of the date of receipt by The Company of the request.

Where The Company determines that the requested change is possible and notifies the relevant User accordingly, The Company shall provide to each User a copy of the request to which The Company has agreed which relates to outages on Network Operator’s User System;

- During Year 0 (including the Programming Phase) each Network Operator shall at The Company's request make available to The Company, such details of automatic and manual load transfer capability of:

  - 12MW or more (averaged over any half hour) for England and Wales;

  - 10MW or more (averaged over any half hour) for Scotland;

between Grid Supply Points.

During Year 0 (including the Programming Phase) each Network Operator shall notify The Company of any revisions to the information provided pursuant to OC2.3.1.4 (c) for Grid Supply Points  as soon as reasonably practicable after the Network Operator becomes aware of the need to make such revisions;

- When necessary, during Year 0, The Company shall notify each User, in writing of those aspects of the NETS outage programme in the period from the 8th week ahead to the 52nd week ahead, which may, in The Company’s reasonable opinion, operationally affect that User including the proposed start dates and end dates of relevant NETS outages.

The Company shall also notify changes to information supplied by The Company pursuant to OC2.3.2.1.4 (i) (x) and (y) except where in relation to a User information was supplied pursuant to OC2.3.1.4. (i). (z). In this latter case: -

- The Company shall, by way of update of the information supplied by it pursuant to OC2.3.1.4 (i). (z), make available at the first time in Year 0 that it updates the NETS Study Network Data Files in respect of Year 0 to each Network Operator who has received an earlier version of the of the NETS Study Network Data Files covering Year 0 which are of relevance to that Network Operator’s System;

- The Company shall notify each relevant Network Operator, as soon as reasonably practicable after it has updated the NETS Study Network Data Files covering Year 0, that it has done so. The Company shall then make available the updated NETS Study Network Data Files covering the remaining balance of Year 0;

- the provisions of OC2.3.1.4. (i) (z) 2., 3. and 4., shall also apply to the provision of data under this part of OC2.3.1.5 (d).

The Company shall also indicate where a need may exist to issue other operational instructions or notifications (for example the requirement for the arming of an Operational Intertripping scheme) or Emergency Instructions to Users in accordance with BC2 to allow the necessary security of the NETS to be maintained except in the case of a Total Shutdown or Partial Shutdown as provided for in OC9 4.3;

- In addition, by the end of each month during Year 0, The Company shall provide to each Generator, Interconnector Owner and each Restoration Contractor (as provided for in OC2.2.1 (f)) a notice containing any revisions to the final NETS outage plan for Year 1;

OC2.3.1.6	Programming Phase

|  | Programming Phase |
| --- | --- |
| Party | By 1600 hours each Thursday |
| Generator and/ or Interconnector Owner | Receives info |
| The Company | Provides info |
| Non-embedded Customer | Receives info |
| Network Operator | Receives info |
| Restoration Contractor | Do nothing |

Figure 10: Overview of obligations in the Programming Phase by 1600 hours each Thursday

Figure 9: Overview of Programming Phase

- 1600 hours each Monday, Tuesday, Wednesday and Thursday

- By 1600 hours each Thursday

  - The Company shall prepare a final NETS outage programme for the following day;

  - The Company shall notify each User of the factors set out in (b) ii. Below;

- By 1600 hours each Thursday

- The Company shall continue to update a preliminary NETS outage programme for the eighth week ahead, a provisional NETS outage programme for the next week ahead;

- The Company shall notify each User, in writing of those aspects of the preliminary NETS outage programme which may operationally affect each User including the proposed start dates and end dates of relevant NETS outages;

The Company shall also notify changes to information supplied by The Company pursuant to OC2.3.1.4 (i) (x) and (y) except where in relation to a User information was supplied pursuant to OC2.3.1.4 (i) (z). In that latter case:

  - The Company shall, by way of update of the information supplied by it pursuant to OC2.3.1.4 (i) (z), make available the NETS Study Network Data Files for the next week ahead;

  - The Company shall notify each relevant Network Operator, as soon as reasonably practicable after it has updated the NETS Study Network Data Files covering the next week ahead that it has done so, and;

  - the provisions of OC2.3.1.4 (c) i., ii. and iv. shall apply to the provision of data under this part of OC2.3.1.6. (a) ii. as if set out in full.

The Company may make available, the NETS Study Network Data Files for the next week ahead where The Company and a particular User agree.

The Company shall also indicate where a need may exist an Operational Intertripping scheme, emergency switching, emergency Demand management or other measures including the issuing of other operational instructions or notifications (for example the requirement for the arming of an Operational Intertripping scheme) or Emergency Instructions to Users in accordance with BC2 to allow the necessary security of the NETS to be maintained.

- By 1000 hours each Friday

Users shall discuss with The Company and confirm to The Company acceptance or otherwise of the requirements detailed under OC2.3.1.6

Network Operators shall confirm for the following week:

- the details of any outages of its User System that will restrict the Maximum Export Capacity and/or Maximum Import Capacity at any Interface Points within its System for the following week; and

- any changes to the previously declared values of the Interface Point Target Voltage/Power Factor;

- By 1600 hours each Friday

- The Company shall finalise the preliminary NETS outage programme up to the seventh week ahead. The Company shall give as much notice as possible to a Generator with nuclear Large Power Stations which may be operationally affected by an outage which is to be included in such programme;

- The Company shall finalise the provisional NETS outage programme for the next week ahead;

- The Company shall finalise the NETS outage programme for the weekend through to the next normal working day;

- In each case, The Company shall indicate the factors set out in (b) ii. above to the relevant Users;

- Where a Generator with nuclear Large Power Stations which may be operationally affected by the preliminary NETS outage programme referred to in i. above is concerned on safety grounds about the effect which an outage within such outage programme might have on one or more of its nuclear Large Power Stations, it may contact The Company to explain its concerns and discuss whether there is an alternative way of taking that outage. If there is such an alternative way, but The Company refuses to adopt that alternative way in taking that outage, that Generator may involve the Disputes Resolution Procedure to decide on the way the outage should be taken. If there is no such alternative way, then The Company may take the outage despite that Generator's concerns.

## OC2.3.2 Data Requirements

OC2.3.2.1	When a Statement of Readiness under the Bilateral Agreement and/or Construction Agreement is submitted, and thereafter in calendar week 24 in each calendar year:

each Generator shall (subject to OC2.3.2.1 (j)) in respect of each of its

Gensets

- submit to The Company in writing the Generation Planning Parameters and the Generator Performance Charts as required;

- the Generation Planning Parameters and the Generator Performance Chart(s) shall reasonably reflect the true operating characteristics of the Genset and shall demonstrate that the Generating Unit meets the Reactive Power Plant performance requirements of CC.6.3.2 or ECC.6.3.2 (as applicable);

- the Generation Planning Parameters and the Generator Performance Chart(s) shall be applied (unless revised under this OC2 or (in the case of the Generator Performance Chart only) BC1 in relation to Other Relevant Data) from the Completion Date, in the case of the ones submitted with the Statement of Readiness, and in the case of the ones submitted in calendar week 24, from the beginning of week 25 onwards;

- Generator Performance Chart(s) shall be in the format indicated in the Planning Code Appendix G and the Generation Planning Parameters shall be as set out in Appendix G of the Planning Code;

- any changes to the Generator Performance Chart or Generation Planning Parameters should be notified to The Company as soon as the Generator becomes aware of the issue and are able to notify The Company through the necessary communication channels;

- Generators should note that amendments to the composition of the Power Generating Module, CCGT Module or Power Park Module at Large Power Stations may only be made in accordance with the principles set out in PC.A.3.2.3 or PC.A.3.2.4 as applicable. If in accordance with PC.A.3.2.3 or PC.A.3.2.4 an amendment is made, any consequential changes to the Generation Planning Parameters should be notified to The Company promptly;

- The Generator Performance Chart must be as described below and demonstrate the limitation on reactive capability of the System voltage at 3% above nominal. It must also include any limitations on output due to the prime mover (both maximum and minimum), Generating Unit step up transformer or User System;

  - for a Synchronous Generating Unit on a Generating Unit specific basis at the Generating Unit stator terminals. It must include details of the Generating Unit transformer parameters;

  - for a Non-Synchronous Generating Unit (excluding a Power Park Unit) on a Generating Unit specific basis at the Grid Entry Point (or User System Entry Point if Embedded);

  - for a Power Park Module, on a Power Park Module specific basis at the Grid Entry Point (or User System Entry Point if Embedded;

  - for a DC Converter on a DC Converter specific basis at the Grid Entry Point (or User System Entry Point if Embedded);

  - for a Synchronous Generating Unit within a Synchronous Power Generating Module, both the Power-Generating Module Performance Chart and Synchronous Generating Unit Performance Chart should be provided;

- For each Generating Unit whose performance varies significantly with ambient temperature, the Generator Performance Chart (including the Synchronous Generating Unit Performance Chart in the case of Synchronous Power Generating Modules) shall show curves for at least two values of ambient temperature so that The Company can assess the variation in performance over all likely ambient temperatures by a process of linear interpolation or extrapolation. One of these curves shall be for the ambient temperature at which the Generating Unit's output, or CCGT Module or Power-Generating Module at a Large Power Station output or Power Park Module’s output, as appropriate, equals its Registered Capacity;

- The Generation Planning Parameters supplied under OC2.3.2.1 shall be used by The Company for operational planning purposes only and not in connection with the operation of the Balancing Mechanism (subject as otherwise permitted in the BC);

Figure 11: Types of Planning Matrices to be Submitted by each Generator to The Company

Each Generator

Submit in writing

CCGT Module Planning Matrix

And

/or

Synchronous Power Generating Module Planning

Matrix

- Each Generator shall in respect of each of its Synchronous Power Generating Modules or CCGT Modules at Large Power Stations submit to The Company in writing a Synchronous Power-Generating Module Planning Matrix and/or a CCGT Module Planning Matrix. It shall be prepared on a best estimate basis relating to how it is anticipated the Power-Generating Module or CCGT Module will be running and shall reasonably reflect the true operating characteristics of the Power-Generating Module or CCGT Module. It shall be applied (unless revised under this OC2) from the Completion Date, in the case of the one submitted with the Statement of Readiness, and in the case of the one submitted in calendar week 24, from the beginning of week 31 onwards. It must show the combination of CCGT Units or Synchronous Power Generating Units which would be running in relation to any given MW output in the format indicated in Appendix G of the Planning Code;

The CCGT Module Planning Matrix or Synchronous Power-Generating Module Planning Matrix

shall be used by The Company for operational planning purposes only and not in connection with the operation of the Balancing Mechanism;

- Each Generator shall in respect of each of its Cascade Hydro Schemes also submit the Generation Planning Parameters detailed at OC2.A.2.6 to OC2.A.2.10 for each Cascade Hydro Scheme. Such parameters need not also be submitted for the individual Gensets within such Cascade Hydro Scheme;

Each Generator

Submit in writing to The Company

Power Park Module Planning

Matrix for each Power Park Module

A graph showing variation in MW output within Intermittent Power Source for that Power Park Module

(In case an amendment is made in accordance with PCA.3.2.4) an updated Power Park Module Planning

Matrix

Each Generator shall in respect of each of its Power Park Modules at Large Power Stations submit to The Company in writing a Power Park Module Planning Matrix.

Figure 12: Types of Planning Matrices and Graph to be Submitted by each Generator to The Company.

Each Generator submission shall;

  - be prepared on a best estimate basis relating to how it is anticipated the Power Park Module will be running and which shall reasonably reflect the operating characteristics of the Power Park Module and the Balancing Mechanism Unit of which it forms part;

  - be applied (unless revised under this OC2) from the Completion Date, in the case of the one submitted with the Statement of Readiness, and in the case of the one submitted in calendar week 24, from the beginning of week 31 onwards;

  - show the number of each type of Power Park Unit in the Power Park Module typically expected to be available to generate and the BM Unit of which it forms part, in the format indicated in Appendix 3 of OC2. The Power Park Module Planning Matrix shall be accompanied by a graph showing the variation in MW output with Intermittent Power Source (e.g. MW vs wind speed) for the Power Park Module. The graph shall indicate the typical value of the Intermittent Power Source for the Power Park Module;

  - be prompt (in case of any changes) and should note that amendments to the composition of the Power Park Module at Large Power Stations may only be made in accordance with the principles set out in PC.A.3.2.4;

  - be used by The Company for operational planning purposes only and not in connection with the operation of the Balancing Mechanism;

- For each Synchronous Generating Unit where the Generator intends to adjust the Generating Unit terminal voltage in response to a MVAr output instruction or a target voltage level instruction in accordance with BC2.A.2.6 the Generator Performance Chart including the Synchronous Generating Unit Performance Chart shall show curves corresponding to the Generating Unit terminal voltage being controlled to its rated value and to its maximum value;

In the case of Restoration Contractors (as provided for in OC2.2.1(f)) who are Generators, it would be expected that the above data to be submitted in accordance with OC2.3.2.1 (a) – (m) would apply.

OC2.3.2.2	Each Network Operator shall by 1000 hours on the day falling seven days before each Operational Day inform The Company in writing of any changes to the circuit details called for in PC.A.2.2.1 which it is anticipated will apply on that Operational Day (under BC1 revisions can be made to this data). This requirement shall also apply to circuits associated with a Distributed Restoration Zone Plan.

OC2.3.2.3	Under Assimilated  Law, Users are required to submit certain data to the Data Publisher for publication. The Company is required to facilitate the collection, verification and processing of data from Users for onward transmission to the Data Publisher.

Each Generator and Restoration Contractor (as provided for in OC2.2.1 (f)) and each Non-Embedded Customer connected to or using the NETS shall provide The Company with such information as required by and set out in DRC Schedule 6 (Users’ outage data EU Transparency Availability Data) in the timescales detailed therein.

## OC2.3	.3 Negative Reserve Active Power Margins

OC2.3.3.1	At a regular time interval, at least once each day (by 1600 hours) and no more frequently than every hour The Company shall, taking into account the Generation Outage Programme and forecast of Output Useable supplied by each Generator a defined in OC2.3.1.2.1 and forecast Demand for the minimum Demand period, calculate and publish:

- the level of the System NRAPM each day within the period 2 to 14 days ahead (inclusive) and for each week the level of risk of System NRAPM within the 2-52 week ahead period; and

- the level of the Localised NRAPM (currently for the main constraint between England and Scotland only) for each day within the period 2 to 14 days ahead (inclusive) having taken into account the appropriate limit on transfers to and from the System Constraint Group and for each week the level of risk of Localised NRAPM within the 2-52 week ahead period.

OC2.3.3.2   Outages Adjustments

- Where necessary The Company shall contact Generators and Interconnector Owners to discuss outages as set out in the following paragraphs of this OC2.3.3.2;

- The Company shall contact all Generators and Interconnector Owners in the case of low System NRAPM or low Localised NRAPM. The Company shall raise with each Generator and Interconnector Owner the problems it is anticipating due to the low System NRAPM or Localised NRAPM and shall discuss;

  - whether any change is possible to the estimate of generating Plant inflexibility; and

  - whether generating Plant or External Interconnection outages can be taken to coincide with the periods of low System NRAPM or Localised NRAPM.

In relation to Generators with nuclear Large Power Stations the discussions on outages can include the issue of whether outages can be taken for re-fuelling purposes to coincide with the relevant low System NRAPM and/or Localised NRAPM periods.

- If agreement is reached with a Generator or an Interconnector Owner, then the Generator or Interconnector Owner may take such outage, as agreed with The Company, and the Generator or Interconnector Owner shall update its Output Useable via the data provision process defined in OC2.3.1.2.1. The Company shall process the updated data which will then be included in the next published update of the System NRAPM and/or Localised NRAPM;

- If on the day prior to an Operational Day, it is apparent from the BM Unit Data submitted by Users under BC1 that System NRAPM and/or Localised NRAPM, is too low, then in accordance with the procedures and requirements set out in BC1.5.5 The Company may contact Users to discuss whether changes to Physical Notifications are possible, and if they are, shall reflect those in the operational plans for the next following Operational Day or shall, in accordance with BC2.9.4 instruct Generators to De-Synchronise specific generating Plant for such period. In determining which generating Plant to instruct, BC2 provides that The Company shall not other than as provided for below instruct to De- Synchronise any generating Plant within an Existing Gas Cooled Reactor Plant;

BC2 further provides that: -

- The Company is permitted to instruct to De-Synchronise any generating Plant within an Existing AGR Plant if that generating Plant within an Existing AGR Plant has failed to offer to be flexible for the relevant instance at the request of The Company provided the request is within the Existing AGR Plant Flexibility Limit;

- The Company shall only instruct any generating Plant within an Existing Magnox Reactor Plant or within an Existing AGR Plant (other than under i. above) to De-Synchronise if the level of System NRAPM (taken together with System constraints) and/or Localised NRAPM is such that it is not possible to avoid De-Synchronising such generating Plant, and provided the power flow across each External Interconnection is either at zero or results in an export of power from the Total System. This provision applies in all cases in the case of System NRAPM, only when the power flow would have a relevant effect.

## OC2.3.4	 Frequency Sensitive Operation

| Party | By 1600 hours each Wednesday |
| --- | --- |
| Generator | Receives info |
| The Company | Provides info |
| Non-Embedded Customer | Do nothing |
| Network Operator | Do nothing |

Figure 13: Overview of Obligations during Frequency Sensitive Operation

Figure 14: Overview of Obligations during Frequency Sensitive Operation by 1600 hours each Wednesday

By 1600 hours each Wednesday

OC2.3.4.1	Using such information as The Company shall consider relevant including forecast Demand, any estimates provided by Generators of generating Plant inflexibility and anticipated plant mix relating to operation in Frequency Sensitive Mode, The Company shall determine for the period 2 to 7 weeks ahead (inclusive) whether it is possible that there will be insufficient generating Plant to operate in Frequency Sensitive Mode (other than that generating Plant within Existing Gas Cooled Reactor Plant which is permitted to operate in Limited Frequency Sensitive Mode at all times under BC3.5.3) to operate in Frequency Sensitive Mode for all or any part of that period.

OC2.3.4.2	BC3.5.3 explains that The Company permits Existing Gas Cooled Reactor Plant other than Frequency Sensitive AGR Units to operate in a Limited Frequency Sensitive Mode at all times.

OC2.3.4.3	If The Company foresees that there will be an insufficiency in generating Plant operating in a Frequency Sensitive Mode, it shall contact Generators in order to seek to agree (as soon as reasonably practicable) that all or some of the generating Plant (the MW amount being determined by The Company but the specific generating Plant involved being determined by the Generator) shall take outages to coincide with such period as The Company shall specify to enable replacement by other generating Plant which can operate in a Frequency Sensitive Mode. If agreement is reached (which unlike the remainder of OC2 will constitute a binding agreement) then the Generator shall take such outage as agreed with The Company. If agreement is not reached, then the provisions of BC2.9.5 May apply.

OC2.3.5 	Operating Margin Data Requirements

| Party | By 1600 hours each Wednesday | Between 1600 hours each Wednesday and 1200 hours each Friday |  | By 1500hours each Friday |  |
| --- | --- | --- | --- | --- | --- |
| Generator | Do nothing | Receives info | Provides info | Receives info | Provides info |
| Interconnector Owner | Do nothing |  |  |  |  |
| The Company | Provides info |  | Receives info | Provides info | Receives info |
| Non-Embedded Customer | Do nothing |  |  |  |  |
| Network Operator |  |  |  |  |  |
| Restoration Contractor |  |  |  |  |  |

Figure 15: Overview of obligations under Operating Margin Data Requirements

Figure 16: Overview of obligations under Operating Margin Data Requirements

OC2.3.5.1	    Modifications to Low Frequency Relay settings for Fast Start from standby

‘Relay settings’ in this OC2.3.5.1 refers to the settings of Low Frequency Relays in respect of generating Plant that is available for start from standby by Low Frequency Relay initiation with Fast Start Capability agreed in the relevant Bilateral Agreement.

By 1600 hours each Wednesday

A change in relay settings shall be sent by The Company no later than 1600 hours on a Wednesday to apply from 1000 hours on the Monday following. The settings allocated to particular Large Power Stations may be interchanged between 49.70Hz and 49.60Hz (or such other System Frequencies as The Company may have specified) provided the overall capacity at each setting and System requirements can, in The Company’s view, be met.

Between 1600 hours each Wednesday and 1200 hours each Friday

If a Generator wishes to discuss or interchange settings it should contact The Company by 1200 hours on the Friday prior to the Monday on which it would like to institute the changes to seek The Company’s agreement. If The Company agrees, The Company shall then send confirmation of the agreed new settings.

By 1500 hours each Friday

If any alterations to relay settings have been agreed, then the updated version of the current relay settings shall be sent to affected Users by 1500 hours on the Friday prior to the Monday on which the changes shall take effect. Once accepted, each Generator (if that Large Power Station is not subject to forced outage or Planned Outage) shall abide by the terms of its latest relay settings.

In addition, The Company shall take account of any Large Power Station unavailability (as notified under OC2.4.1.2 submissions) in its total Operating Reserve policy.

The Company may from time to time, for confirmation purposes only, issue the latest version of the current relay settings to each affected Generator.

OC2.3.5.2	   Operational Planning Margin Requirements

At a regular time interval, at least once each day (by 1600 hours) and no more frequently than every hour

The Company shall provide its best estimate of the level of Operating Reserve to be utilised by The Company in connection with the operation of the Balancing Mechanism covering a 2-14 day ahead period (with a daily peak demand resolution) and the 2–52-week resolution (with a weekly resolution focusing on the peak demand of the week). This level shall be purely indicative.

This Operational Planning Margin requirements indication shall also note the possible level of High Frequency Response to be utilised by The Company in connection with the operation of the Balancing Mechanism in the week beginning with the Operational Day commencing during the subsequent Monday, which level shall be purely indicative.

OC2.	3.6            In the event that:

- a Non-Embedded Customer experiences the planned unavailability of its Apparatus resulting in the reduction of Demand of 100MW or more, or a change to the planned unavailability of its Apparatus resulting in a change in Demand of 100MW or more, for one Settlement Period or longer; or

- a Non-Embedded Customer experiences a change in the actual availability of its Apparatus resulting in a change in Demand of 100MW or greater; or

- a Generator experiences a planned unavailability of a Generating Unit resulting in a change of 100MW or more in the Output Useable of the associated Power-Generating Module below its previously notified availability, which is expected to last one Settlement Period or longer and up to three years ahead; or

- a Generator experiences a change of 100MW or more in the Maximum Export Limit of any generating Plant which is expected to last one Settlement Period or longer; or

- a Generator experiences a planned unavailability resulting in a change of 100MW or more in its aggregated Output Useable below its previously notified availability for a Power Station with a Registered Capacity of 200MW or more and which is expected to last one Settlement Period or longer and up to three years ahead, save where data has been provided pursuant to OC.2.3.6 (c) above; or

- a Generator experiences a change of 100MW or more in the aggregated Maximum Export Limit of a Power Station with a Registered Capacity of 200MW or more, which is expected to last one Settlement Period or longer, save where data has been provided pursuant to OC.2.3.6 (d) above

such Non-Embedded Customer or Generator shall provide The Company with the EU Transparency Availability Data in accordance with DRC Schedule 6 (Users’ Outage Data) using either MODIS or with prior agreement with The Company directly into the Elexon Portal and, with reference to Assimilated Law Chapter III, Article 8(1) of retained REMIT Implementing Regulation 1348/2014.

OC2.3.7		The Company shall for each day publish the actual largest secured loss of generation (ie, the loss of generation against which, as a requirement of the Licence Standards, the NETS must be secured) or loss of import from External Interconnections for each settlement period on The Company’s website.

# OC2.4	Space Weather Events

OC2.4.1

Figure 17: Overview of Space Weather Event timeline for Prepare Notification

In addition to the requirements of OC2.3, where The Company issues a Space Weather Prepare Notification in accordance with OC7.4.9, Generators, Interconnector Owners and Restoration Contractors shall;

- within 3 hours of The Company issuing a Space Weather Prepare Notification submit a Space Weather Output Usable Declaration to The Company (for the avoidance of doubt where no Space Weather Output Usable Declaration is submitted, The Company shall assume there to have been a declaration stating no impact to availability due to space weather). In the case of Interconnector Owners, they may take such steps that they consider appropriate to inform any relevant parties (such as, but not limited to, any other TSO (as defined in Assimilated Law) and market participants) as they consider to be appropriate. For the avoidance of doubt, The Company shall be able to inform any relevant parties of any space weather related notifications it has issued in accordance with the Grid Code; and

- where a Space Weather Imminent Notification is issued by The Company in accordance with OC7.4.9, comply with their submitted Space Weather Output Usable Declaration, unless an Event prevents them from doing so.

OC2.4.2

Figure 18: Overview of Space Weather Event timeline for Imminent Notification

Where The Company issues a Space Weather Imminent Notification without first issuing a Space Weather Prepare Notification, Generators, Interconnector Owners and Restoration Contractors shall;

- as soon as practicable submit a Space Weather Output Usable Declaration to The Company; and

- as soon as practicable comply with their Space Weather Output Usable Declaration as submitted in accordance with OC2.4.2(a), unless an Event prevents them from doing so.

OC2.4.3 	Where a Space Weather Experienced Notification is issued by The Company then the User where relevant shall submit a Space Weather Outcome Statement as soon as reasonably practicable.

OC2.4.4	Where a Space Weather Outcome Statement has been submitted to The Company, this may be shared by The Company with the Met Office, the Authority and the Secretary of State (or such other person or team nominated by them to act on their behalf with respect to receiving Space Weather Outcome Statements).  Where any other User(s) has neighbouring Plant and Apparatus (being in close electrical proximity to the asset(s) to which the Space Weather Outcome Statement relates) which might also be affected, The Company will seek the agreement of the User to share that information with the neighbouring User(s). Such agreement shall not be unreasonably withheld.

OC2.4.5	Where The Company issues a Space Weather Cessation Notification in accordance with OC7.4.9 following the issuing of a Space Weather Imminent Notification or a Space Weather Experienced Notification this will revert to a Space Weather Prepare Notification level. Generators, Interconnector Owners and Restoration Contractors shall, within 3 hours of the issuing of a Space Weather Cessation Notification, submit any revision to their Space Weather Output Usable Declaration to The Company (for the avoidance of doubt where such notification is not provided to The Company, then the Space Weather Output Usable Declaration as submitted under OC2.4.1(a) or OC2.4.2(a) will prevail).

OC2.4.6	Where The Company issues a Space Weather Cancellation Notification in accordance with OC7.4.9 following the issuing of a Space Weather Prepare Notification, Space Weather Imminent Notification or a Space Weather Experienced Notification, then the Space Weather Output Usable Declarations as submitted under OC2.4.1 or OC2.4.2 shall cease to have effect and User’s Plant and Apparatus availability shall return to normal service in the timescales set out in the Space Weather Output Usable Declaration previously submitted.

OC2 APPENDIX 1 -

GENERATION PLANNING PARAMETERS

# OC2.A.2	Generation Planning Parameters

The following parameters are required in respect of each Genset.

OC2.A.2.1	Regime Unavailability

Where applicable the following information must be recorded for each Genset.

Earliest synchronising time:

- Monday

Tuesday to Friday

Saturday to Sunday

Latest de-synchronising time:

- Monday to Thursday

Friday

Saturday to Sunday

OC2. A.2.2	Synchronising Intervals

  - The synchronising interval between Generating Units in a Synchronising Group

assuming all Generating Units have been Shutdown for 48 hours;

  - The Synchronising Group within the Power Station to which each Generating Units should be allocated.

OC2.A.2.3	De-Synchronising Interval

A fixed value De-Synchronising interval between Gensets within a Synchronising Group.

OC2.A.2.4	Synchronising Generation

The amount of MW produced at the moment of Synchronising assuming the Generating Unit has been Shutdown for 48 hours.

OC2.A.2.5	Minimum Non-zero time (MNZT)

The minimum period on-load between Synchronising and De-Synchronising assuming the Generating Unit has been Shutdown for 48 hours.

OC2.A.2.6	Run-Up rates

A run-up characteristic consisting of up to three stages from Synchronising Generation to Output Useable with up to two intervening break points assuming the Generating Unit has been Shutdown for 48 hours.

OC2.A.2.7	  Run-down rates

A run-down characteristic consisting of up to three stages from Output Useable to De- Synchronising with breakpoints at up to two intermediate load levels.

OC2.A.2.8	  Notice to Deviate from Zero (NDZ)

The period of time normally required to Synchronise a Generating Unit following instruction from The Company assuming the Generating Unit has been Shutdown for 48 hours.

OC2.A.2.9	  Minimum Zero time (MZT)

The minimum interval between De-Synchronising and Synchronising a Generating Unit.

OC2.A.2.10

Gas Turbine Units loading parameters

- Loading rate for fast starting

- Loading rate for slow starting

# OC2 APPENDIX 2 – PLANNING MATRIX FOR CCGT MODULES and SYNCHRONOUS GENERATING UNITS

Planning Matrix Example Form

| Power Generating MODULE OUTPUT |  | GENERATING UNITS AVAILABLE |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1st GT | 2nd GT | 3rd GT | 4th GT | 5th GT | 6th GT | 1st ST | 2nd ST | 3rd ST |
| OUTPUT USEABLE |  | OUTPUT USEABLE |  |  |  |  |  |  |  |  |  |
| MW |  |  |  |  |  |  |  |  |  |
| 0MW to 150MW |  |  |  |  |  |  |  |  |  |
| 151MW to 250MW |  |  |  |  |  |  |  |  |  |
| 251MW to 300MW |  |  |  |  |  |  |  |  |  |
| 301MW to 400MW |  |  |  |  |  |  |  |  |  |
| 401MW to 450MW |  |  |  |  |  |  |  |  |  |
| 451MW to 550MW |  |  |  |  |  |  |  |  |  |

# OC2 APPENDIX 3 – POWER PARK MODULE PLANNING MATRIX

Power Park Module Planning Matrix Example Form

| BM Unit Name |  |  |  |  |
| --- | --- | --- | --- | --- |
| Power Park Module [unique identifier] |  |  |  |  |
| POWER PARK UNIT AVAILABILITY | POWER PARK UNITS |  |  |  |
|  | Type A | Type B | Type C | Type D |
| Description (Make/Model) |  |  |  |  |
| Number of units |  |  |  |  |
| Power Park Module [unique identifier] |  |  |  |  |
| POWER PARK UNIT AVAILABILITY | POWER PARK UNITS |  |  |  |
|  | Type A | Type B | Type C | Type D |
| Description (Make/Model) |  |  |  |  |
| Number of units |  |  |  |  |

The Power Park Module Planning Matrix may have as many columns as are required to provide information on the different make and model for each type of Power Park Unit in a Power Park Module and as many rows as are required to provide information on the Power Park Modules within each BM Unit. The description is required to assist identification of the Power Park Units within the Power Park Module and correlation with data provided under the Planning Code.

#### < END OF OPERATING CODE NO. 2 >