## Slide 1: SQSS Panel
Wednesday, 27 May 2026
Microsoft Teams

## Slide 2: WELCOME

## Slide 3: Purpose of Panel & Duties of Panel Members

## Slide 4: Approval of Panel Minutes
Approval of Minutes from the SQSS Panel held on 24 March 2026 and Special Panel meeting held on 28 April 2026

## Slide 5: Action Log

## Slide 6: Action Log
Action number | Panel Raised | Owner | Action | Comment | Due by | Status
40.8 | Mar-24 | AJ | ESO to report on progress of GC0117 and if an SQSS modification is required, when this will be raised. | 28.04.26 AJ gave an update: The Workgroup is rerunning the cost-benefit analysis (CBA) using the latest data and has sought stakeholder feedback on key sensitivities. Further updates will be provided as the CBA progresses. No further action is expected until Ofgem decides on the GC117 send-back. | TBC | Open
42 | Sep-24 | AG / PD | AG to talk to Ofgem Lawyers for clarification of “Company” / Code references within licence/code | SMC to add to housekeeping modification | TBC | Open
47 | Dec-25 | GG | 5.12.25 GG to consider the necessity of drafting a consequential SQSS Modificaiton alongside GC0117 | GG advised not in a position to raise an SQSS Mod until the GC0117 send back has been completed. | TBC | Open
48 | 24-Mar | All | Review updated GSR036 proposal, legal text, and case studies and provide comments | Panel to review |  | Open

## Slide 7: Action Log
Action number | Panel Raised | Owner | Action | Comment | Due by | Status
49 | 24-Mar | SMC | SMC to organise and run an informal SQSS housekeeping / formatting workshop for GSR 037 prior to modification going straight to CAC. | 28.04.26 CN updated the Panel and confirmed SMC had held three to four workshops with interested parties. The Panel noted the engagement to date and that the work is nearing completion. |  | Open
52 | 28-Apr | TP | To review historic minutes/notes to confirm intent, and (2) liaise with SMC with regard to including any needed text changes in the next housekeeping modification, with an update at the May Panel | Passed to SMC to add to Housekeeping Mod | May Panel | Open
53 | 28-Apr | BJ/CW | BJ/CW to give Ofgem view on FRCR Governance |  | May Panel | Open
54 | 28-Apr | TP | To send out request (via Teams) to each Panel member to identify their preferred FRCR option(s) for 2027 and longer term. | Completed | May Panel | Open
55 | 28-Apr | NESO/FRCR Team | NESO/FRCR team: consider viable options in light of wider process changes (incl. code manager context). | For discussion at future Panel | TBC | Open

## Slide 8: Authority Decisions and Update
The Authority’s publication on decisions can be found on their website below:​
Energy codes | Ofgem
No new decisions have been made on SQSS modifications since the last Panel meeting.​
​​
The Authority’s publication on decisions can be found on their website below:​​
Energy codes | Ofgem
​

## Slide 9: New Modification
GSR036: System Access Reform: Review of the voltage limits
Dozie Nnabuife (NESO)

## Slide 10: Critical Friend Feedback: GSR036
Code Administrator comments | Amendments made by the Proposer
Suggested making paragraphs shorter for readability Consistency in the word used “Proposal or Modification” Review of font size used throughout Updated Acronyms Annex suggestions for paragraph shortening of wording | ​The Proposer accepted the Critical Friend Check and returned documents updated as required and chose not to change the paragraph detail.

## Slide 11: GSR036 Impact Assessment

## Slide 12: Introduction
GSR036 proposes reverting the 275kV upper voltage limit from +9% to +10%, restoring the pre‑2017 SQSS position
The current +9% limit constrains transmission development, slowing outage planning and network growth needed for 2030 and 2050 targets.
The change has a medium industry impact, could benefit Transmission Owners, NESO, Network Operators, Interconnectors, and Generators by enabling more efficient outage scheduling, fewer rejections, and faster grid connections without compromising asset integrity.

## Slide 13: Problem Statement
  NETS SQSS Section 6 voltage limits for 200kV–300kV set too low
  No short-term flexibility, even when safe
  Restricts efficient upgrades and maintenance
  Revise upper voltage limit to +10% for 275kV and similar ranges

## Slide 14: Proposed Solution
Route : Standard Governance modification to proceed to Code Administrator Consultation Update SQSS
  - Revise upper voltage limit to +10% for 275kV and similar ranges
(a) Voltage Limits on Transmission Networks |  |  | 
Nominal Voltage | PU Value (1pu relates to the Nominal Voltage) | Minimum (percentage of Nominal Voltage) | Maximum (percentage of Nominal Voltage)
Greater than 300kV | 0.95pu-1.05pu | -5% Note 6 | +5%
200kV up to 300kV | 0.95pu-1.09pu 1.10pu | -5% Note 6 | +9% +10%
132kV up to and including 200kV | 0.95pu-1.10pu | -5% Note 6 | +10%
(b) Voltages to be Achievable at Interfaces to Distribution Networks and Non-Embedded Customers |  |  | 
Any Nominal Voltage | Target voltages and voltage ranges as agreed with the relevant Distribution Network Operators or Non-Embedded Customers, within the limits of Table 6.4 |  | 
(a) Voltage Limits on Transmission Networks # |  |  | 
Nominal Voltage | PU Value (1pu relates to the Nominal Voltage) | Minimum (percentage of Nominal Voltage) | Maximum (percentage of Nominal Voltage)
Greater than 300kV | 0.90pu-1.05pu | -10% | +5% Note 7
200kV up to and including 300kV | 0.95pu-1.09pu 1.10pu | -10% | +9% +10%
132kV up to and including 200kV | 0.90pu-1.10pu | -10% | +10%
(b) Voltage Limits at Interfaces to Distribution Networks and Non-Embedded Customers |  |  | 
Nominal Voltage |  |  | 
132kV | 0.90pu-1.10pu | -10% | +10%
At less than 132kV | 0.94pu-1.06pu | -6% | +6%
Table 6.3 Pre-Fault Steady State Voltage Limits and Targets in Operational Timescales
Table 6.4 Steady State Voltage Limits and Targets in Operational Timescales

## Slide 15: Impact on resilience and 275KV steady state voltage increase
No material impact on system resilience is anticipated from increasing the 200–300 kV SQSS voltage limits, based on TO’s consent.
Reverting the 275 kV upper voltage limit to 1.1pu (302.5 kV) restores the pre‑2017 SQSS position and corrects a temporary deviation introduced to align with EU standards.
The change is supported by Transmission Owners and NESO, aligns with Grid Code CC.6.1.4, and reflects voltage levels already used in practice on 275 kV networks.
Transmission equipment is designed to withstand 1.1 pu, with negligible impact on generation, as relevant electrical specifications already reference this capability.
Transmission Acceleration Public Consultation | National Energy System Operator

## Slide 16: Case Studies
Case studies illustrate the operational impact of increasing the 275 kV voltage limit, using scenarios derived from NESO’s Voltage Event Reports (VER).
No real system events have exceeded the current +9% limit at 275 kV; all examples are based on calculated voltages from Power Network Analyser (PNA) simulations representing insecure fault conditions.
Voltage issues are typically identified first on the 400 kV network, due to its stricter +5% limit, prompting operational actions before 275 kV voltage limits are reached.

## Slide 17: Case Study 1
Outage combinations in West London and South Wales led to elevated post‑fault voltages, reaching 300–301 kV at two West London substations, slightly exceeding the current +9% (300 kV) limit under lightly loaded overnight conditions.
Voltage control options were limited, with an interconnector STATCOM unavailable and a Voltage Control Circuit (VCC) required to remain in service, reducing operational flexibility.
Operational mitigations were assessed but not viable in real time, as the only action capable of reducing voltage within current limits introduced unacceptable additional demand (single‑circuit) risk.
Under the proposed +10% limit (302.5 kV), the scenario would be compliant and secure, allowing the outage to proceed without additional intervention, with demand security maintained through reinstatement of the VCC.

## Slide 18: Case Study 2
Elevated post‑fault voltages were observed in the West Midlands following changes in wind generation output, reducing north–south power flows and increasing system voltage gain, with a worst‑case voltage of 304 kV at a key substation under low overnight demand.
Mitigation options were limited, as the affected substations had restricted access to reactive compensation or controllable generation, and no tested operational actions successfully reduced voltages to within secure limits.
The most severe contingency was a double‑circuit fault, resulting in post‑fault voltages exceeding both the current and proposed +10% operational limits.
The exceedance was driven by system conditions rather than asset design, and while the +10% limit would not resolve this specific scenario, it would provide greater operational flexibility and reduce constraints for lower‑magnitude voltage events.

## Slide 19: Case Study 3
High post‑fault voltages were simulated in the Northwest following a traffic‑related loss of a single circuit and synchronous compensation, with regional generation unavailable due to planned outages under low overnight demand.
A subsequent double‑circuit contingency resulted in voltage exceedances, reaching 302 kV at the most affected substation and 301 kV at a secondary site, indicating an insecure condition under current limits.
The scenario represents a low‑probability Mult contingency, combining a planned outage, a fault‑induced outage, and an additional double‑circuit event, with post‑fault voltages in the +9% to +10% range.
Under the proposed +10% post‑fault voltage limit, all voltages would remain secure, removing the need for a Voltage Event Report (VER) and improving security of supply and operational resilience during rare contingency events

## Slide 20: Case Study 4
Simulated overnight conditions in the Northeast of England showed elevated post‑fault voltages when key generators and reactive compensation equipment were unavailable, with a worst‑case voltage of ~301 kV following a single‑circuit contingency.
The scenario represents a medium‑probability event, combining unavailability of strategically significant generation, loss of reactive equipment, and a subsequent single‑circuit fault, with voltages reaching between +9% and +10% of nominal.
Under the proposed +10% post‑fault voltage limit, the system would remain within secure operating thresholds, avoiding a security or compliance issue.
The increased limit enables reactive equipment outages (e.g. reactors) to be scheduled without compromising stability, reducing unnecessary operational costs and improving system flexibility.

## Slide 21: Conclusion
Transmission assets are designed to withstand 1.1pu (302.5 kV), consistent with Grid Code CC.6.1.4 and existing electrical specifications, which continue to reference this capability.
Case studies demonstrate systemwide benefits from increasing the post‑fault voltage limit to +10%, enabling more outages to proceed without breaching SQSS security criteria.
Operational efficiency is improved, with fewer unnecessary interventions and Voltage Event Reports (VERs), and reduced reliance on additional generation dispatch or reactive support.
Overall system security and resilience remains , as increased voltage margins improve flexibility during abnormal conditions, support demand security, and contribute to a more robust energy infrastructure.

## Slide 22: GSR036 Asks of Panel
AGREE that this Modification has a clearly defined defect and scope​ ​
AGREE that this Modification should proceed to Code Administrator Consultation
NOTE the proposed timeline

## Slide 23: GSR036 Proposed Timeline
Milestone​ | Date​
Modification presented to Panel​ | 20 May 2026
Code Administrator Consultation (15 Working days) | 25 May 2026 - 12 June 2026
Draft Final Modification Report (DFMR) issued to Panel (5 working days) | 13 July 2026
Panel undertake DFMR recommendation vote | 28 July 2026
Final Modification Report issued to Ofgem | 11 August 2026
Ofgem Decision | TBC
Implementation date | 10 Business Days after Decision

## Slide 24: Inflight Modification Updates
GSR037 Timeline Update
GSR038 Withdrawal
GSR035 Timeline Options

## Slide 25: GSR037 ‘Formatting and Housekeeping’ Timeline Update
Rationale: The Code Administrator Consultation has been delayed due to an informal meeting being required to resolve additional questions.
Workgroups Remaining: n/a
 | Code Administrator Consultation | DFMR issued to Panel | FMR issued to Ofgem | Decision Date | Implementation Date
Previous timeline | 27 March 2026 – 21 April 2026 | 12 May 2026 | 04 June 2026 | TBC | 10 Business Days after Authority decision
New timeline | 19 May 2026 – 16 June 2026 | 14 July 2026 | 05 August 2026 | TBC | 10 Business Days after Authority decision
GSR037– the asks of Panel
AGREE revised timeline

## Slide 26: GSR038: ‘Single Transformer Offshore AC Substations’ Withdrawal
GSR038 – the asks of Panel
AGREE that the Modification can be withdrawn
The Proposer withdrew their support for GSR038 on 20 March 2026. A withdrawal window was opened up for 5 Business Days from this date.
No parties came forward to become the Proposer for this Modification.

## Slide 27: GSR035 'System Access Reform : Review of the operational requirements on the Onshore Systems' Timeline Update
Rationale: An additional Workgroup meeting is required for the Workgroup to discuss Appendix K. This has resulted in the Workgroup Consultation being pushed back and therefore a timeline extension is required.
Workgroups Remaining: 1 before Workgroup Consultation
 | Code Administrator Consultation | DFMR issued to Panel | FMR issued to Ofgem | Decision Date | Implementation Date
Previous timeline | 05 August – 27 August 2026 | 15 September 2026 | 06 October 2026 | TBC | 10BD following Authority Decision
New timeline | TBC | TBC | TBC | TBC | TBC
GSR035– the asks of Panel
AGREE revised timeline option

## Slide 28: GSR035 Proposed Timeline – Option 1
Milestone​ | Date​ | Milestone​ | Date​
Modification presented to Panel​ | 05 December 2025 | Code Administrator Consultation (15 Business Days) | 11 August – 01 September 2026
Workgroup Nominations (20 Business Days holiday period)​ ​ | 22 January 2026 – 12 February 2026 | Draft Final Modification Report (DFMR) issued to Panel (5 Business Days)​ | 15 September 2026
Workgroup 6 – approve Workgroup Consultation document | 03 June 2026 | Panel undertake DFMR recommendation vote ​ | 29 September 2026
Workgroup Consultation (10 Business Days)​ | 08 June – 22 June 2026 | Final Modification Report issued to Panel to check votes recorded correctly | 29 September 2026 to 05 October 2026
Workgroup 5 – review consultation feedback ad build Workgroup Report Workgroup 6 – Review Workgroup Report and vote | 30 June 2026 20 July 2026 | Final Modification Report issued to Ofgem​ | 06 October 2026
Workgroup report issued to Panel (5 Business Days)​ | 23 July 2026 | Ofgem decision ​ | TBC
Panel sign off that Workgroup Report has met its Terms of Reference​ | 10 August 2026 (Special Panel) | Implementation Date ​ | 10 Business Days after Authority decision

## Slide 29: GSR035 Proposed Timeline – Option 2
Milestone​ | Date​ | Milestone​ | Date​
Modification presented to Panel​ | 05 December 2025 | Code Administrator Consultation (15 Business Days) | 27 August -18 September 2026
Workgroup Nominations (20 Business Days holiday period)​ ​ | 22 January 2026 – 12 February 2026 | Draft Final Modification Report (DFMR) issued to Panel (10 Business Days)​ | 23 September 2026
Workgroup 6 - approve Workgroup Consultation document | 03 June 2026 | Panel undertake DFMR recommendation vote ​ | 08 October 2026 (Special Panel)
Workgroup Consultation (15 Business Days)​ | 10 June – 01 July 2026 | Final Modification Report issued to Panel to check votes recorded correctly | 08 October – 15 October 2026
Workgroup 5 – review consultation feedback ad build Workgroup Report Workgroup 6 – Review Workgroup Report and vote | 28 July 05 August | Final Modification Report issued to Ofgem​ | 16 October 2026
Workgroup report issued to Panel (10 Business Days)​ | 11 August | Ofgem decision ​ | TBC
Panel sign off that Workgroup Report has met its Terms of Reference​ | 26 August (Special Panel) | Implementation Date ​ | 10 Business Days after Authority decision

## Slide 30: Updates on other industry codes
23 April 2026 Grid Code Review Panel Papers and Headline Report
24 April 2026 CUSC Panel Papers and Headline Report
29 April 2026 STC Panel Papers and Headline Report

## Slide 31: Any other business
Prioritisation - Establishing a harmonised prioritisation process in the Industry Codes: statutory consultation

## Slide 32: The Prioritisation Framework
Three Prioritisation Criteria:
1. Alignment with SDS
Does the modification support “Act now”, “Think and plan”, or “Listen and wait” policy areas?
2. Importance
Value, risk, criticality to stakeholders, and systemic impact
3. Complexity
Level of resource, system/process change, cross-code impact, and implementation effort
Two Prioritisation Categories:
1. Standard Priority: Follows typical timelines; may pause if dependent on other changes
2. High Priority: Requires faster progression but not necessarily urgent
Equal Weighting: All criteria are considered equally in determining priority
Relative prioritisation: Mods assessed against other live proposals to make sure ‘high priority’ reserved for most pressing proposals
Urgent modification process remains the same

## Slide 33: Activities ahead of the next Panel Meeting
Modification Proposal Deadline for November Panel | 07 July 2026
Papers Day | 14 July 2026
Panel Meeting | 28 July 2026 Teams

## Slide 34: Close
Teri Puddefoot
Chair, SQSS Panel