## Slide 1: GSR036 Impact Assessment

## Slide 2: Introduction
GSR036 proposes reverting the 275kV upper voltage limit from +9% to +10%, restoring the pre‑2017 SQSS position
The current +9% limit constrains transmission development, slowing outage planning and network growth needed for 2030 and 2050 targets.
The change has a medium industry impact, could benefit Transmission Owners, NESO, Network Operators, Interconnectors, and Generators by enabling more efficient outage scheduling, fewer rejections, and faster grid connections without compromising asset integrity.

## Slide 3: Problem Statement
  NETS SQSS Section 6 voltage limits for 200kV–300kV set too low
  No short-term flexibility, even when safe
  Restricts efficient upgrades and maintenance
  Revise upper voltage limit to +10% for 275kV and similar ranges

## Slide 4: Proposed Solution
Route : Standard Governance modification to proceed to Code Administrator Consultation
  Update SQSS
  - Revise upper voltage limit to +10% for 275kV and similar ranges
(a) Voltage Limits on Transmission Networks |  |  | 
Nominal Voltage | PU Value (1pu relates to the Nominal Voltage) | Minimum (percentage of Nominal Voltage) | Maximum (percentage of Nominal Voltage)
Greater than 300kV | 0.95pu-1.05pu | -5% Note 6 | +5%
200kV up to 300kV | 0.95pu-1.09pu 1.10pu | -5% Note 6 | +9% +10%
132kV up to and including 200kV | 0.95pu-1.10pu | -5% Note 6 | +10%
(b) Voltages to be Achievable at Interfaces to Distribution Networks and Non-Embedded Customers |  |  | 
Any Nominal Voltage | Target voltages and voltage ranges as agreed with the relevant Distribution Network Operators or Non-Embedded Customers, within the limits of Table 6.4 |  | 
(a) Voltage Limits on Transmission Networks |  |  | 
Nominal Voltage | PU Value (1pu relates to the Nominal Voltage) | Minimum (percentage of Nominal Voltage) | Maximum (percentage of Nominal Voltage)
Greater than 300kV | 0.90pu-1.05pu | -10% | +5% Note 7
200kV up to and including 300kV | 0.95pu-1.09pu 1.10pu | -10% | +9% +10%
132kV up to and including 200kV | 0.90pu-1.10pu | -10% | +10%
(b) Voltage Limits at Interfaces to Distribution Networks and Non-Embedded Customers |  |  | 
Nominal Voltage |  |  | 
132kV | 0.90pu-1.10pu | -10% | +10%
At less than 132kV | 0.94pu-1.06pu | -6% | +6%
Table 6.3 Pre-Fault Steady State Voltage Limits and Targets in Operational Timescales
Table 6.4 Steady State Voltage Limits and Targets in Operational Timescales

## Slide 5: Impact on resilience and 275KV steady state voltage increase
No material impact on system resilience is anticipated from increasing the 200–300 kV SQSS voltage limits, based on TO’s consent.
Reverting the 275 kV upper voltage limit to 1.1pu (302.5 kV) restores the pre‑2017 SQSS position and corrects a temporary deviation introduced to align with EU standards.
The change is supported by Transmission Owners and NESO, aligns with Grid Code CC.6.1.4, and reflects voltage levels already used in practice on 275 kV networks.
Transmission equipment is designed to withstand 1.1 pu, with negligible impact on generation, as relevant electrical specifications already reference this capability.
Transmission Acceleration Public Consultation | National Energy System Operator

## Slide 6: Case Studies
Case studies illustrate the operational impact of increasing the 275 kV voltage limit, using scenarios derived from NESO’s Voltage Event Reports (VER).
No real system events have exceeded the current +9% limit at 275 kV; all examples are based on calculated voltages from Power Network Analyser (PNA) simulations representing insecure fault conditions.
Voltage issues are typically identified first on the 400 kV network, due to its stricter +5% limit, prompting operational actions before 275 kV voltage limits are reached.

## Slide 7: Case Study 1
Outage combinations in West London and South Wales led to elevated post‑fault voltages, reaching 300–301 kV at two West London substations, slightly exceeding the current +9% (300 kV) limit under lightly loaded overnight conditions.
Voltage control options were limited, with an interconnector STATCOM unavailable and a Voltage Control Circuit (VCC) required to remain in service, reducing operational flexibility.
Operational mitigations were assessed but not viable in real time, as the only action capable of reducing voltage within current limits introduced unacceptable additional demand (single‑circuit) risk.
Under the proposed +10% limit (302.5 kV), the scenario would be compliant and secure, allowing the outage to proceed without additional intervention, with demand security maintained through reinstatement of the VCC.

## Slide 8: Case Study 2
Elevated post‑fault voltages were observed in the West Midlands following changes in wind generation output, reducing north–south power flows and increasing system voltage gain, with a worst‑case voltage of 304 kV at a key substation under low overnight demand.
Mitigation options were limited, as the affected substations had restricted access to reactive compensation or controllable generation, and no tested operational actions successfully reduced voltages to within secure limits.
The most severe contingency was a double‑circuit fault, resulting in post‑fault voltages exceeding both the current and proposed +10% operational limits.
The exceedance was driven by system conditions rather than asset design, and while the +10% limit would not resolve this specific scenario, it would provide greater operational flexibility and reduce constraints for lower‑magnitude voltage events.

## Slide 9: Case Study 3
High post‑fault voltages were simulated in the Northwest following a traffic‑related loss of a single circuit and synchronous compensation, with regional generation unavailable due to planned outages under low overnight demand.
A subsequent double‑circuit contingency resulted in voltage exceedances, reaching 302 kV at the most affected substation and 301 kV at a secondary site, indicating an insecure condition under current limits.
The scenario represents a low‑probability Mult contingency, combining a planned outage, a fault‑induced outage, and an additional double‑circuit event, with post‑fault voltages in the +9% to +10% range.
Under the proposed +10% post‑fault voltage limit, all voltages would remain secure, removing the need for a Voltage Event Report (VER) and improving security of supply and operational resilience during rare contingency events

## Slide 10: Case Study 4
Simulated overnight conditions in the Northeast of England showed elevated post‑fault voltages when key generators and reactive compensation equipment were unavailable, with a worst‑case voltage of ~301 kV following a single‑circuit contingency.
The scenario represents a medium‑probability event, combining unavailability of strategically significant generation, loss of reactive equipment, and a subsequent single‑circuit fault, with voltages reaching between +9% and +10% of nominal.
Under the proposed +10% post‑fault voltage limit, the system would remain within secure operating thresholds, avoiding a security or compliance issue.
The increased limit enables reactive equipment outages (e.g. reactors) to be scheduled without compromising stability, reducing unnecessary operational costs and improving system flexibility.

## Slide 11: Conclusion
Transmission assets are designed to withstand 1.1pu (302.5 kV), consistent with Grid Code CC.6.1.4 and existing electrical specifications, which continue to reference this capability.
Case studies demonstrate systemwide benefits from increasing the post‑fault voltage limit to +10%, enabling more outages to proceed without breaching SQSS security criteria.
Operational efficiency is improved, with fewer unnecessary interventions and Voltage Event Reports (VERs), and reduced reliance on additional generation dispatch or reactive support.
Overall system security and resilience remains , as increased voltage margins improve flexibility during abnormal conditions, support demand security, and contribute to a more robust energy infrastructure.

## Slide 12: Thank you