## Note
Note to 2025 ETYS Appendix B
SHE Transmission has migrated its modelling software platform from PSS®E to PowerFactory. As a result, certain dataset names and/or values relating to SHE Transmission areas may differ from those previously used or observed. These differences may reflect platform-specific modelling approaches, data structures, naming conventions, or calculation methodologies, and do not, in themselves, indicate an error, omission, or inconsistency. Any material differences should be reviewed and assessed on a case-by-case basis.
All ratings provided in the subsequent sections represent the post fault thermal ratings of the equipment, with the exception of those with the value '9999' or higher (in tab B-2-1a/B-2-2a) where these values are uesed to indecate bus couplers or short cables.
SSSC refers to Static Synchronous Series Compensators (Power flow control devices)
All future year data is non-binding and is liable to change.

## Menu
Electricity Ten Year Statement (ETYS) 2025
Appendix B - Supplementary Technical Data
Table | Title
B-1-1a | SHE Transmission Index of Substation Codes
B-1-1b | SPT Index of Substation Codes
B-1-1c | NGET Index of Substation Codes
B-1-1d | OFTO Index of Substation Codes
B-2-1a | SHE Transmission Circuits 2025/26
B-2-1b | SPT Circuits 2025/26
B-2-1c | NGET Circuits 2025/26
B-2-1d | OFTO Circuits 2025/26
B-2-2a | SHE Transmission Circuit Changes 2026/27 to 2033/34
B-2-2b | SPT Circuit Changes 2026/27 to 2033/34
B-2-2c | NGET Circuit Changes 2026/27 to 2033/34
B-2-2d | OFTO Circuit Changes 2026/27 to 2033/34
B-3-1a | SHE Transmission Transformers Winter 2025/26
B-3-1b | SPT Transformers Winter 2025/26
B-3-1c | NGET Transformers Winter 2025/26
B-3-1d | OFTO Transformers Winter 2025/26
B-3-2a | SHE Transmission Transformer Changes 2026/27 to 2033/34
B-3-2b | SPT Transformer Changes 2026/27 to 2033/34
B-3-2c | NGET Transformer Changes 2026/27 to 2033/34
B-3-2d | OFTO Transformer Changes 2026/27 to 2033/34
B-4-1a | SHE Transmission Reactive Compensation Equipment Winter 2025/26
B-4-1b | SPT Reactive Compensation Equipment Winter 2025/26
B-4-1c | NGET Reactive Compensation Equipment Winter 2025/26
B-4-1d | OFTO Reactive Compensation Equipment Winter 2025/26
B-4-2a | SHE Transmission Reactive Compensation Equipment Changes 2026/27 to 2033/34
B-4-2b | SPT Reactive Compensation Equipment Changes 2026/27 to 2033/34
B-4-2c | NGET Reactive Compensation Equipment Changes 2026/27 to 2033/34
B-4-2d | OFTO Reactive Compensation Equipment Changes 2026/27 to 2033/34
B.5.1 | Intra GB HVDC 2025/26 to 2033/34

## B-1-1a
B-1-1a - SHE Transmission Index of Substation Codes
Site Code | Site Name | Voltage (kV)
ABBA | ABERDEEN BAY WINDFARM | 132
ABED | ABERARDER ONSHORE WIND FARM | 132
ABED | ABERARDER ONSHORE WIND FARM | 33
ABNE | ABERNETHY | 132
ABNE | ABERNETHY | 33
ACHE | ACHANY EXTENSION | 132
ACHE | ACHANY EXTENSION | 33
AIGA | AIGAS HYDRO | 132
AIGA | AIGAS HYDRO | 11
AIGN | AIGAS NORTH | 132
AIGN | AIGAS NORTH | 11
ALNE | ALNESS GSP | 132
ALNE | ALNESS GSP | 33
ALYT | ALYTH | 275
ALYT | ALYTH | 400
ANSN | AN SUIDHE NORTH | 275
ANSN | AN SUIDHE NORTH | 33
ANSU | AN SUIDHE | 132
ANSU | AN SUIDHE | 33
ARBR | ARBROATH | 132
ARBR | ARBROATH | 33
ARDK | ARDKINGLAS WIND | 132
ARDK | ARDKINGLAS WIND | 33
ARMO | ARDMORE | 132
ARMO | ARDMORE | 33
AYRE | AYRE OFFSHORE WIND FARM | 400
BALA | BALALLAN | 132
BANN | BANNISKIRK | 275
BANN | BANNISKIRK | 400
BEAT | BEATRICE ONSHORE | 400
BEAU | BEAULY | 132
BEAU | BEAULY | 275
BEAU | BEAULY | 400
BEAU | BEAULY | 33
BEIB | BEINN BHURAICH | 132
BEIB | BEINN BHURAICH | 33
BEIN | BEINNEUN WIND FARM | 132
BEIN | BEINNEUN WIND FARM | 33
BELK | BELLROCK | 400
BERB | BERRY BURN | 275
BERB | BERRY BURN | 33
BEWF | BEAW FIELD | 132
BEWF | BEAW FIELD | 33
BHLA | BHLARAIDH WIND FARM | 132
BHLA | BHLARAIDH WIND FARM | 33
BING | BINGALLY | 132
BING | BINGALLY | 400
BLEX | BHLARAIDH EXTENSION | 132
BLEX | BHLARAIDH EXTENSION | 33
BLGH | BLARGHOUR | 132
BLGH | BLARGHOUR | 33
BLHI | BLACKHILLOCK | 132
BLHI | BLACKHILLOCK | 275
BLHI | BLACKHILLOCK | 400
BOAG | BOAT OF GARTEN | 132
BOAG | BOAT OF GARTEN | 33
BONB | BONNYBRIDGE BORDER NODE | 275
BONB | BONNYBRIDGE BORDER NODE | 400
BRCW | BRACO WEST | 275
BRCW | BRACO WEST | 132
BRCW | BRACO WEST | 33
BREC | BRECHIN | 132
BRID | BRIDGE OF DUN | 132
BRID | BRIDGE OF DUN | 33
BROA | BROADFORD | 132
BROA | BROADFORD | 33
BROR | BRORA | 132
BROR | BRORA | 33
BUCH | BUCHAN | 400
BUMU | BURGHMUIR | 132
BUMU | BURGHMUIR | 33
CAAD | CARRADALE | 132
CAAD | CARRADALE | 33
CAAI | CARNAIG | 132
CAAI | CARNAIG | 400
CAIN | CAIRNFORD | 275
CAIN | CAIRNFORD | 33
CALO | CALEDONIA OFFSHORE | 400
CASS | CASSLEY | 132
CASS | CASSLEY | 33
CEAN | CEANNACROC | 132
CEAN | CEANNACROC | 11
CENS | CENTRAL SHETLAND | 132
CENS | CENTRAL SHETLAND | 275
CHAR | CHARLESTON | 132
CHAR | CHARLESTON | 33
CHLS | CHLEANSAID | 132
CHLS | CHLEANSAID | 33
CLAC | CLACHAN | 132
CLAC | CLACHAN | 11
CLAT | CLACHAN 2 | 132
CLAT | CLACHAN 2 | 33
CLAY | CLAYHILLS | 132
CLAY | CLAYHILLS | 33
CLGO | CLASH GOUR WIND FARM | 132
CLGO | CLASH GOUR WIND FARM | 275
CLGO | CLASH GOUR WIND FARM | 33
CLOI | CLOICHE WIND FARM | 132
CLOI | CLOICHE WIND FARM | 33
CLUN | CLUNIE | 132
CLUN | CLUNIE | 11
CMBS | CAMBUSHINNIE | 400
CMBS | CAMBUSHINNIE | 132
CNBH | CNOC BUIDHE | 132
CNBH | CNOC BUIDHE | 33
COGA | CORRIEGARTH WIND FARM | 132
COGA | CORRIEGARTH WIND FARM | 33
COGL | COIRE GLAS PUMPED STORAGE | 400
COIM | COIRE MASHIE | 400
CONN | CONNAGILL | 132
CONN | CONNAGILL | 275
CORI | CORRIEMOILLIE | 132
CORI | CORRIEMOILLIE | 33
COUA | COUPAR ANGUS | 132
COUA | COUPAR ANGUS | 33
CRAI | CRAIGIEBUCKLER | 132
CRAI | CRAIGIEBUCKLER | 33
CRAR | CRARAE | 132
CRAR | CRARAE | 33
CRAS | CRARAE SOUTH | 275
CRAS | CRARAE SOUTH | 33
CRDH | CREAG DHUBH | 132
CRDH | CREAG DHUBH | 275
CREA | CREAG RIABHACH WINDFARM | 132
CREA | CREAG RIABHACH WINDFARM | 33
CRMU | CRAIG MURRAIL | 275
CRMU | CRAIG MURRAIL | 33
CRSN | CROSSAIG NORTH | 132
CRSN | CROSSAIG NORTH | 275
CRSS | CROSSAIG | 132
CRSS | CROSSAIG | 275
CRSS | CROSSAIG | 33
CULL | CULLIGRAN | 132
CULL | CULLIGRAN | 11
CWIN | CERULEAN WINDS INTOG | 400
DAAS | DALLAS SUBSTATION | 275
DAAS | DALLAS SUBSTATION | 33
DALB | DALMALLY BORDER NODE | 275
DEAN | DEANIE | 132
DEAN | DEANIE | 11
DEAW | DEANIE WEST | 132
DEAW | DEANIE WEST | 11
DELL | DELL | 132
DELL | DELL | 33
DLCH | DALCHORK | 132
DONW | DOUNREAY WEST | 275
DONW | DOUNREAY WEST | 33
DORE | DORENELL WIND FARM | 132
DORE | DORENELL WIND FARM | 33
DOUN | DOUNREAY | 132
DOUN | DOUNREAY | 275
DOUN | DOUNREAY | 33
DUBE | DUNBEATH | 132
DUBE | DUNBEATH | 33
DUDH | DUDHOPE | 132
DUDH | DUDHOPE | 33
DUGR | DUNVEGAN GRID | 132
DUGR | DUNVEGAN GRID | 33
DUNM | DUNMAGLASS | 132
DUNM | DUNMAGLASS | 33
DUNO | DUNOON | 132
DUNO | DUNOON | 33
DYCE | DYCE | 132
DYCE | DYCE | 33
EABA | EARBA | 400
EDAY | EDAY | 132
EDAY | EDAY | 33
EDIN | EDINBANE 132/33KV | 132
EDIN | EDINBANE 132/33KV | 33
ELCH | ELCHIES | 132
ELCH | ELCHIES | 33
ELGI | ELGIN | 132
ELGI | ELGIN | 33
EMMO | EMMOCK | 275
EMMO | EMMOCK | 400
ERRO | ERROCHTY | 132
ERRO | ERROCHTY | 11
ERRO | ERROCHTY | 33
FAAR | FARR WINDFARM | 132
FAAR | FARR WINDFARM | 33
FARI | FARIGAIG | 275
FARI | FARIGAIG | 132
FASN | FASNAKYLE | 275
FASN | FASNAKYLE | 132
FASN | FASNAKYLE | 33
FAUG | FORT AUGUSTUS | 132
FAUG | FORT AUGUSTUS | 275
FAUG | FORT AUGUSTUS | 400
FAUG | FORT AUGUSTUS | 33
FERO | FERNOCH WIND | 132
FERO | FERNOCH WIND | 33
FETT | FETTERESSO | 275
FETT | FETTERESSO | 400
FETT | FETTERESSO | 132
FETT | FETTERESSO | 33
FIDD | FIDDES | 132
FIDD | FIDDES | 33
FINL | FINLARIG | 132
FINL | FINLARIG | 11
FINS | ORKNEY FINSTOWN | 132
FINS | ORKNEY FINSTOWN | 275
FINS | ORKNEY FINSTOWN | 33
FNLN | FANELLAN | 400
FOYE | FOYERS | 275
FRAS | FRASERBURGH | 132
FRAS | FRASERBURGH | 33
FWIL | FORT WILLIAM | 132
FWIL | FORT WILLIAM | 33
FYRI | FYRISH | 275
FYRI | FYRISH | 132
GARB | GARELOCH BOUNDARY | 132
GARV | GARVARY | 132
GARV | GARVARY | 33
GILB | GILLS BAY SUBSTATION | 132
GLAG | GLENAGNES | 132
GLDO | GLENDOE SUBSTATION | 132
GLDY | GLENDYE | 132
GLDY | GLENDYE | 33
GLEN | GLENMORISTON | 132
GLEN | GLENMORISTON | 11
GLFA | GLENFARCLAS | 132
GLFA | GLENFARCLAS | 33
GLRB | GLENROTHES BOUNDARY | 275
GLRB | GLENROTHES BOUNDARY | 400
GLUE | GLEN ULLINISH EXTENSION | 132
GLUE | GLEN ULLINISH EXTENSION | 33
GORW | GORDONBUSH WINDFARM | 275
GORW | GORDONBUSH WINDFARM | 33
GREM | GREMISTA | 132
GREM | GREMISTA | 33
GRIF | GRIFFIN WINDFARM (SSE) | 132
GRIF | GRIFFIN WINDFARM (SSE) | 33
GRNS | GREENS | 400
GRNV | GREEN VOLT OFFSHORE WIND FARM | 400
GRUB | GRUDIE BRIDGE | 132
GRUB | GRUDIE BRIDGE | 33
HARI | HARRIS | 132
HARI | HARRIS | 33
HEBW | HEBRIDEAN WIND | 132
HEBW | HEBRIDEAN WIND | 33
HEST | HESTA HEAD | 132
HEST | HESTA HEAD | 33
HICL | HIGH CONSTELLATION | 132
HICL | HIGH CONSTELLATION | 33
HOME | HOLLANDMEY | 132
HOME | HOLLANDMEY | 33
HUNN | HUNTERSTON NORTH | 275
HURL | HURLIE | 400
INGA | INVERGARRY | 132
INGA | INVERGARRY | 11
INNE | INVERNESS | 132
INNE | INVERNESS | 33
INVB | INVERANAN BOUNDARY | 275
INVE | INVERARAY | 132
INVR | INVERARNAN | 132
KEIC | KEITH GREENER GRID PARK | 132
KEIT | KEITH | 275
KEIT | KEITH | 132
KEIT | KEITH | 33
KERG | KERGORD | 132
KIIN | KILLIN | 132
KIIN | KILLIN | 33
KILO | KINLOCHLEVEN | 132
KILO | KINLOCHLEVEN | 33
KINA | KINARDOCHY | 275
KINA | KINARDOCHY | 400
KINA | KINARDOCHY | 132
KINB | KINCARDINE BOUNDARY | 275
KINB | KINCARDINE BOUNDARY | 400
KINM | KINMUCK | 400
KINM | KINMUCK | 33
KINT | KINTORE | 132
KINT | KINTORE | 275
KINT | KINTORE | 400
KINT | KINTORE | 33
KION | KILMORACK NORTH | 132
KION | KILMORACK NORTH | 11
KIOR | KILMORACK | 132
KIOR | KILMORACK | 11
KIWF | KIRKAN | 275
KIWF | KIRKAN | 33
KNOC | KNOCKNAGAEL | 275
KNOC | KNOCKNAGAEL | 132
KNOC | KNOCKNAGAEL | 33
KRKN | KIRKTON | 132
KRKN | KIRKTON | 33
LAFD | LADYFIELD | 132
LAFD | LADYFIELD | 33
LAIR | LAIRG | 132
LAIR | LAIRG | 33
LAIS | LAIRG SOUTH | 132
LAIS | LAIRG SOUTH | 33
LEWI | LEWIS SUBSTATION | 132
LEWI | LEWIS SUBSTATION | 400
LIMK | LIMEKILNS WINDFARM | 132
LIMK | LIMEKILNS WINDFARM | 33
LKEM | LOCH KEMP PUMPED STORAGE | 275
LOCA | LOCH NA CATHRACH | 275
LOCA | LOCH NA CATHRACH | 11
LOCB | LOCH BUIDHE | 132
LOCB | LOCH BUIDHE | 275
LOCH | LOCHAY | 132
LOCH | LOCHAY | 11
LOCL | LOCH LUNDIE | 400
LOCL | LOCH LUNDIE | 132
LOFA | LOCH FEARNA | 400
LOFA | LOCH FEARNA | 11
LOSD | LONGSIDE | 400
LOSD | LONGSIDE | 132
LOYE | LOCHAY EAST | 132
LOYE | LOCHAY EAST | 11
LUIC | LUICHART | 132
LUIC | LUICHART | 11
LUNA | LUNANHEAD | 132
LUNA | LUNANHEAD | 33
LUNH | LUNANHEAD 2 | 275
LUNH | LUNANHEAD 2 | 33
LYND | LYNDHURST | 132
LYND | LYNDHURST | 33
MACD | MACDUFF | 132
MACD | MACDUFF | 33
MELG | MELGARVE SUBSTATION | 132
MELG | MELGARVE SUBSTATION | 400
MEYG | MEYGEN | 132
MEYG | MEYGEN | 33
MILC | MILTON OF CRAIGIE | 132
MILC | MILTON OF CRAIGIE | 33
MILW | MILLENIUM WIND | 132
MILW | MILLENIUM WIND | 33
MORF | MORAY EAST ONSHORE | 400
MOSS | MOSSFORD | 132
MOSS | MOSSFORD | 11
MOWO | MORAY WEST ONSHORE | 400
MSHL | MOSSY HILL | 132
MSHL | MOSSY HILL | 33
MUAI | MUAITHEBHEAL WIND FARM | 132
MUAI | MUAITHEBHEAL WIND FARM | 33
MYBS | MYBSTER | 132
MYBS | MYBSTER | 33
NAIR | NAIRN | 132
NAIR | NAIRN | 33
NANT | NANT (LOCH NANT) | 132
NANT | NANT (LOCH NANT) | 11
NCCS | NEW CAIRNFORD COLLECTOR SUBSTATION | 275
NCCS | NEW CAIRNFORD COLLECTOR SUBSTATION | 33
NCCS | NEW CAIRNFORD COLLECTOR SUBSTATION | 132
NECS | NEW EAST COAST SUBSTATION | 275
NECS | NEW EAST COAST SUBSTATION | 132
NEDE | NEW DEER | 400
NEMA | NEWMACHAR | 132
NEMA | NEWMACHAR | 400
NORS | NORTHERN SHETLAND | 275
NPIC | SPIORAD NA MARA OFFSHORE WIND FARM | 400
NWGL | NORTH CONNECT | 400
ORRI | ORRIN | 132
ORRI | ORRIN | 11
ORRI | ORRIN | 33
OSSI | OSSIAN | 275
OURA | OURACK WIND FARM | 132
OURA | OURACK WIND FARM | 33
OWFD | PENTLAND FLOATING OFFSHORE WINDFARM | 132
OWPL | OWPL WINDFARM | 400
PEHE | PETERHEAD | 132
PEHE | PETERHEAD | 275
PEHE | PETERHEAD | 400
PEHG | PETERHEAD GRANGE | 132
PEHG | PETERHEAD GRANGE | 33
PEHS | PETERHEAD SHELL | 11
PERS | PERSLEY | 132
PERS | PERSLEY | 275
PERS | PERSLEY | 33
PHCC | PETERHEAD CARBON CAPTURE | 20.5
PORA | PORT ANN | 132
PORA | PORT ANN | 33
QUOI | QUOICH | 132
QUOI | QUOICH | 11
RANN | RANNOCH | 132
RANN | RANNOCH | 33
REDM | REDMOSS | 132
REDM | REDMOSS | 33
ROTI | ROTHIENORMAN | 400
ROTI | ROTHIENORMAN | 33
SALM | SALAMANDER OFFSHORE WIND FARM | 132
SFEE | ST FERGUS EAST | 132
SFEE | ST FERGUS EAST | 11
SFEG | ST FERGUS GAS TERMINAL | 132
SFEM | ST FERGUS MOBIL | 132
SFER | ST FERGUS | 132
SFEV | ST FERGUS VSD | 132
SFIL | ST FILLANS | 132
SFIL | ST FILLANS | 11
SGRX | SEAGREEN ONE 275KV ONSHORE | 275
SHIN | SHIN | 132
SHIN | SHIN | 33
SHIN | SHIN | 11
SINC | SINCLAIR OFFSHORE | 132
SLCK | SLICKLY WIND FARM | 132
SLOY | SLOY | 132
SLOY | SLOY | 11
SOYK | STRATH OYKEL WIND FARM | 132
SOYK | STRATH OYKEL WIND FARM | 33
SPIT | SPITTAL | 275
SPIT | SPITTAL | 132
STCS | STRATHY COLLECTOR STATION | 132
STMR | STROMAR OFFSHORE WIND FARM | 400
STNG | STANNERGATE | 132
STOR | STORNOWAY | 132
STOR | STORNOWAY | 33
STRB | STRATH BRORA WIND | 275
STRB | STRATH BRORA WIND | 33
STRI | STRICHEN | 132
STRI | STRICHEN | 33
STRL | STRONELAIRG WIND FARM (SSE) | 132
STRL | STRONELAIRG WIND FARM (SSE) | 33
STRW | STRATHY WIND | 132
STRW | STRATHY WIND | 33
STSO | STRATHY SOUTH | 132
STSO | STRATHY SOUTH | 33
STWO | STRATHY WOOD | 132
STWO | STRATHY WOOD | 33
TARL | TARLAND | 132
TARL | TARLAND | 33
TAYN | TAYNUILT | 132
TAYN | TAYNUILT | 33
TEAL | TEALING | 275
TEAL | TEALING | 132
TEAL | TEALING | 33
TEAS | TEALING SOLAR AND STORAGE | 132
TEAS | TEALING SOLAR AND STORAGE | 33
THSC | THURSO SOUTH SYNC. COMP | 275
THUS | THURSO SOUTH | 275
THUS | THURSO SOUTH | 132
THUS | THURSO SOUTH | 33
TLSK | TALISK OFFSHORE WIND FARM | 400
TNGF | TANGY IV | 132
TNGF | TANGY IV | 33
TOMT | TOMATIN | 132
TOMT | TOMATIN | 275
TOSY | TOMCHRASKY | 132
TOSY | TOMCHRASKY | 33
TUMB | TUMMEL BRIDGE | 132
TUMB | TUMMEL BRIDGE | 11
TUMM | TUMMEL | 132
TUMM | TUMMEL | 275
VIKE | VIKING ENERGY WIND FARM | 132
VIKE | VIKING ENERGY WIND FARM | 33
WFIB | WESTFIELD BOUNDARY | 275
WFIB | WESTFIELD BOUNDARY | 400
WHTB | WHISTLEFIELD BORDER | 132
WIOW | WILLOWDALE | 132
WIOW | WILLOWDALE | 33
WOHI | WOODHILL | 132
WOHI | WOODHILL | 33
YELL | YELL | 132
YELL | YELL | 275

## B-1-1b
B-1-1b - SPT Index of Substation Codes
Site Code | Site Name | Voltage (kV)
AIKE | AIKENGALL | 33
AREC | ARECLEOCH | 132
AREC | ARECLEOCH | 33
AREX | ARECLEOCH EXTENSION | 132
AREX | ARECLEOCH EXTENSION | 33
ARFO | ARTFIELD FOREST | 132
AUCH | AUCHENCROSH | 275
AUCW | AUCHENWYND | 132
AYR- | AYR | 275
AYR- | AYR | 33
AYRS | AYRSHIRE GRID COLLECTOR | 400
AGSF | AYRSHIRE GRID SERVICES FACILITY | 400
BAIN | BAINSFORD | 132
BAIN | BAINSFORD | 33
BANR | BANKEND RIG | 132
BANR | BANKEND RIG | 33
BANK | BANKHEAD | 400
BAGA | BATHGATE | 132
BAGA | BATHGATE | 33
BTCK | BEATTOCK | 400
BTCK | BEATTOCK | 132
BTCK | BEATTOCK | 33
BENB | BENBRACK WIND FARM | 132
BENB | BENBRACK WIND FARM | 33
BERW | BERWICK | 132
BERW | BERWICK | 33
BILS | BILSDEAN | 400
BLCW | BLACKCRAIG | 132
BLCW | BLACKCRAIG | 33
BLKS | BLACKCRAIG SOUTH | 33
BLAH | BLACKHILL | 132
BLAH | BLACKHILL | 33
BLKL | BLACKLAW | 132
BLKL | BLACKLAW | 33
BLLX | BLACKLAW EXTENSION | 132
BLLX | BLACKLAW EXTENSION | 33
BODI | BODINGLEE WINDFARM | 132
BONN | BONNYBRIDGE | 400
BONN | BONNYBRIDGE | 275
BONN | BONNYBRIDGE | 132
BONN | BONNYBRIDGE | 33
BONB | BONNYBRIDGE BORDER NODE | 400
BONB | BONNYBRIDGE BORDER NODE | 275
BPGR | BP GRANGEMOUTH | 33
BRAP | BRAEHEAD PARK | 132
BRAP | BRAEHEAD PARK | 33
BRNX | BRANXTON | 400
BREE | BREEZY HILL | 132
BROT | BROKEN CROSS TEE | 132
BROX | BROXBURN | 132
BROX | BROXBURN | 33
BUSB | BUSBY | 275
CATY | CARNTYNE | 132
CATY | CARNTYNE | 33
CRCK | CARRICK | 275
CRCK | CARRICK | 33
CAFA | CARSFAD | 132
CAFA | CARSFAD | 11
CHAP | CHAPELCROSS | 132
CPCR | CHAPELCROSS PV | 132
CHAP | CHAPELCROSS | 33
CHAS | CHARLOTTE STREET | 275
CHAS | CHARLOTTE STREET | 33
CHMO | CHIRMORIE | 132
CLAW | CLAWFIN | 132
CLFO | CLOICH FOREST | 132
CLFO | CLOICH FOREST | 33
CLOU | CLOUD HILL | 132
CLYN | CLYDE NORTH | 275
CLYN | CLYDE NORTH | 33
CLYS | CLYDE SOUTH | 275
CLYS | CLYDE SOUTH | 33
CLYM | CLYDE'S MILL | 400
CLYM | CLYDE'S MILL | 275
CLYM | CLYDE'S MILL | 33
COAL | COALBURN | 400
COAL | COALBURN | 132
COAL | COALBURN | 33
COAB | COALBURN BATTERY STORAGE FACILITY | 400
COBA | COALBURN BATTERY STORAGE TWO | 400
COBA | COALBURN BATTERY STORAGE TWO | 33
COAN | COALBURN NORTH | 400
COAN | COALBURN NORTH | 132
COAT | COATBRIDGE | 275
COAT | COATBRIDGE | 33
COCK | COCKENZIE | 400
COCK | COCKENZIE | 275
COCK | COCKENZIE | 33
COLD | COLDSTREAM COLLECTOR | 132
CONL | CONLAND | 400
CONL | CONLAND | 275
COYL | COYLTON | 275
COYL | COYLTON | 132
COYL | COYLTON | 33
COYT | COYLTON TEE | 132
COYW | COYLTON WEST | 275
CRAG | CRAIGIE | 400
CRFO | CRAWFORDJOHN SUBSTATION | 132
CREA | CREAMLY BURN | 132
CROO | CROOKSTON | 132
CROO | CROOKSTON | 33
CRDY | CROSSDYKES | 33
CRUA | CRUACHAN | 275
CRYR | CRYSTAL RIG | 400
CRYR | CRYSTAL RIG | 132
CRYR | CRYSTAL RIG | 33
CCSS | CUMBERHEAD COLLECTOR | 132
CCSS | CUMBERHEAD COLLECTOR | 33
CUMW | CUMBERHEAD WEST | 132
CUMW | CUMBERHEAD WEST | 33
CUMH | CUMBERHEAD WF SUBSTATION | 33
CUMB | CUMBERNAULD | 275
CUMB | CUMBERNAULD | 132
CUMB | CUMBERNAULD | 33
CUPA | CUPAR | 132
CUPA | CUPAR | 33
CURR | CURRIE | 275
CURR | CURRIE | 132
CURR | CURRIE | 33
CURR | CURRIE | 11
DAER | DAER | 132
DAER | DAER | 33
DALL | DALMALLY | 275
DALB | DALMALLY BORDER NODE | 275
DALM | DALMARNOCK | 275
DALM | DALMARNOCK | 132
DALM | DALMARNOCK | 33
DENN | DENNY NORTH | 400
DENN | DENNY NORTH | 275
DENN | DENNY NORTH | 132
DESA | DERSALLOCH | 132
DESA | DERSALLOCH | 33
DEBS | DEVILLA BATTERY STORAGE FACILITY | 275
DEBS | DEVILLA BATTERY STORAGE FACILITY | 33
DEVM | DEVOL MOOR | 400
DEVM | DEVOL MOOR | 132
DEVM | DEVOL MOOR | 33
DEVO | DEVONSIDE | 132
DEVO | DEVONSIDE | 33
DEWP | DEWAR PLACE | 275
DEWP | DEWAR PLACE | 33
DONO | DOUGLAS NORTH COLLECTOR | 132
DONO | DOUGLAS NORTH COLLECTOR | 33
DRUM | DRUMCHAPEL | 275
DRUM | DRUMCHAPEL | 33
DRCR | DRUMCROSS | 132
DRCR | DRUMCROSS | 33
DRUR | DRUMSHORELAND ROAD | 132
DUMF | DUMFRIES | 132
DUMF | DUMFRIES | 33
DUNB | DUNBAR | 132
DUNB | DUNBAR | 33
DUNF | DUNFERMLINE | 132
DUNF | DUNFERMLINE | 33
DUNH | DUNHILL | 132
DUNH | DUNHILL | 33
DUNE | DUNLAW EXTENSION | 132
DUNE | DUNLAW EXTENSION | 33
EAST | EARLSTOUN | 132
EAST | EARLSTOUN | 11
EKIL | EAST KILBRIDE | 275
EKIL | EAST KILBRIDE | 33
EKIS | EAST KILBRIDE SOUTH | 275
EKIS | EAST KILBRIDE SOUTH | 33
EERH | EASTERHOUSE | 275
EERH | EASTERHOUSE | 33
ECCF | ECCLEFECHAN | 132
ECCL | ECCLES | 400
ECCL | ECCLES | 132
ECCL | ECCLES | 33
ELDE | ELDERSLIE | 132
ELDE | ELDERSLIE | 33
ELVA | ELVANFOOT | 400
ELVA | ELVANFOOT | 275
ELVA | ELVANFOOT | 132
ELVA | ELVANFOOT | 33
ENHI | ENOCH HILL WIND FARM | 132
ENHI | ENOCH HILL WIND FARM | 33
ERSK | ERSKINE | 132
ERSK | ERSKINE | 33
ESST | ESSENSIDE | 132
EUCH | EUCHANHEAD | 132
EUCH | EUCHANHEAD | 33
EWEH | EWE HILL | 132
EWEH | EWE HILL | 33
FALL | FALLAGO | 400
FALL | FALLAGO | 132
FALL | FALLAGO | 33
FASI | FAW SIDE | 132
FIGS | FIFE GRID SERVICES COLLECTOR | 275
FINN | FINNIESTON | 132
FINN | FINNIESTON | 33
GALN | GALA NORTH | 400
GALN | GALA NORTH | 132
GALA | GALASHIELS | 132
GALA | GALASHIELS | 33
GALA | GALASHIELS | 25
GAWH | GALAWHISTLE | 132
GAWH | GALAWHISTLE | 33
GARE | GARELOCH | 132
GARB | GARELOCH BOUNDARY | 132
GARC | GARTCLASH COLLECTOR | 275
GIFF | GIFFNOCK | 275
GIFF | GIFFNOCK | 33
GLAP | GLEN APP | 33
GLGL | GLENGLASS | 132
GLGL | GLENGLASS | 33
GLLE | GLENLEE | 132
GLLE | GLENLEE | 11
GLLU | GLENLUCE | 132
GLLU | GLENLUCE | 33
GLMU | GLENMUCKLOCH | 33
GHPS | GLENMUCKLOCH HYDRO PUMPED STORAGE | 400
GHPS | GLENMUCKLOCH HYDRO PUMPED STORAGE | 132
GLNI | GLENNISTON | 132
GLNI | GLENNISTON | 33
GLRO | GLENROTHES | 275
GLRO | GLENROTHES | 33
GLRB | GLENROTHES BOUNDARY | 400
GLRB | GLENROTHES BOUNDARY | 275
GNSH | GLENSHIMMEROCH | 132
GORG | GORGIE | 132
GORG | GORGIE | 33
GOVA | GOVAN | 132
GOVA | GOVAN | 33
GRMO | GRANGEMOUTH | 275
GRMO | GRANGEMOUTH | 33
GBRN | GREENBURN | 132
GRNA | GRETNA | 400
GRNA | GRETNA | 132
GRNA | GRETNA | 33
HADH | HADYARD HILL | 132
HADH | HADYARD HILL | 33
HAGR | HAGGS ROAD | 132
HAGR | HAGGS ROAD | 33
HAHA | HAGSHAW HILL PHASE 1 | 33
HAGH | HAGSHAW HILL PHASE 2 | 33
HALB | HALBEATH | 132
HARB | HARBURY | 400
HARB | HARBURY | 132
HARB | HARBURY | 33
HRCR | HARE CRAIG | 33
HARE | HARESTANES | 132
HARE | HARESTANES | 33
HAKB | HARKER BORDER NODE | 400
HAKB | HARKER BORDER NODE | 132
HARR | HARTING RIG WIND FARM | 33
HAWI | HAWICK | 132
HAWI | HAWICK | 33
HAZE | HAZELSIDE | 132
HLND | HEATHLAND | 132
HLND | HEATHLAND | 33
HELE | HELENSBURGH | 132
HELE | HELENSBURGH | 33
HILB | HILL OF BEATH | 132
HOLM | HOLM HILL | 132
HORI | HOPSRIG COLLECTOR | 132
HORI | HOPSRIG COLLECTOR | 33
HUER | HUNTERSTON | 400
HUER | HUNTERSTON | 132
HBES | HUNTERSTON BATTERY STORAGE | 400
HUCS | HUNTERSTON CONVERTER STATION | 400
HUNE | HUNTERSTON EAST | 400
HUNE | HUNTERSTON EAST | 132
HESF | HUNTERSTON ENERGY STORAGE FACILITY | 400
HUNF | HUNTERSTON FARM | 132
HUNF | HUNTERSTON FARM | 33
HUNN | HUNTERSTON NORTH | 400
HUNN | HUNTERSTON NORTH | 275
HUNN | HUNTERSTON NORTH | 33
HUNP | HUNTERSTON PORT | 400
INWI | INNERWICK | 132
INVR | INVERARNAN | 275
INVB | INVERARNAN BORDER NODE | 275
INKE | INVERKEITHING | 132
INKE | INVERKEITHING | 33
JOHN | JOHNSTONE | 132
JOHN | JOHNSTONE | 33
JUNA | JUNCTION A | 132
JUNB | JUNCTION B | 132
JUNV | JUNCTION V | 132
KAIM | KAIMES | 275
KAIM | KAIMES | 33
KEIH | KEITHSHILL | 33
KEOO | KENDOON | 132
KEOO | KENDOON | 11
KENN | KENNOXHEAD | 132
KENE | KENNOXHEAD WINDFARM EXTENSION | 33
KEPP | KEPPEN BURN TEE | 400
KLBG | KILBAGGIE | 275
KILB | KILBOWIE | 132
KILB | KILBOWIE | 33
KILB | KILBOWIE | 11
KILG | KILGALLIOCH | 275
KILG | KILGALLIOCH | 33
KIER | KILLERMONT | 132
KIER | KILLERMONT | 33
KILS | KILMARNOCK SOUTH | 400
KILS | KILMARNOCK SOUTH | 275
KILS | KILMARNOCK SOUTH | 132
KILS | KILMARNOCK SOUTH | 33
KILT | KILMARNOCK TOWN | 275
KILT | KILMARNOCK TOWN | 33
KILW | KILWINNING | 132
KILW | KILWINNING | 33
KINC | KINCARDINE | 275
KINB | KINCARDINE BORDER NODE | 400
KINB | KINCARDINE BORDER NODE | 275
KINN | KINCARDINE NORTH | 400
KINN | KINCARDINE NORTH | 275
KNCR | KNOCKCRONAL | 33
KNOK | KNOCKODHAR WIND FARM | 132
KNOK | KNOCKODHAR WIND FARM | 33
KNSH | KNOCKSHEE | 132
KYPE | KYPE MUIR | 132
KYPE | KYPE MUIR | 33
LMEP | LAIRDMANNOCH ENERGY PARK SOLAR | 132
LAMB | LAMBHILL | 400
LAMB | LAMBHILL | 275
LALE | LAND AT LEITHOLM | 132
LEGR | LEGBRANNOCK ROAD SUBSTATION | 275
LETH | LETHANS | 132
LEVE | LEVEN | 132
LEVE | LEVEN | 33
LEVT | LEVEN TEE | 132
LINM | LINNMILL | 132
LINM | LINNMILL | 33
LING | LIVINGSTON | 132
LING | LIVINGSTON | 33
LOAN | LONGANNET | 275
LORG | LORG WIND FARM | 132
LORG | LORG WIND FARM | 33
LYLS | LYLESTONE | 132
MARG | MARGREE | 33
MAHI | MARK HILL | 275
MAHI | MARK HILL | 132
MAHI | MARK HILL | 33
MAYB | MAYBOLE | 132
MAYB | MAYBOLE | 33
MAYT | MAYBOLE TEE | 132
MEAD | MEADOWHEAD | 132
MEAC | MEADOWMILL COLLECTOR | 132
MOIL | MID MOIL | 275
MOIL | MID MOIL | 132
MIDM | MIDDLE MUIR | 132
MIDM | MIDDLE MUIR | 33
MINN | MINNYGAP | 33
MOFF | MOFFAT | 400
MOFF | MOFFAT | 132
MOFF | MOFFAT | 33
MONQ | MONQUHILL | 33
MONB | MONTIFODE BURN | 132
MOSM | MOSSMORRAN | 400
MOSM | MOSSMORRAN | 275
MOSM | MOSSMORRAN | 132
MOSM | MOSSMORRAN | 33
MOSH | MOSSMORRAN SHELL | 132
MOSH | MOSSMORRAN SHELL | 11
NEIL | NEILSTON | 400
NEIL | NEILSTON | 275
NEIL | NEILSTON | 132
NEIL | NEILSTON | 33
NECU | NEW CUMNOCK | 275
NECU | NEW CUMNOCK | 132
NEAR | NEWARTHILL | 275
NEAR | NEWARTHILL | 33
NEWL | NEWLANDS HILL | 132
NEWL | NEWLANDS HILL | 33
NETS | NEWTON STEWART | 132
NETS | NEWTON STEWART | 33
NOKY | NORTH KYLE | 132
NOKY | NORTH KYLE | 33
NLAN | NORTH LANRIGG BATTERY STORAGE | 275
NLEI | NORTH LOWTHER ENERGY INITIATIVE | 132
NLEI | NORTH LOWTHER ENERGY INITIATIVE | 33
OFOA | OLD FOREST OF AE | 132
OFOA | OLD FOREST OF AE | 33
OLDT | OLD TOLL COLLECTOR | 275
OLDH | OLDHAMSTOCKS | 400
OLDH | OLDHAMSTOCKS | 132
OHLL | OVERHILL | 132
PAIS | PAISLEY | 132
PAIS | PAISLEY | 33
PART | PARTICK | 132
PART | PARTICK | 33
PLOE | PENCLOE | 33
PLEC | PLEAN COUNTRY PARK | 275
POGB | POGBIE | 33
PORD | PORT DUNDAS | 275
PORD | PORT DUNDAS | 33
POOB | PORTOBELLO | 275
POOB | PORTOBELLO | 33
PRST | PRIESTGILL | 33
QUAN | QUANTANS HILL | 132
QUAN | QUANTANS HILL | 33
RAVE | RAVENSCRAIG | 33
REDH | REDHOUSE | 132
REDH | REDHOUSE | 33
REDS | REDSHAW | 400
REDS | REDSHAW | 132
REDS | REDSHAW | 33
KIRH | ROGER HILL FARM | 132
SACO | SALTCOATS | 132
SACO | SALTCOATS | 33
SAKN | SANDY KNOWE | 132
SAKN | SANDY KNOWE | 33
SNQR | SANQUHAR | 33
SANQ | SANQUHAR 2A WIND FARM | 132
SCOP | SCOOP HILL WIND FARM | 132
SERG | SERGEANTLAW | 132
SHRG | SHEPHERDS RIG | 132
SHRG | SHEPHERDS RIG | 33
SHRU | SHRUBHILL | 275
SHRU | SHRUBHILL | 33
SIGH | SIGHTHILL | 275
SIGH | SIGHTHILL | 33
SMEA | SMEATON | 400
SMEA | SMEATON | 275
SMEA | SMEATON | 132
SMEA | SMEATON | 33
SOKY | SOUTH KYLE | 132
SPAV | SPANGO VALLEY | 132
SPAV | SPANGO VALLEY | 33
SPRB | SPIREBUSH RENEWABLE ENERGY | 132
SANX | ST ANDREWS CROSS | 132
SANX | ST ANDREWS CROSS | 33
STWB | STELLA WEST BORDER NODE | 400
STIR | STIRLING | 132
STIR | STIRLING | 33
STOC | STRANOCH | 132
STOC | STRANOCH | 33
STHA | STRATHAVEN | 400
STHA | STRATHAVEN | 275
STHA | STRATHAVEN | 33
STLE | STRATHLEVEN | 132
STLE | STRATHLEVEN | 33
TELR | TELFORD ROAD | 132
TELR | TELFORD ROAD | 33
THRN | THORNTONLOCH | 400
TODD | TODDLEBURN | 33
TONG | TONGLAND | 132
TONG | TONGLAND | 33
TONG | TONGLAND | 11
TORN | TORNESS | 400
TORN | TORNESS | 132
TOCS | TORNESS CONVERTER STATION | 400
TRLO | TRALORG | 33
WGEO | WEST GEORGE STREET | 275
WGEO | WEST GEORGE STREET | 33
WESE | WESTERDOD | 132
WESL | WESTERTON LANE | 275
WFIE | WESTFIELD | 400
WFIE | WESTFIELD | 275
WFIE | WESTFIELD | 132
WFIE | WESTFIELD | 33
WFIB | WESTFIELD BOUNDARY | 400
WFIB | WESTFIELD BOUNDARY | 275
WESS | WESTGILL SIKE | 400
WESS | WESTGILL SIKE | 132
WHTL | WHISTLEFIELD | 132
WHTL | WHISTLEFIELD | 33
WHTB | WHISTLEFIELD BOUNDARY | 132
WHIF | WHITEHILL FARM | 400
WHHO | WHITEHOUSE | 275
WHHO | WHITEHOUSE | 33
WLEE | WHITELEE | 275
WLEE | WHITELEE | 33
WLEX | WHITELEE EXTENSION | 275
WLEX | WHITELEE EXTENSION | 33
WMHL | WHITEMINHILL ENERGY PARK | 275
WMHL | WHITEMINHILL ENERGY PARK | 33
WNUK | WHITENEUK | 132
WHLL | WHITESIDE HILL | 33
WIYH | WINDYHILL | 400
WIYH | WINDYHILL | 275
WIYH | WINDYHILL | 132
WIYH | WINDYHILL | 33
WISH | WISHAW | 400
WISH | WISHAW | 275
WISH | WISHAW | 132
WISH | WISHAW | 33

## B-1-1c
B-1-1c - NGET Index of Substation Codes
Site Code | Site Name | Voltage (kV)
ABEB | ABERTHAW (NGED) | 132
ABHA | ABHAM | 400
ABHA | ABHAM | 132
ABTB | ABERTHAW B | 132
ABTB | ABERTHAW B | 275
ABTH | ABERTHAW | 275
ABTH | ABERTHAW | 132
ALDW | ALDWARKE | 275
ALDW | ALDWARKE | 33
ALST | ALPHA STEEL | 33
ALVE | ALVERDISCOTT | 400
ALVE | ALVERDISCOTT | 132
AMEM | AMERSHAM MAIN | 400
AMEM | AMERSHAM MAIN | 132
AXMI | AXMINSTER | 400
AXMI | AXMINSTER | 132
BAGB | BAGLAN BAY | 275
BARK | BARKING | 275
BARK | BARKING | 400
BARK | BARKING | 132
BARW | BARKING WEST | 33
BAYB | BAYBROOKE | 400
BEDD | BEDDINGTON | 275
BEDD | BEDDINGTON | 400
BEDD | BEDDINGTON | 132
BEDT | BEDDINGTON TEE | 132
BENR | BENGEWORTH ROAD | 400
BENR | BENGEWORTH ROAD | 132
BESW | BERKSWELL | 275
BESW | BERKSWELL | 132
BICF | BICKER FEN | 400
BICF | BICKER FEN | 132
BIGG | BIGGLESWADE | 132
BIGG | BIGGLESWADE | 400
BIRK | BIRKENHEAD | 275
BIRK | BIRKENHEAD | 132
BIRW | BIRKHILL WOOD | 400
BISW | BISHOPS WOOD | 275
BISW | BISHOPS WOOD | 132
BLNE | BLYTH NORTH EAST | 400
BLNE | BLYTH NORTH EAST | 275
BLYT | BLYTH | 275
BLYT | BLYTH | 400
BLYT | BLYTH | 132
BLYT | BLYTH | 66
BODE | BODELWYDDAN | 400
BOLN | BOLNEY | 400
BOLN | BOLNEY | 132
BOLN | BOLNEY | 33
BOTW | BOTLEY WOOD | 400
BOTW | BOTLEY WOOD | 132
BRAI | BRAINTREE | 400
BRAI | BRAINTREE | 132
BRAW | BRADFORD WEST | 275
BRAW | BRADFORD WEST | 400
BRAW | BRADFORD WEST | 132
BRAW | BRADFORD WEST | 33
BRED | BREDBURY | 275
BRED | BREDBURY | 132
BRFO | BRAMFORD | 400
BRFO | BRAMFORD | 132
BRIM | BRIMSDOWN | 275
BRIM | BRIMSDOWN | 400
BRIM | BRIMSDOWN | 132
BRIN | BRINSWORTH | 275
BRIN | BRINSWORTH | 400
BRLE | BRAMLEY | 400
BRLE | BRAMLEY | 132
BRWA | BRIDGWATER | 400
BRWA | BRIDGWATER | 132
BRYN | BRYNCIR | 400
BRYN | BRYNCIR | 132
BULL | BULLS LODGE | 400
BURW | BURWELL MAIN | 400
BURW | BURWELL MAIN | 132
BUSH | BUSHBURY | 275
BUSH | BUSHBURY | 132
BUST | BUSTLEHOLME | 275
BUST | BUSTLEHOLME | 400
BUST | BUSTLEHOLME | 132
BUTE | BUTE | 132
CAMA | CAMBRIDGE ARMS | 132
CAML | CAMBLESFORTH | 66
CANT | CANTERBURY NORTH | 400
CANT | CANTERBURY NORTH | 132
CAPE | CAPENHURST | 132
CAPE | CAPENHURST | 400
CAPE | CAPENHURST | 275
CARE | CARDIFF EAST | 275
CARE | CARDIFF EAST | 132
CARL | CARLISLE | 400
CARR | CARRINGTON | 275
CARR | CARRINGTON | 400
CARR | CARRINGTON | 132
CELL | CELLARHEAD | 400
CELL | CELLARHEAD | 132
CHIC | CHICKERELL | 400
CHIC | CHICKERELL | 132
CHIL | CHILLING | 400
CHSI | CHESSINGTON | 275
CHSI | CHESSINGTON | 132
CHTE | CHESTERFIELD | 275
CHTE | CHESTERFIELD | 400
CHTE | CHESTERFIELD | 132
CHUE | CHAFFORD HUNDRED EAST | 400
CILF | CILFYNYDD | 275
CILF | CILFYNYDD | 400
CITR | CITY ROAD | 400
CITR | CITY ROAD | 132
CLEH | CLEVE HILL | 400
CONQ | CONNAHS QUAY | 400
CONQ | CONNAHS QUAY | 132
COSO | CORYTON SOUTH | 400
COTS | POWER STATION - COTE SOLAR | 400
COTS | POWER STATION - COTE SOLAR | 132
COTT | COTTAM | 400
COVE | COVENTRY | 275
COVE | COVENTRY | 132
COWL | COWLEY | 400
COWL | COWLEY | 132
COWT | COWBRIDGE TEE | 275
CREB | CREYKE BECK | 275
CREB | CREYKE BECK | 400
CREB | CREYKE BECK | 132
CUJT | CULHAM JET TEE | 400
CULJ | CULHAM JET | 400
CULJ | CULHAM JET | 33
DAIN | DAINES | 400
DAMC | DAMHEAD CREEK | 400
DIDC | DIDCOT | 400
DIDC | DIDCOT | 33
DIDC | DIDCOT | 132
DINO | DINORWIG | 400
DISS | DISS | 400
DRAK | DRAKELOW | 400
DRAK | DRAKELOW | 275
DRAK | DRAKELOW | 132
DRAX | DRAX | 400
DRAX | DRAX | 132
DUNG | DUNGENESS | 400
DUNG | DUNGENESS | 275
EACS | EAST ANGLIA COASTAL SUBSTATION | 400
EALI | EALING | 275
EALI | EALING | 66
EASO | EATON SOCON | 400
EASO | EATON SOCON | 132
ECLA | EAST CLAYDON | 400
ECLA | EAST CLAYDON | 132
EGGB | EGGBOROUGH | 400
ELLA | ELLAND | 275
ELLA | ELLAND | 132
ELST | ELSTREE | 132
ELST | ELSTREE | 275
ELST | ELSTREE | 400
ENDE | ENDERBY | 400
ENDE | ENDERBY | 132
EXET | EXETER | 400
EXET | EXETER | 132
FARM | FARMOOR | 400
FAWL | FAWLEY | 400
FAWL | FAWLEY | 132
FECK | FECKENHAM | 400
FECK | FECKENHAM | 275
FECK | FECKENHAM | 66
FENW | FENWICK TEE | 400
FERR | FERRYBRIDGE | 275
FERR | FERRYBRIDGE | 400
FERR | FERRYBRIDGE | 132
FERR | FERRYBRIDGE | 66
FFES | FFESTINIOG | 275
FIDF | FIDDLERS FERRY | 275
FIDF | FIDDLERS FERRY | 132
FLEE | FLEET | 400
FLEE | FLEET | 132
FLEE | FLEET | 33
FLIB | FLINTSHIRE BRIDGE | 400
FOUR | FOURSTONES | 275
FOUR | FOURSTONES | 33
FOUR | FOURSTONES | 20.5
FRIN | FRISTON NORTH | 400
FROD | FRODSHAM | 400
FROD | FRODSHAM | 275
FROD | FRODSHAM | 132
GART | GARTH CABLE COMPOUND | 400
GOTH | GOTHAM | 400
GRAI | GRAIN | 400
GRAI | GRAIN | 132
GRAN | GRANGE | 66
GREN | GRENDON | 400
GREN | GRENDON | 132
GRIW | GRIMSBY WEST | 400
GRIW | GRIMSBY WEST | 132
GRST | GREYSTONES | 275
GRST | GREYSTONES | 66
GRTO | GRANGETOWN | 66
GWYD | GWYDDELWERN | 400
GWYN | GWYNEDD | 400
HACK | HACKNEY | 275
HACK | HACKNEY | 400
HACK | HACKNEY | 66
HACK | HACKNEY | 132
HAKB | HARKER BOUNDARY | 132
HAKB | HARKER BOUNDARY | 400
HAMB | HAMBLETON | 400
HAMH | HAMS HALL | 275
HAMH | HAMS HALL | 400
HARG | HARKER GIS | 400
HARG | HARKER GIS | 132
HARK | HARKER | 132
HARK | HARKER | 275
HARK | HARKER | 400
HARK | HARKER | 33
HARM | HARTMOOR | 275
HARM | HARTMOOR | 66
HATL | HARTLEPOOL | 275
HAWP | HAWTHORN PIT | 275
HAWP | HAWTHORN PIT | 400
HAWP | HAWTHORN PIT | 66
HEDO | HEDON (GIS) | 275
HEND | HENDON | 132
HEYS | HEYSHAM | 400
HEYS | HEYSHAM | 132
HIBU | HIGHBURY | 400
HIGB | HIGH MARNHAM-B | 400
HIGB | HIGH MARNHAM-B | 33
HIGB | HIGH MARNHAM-B | 275
HIGM | HIGH MARNHAM | 275
HIGM | HIGH MARNHAM | 400
HIMB | HIGH MARNHAM SUBSTATION-B | 275
HINP | HINKLEY POINT | 400
HINP | HINKLEY POINT | 275
HUMR | HUMBER REFINERY | 400
HUMR | HUMBER REFINERY | 33
HURS | HURST | 275
HURS | HURST | 132
HUTT | HUTTON | 400
HUTT | HUTTON | 132
HYCL | HYLTON CASTLE | 66
HYLC | HYLTON CASTLE | 275
ICKE | ICKENHAM | 275
IMPP | IMPERIAL PARK | 400
IMPP | IMPERIAL PARK | 33
IMPP | IMPERIAL PARK | 132
INCE | INCE | 132
INDQ | INDIAN QUEENS | 400
INDQ | INDIAN QUEENS | 132
INDQ | INDIAN QUEENS | 33
INGL | INGLEBOROUGH CONVERTER STATION | 400
IROA | IRON ACTON | 132
IROA | IRON ACTON | 275
IRON | IRONBRIDGE | 400
IRON | IRONBRIDGE | 132
ISLI | ISLINGTON | 132
IVER | IVER | 275
IVER | IVER | 400
IVER | IVER | 132
IVER | IVER | 66
JORD | JORDANTHORPE | 275
JORD | JORDANTHORPE | 33
JUNB | JUNCTION B | 132
JUNV | JUNCTION V | 132
KEAD | KEADBY | 400
KEAD | KEADBY | 132
KEAR | KEARSLEY | 275
KEAR | KEARSLEY | 400
KEAR | KEARSLEY | 132
KEAR | KEARSLEY | 33
KEMS | KEMSLEY | 400
KEMS | KEMSLEY | 132
KENG | KENSAL GREEN | 400
KENG | KENSAL GREEN | 66
KIBY | KIRKBY | 275
KIBY | KIRKBY | 132
KIBY | KIRKBY | 400
KILA | KILN LANE | 400
KILL | KILLINGHOLME | 400
KINO | KINGSNORTH | 400
KINO | KINGSNORTH | 132
KIRK | KIRKSTALL | 275
KIRK | KIRKSTALL | 132
KITW | KITWELL | 275
KITW | KITWELL | 132
KLYN | KINGS LYNN | 400
KNAR | KNARESBOROUGH | 275
KNAR | KNARESBOROUGH | 132
LACK | LACKENBY | 275
LACK | LACKENBY | 400
LACK | LACKENBY | 66
LAGA | LANGAGE | 400
LALE | LALEHAM | 275
LALE | LALEHAM | 132
LAND | LANDULPH | 400
LAND | LANDULPH | 132
LCNA | LINCOLNSHIRE COASTAL NODE A | 400
LCNB | LINCOLNSHIRE COASTAL NODE B | 400
LECH | LETCHMORE HEATH | 400
LEGA | LEGACY | 400
LEGA | LEGACY | 132
LEIB | LEIGHTON BUZZARD | 400
LEIS | LEISTON | 132
LEIS | LEISTON | 400
LEMR | LEA MARSTON | 132
LETH | LETCHMORE HEATH | 132
LHOR | LITTLE HORSTED | 400
LHOR | LITTLE HORSTED | 132
LISD | LISTER DRIVE | 275
LISD | LISTER DRIVE | 132
LITB | LITTLE BARFORD | 132
LITT | LITTLEBROOK | 400
LITT | LITTLEBROOK | 275
LITT | LITTLEBROOK | 132
LLFG | LLANDYFAELOG | 400
LLFG | LLANDYFAELOG | 132
LODR | LODGE ROAD | 66
LOFI | LONGFIELD | 400
LONL | LONG LANE | 400
LOVE | LOVEDEAN | 400
LOVE | LOVEDEAN | 132
LOWF | LOW FARM PV | 132
LOWF | LOW FARM PV | 400
MACC | MACCLESFIELD | 400
MACC | MACCLESFIELD | 275
MACC | MACCLESFIELD | 33
MAGA | MARGAM | 275
MANN | MANNINGTON | 400
MANN | MANNINGTON | 132
MANN | MANNINGTON | 33
MARH | MARKET HARBOROUGH | 400
MARV | MARSTON VALE | 400
MAWO | MARCHWOOD | 400
MEDB | MEDBURN TEE B | 400
MEDW | MEDWAY | 400
MELK | MELKSHAM | 400
MELK | MELKSHAM | 275
MELK | MELKSHAM | 132
MELK | MELKSHAM | 33
MIDL | MIDDLETON | 400
MIDL | MIDDLETON | 132
MILH | MILL HILL | 275
MILH | MILL HILL | 132
MILP | MILTON PARK | 33
MINC | MINSTER CONVERTER STATION | 400
MINS | MINSTER | 400
MITY | MINETY | 400
MITY | MINETY | 132
MITY | MINETY | 33
MONF | MONK FRYSTON | 275
MONF | MONK FRYSTON | 400
MURT | MURTON CONVERTER STATION | 400
NECH | NECHELLS | 275
NECH | NECHELLS | 132
NECL | EAST CLAYDON (NEW) | 400
NECL | EAST CLAYDON (NEW) | 132
NECT | NECTON | 400
NEEP | NEEPSEND | 275
NEEP | NEEPSEND | 400
NEEP | NEEPSEND | 33
NERY | NEW RYHALL | 400
NEWX | NEW CROSS | 400
NEWX | NEW CROSS | 275
NEWX | NEW CROSS | 132
NEWX | NEW CROSS | 66
NFLE | NORTHFLEET EAST | 400
NFLE | NORTHFLEET EAST | 132
NHYD | NORTH HYDE | 275
NHYD | NORTH HYDE | 66
NINF | NINFIELD | 400
NINF | NINFIELD | 132
NORE | NORTON EAST | 400
NORL | NORTON LEES | 275
NORL | NORTON LEES | 33
NORM | NORWICH MAIN | 132
NORM | NORWICH MAIN | 400
NORM | NORWICH MAIN | 33
NORT | NORTON | 275
NORT | NORTON | 400
NORT | NORTON | 132
NORW | NORWICH | 132
NOTR | NORWICH TROWSE | 132
NURS | NURSLING | 400
NURS | NURSLING | 132
NWAR | NEW WARLEY | 132
OCKH | OCKER HILL | 275
OCKH | OCKER HILL | 132
OFFE | OFFERTON | 275
OFFE | OFFERTON | 33
OLDB | OLDBURY | 400
OLDB | OLDBURY | 275
OLDB | OLDBURY | 132
OLDS | OLDBURY ON SEVERN | 132
OSBA | OSBALDWICK | 400
OSBA | OSBALDWICK | 132
OVTO | OVERTON | 275
OVTO | OVERTON | 400
PADI | PADIHAM | 400
PADI | PADIHAM | 132
PAFB | PATFORD BRIDGE | 400
PELH | PELHAM | 400
PELH | PELHAM | 132
PEMB | PEMBROKE | 400
PEMB | PEMBROKE | 132
PENE | PENWORTHAM EAST | 132
PENI | PENISARWAUN | 400
PENN | PENN | 275
PENN | PENN | 400
PENN | PENN | 132
PENT | PENTIR | 400
PENT | PENTIR | 132
PENW | PENWORTHAM WEST | 132
PERH | PENRHOS | 132
PEWO | PENWORTHAM | 275
PEWO | PENWORTHAM | 400
PITS | PITSMOOR | 275
PITS | PITSMOOR | 33
POPP | POPPLETON | 275
POPP | POPPLETON | 33
PORH | PORT HAM | 132
PORT | PORT TABLOT | 33
PORT | PORT TABLOT | 275
PUDM | PUDDING MILL LANE | 400
PURI | PURITON TEE | 400
PYLE | PYLE | 275
PYLE | PYLE | 132
QNTN | QUAINTON | 400
QUER | QUERNMOOR | 400
RAIN | RAINHILL | 275
RAIN | RAINHILL | 132
RASS | RASSAU | 400
RASS | RASSAU | 132
RATS | RATCLIFFE-ON-SOAR | 400
RATS | RATCLIFFE-ON-SOAR | 275
RATS | RATCLIFFE-ON-SOAR | 132
RAYL | RAYLEIGH | 400
RAYL | RAYLEIGH | 33
RAYM | RAYLEIGH MAIN | 132
REBR | REDBRIDGE | 275
REBR | REDBRIDGE | 33
RHIG | RHIGOS | 400
RICH | RICHBOROUGH | 400
RICH | RICHBOROUGH | 132
ROCH | ROCHDALE | 275
ROCH | ROCHDALE | 400
ROCH | ROCHDALE | 132
ROCK | ROCKSAVAGE | 400
ROCK | ROCKSAVAGE | 132
ROWD | ROWDOWN | 400
RUGE | RUGELEY | 400
RUGE | RUGELEY | 132
RYEH | RYE HOUSE | 400
RYEH | RYE HOUSE | 132
RYHA | RYHALL | 400
SAEN | SALTEND NORTH | 275
SAEN | SALTEND NORTH | 132
SAES | SALTEND SOUTH | 275
SAFO | SANDFORD | 400
SAFO | SANDFORD | 132
SALH | SALTHOLME | 400
SALH | SALTHOLME | 275
SALH | SALTHOLME | 132
SASA | ST ASAPHS | 132
SAXM | SAXMUNDHAM CONVERTER STATION | 400
SEAB | SEABANK | 400
SEAB | SEABANK | 132
SELL | SELLINDGE | 400
SELL | SELLINDGE | 132
SHBA | SOUTH HUMBER BANK | 400
SHEC | SHEFFIELD CITY | 275
SHEC | SHEFFIELD CITY | 33
SHEE | SHEERNESS | 132
SHPT | SHIPTON TEE | 400
SHRE | SHREWSBURY | 400
SHRE | SHREWSBURY | 132
SHUR | SHURTON | 400
SING | SINGLEWELL | 400
SIZE | SIZEWELL | 400
SIZE | SIZEWELL | 132
SJOW | ST JOHNS WOOD | 400
SJOW | ST JOHNS WOOD | 275
SJOW | ST JOHNS WOOD | 132
SKLG | SKELTON GRANGE | 275
SKLG | SKELTON GRANGE | 132
SMAN | SOUTH MANCHESTER | 275
SMAN | SOUTH MANCHESTER | 132
SPEN | SPENNYMOOR | 400
SPEN | SPENNYMOOR | 132
SPLN | SPALDING NORTH | 400
SSHI | SOUTH SHIELDS | 275
SSHI | SOUTH SHIELDS | 33
STAH | STANAH | 400
STAH | STANAH | 132
STAL | STALYBRIDGE | 400
STAL | STALYBRIDGE | 275
STAL | STALYBRIDGE | 132
STAY | STAYTHORPE | 400
STEN | STELLA NORTH | 132
STES | STELLA SOUTH | 132
STEW | STELLA WEST | 275
STEW | STELLA WEST | 400
STOB | STOKE BARDOLPH | 400
STOB | STOKE BARDOLPH | 132
STSB | STOCKSBRIDGE | 400
STWB | STELLA WEST BORDER NODE | 400
STWT | STELLA WEST TEE | 400
STYC | STAYTHORPE C | 132
SUND | SUNDON | 400
SUND | SUNDON | 132
SUND | SUNDON | 33
SWAN | SWANSEA NORTH | 400
SWAN | SWANSEA NORTH | 275
SWAN | SWANSEA NORTH | 132
TADT | TADCASTER TEE | 275
TAUN | TAUNTON | 400
TAUN | TAUNTON | 132
TEMP | TEMPLEBOROUGH | 275
TEMP | TEMPLEBOROUGH | 33
THOM | THORPE MARSH | 275
THOM | THORPE MARSH | 400
THOM | THORPE MARSH | 66
THTO | THORNTON | 400
THUR | THURCROFT | 275
THUR | THURCROFT | 66
TIBB | TILBURY B | 400
TIBB | TILBURY B | 275
TILB | TILBURY | 275
TILB | TILBURY | 400
TILB | TILBURY | 132
TILN | TILBURY NORTH | 400
TINP | TINSLEY PARK | 275
TINP | TINSLEY PARK | 33
TODP | TOD POINT | 275
TODP | TOD POINT | 66
TOTT | TOTTENHAM | 275
TOTT | TOTTENHAM | 132
TRAW | TRAWSFYNYDD | 400
TRAW | TRAWSFYNYDD | 275
TRAW | TRAWSFYNYDD | 132
TREM | TREMORFA | 275
TREM | TREMORFA | 33
TREU | TREUDDYN | 400
TWIN | TWINSTEAD | 400
TWIN | TWINSTEAD | 132
TYNE | TYNEMOUTH | 275
TYNE | TYNEMOUTH | 132
TYNE | TYNEMOUTH | 11
UPPB | UPPER BOAT | 275
UPPB | UPPER BOAT | 33
UPPB | UPPER BOAT | 132
USKM | USKMOUTH | 132
USKM | USKMOUTH | 275
UXBM | UXBRIDGE MOOR | 400
UXBM | UXBRIDGE MOOR | 132
WAEN | WALLEND | 400
WALB | WALPOLE 'B' | 400
WALH | WALHAM | 400
WALP | WALPOLE | 400
WALP | WALPOLE | 132
WALX | WALTHAM CROSS | 275
WALX | WALTHAM CROSS | 400
WANB | WANLASS BECK | 33
WANB | WANLASS BECK GIS | 400
WARL | WARLEY | 275
WARL | WARLEY | 400
WARL | WARLEY | 132
WASF | WASHWAY FARM | 275
WASF | WASHWAY FARM | 132
WATS | WATFORD SOUTH | 275
WATS | WATFORD SOUTH | 132
WBOL | WEST BOLDON | 275
WBOL | WEST BOLDON | 66
WBUR | WEST BURTON | 400
WBUR | WEST BURTON | 132
WEMA | WESTON MARSH | 400
WHAM | WEST HAM | 400
WHAM | WEST HAM | 132
WHGA | WHITEGATE | 275
WHGA | WHITEGATE | 132
WHSO | WHITSON | 400
WHSO | WHITSON | 275
WHSO | WHITSON | 33
WIBA | WINCOBANK | 275
WIBA | WINCOBANK | 33
WIEN | WILLENHALL | 275
WIEN | WILLENHALL | 132
WILE | WILLINGTON EAST | 400
WILL | WILLINGTON | 132
WILT | WILTON | 275
WIMB | WIMBLEDON | 275
WIMB | WIMBLEDON | 400
WIMB | WIMBLEDON | 132
WISD | WILLESDEN | 275
WISD | WILLESDEN | 400
WISD | WILLESDEN | 132
WISD | WILLESDEN | 66
WMAA | WESTON MARSH A | 400
WMAB | WESTON MARSH B | 400
WMEL | WEST MELTON | 275
WMEL | WEST MELTON | 132
WOOL | WOOLAVINGTON | 400
WOOL | WOOLAVINGTON | 132
WREH | WREN HALL CONVERTER STATION | 400
WTHU | WEST THURROCK | 400
WTHU | WEST THURROCK | 33
WWEY | WEST WEYBRIDGE | 400
WWEY | WEST WEYBRIDGE | 275
WWEY | WEST WEYBRIDGE | 132
WYLF | WYLFA | 400
WYLF | WYLFA | 132
WYMO | WYMONDLEY | 400
WYMO | WYMONDLEY | 132
YAXL | YAXLEY | 400
YAXT | YAXLEY TEE | 400

## B-1-1d
B-1-1d - OFTO Index of Substation Codes
Site Code | Site Name | Voltage (kV)
BBWO | BURBO BANK EXTENSION ONSHORE | 400
BBWO | BURBO BANK EXTENSION ONSHORE | 220
BBWW | BURBO BANK EXTENSION OFFSHORE | 220
BBWW | BURBO BANK EXTENSION OFFSHORE | 33
BEAT | BEATRICE ONSHORE | 400
BEAT | BEATRICE ONSHORE | 220
BEIW | BEATRICE OFFSHORE | 220
BEIW | BEATRICE OFFSHORE | 33
BOSO | BARROW ONSHORE | 132
BOSW | BARROW OFFSHORE | 132
BOSW | BARROW OFFSHORE | 33
DBAO | DOGGER BANK A ONSHORE | 400
DBAW | DOGGER BANK A OFFSHORE | 220
DBAW | DOGGER BANK A OFFSHORE | 33
DBBO | DOGGER BANK B ONSHORE | 400
DBBW | DOGGER BANK B OFFSHORE | 220
DBBW | DOGGER BANK B OFFSHORE | 33
DBCO | DOGGER BANK C ONSHORE | 400
DBCW | DOGGER BANK C OFFSHORE | 220
DBCW | DOGGER BANK C OFFSHORE | 66
DUDO | DUDGEON ONSHORE | 132
DUDW | DUDGEON OFFSHORE | 132
DUDW | DUDGEON OFFSHORE | 33
EAAW | EAST ANGLIA ONE OFFSHORE | 220
EAAW | EAST ANGLIA ONE OFFSHORE | 66
EABO | EAST ANGLIA TWO ONSHORE | 400
EABO | EAST ANGLIA TWO ONSHORE | 275
EACO | EAST ANGLIA THREE ONSHORE | 400
EANO | EAST ANGLIA ONE NORTH ONSHORE | 400
EANO | EAST ANGLIA ONE NORTH ONSHORE | 220
EANW | EAST ANGLIA ONE NORTH OFFSHORE | 220
EANW | EAST ANGLIA ONE NORTH OFFSHORE | 66
GALO | GALLOPER ONSHORE | 132
GANW | GALLOPER NORTH OFFSHORE | 132
GANW | GALLOPER NORTH OFFSHORE | 33
GGON | GREATER GABBARD ONSHORE | 132
GREG | GREATER GABBARD OFFSHORE | 132
GREG | GREATER GABBARD OFFSHORE | 33
GUNS | GUNFLEET SANDS OFFSHORE | 132
GUNS | GUNFLEET SANDS OFFSHORE | 33
GWAW | GWYNT-Y-MOR OFFSHORE A | 132
GWAW | GWYNT-Y-MOR OFFSHORE A | 33
GWBW | GWYNT-Y-MOR OFFSHORE B | 132
GWBW | GWYNT-Y-MOR OFFSHORE B | 33
GWYO | GWYNT-Y-MOR ONSHORE | 132
HOWA | HORNSEA ONE ONSHORE | 400
HOWA | HORNSEA ONE ONSHORE | 220
HOWB | HORNSEA TWO ONSHORE | 400
HOWB | HORNSEA TWO ONSHORE | 220
HOWC | HORNSEA THREE ONSHORE | 400
HOWD | HORNSEA FOUR ONSHORE | 400
HOWD | HORNSEA FOUR ONSHORE | 220
HOWR | HORNSEA REACTOR PLATFORM | 220
HOWW | HORNSEA OFFSHORE | 400
HOWW | HORNSEA OFFSHORE | 220
HOWW | HORNSEA OFFSHORE | 66
HOWW | HORNSEA OFFSHORE | 33
HUMO | HUMBER GATEWAY ONSHORE | 275
HUMO | HUMBER GATEWAY ONSHORE | 132
HUMO | HUMBER GATEWAY ONSHORE | 33
HUMW | HUMBER GATEWAY OFFSHORE | 132
HUMW | HUMBER GATEWAY OFFSHORE | 33
INCO | INCH CAPE ONSHORE | 275
INCO | INCH CAPE ONSHORE | 220
INCW | INCH CAPE OFFSHORE | 275
INCW | INCH CAPE OFFSHORE | 66
LINO | LINCS ONSHORE | 400
LINO | LINCS ONSHORE | 132
LINS | LINCS OFFSHORE | 132
LINS | LINCS OFFSHORE | 33
LOAW | LONDON ARRAY OFFSHORE WIND FARM - PLATFORM 1 | 150
LOAW | LONDON ARRAY OFFSHORE WIND FARM - PLATFORM 1 | 33
LONO | LONDON ARRAY ONSHORE | 400
LONO | LONDON ARRAY ONSHORE | 150
LOYW | LONDON ARRAY OFFSHORE WIND FARM - PLATFORM 2 | 150
LOYW | LONDON ARRAY OFFSHORE WIND FARM - PLATFORM 2 | 33
MORF | MORAY EAST ONSHORE | 275
MORO | MORAY EAST ONSHORE | 220
MOWE | MORAY EAST OFFSHORE | 220
MOWE | MORAY EAST OFFSHORE | 66
MOWO | MORAY WEST ONSHORE | 400
MOWO | MORAY WEST ONSHORE | 220
MOWW | MORAY WEST OFFSHORE | 220
MOWW | MORAY WEST OFFSHORE | 66
NNGO | NEART NA GAOITHE ONSHORE | 400
NNGO | NEART NA GAOITHE ONSHORE | 220
NNGW | NEART NA GAOITHE OFFSHORE | 220
NNGW | NEART NA GAOITHE OFFSHORE | 66
ORMO | ORMONDE ONSHORE | 132
ORMO | ORMONDE ONSHORE | 33
ORMW | ORMONDE OFFSHORE | 132
ORMW | ORMONDE OFFSHORE | 33
RACO | RACEBANK ONSHORE | 400
RACO | RACEBANK ONSHORE | 220
RACW | RACEBANK OFFSHORE | 220
RACW | RACEBANK OFFSHORE | 33
RAMW | RAMPION OFFSHORE | 150
RAMW | RAMPION OFFSHORE | 33
RORE | ROBIN RIGG EAST ONSHORE | 132
RORE | ROBIN RIGG EAST ONSHORE | 33
RORW | ROBIN RIGG WEST ONSHORE | 132
RORW | ROBIN RIGG WEST ONSHORE | 33
RREW | ROBIN RIGG EAST OFFSHORE | 132
RRWW | ROBIN RIGG WEST OFFSHORE | 132
SGRO | SEAGREEN ONE 220KV ONSHORE | 220
SGRW | SEAGREEN ONE OFFSHORE | 220
SGRW | SEAGREEN ONE OFFSHORE | 66
SGRX | SEAGREEN ONE 275KV ONSHORE | 275
SOFW | SOFIA OFFSHORE | 400
SOFW | SOFIA OFFSHORE | 66
SSAW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 1 | 132
SSAW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 1 | 33
SSBW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 2 | 132
SSBW | SHERRINGHAM SHOAL OFFSHORE PLATFORM 2 | 33
THAW | THANET WIND ONSHORE | 132
THOW | THANET WIND OFFSHORE | 132
THOW | THANET WIND OFFSHORE | 33
TKNE | TRITON KNOLL EAST OFFSHORE | 220
TKNE | TRITON KNOLL EAST OFFSHORE | 66
TKNO | TRITON KNOLL ONSHORE | 400
TKNO | TRITON KNOLL ONSHORE | 220
TKNW | TRITON KNOLL WEST OFFSHORE | 220
TKNW | TRITON KNOLL WEST OFFSHORE | 66
TWNE | TWINEHAM ONSHORE | 400
TWNE | TWINEHAM ONSHORE | 150
VGEO | VANGUARD EAST ONSHORE | 400
VGEW | VANGUARD EAST OFFSHORE | TBC
VGWO | VANGUARD WEST ONSHORE | 400
VGWW | VANGUARD WEST OFFSHORE | TBC
WAAO | WALNEY 1 ONSHORE | 132
WAAW | WALNEY 1 OFFSHORE | 132
WAAW | WALNEY 1 OFFSHORE | 33
WABO | WALNEY 2 ONSHORE | 132
WABW | WALNEY 2 OFFSHORE | 132
WABW | WALNEY 2 OFFSHORE | 33
WACW | WALNEY 3 OFFSHORE | 220
WACW | WALNEY 3 OFFSHORE | 33
WADW | WALNEY 4 OFFSHORE | 220
WADW | WALNEY 4 OFFSHORE | 33
WDSO | WEST OF DUDDON SANDS ONSHORE | 400
WDSO | WEST OF DUDDON SANDS ONSHORE | 155
WDSW | WEST OF DUDDON SANDS OFFSHORE | 155
WDSW | WEST OF DUDDON SANDS OFFSHORE | 33
WERO | WESTERMOST ROUGH OFFSHORE | 150
WERO | WESTERMOST ROUGH ONSHORE | 275
WERW | WESTERMOST ROUGH OFFSHORE | 150
WERW | WESTERMOST ROUGH OFFSHORE | 33
WOWE | WALNEY EXTENSION | 400
WOWE | WALNEY EXTENSION | 220
ALVE | ALVERDISCOTT | 400
BANN | BANNISKIRK | 400
BICF | BICKER FEN | 400
BIRW | BIRKHILL WOOD | 400
BLYT | BLYTH | 400
BODE | BODELWYDDAN | 400
BOLN | BOLNEY | 400
BRFO | BRAMFORD | 400
BRNX | BRANXTON | 400
BRST | BURSTALL | 275
BRST | BURSTALL | 400
CLEH | CLEVE HILL | 400
CLTO | CLACTON | 132
COCK | COCKENZIE | 275
CREB | CREYKE BECK | 400
CRYR | CRYSTAL RIG | 400
EOWF | EREBUS OFFSHORE WINDFARM | 132
EOWF | EREBUS OFFSHORE WINDFARM | 66
EOWL | EREBUS OFFSHORE WINDFARM | 132
GRNS | GREENS | 400
HAWP | HAWTHORN PIT | 400
HEDO | HEDON | 275
HEYS | HEYSHAM | 400
KILL | KILLINGHOLME | 400
LACK | LACKENBY | 400
LEIS | LEISTON | 132
LEWI | LEWIS | 400
LINC | LINCOLN | 400
LOSD | LONGSIDE | 400
MIDL | MIDDLETON | 400
NECT | NECTON | 400
NEDE | NEW DEER | 400
NORM | NORWICH MAIN | 400
PEHE | PETERHEAD | 132
PEHE | PETERHEAD | 400
PEMB | PEMBROKE | 132
PEMB | PEMBROKE | 400
PEWO | PENWORTHAM | 400
SALL | SALLE | 132
SHET | SHETLAND | 400
SPIT | SPITTAL | 400
WALP | WALPOLE | 400
WEMA | WESTON MARSH | 400

## B-2-1a
B-2-1a - SHE Transmission Circuits for 2025/26
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABBA1- | DYCE1K | 1.93 | 7.8 | Composite | 0.206 | 1.6667 | 10.2395 | 173 | 158 | 158 | 158
ABNE1Q | CHAR11 | 24.5 | 0 | OHL | 2.22 | 5.4644 | 1.248 | 133 | 124 | 106 | 124
ABNE1R | GRIF1T | 34.95 | 8.62 | Composite | 3.4188 | 8.6024 | 11.99 | 133 | 124 | 106 | 124
AIGA1Q | KIOR1A | 2.39 | 0.32 | Composite | 0.2456 | 0.6107 | 0.137 | 133 | 124 | 106 | 124
ALNE1Q | FYRI11 | 0 | 2.1 | Cable | 0.0378 | 0.294 | 2.52 | 158 | 146 | 146 | 146
ALNE1R | FYRI11 | 0 | 2.1 | Cable | 0.0378 | 0.294 | 2.52 | 158 | 146 | 146 | 146
ALYT21 | TEAL21 | 16.2 | 0 | OHL | 0.0731 | 0.6723 | 4.3975 | 1096 | 1029 | 924 | 1029
ALYT21 | FETT21 | 67.35 | 0 | OHL | 0.3038 | 2.7952 | 18.282 | 1096 | 1029 | 924 | 1029
ALYT21 | KINB2J | 69.28 | 0 | OHL | 0.3156 | 2.9044 | 18.9959 | 1096 | 1029 | 924 | 1029
ALYT21 | FETT21 | 67.35 | 0 | OHL | 0.3038 | 2.7952 | 18.282 | 1096 | 1029 | 924 | 1029
ALYT21 | KINB2K | 69.98 | 0 | OHL | 0.3156 | 2.9044 | 18.9959 | 1096 | 1029 | 924 | 1029
ALYT21 | TEAL21 | 16.2 | 0 | OHL | 0.0731 | 0.6723 | 4.3975 | 1096 | 1029 | 924 | 1029
ANSU1- | INVE11 | 11.35 | 0 | OHL | 0.1783 | 1.8641 | 0.7847 | 741 | 709 | 659 | 709
ANSU1- | PORA1A | 24.95 | 0 | OHL | 0.3919 | 4.0977 | 1.725 | 741 | 709 | 659 | 709
ARBR1A | TEAL11 | 8.7 | 0 | OHL | 0.3404 | 1.8444 | 0.469 | 183 | 160 | 149 | 160
ARBR1A | ARBR1Q | 14.5 | 0 | OHL | 1.3138 | 3.2638 | 0.732 | 133 | 124 | 106 | 124
ARBR1A | BREC1R | 26.1 | 0 | OHL | 2.7415 | 6.2598 | 1.2479 | 112 | 104 | 90 | 104
ARBR1R | TEAL11 | 23.2 | 0 | OHL | 1.6542 | 5.1082 | 1.201 | 133 | 124 | 106 | 124
ARDK1- | INVE11 | 9 | 0 | OHL | 0.8154 | 1.9227 | 0.4827 | 133 | 124 | 106 | 124
ARDK1- | INVR1A | 10.01 | 0 | OHL | 0.9082 | 2.2248 | 0.5165 | 133 | 124 | 106 | 124
ARMO1- | DUGR1Q | 14 | 0 | OHL | 1.7707 | 3.0753 | 0.7292 | 99 | 92 | 79 | 92
BEAT4- | BLHI41 | 0 | 0.6 | Cable | 0.002 | 0.006 | 4.645 | 321 | 321 | 321 | 321
BEAT4- | BLHI41 | 0 | 0.6 | Cable | 0.002 | 0.006 | 4.645 | 321 | 321 | 321 | 321
BEAU11 | ORRI1A | 10.74 | 3.09 | Composite | 0.2703 | 2.4641 | 11.0486 | 444 | 403 | 403 | 403
BEAU11 | ORRI1B | 10.73 | 3.06 | Composite | 0.2703 | 2.4641 | 11.0486 | 444 | 403 | 403 | 403
BEAU11 | INNE1Q | 13.4 | 2.4 | Composite | 0.7004 | 3.1184 | 4.6491 | 242 | 229 | 209 | 229
BEAU11 | INNE1R | 13.4 | 2.4 | Composite | 0.7004 | 3.1184 | 4.6491 | 242 | 229 | 209 | 229
BEAU11 | CULL1A | 14 | 0 | OHL | 1.2712 | 3.2094 | 0.6977 | 133 | 124 | 106 | 124
BEAU11 | KIOR1A | 1.3 | 0 | OHL | 0.1178 | 0.292 | 0.0658 | 133 | 124 | 106 | 124
BEAU11 | KNOC11 | 16.74 | 0.8 | Composite | 1.5661 | 3.9096 | 1.9913 | 133 | 124 | 106 | 124
BEAU11 | SHIN11 | 60.87 | 2.03 | Composite | 5.5872 | 13.815 | 5.5339 | 133 | 124 | 106 | 124
BEAU11 | KNOC11 | 16.75 | 0.76 | Composite | 1.5653 | 3.9062 | 1.9356 | 133 | 124 | 106 | 124
BEAU11 | SHIN11 | 60.87 | 2 | Composite | 5.5863 | 13.8123 | 5.4941 | 126 | 117 | 101 | 117
BEAU21 | FASN2Q | 25.3 | 0 | OHL | 0.0687 | 0.9878 | 7.3866 | 1905 | 1839 | 1705 | 1839
BEAU21 | KNOC21 | 16.8 | 1.47 | Composite | 0.0989 | 0.7086 | 13.1339 | 931 | 881 | 791 | 881
BEAU21 | KNOC21 | 16.8 | 1.29 | Composite | 0.0986 | 0.7042 | 12.1075 | 931 | 881 | 791 | 881
BEAU21 | FYRI2K | 30.5 | 0 | OHL | 0.1893 | 1.5394 | 6.6548 | 702 | 665 | 599 | 665
BEAU21 | FYRI2J | 30.5 | 0 | OHL | 0.1893 | 1.5394 | 6.6548 | 702 | 665 | 599 | 665
BEAU4- | FAUG41 | 48.6 | 0 | OHL | 0.0624 | 0.8968 | 30.0204 | 2771 | 2674 | 2480 | 2674
BEIN1- | MILW1A | 2.8 | 0 | OHL | 0.1937 | 0.6596 | 0.1351 | 270 | 265 | 260 | 265
BEIN1- | CEAN1Q | 0.87 | 0 | OHL | 0.0602 | 0.2049 | 0.042 | 270 | 265 | 260 | 265
BERB2Q | BLHI21 | 46.26 | 0 | OHL | 0.2661 | 1.8527 | 13.0844 | 934 | 881 | 791 | 881
BERB2Q | KNOC21 | 43.1 | 0 | OHL | 0.2703 | 1.8816 | 13.2881 | 934 | 881 | 791 | 881
BHLA1- | GLEN1- | 0 | 7.8 | Cable | 0.1425 | 0.6104 | 28.363 | 208 | 187 | 187 | 187
BLHI11 | DORE1K | 23.4 | 0.08 | Composite | 1.1691 | 5.1991 | 1.3433 | 203 | 176 | 176 | 176
BLHI11 | DORE1J | 23.4 | 0.06 | Composite | 1.1688 | 5.197 | 1.3118 | 203 | 176 | 176 | 176
BLHI11 | MACD1R | 37.77 | 3.26 | Composite | 3.4652 | 8.6754 | 6.653 | 133 | 124 | 106 | 124
BLHI11 | MACD1Q | 37.8 | 3.26 | Composite | 3.4679 | 8.6823 | 6.6545 | 133 | 124 | 106 | 124
BLHI21 | DAAS2- | 32.67 | 0 | OHL | 0.19 | 1.3225 | 9.3396 | 934 | 881 | 791 | 881
BLHI21 | CAIN2- | 9.77 | 0 | OHL | 0.0562 | 0.3913 | 2.7634 | 934 | 881 | 791 | 881
BLHI21 | KINT21 | 50.85 | 0 | OHL | 0.2926 | 2.0366 | 14.3827 | 934 | 881 | 791 | 881
BLHI21 | KEIT2R | 0 | 2.49 | Cable | 0.0067 | 0.0455 | 14.2571 | 585 | 546 | 546 | 546
BLHI21 | KEIT2Q | 0 | 2.41 | Cable | 0.0065 | 0.0441 | 13.7991 | 585 | 546 | 546 | 546
BLHI41 | MOWO41 | 0 | 3 | Cable | 0 | 0.0098 | 0.0323 | 22.7026 | 470 | 470 | 470
BLHI41 | MOWO41 | 0 | 3 | Cable | 0 | 0.0098 | 0.0323 | 22.7026 | 470 | 470 | 470
BLHI41 | ROTI41 | 35.4 | 0 | OHL | 0.0708 | 0.6971 | 20.3565 | 1995 | 1926 | 1788 | 1926
BLHI41 | ROTI41 | 35.4 | 0 | OHL | 0.0708 | 0.6971 | 20.3565 | 1995 | 1926 | 1788 | 1926
BOAG1Q | TOMT11 | 19.19 | 5.83 | Composite | 1.3653 | 5.1398 | 9.1417 | 213 | 190 | 190 | 190
BOAG1Q | GLFA1- | 24.82 | 8.4 | Composite | 2.468 | 6.4866 | 11.7598 | 126 | 117 | 101 | 117
BOAG1R | TOMT11 | 19.19 | 5.84 | Composite | 1.3655 | 5.141 | 9.1556 | 213 | 190 | 190 | 190
BONB2J | BRCW2K | 10.1 | 0 | OHL | 0.0274 | 0.3943 | 2.9488 | 1905 | 1839 | 1705 | 1839
BONB4- | MELG41 | 126.483 | 0 | OHL | 0.1623 | 2.334 | 78.1291 | 2771 | 2674 | 2480 | 2674
BRCW2J | KINA21 | 59.185 | 0 | OHL | 0.1607 | 2.3107 | 17.2798 | 1905 | 1839 | 1705 | 1839
BREC1Q | BRID1J | 5.1 | 0 | OHL | 0.5358 | 1.1593 | 0.2548 | 112 | 104 | 90 | 104
BREC1Q | FIDD11 | 29.85 | 0.55 | Composite | 3.1469 | 6.4992 | 2.3331 | 112 | 104 | 90 | 104
BREC1R | BRID1K | 5.1 | 0 | OHL | 0.5358 | 1.1593 | 0.2548 | 112 | 104 | 90 | 104
BROA1Q | QUOI1Q | 63.4 | 0 | OHL | 8.0463 | 14.7684 | 3.1158 | 99 | 92 | 79 | 92
BROA1Q | EDIN1- | 44.9 | 0 | OHL | 5.679 | 9.8631 | 2.3388 | 99 | 92 | 79 | 92
BROR1- | BROR1A | 1.16 | 0 | OHL | 0.1 | 0.254 | 0.0545 | 133 | 124 | 106 | 124
BROR1A | DUBE1- | 38.56 | 0 | OHL | 3.4959 | 8.6661 | 1.9516 | 126 | 117 | 101 | 117
BROR1A | LOCB11 | 25.74 | 0.28 | Composite | 2.3529 | 5.8381 | 1.6798 | 126 | 117 | 101 | 117
BUMU1Q | CHAR11 | 42.2 | 0 | OHL | 3.8238 | 9.4121 | 2.1497 | 133 | 124 | 106 | 124
BUMU1R | GRIF1S | 24.65 | 8.62 | Composite | 2.4857 | 6.3104 | 11.4645 | 133 | 124 | 106 | 124
CAAD1Q | CRSS11 | 13.08 | 0 | OHL | 0.3019 | 2.6267 | 0.7513 | 448 | 430 | 398 | 430
CAAD1R | CRSS11 | 13.08 | 0 | OHL | 0.3019 | 2.6267 | 0.7513 | 448 | 430 | 398 | 430
CAIN2- | KINT21 | 41.08 | 0 | OHL | 0.2363 | 1.6453 | 11.6193 | 934 | 881 | 791 | 881
CASS1Q | DLCH11 | 25.314 | 0 | OHL | 2.3762 | 6.2502 | 1.2558 | 133 | 124 | 106 | 124
CHAR11 | COUA1A | 3.9 | 0 | OHL | 0.1526 | 0.825 | 0.2107 | 229 | 211 | 183 | 211
CHAR11 | COUA1B | 3.9 | 0 | OHL | 0.1526 | 0.825 | 0.2107 | 229 | 211 | 183 | 211
CHAR1S | GLAG1S | 1.4 | 0.91 | Composite | 0.141 | 0.3602 | 1.7109 | 130 | 120 | 120 | 120
CHAR1S | LYND1Q | 1.9 | 0 | OHL | 0.1722 | 0.4238 | 0.0968 | 126 | 117 | 101 | 117
CHAR1S | CHAR11 | 0 | 1 | Cable | 0 | 0 | 0.0005 | 126 | 117 | 101 | 117
CHAR1T | GLAG1N | 1.4 | 0.91 | Composite | 0.141 | 0.3602 | 1.7109 | 130 | 120 | 120 | 120
CHAR1T | LYND1R | 1.9 | 0 | OHL | 0.1722 | 0.4238 | 0.0968 | 126 | 117 | 101 | 117
CHAR1T | CHAR11 | 0 | 1 | Cable | 0 | 0 | 0.0005 | 126 | 117 | 101 | 117
CLAC1Q | SLOY11 | 13.05 | 1.37 | Composite | 1.254 | 2.953 | 2.587 | 133 | 124 | 106 | 124
CLAC1Q | INVE11 | 8.4 | 0 | OHL | 0.7612 | 1.8869 | 0.4249 | 126 | 117 | 101 | 117
CLAY1Q | WIOW1Q | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.8968 | 156 | 129 | 129 | 129
CLAY1Q | REDM1Q | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLAY1T | WIOW1R | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.8968 | 156 | 129 | 129 | 129
CLAY1T | REDM1R | 0 | 4.8 | Cable | 0.19 | 0.28 | 9.82 | 120 | 100 | 100 | 100
CLUN1Q | CLUN1S | 0.34 | 0 | OHL | 0.0308 | 0.0764 | 0.0172 | 126 | 117 | 101 | 117
CLUN1R | CLUN1T | 0.34 | 0 | OHL | 0.0308 | 0.0764 | 0.0172 | 126 | 117 | 101 | 117
CLUN1S | COUA1N | 38.1 | 0 | OHL | 1.9019 | 8.3336 | 2.0059 | 242 | 229 | 209 | 229
CLUN1S | ERRO11 | 15.4 | 0 | OHL | 1.3955 | 3.4593 | 0.779 | 126 | 117 | 101 | 117
CLUN1T | COUA1S | 38.1 | 0 | OHL | 1.9019 | 8.3336 | 2.0059 | 242 | 229 | 209 | 229
CLUN1T | ERRO11 | 15.4 | 0 | OHL | 1.3955 | 3.4593 | 0.779 | 126 | 117 | 101 | 117
COGA1- | FARI1J | 13.9 | 4.11 | Composite | 0.7576 | 3.1671 | 6.9378 | 228 | 193 | 193 | 193
CONN1J | STRW1- | 11.98 | 0.95 | Composite | 0.6221 | 2.5859 | 2.1934 | 200 | 178 | 178 | 178
CONN2Q | DOUN21 | 10.34 | 0 | OHL | 0.0642 | 0.5219 | 2.2561 | 702 | 665 | 599 | 665
CONN2Q | LOCB21 | 76.34 | 0 | OHL | 0.4737 | 3.8531 | 16.6568 | 702 | 665 | 599 | 665
CONN2R | DOUN21 | 10.34 | 0 | OHL | 0.0642 | 0.5219 | 2.2561 | 702 | 665 | 599 | 665
CONN2R | GORW2- | 47.76 | 0 | OHL | 0.2964 | 2.4119 | 10.4171 | 702 | 665 | 599 | 665
CORI11 | LUIC1A | 10.06 | 0 | OHL | 0.2389 | 2.2548 | 0.5466 | 464 | 446 | 414 | 446
CORI11 | LUIC1B | 10.05 | 0 | OHL | 0.2408 | 2.2728 | 0.5507 | 464 | 446 | 414 | 446
CORI11 | MOSS1A | 1.45 | 0.71 | Composite | 0.0939 | 0.3834 | 0.9158 | 126 | 117 | 117 | 117
CORI11 | MOSS1B | 1.45 | 0.63 | Composite | 0.0915 | 0.3759 | 0.8212 | 126 | 117 | 117 | 117
COUA1A | COUA1S | 14.6 | 0 | OHL | 0.7289 | 3.1936 | 0.7686 | 242 | 229 | 209 | 229
COUA1A | TEAL11 | 5.6 | 0 | OHL | 0.2191 | 1.1846 | 0.3025 | 229 | 212 | 183 | 212
COUA1B | COUA1N | 14.6 | 0 | OHL | 0.7289 | 3.1936 | 0.7686 | 242 | 229 | 209 | 229
COUA1B | TEAL11 | 5.6 | 0 | OHL | 0.2191 | 1.1846 | 0.3025 | 229 | 212 | 183 | 212
CRAI11 | REDM1R | 6.8 | 0 | OHL | 0.4795 | 1.4826 | 0.3548 | 157 | 146 | 126 | 146
CRAI11 | REDM1Q | 6.8 | 0 | OHL | 0.4795 | 1.4826 | 0.3548 | 157 | 146 | 126 | 146
CRAI11 | KINT11 | 16.4 | 1.37 | Composite | 0.86 | 3.6999 | 2.6736 | 148 | 137 | 137 | 137
CRAI11 | KINT11 | 16.4 | 1.36 | Composite | 0.8596 | 3.6993 | 2.6604 | 148 | 137 | 137 | 137
CRAI11 | TARL1A | 4.7 | 0 | OHL | 0.4259 | 1.0557 | 0.2378 | 133 | 124 | 106 | 124
CRAI11 | TARL1B | 4.7 | 0 | OHL | 0.4259 | 1.0557 | 0.2378 | 133 | 124 | 106 | 124
CRAI11 | WOHI1R | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAI11 | WOHI1Q | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120
CRAR1R | PORA11 | 13.72 | 0 | OHL | 0.2155 | 2.2533 | 0.9486 | 741 | 709 | 659 | 709
CRAR1R | INVE11 | 22.58 | 0 | OHL | 0.3547 | 3.7085 | 1.5611 | 741 | 709 | 659 | 709
CREA1- | DLCH11 | 20.6 | 1.44 | Composite | 1.043 | 4.3687 | 3.314 | 242 | 229 | 209 | 229
CRSS11 | PORA1A | 44.7 | 0 | OHL | 0.7021 | 7.3414 | 3.0905 | 741 | 709 | 659 | 709
CRSS12 | PORA11 | 44.7 | 0 | OHL | 0.7021 | 7.3414 | 3.0905 | 741 | 709 | 659 | 709
CRSS2A | HUNN2C | 0 | 39.71 | Cable | 0.6223 | 1.1986 | 81.312 | 240 | 240 | 240 | 240
CRSS2B | HUNN2D | 0 | 40.16 | Cable | 0.6335 | 1.2235 | 82.8234 | 240 | 240 | 240 | 240
CULL1A | CULL1- | 0.26 | 0 | OHL | 0.0236 | 0.06 | 0.0129 | 133 | 124 | 106 | 124
CULL1A | DEAN1Q | 9 | 0 | OHL | 0.8178 | 2.0781 | 0.4461 | 133 | 124 | 106 | 124
DAAS2- | KNOC21 | 56.32 | 0 | OHL | 0.3465 | 2.4118 | 17.033 | 934 | 881 | 791 | 881
DLCH11 | LOCB11 | 17 | 0.83 | Composite | 0.4024 | 3.4774 | 2.4655 | 373 | 373 | 373 | 373
DLCH11 | LOCB11 | 17 | 0.92 | Composite | 0.4035 | 3.4843 | 2.6269 | 373 | 373 | 373 | 373
DLCH11 | LAIR1Q | 4.52 | 0 | OHL | 0.4097 | 1.0644 | 0.2192 | 133 | 124 | 106 | 124
DOUN11 | LIMK1- | 4.85 | 1.05 | Composite | 0.2574 | 1.1028 | 2.0714 | 203 | 203 | 203 | 203
DOUN21 | THUS21 | 15.4 | 0 | OHL | 0.0819 | 0.8188 | 3.3263 | 967 | 929 | 862 | 929
DOUN21 | THUS21 | 15.4 | 0 | OHL | 0.0819 | 0.8188 | 3.3263 | 967 | 929 | 862 | 929
DUBE1- | MYBS1R | 20.84 | 0 | OHL | 1.8884 | 4.6812 | 1.0542 | 126 | 117 | 101 | 117
DUDH1Q | MILC1T | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUDH1Q | GLAG1S | 0 | 1.95 | Cable | 0.0585 | 0.115 | 2.73 | 124 | 114 | 114 | 114
DUDH1R | MILC1V | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 113 | 113 | 113
DUDH1R | GLAG1N | 0 | 1.95 | Cable | 0.0585 | 0.115 | 2.73 | 124 | 114 | 114 | 114
DUGR1Q | EDIN1- | 9 | 0 | OHL | 1.1383 | 1.977 | 0.4688 | 99 | 92 | 79 | 92
DUNM1- | FARI1K | 6 | 4.07 | Composite | 0.3635 | 1.5267 | 6.5106 | 228 | 193 | 193 | 193
DUNO1Q | WHTB1S | 18.1 | 0 | OHL | 2.2898 | 4.0762 | 0.912 | 99 | 92 | 79 | 92
DUNO1R | WHTB1T | 18.1 | 0 | OHL | 2.2898 | 4.0762 | 0.912 | 99 | 92 | 79 | 92
DYCE1J | KINT11 | 10.17 | 1.9 | Composite | 0.6713 | 2.3094 | 3.7468 | 145 | 131 | 116 | 131
DYCE1K | KINT11 | 10.17 | 1.9 | Composite | 0.6713 | 2.3094 | 3.7468 | 150 | 141 | 141 | 141
ELGI1Q | NAIR1Q | 33.9 | 1.8 | Composite | 1.7277 | 7.4428 | 3.2007 | 242 | 229 | 209 | 229
ELGI1Q | KEIT11 | 27.4 | 0 | OHL | 1.368 | 5.9739 | 1.4473 | 242 | 229 | 209 | 229
ELGI1R | NAIR1R | 33.9 | 1.8 | Composite | 1.7277 | 7.4428 | 3.2007 | 242 | 229 | 209 | 229
ELGI1R | KEIT11 | 27.4 | 0 | OHL | 1.368 | 5.9739 | 1.4473 | 242 | 229 | 209 | 229
ERRO11 | TUMM1J | 0 | 1.33 | Cable | 0.0137 | 0.0977 | 2.5681 | 301 | 279 | 279 | 279
ERRO11 | TUMM1K | 0 | 1.3 | Cable | 0.0134 | 0.0955 | 2.5101 | 301 | 279 | 279 | 279
ERRO11 | GRIF1S | 22.61 | 3.37 | Composite | 2.1516 | 5.3614 | 5.1 | 133 | 124 | 106 | 124
ERRO11 | KIIN11 | 36.9 | 0 | OHL | 3.3529 | 8.52 | 1.8289 | 133 | 124 | 106 | 124
ERRO11 | GRIF1T | 22.61 | 3.37 | Composite | 2.1516 | 5.3614 | 5.1 | 133 | 124 | 106 | 124
ERRO11 | TUMB1Q | 1 | 0 | OHL | 0.0906 | 0.2239 | 0.0507 | 126 | 117 | 101 | 117
ERRO11 | TUMB1R | 1 | 0 | OHL | 0.0906 | 0.2239 | 0.0507 | 126 | 117 | 101 | 117
FAAR1Q | TOMT11 | 7.03 | 0.17 | Composite | 0.3546 | 1.5522 | 0.6065 | 111 | 103 | 103 | 103
FAAR1R | TOMT11 | 7.03 | 0.17 | Composite | 0.3546 | 1.5522 | 0.6065 | 111 | 103 | 103 | 103
FARI2J | FOYE2- | 8.4 | 0 | OHL | 0.0483 | 0.3306 | 2.4235 | 934 | 881 | 791 | 881
FARI2J | KNOC21 | 14.9 | 0 | OHL | 0.0857 | 0.5864 | 4.2989 | 934 | 881 | 791 | 881
FARI2K | FOYE2- | 8.4 | 0 | OHL | 0.0483 | 0.3306 | 2.4235 | 934 | 881 | 791 | 881
FARI2K | KNOC21 | 14.9 | 0 | OHL | 0.0857 | 0.5864 | 4.2989 | 934 | 881 | 791 | 881
FASN2R | FAUG2R | 25.4 | 0 | OHL | 0.0689 | 0.9917 | 7.4157 | 1905 | 1839 | 1705 | 1839
FAUG11 | QUOI1Q | 28.2 | 0.595 | Composite | 1.4122 | 5.8889 | 3.3379 | 484 | 458 | 418 | 458
FAUG11 | GLEN1- | 11.29 | 0.36 | Composite | 0.7806 | 2.5655 | 0.5636 | 270 | 265 | 260 | 265
FAUG11 | MILW1A | 12.19 | 0.34 | Composite | 0.8429 | 2.7775 | 0.6071 | 270 | 265 | 260 | 265
FAUG11 | FWIL1R | 43.4 | 0.17 | Composite | 3.0015 | 9.574 | 2.5317 | 255 | 247 | 237 | 247
FAUG11 | FWIL1A | 8.5 | 0.25 | Composite | 0.5902 | 1.8877 | 0.8859 | 255 | 247 | 237 | 247
FAUG11 | GLDO1G | 0 | 7.149 | Cable | 0.3214 | 0.6887 | 6.7149 | 136 | 126 | 126 | 126
FAUG2Q | TUMM2J | 77.2 | 0 | OHL | 0.2096 | 3.014 | 22.5395 | 1905 | 1839 | 1705 | 1839
FAUG41 | MELG41 | 24.01 | 0 | OHL | 0.0308 | 0.4431 | 14.8311 | 2771 | 2674 | 2480 | 2674
FERO1- | TAYN1A | 5.24 | 0 | OHL | 0.6451 | 1.1203 | 0.2657 | 99 | 92 | 79 | 92
FETT21 | KINT21 | 32.15 | 0 | OHL | 0.145 | 1.3343 | 8.727 | 1096 | 1029 | 924 | 1029
FETT21 | KINT21 | 32.15 | 0 | OHL | 0.145 | 1.3343 | 8.727 | 1096 | 1029 | 924 | 1029
FIDD1Q | TARL1B | 25 | 0.55 | Composite | 2.6452 | 6.016 | 2.2253 | 112 | 104 | 90 | 104
FINL1Q | KIIN11 | 2.1 | 0 | OHL | 0.1905 | 0.5022 | 0.1003 | 133 | 124 | 106 | 124
FOYE2J | FOYE2- | 0 | 1 | Cable | 0.01 | 0.024 | 6.22 | 400 | 400 | 400 | 400
FRAS1Q | STRI1A | 10.1 | 0 | OHL | 0.9152 | 2.2687 | 0.5109 | 126 | 117 | 101 | 117
FRAS1R | STRI1B | 10.1 | 0 | OHL | 0.9152 | 2.2687 | 0.5109 | 126 | 117 | 101 | 117
FWIL1A | FWIL1Q | 34.9 | 0 | OHL | 2.4122 | 7.6909 | 1.7898 | 255 | 247 | 237 | 247
FWIL1A | INGA1Q | 2.4 | 0.13 | Composite | 0.2176 | 0.5738 | 0.1148 | 133 | 124 | 106 | 124
FWIL1R | KILO1- | 24.5 | 0 | OHL | 2.2221 | 5.7465 | 1.1975 | 161 | 154 | 141 | 154
FYRI2J | LOCB21 | 35.93 | 0 | OHL | 0.223 | 1.8135 | 7.8396 | 702 | 665 | 599 | 665
FYRI2K | LOCB21 | 35.93 | 0 | OHL | 0.223 | 1.8135 | 7.8396 | 702 | 665 | 599 | 665
GARB1Q | SLOY11 | 14.9 | 0.13 | Composite | 1.3569 | 3.3548 | 0.9351 | 133 | 124 | 106 | 124
GARB1R | SLOY11 | 14.9 | 0.15 | Composite | 1.358 | 3.3561 | 0.963 | 133 | 124 | 106 | 124
GARB1S | SLOY11 | 14.9 | 0.12 | Composite | 1.3559 | 3.3543 | 0.9211 | 133 | 124 | 106 | 124
GARB1T | SLOY11 | 14.9 | 0.16 | Composite | 1.3585 | 3.3567 | 0.9769 | 133 | 124 | 106 | 124
GLFA1- | KEIT11 | 29.6 | 0 | OHL | 2.6896 | 6.8345 | 1.4671 | 126 | 117 | 101 | 117
GLRB2- | TEAL21 | 38.8 | 0 | OHL | 0.175 | 1.5935 | 10.6476 | 1096 | 1029 | 924 | 1029
GORW2- | STRB2- | 10.3 | 0 | OHL | 0.0639 | 0.5199 | 2.2474 | 702 | 665 | 599 | 665
GRUB1Q | MOSS1A | 2.73 | 0 | OHL | 0.1363 | 0.5971 | 0.1437 | 224 | 212 | 190 | 212
GRUB1R | MOSS1B | 2.73 | 0 | OHL | 0.1363 | 0.5971 | 0.1437 | 224 | 212 | 190 | 212
INNE1J | KNOC11 | 0 | 4.57 | Cable | 0.1065 | 0.3882 | 6.5056 | 155 | 150 | 150 | 150
INNE1L | KNOC11 | 0 | 4.48 | Cable | 0.1044 | 0.3805 | 6.3775 | 155 | 150 | 150 | 150
INNE1Q | NAIR1Q | 28.3 | 1.5 | Composite | 1.4286 | 6.2654 | 3.8105 | 242 | 229 | 209 | 229
INNE1R | NAIR1R | 28.3 | 1.5 | Composite | 1.4286 | 6.2654 | 3.8105 | 242 | 229 | 209 | 229
INVE11 | SLOY11 | 21.4 | 1.28 | Composite | 2.0074 | 4.9202 | 2.861 | 126 | 117 | 101 | 117
INVE11 | TAYN1A | 16.29 | 0 | OHL | 2.0608 | 3.6685 | 0.8208 | 99 | 92 | 79 | 92
INVE11 | NANT1A | 15.1 | 0 | OHL | 1.9103 | 3.4005 | 0.7609 | 99 | 92 | 79 | 92
INVR11 | INVR1A | 5.55 | 0.27 | Composite | 0.517 | 1.2631 | 0.6574 | 133 | 124 | 106 | 124
INVR11 | SLOY11 | 10.72 | 0.55 | Composite | 1.0001 | 2.4415 | 1.3095 | 133 | 124 | 106 | 124
INVR11 | KIIN11 | 24.27 | 9.31 | Composite | 2.5006 | 6.3589 | 12.1336 | 130 | 124 | 106 | 124
INVR11 | KIIN11 | 24.27 | 9.31 | Composite | 2.5006 | 6.3589 | 12.1336 | 130 | 124 | 106 | 124
INVR1A | SLOY11 | 5.17 | 0.28 | Composite | 0.4831 | 1.1784 | 0.6521 | 133 | 124 | 106 | 124
KEIC1- | KEIT11 | 0 | 0.31 | Cable | 0.0043 | 0.0315 | 0.4989 | 160 | 160 | 160 | 160
KERG11 | VIKE1P | 0 | 0.097 | Cable | 0.0018 | 0.0068 | 0.1142 | 188 | 188 | 188 | 188
KERG11 | VIKE1R | 0 | 0.117 | Cable | 0.0021 | 0.0082 | 0.1377 | 188 | 188 | 188 | 188
KERG11 | VIKE1Q | 0 | 0.153 | Cable | 0.0028 | 0.0107 | 0.1801 | 188 | 188 | 188 | 188
KERG11 | VIKE1S | 0 | 0.182 | Cable | 0.0033 | 0.0127 | 0.2142 | 188 | 188 | 188 | 188
KIIN11 | LOCH1- | 2.4 | 0 | OHL | 0.2177 | 0.5739 | 0.1147 | 133 | 124 | 106 | 124
KIIN11 | SFIL1Q | 17.03 | 4.57 | Composite | 1.6926 | 4.5178 | 6.1671 | 130 | 124 | 106 | 124
KINA21 | TUMM2K | 4.008 | 0 | OHL | 0.0109 | 0.1565 | 1.1702 | 1905 | 1839 | 1705 | 1839
KINT11 | TARL1A | 15.55 | 0.12 | Composite | 1.6375 | 3.6321 | 0.7615 | 112 | 104 | 90 | 104
KINT21 | KINT2B | 0 | 1 | Cable | 0 | 0 | 0.0024 | 9999 | 9999 | 9999 | 9999
KINT21 | KINT2C | 0 | 1 | Cable | 0 | 0 | 0.0024 | 9999 | 9999 | 9999 | 9999
KINT21 | PERS2R | 28.2 | 0 | OHL | 0.1272 | 1.1707 | 7.6537 | 1096 | 1029 | 924 | 1029
KINT21 | PEHE21 | 50.4 | 0 | OHL | 0.2273 | 2.0919 | 13.6803 | 1096 | 1029 | 924 | 1029
KINT21 | TEAL21 | 100.6 | 0 | OHL | 0.546 | 5.1177 | 22.7033 | 695 | 643 | 548 | 643
KINT21 | TEAL21 | 100.6 | 0 | OHL | 0.546 | 5.1177 | 22.7033 | 695 | 643 | 548 | 643
KINT2A | KINT21 | 0 | 1 | Cable | 0 | 0 | 0.0024 | 9999 | 9999 | 9999 | 9999
KINT41 | ROTI41 | 23.2 | 0 | OHL | 0.0464 | 0.4569 | 13.341 | 1995 | 1926 | 1788 | 1926
KINT41 | ROTI41 | 23.2 | 0 | OHL | 0.0464 | 0.4569 | 13.341 | 1995 | 1926 | 1788 | 1926
KIOR1A | KIOR1- | 0.48 | 0.21 | Composite | 0.0435 | 0.1149 | 0.023 | 133 | 124 | 106 | 124
KNOC21 | TOMT2J | 18.6 | 0.51 | Composite | 0.1002 | 1.0047 | 7.0346 | 810 | 762 | 686 | 762
KNOC21 | TOMT2K | 18.6 | 0.17 | Composite | 0.0994 | 0.9942 | 5.0232 | 810 | 762 | 686 | 762
LIMK1- | LIMK1A | 4.9 | 0 | OHL | 0.245 | 1.014 | 0.652 | 203 | 193 | 176 | 193
LOCB11 | MYBS1Q | 85.3 | 0.38 | Composite | 7.74 | 19.1943 | 4.818 | 126 | 117 | 101 | 117
LOCB11 | SHIN11 | 7.73 | 0.66 | Composite | 0.7762 | 1.9379 | 1.3884 | 126 | 117 | 101 | 117
LOCB11 | SHIN11 | 7.7 | 0.73 | Composite | 0.7779 | 1.9432 | 1.4679 | 126 | 117 | 101 | 117
LOCB21 | STRB2- | 18.59 | 0.26 | Composite | 0.1182 | 0.9629 | 5.4342 | 702 | 651 | 599 | 651
LUIC1A | ORRI1A | 5.33 | 0 | OHL | 0.1277 | 1.2057 | 0.2919 | 464 | 446 | 414 | 446
LUIC1A | LUIC1Q | 0.3 | 0 | OHL | 0.0074 | 0.0702 | 0.0168 | 464 | 446 | 414 | 446
LUIC1B | ORRI1B | 5.35 | 0 | OHL | 0.1246 | 1.1764 | 0.2852 | 464 | 446 | 414 | 446
LUIC1B | LUIC1R | 0.32 | 0 | OHL | 0.006 | 0.0566 | 0.0137 | 464 | 446 | 414 | 446
LUNA1Q | TEAL11 | 17.9 | 0 | OHL | 0.7004 | 3.7864 | 0.967 | 183 | 160 | 149 | 160
LUNA1R | TEAL11 | 17.9 | 0 | OHL | 0.7004 | 3.7864 | 0.967 | 183 | 160 | 149 | 160
MELG11 | STRL1- | 0 | 10 | Cable | 0.0752 | 0.8058 | 18.175 | 286 | 277 | 277 | 277
MILC1T | TEAL11 | 6.8 | 0 | OHL | 0.2661 | 1.4416 | 0.3666 | 183 | 160 | 149 | 160
MILC1V | TEAL11 | 6.8 | 0 | OHL | 0.2661 | 1.4416 | 0.3666 | 183 | 160 | 149 | 160
MILW1A | MILW1- | 1.3 | 0 | OHL | 0.0898 | 0.2731 | 0.0705 | 270 | 265 | 260 | 265
MORF4- | NEDE41 | 0 | 0.06 | Cable | 0.0027 | 0.001 | 0.27 | 398 | 398 | 398 | 398
MORF4- | NEDE41 | 0 | 0.1 | Cable | 0.0043 | 0.002 | 0.42 | 398 | 398 | 398 | 398
MORF4- | NEDE41 | 0 | 0.15 | Cable | 0.001 | 0.003 | 0.67 | 398 | 398 | 398 | 398
MOSS1A | MOSS1R | 0.21 | 0 | OHL | 0.019 | 0.0498 | 0.0102 | 133 | 124 | 106 | 124
MOSS1B | MOSS1Q | 0.21 | 0 | OHL | 0.019 | 0.0498 | 0.0102 | 133 | 124 | 106 | 124
MYBS1Q | SPIT11 | 3.99 | 0 | OHL | 0.3615 | 0.8963 | 0.2018 | 126 | 117 | 101 | 117
MYBS1R | SPIT11 | 3.99 | 0 | OHL | 0.3615 | 0.8963 | 0.2018 | 126 | 117 | 101 | 117
MYBS1S | SPIT11 | 5 | 0 | OHL | 0.1154 | 1.0041 | 0.2872 | 464 | 446 | 414 | 446
MYBS1T | SPIT11 | 5 | 0 | OHL | 0.1154 | 1.0041 | 0.2872 | 464 | 446 | 414 | 446
NANT1A | NANT1- | 4.2 | 0 | OHL | 0.5317 | 1.0297 | 0.1955 | 99 | 92 | 79 | 92
NANT1A | TAYN1Q | 7.6 | 0 | OHL | 0.9615 | 1.7124 | 0.3828 | 99 | 92 | 79 | 92
NEDE41 | ROTI41 | 17.3 | 0 | OHL | 0.0346 | 0.3407 | 9.9482 | 1995 | 1926 | 1788 | 1926
NEDE41 | PEHE41 | 30.04 | 0 | OHL | 0.0601 | 0.5916 | 17.2743 | 1995 | 1926 | 1788 | 1926
NEDE41 | ROTI41 | 17.3 | 0 | OHL | 0.0346 | 0.3407 | 9.9482 | 1995 | 1926 | 1788 | 1926
NEDE41 | PEHE41 | 30.04 | 0 | OHL | 0.0601 | 0.5916 | 17.2743 | 1995 | 1926 | 1788 | 1926
ORRI1A | ORRI1Q | 0.08 | 0 | OHL | 0.0021 | 0.0196 | 0.0048 | 464 | 446 | 414 | 446
ORRI1B | ORRI1R | 0.21 | 0 | OHL | 0.0049 | 0.0467 | 0.0109 | 464 | 446 | 414 | 446
PEHE11 | PEHG1A | 6.03 | 0.77 | Composite | 0.3142 | 1.498 | 1.5553 | 203 | 176 | 176 | 176
PEHE11 | PEHG1B | 6.03 | 0.77 | Composite | 0.3142 | 1.498 | 1.5553 | 203 | 176 | 176 | 176
PEHE11 | SFER11 | 11.3 | 3 | Composite | 0.6686 | 2.6356 | 4.7266 | 186 | 186 | 186 | 186
PEHE21 | PERS2Q | 47.6 | 0 | OHL | 0.2147 | 1.9755 | 12.9208 | 1096 | 1029 | 924 | 1029
PEHE21 | PEHE23 | 0 | 1 | Cable | 0 | 0 | 0.0024 | 776 | 776 | 776 | 776
PEHE21 | PEHE24 | 0 | 1 | Cable | 0 | 0 | 0.0024 | 313 | 313 | 313 | 313
PEHE21 | PEHE25 | 0 | 1 | Cable | 0 | 0 | 0.0024 | 313 | 313 | 313 | 313
PEHE21 | PEHE26 | 0 | 1 | Cable | 0 | 0 | 0.0024 | 313 | 313 | 313 | 313
PEHE22 | PEHE21 | 0 | 1 | Cable | 0 | 0 | 0.0024 | 776 | 776 | 776 | 776
PEHG1A | SFER1K | 6.1 | 0 | OHL | 0.3046 | 1.3343 | 0.3211 | 242 | 229 | 209 | 229
PEHG1B | SFER1J | 6.1 | 0 | OHL | 0.3046 | 1.3343 | 0.3211 | 242 | 229 | 209 | 229
PEHG1Q | PEHG1A | 1.8 | 0 | OHL | 0.0899 | 0.3937 | 0.0948 | 242 | 229 | 209 | 229
PEHG1R | PEHG1B | 1.8 | 0 | OHL | 0.0899 | 0.3937 | 0.0948 | 242 | 229 | 209 | 229
PERS11 | PERS12 | 0 | 1 | Cable | 0 | 0 | 0.0005 | 9999 | 9999 | 9999 | 9999
PERS11 | WIOW1R | 0 | 3.7 | Cable | 0.0835 | 0.2208 | 5.1039 | 156 | 129 | 129 | 129
PERS11 | WIOW1Q | 0 | 3.7 | Cable | 0.0835 | 0.2208 | 5.1039 | 156 | 129 | 129 | 129
PORA11 | PORA1R | 6.14 | 0 | OHL | 0.7766 | 1.383 | 0.3092 | 99 | 92 | 79 | 92
PORA1A | PORA1Q | 6.14 | 0 | OHL | 0.7766 | 1.383 | 0.3092 | 99 | 92 | 79 | 92
QUOI1Q | QUOI1- | 1.6 | 0 | OHL | 0.1451 | 0.3741 | 0.0783 | 151 | 142 | 128 | 142
RANN1Q | TUMB1Q | 23.8 | 0 | OHL | 2.1566 | 5.3242 | 1.2091 | 126 | 117 | 101 | 117
RANN1R | TUMB1R | 23.8 | 0 | OHL | 2.1566 | 5.3247 | 1.209 | 126 | 117 | 101 | 117
SFEE1A | SFEG1S | 0.39 | 0 | OHL | 0.0353 | 0.0876 | 0.0197 | 126 | 117 | 101 | 117
SFEE1A | SFER11 | 1.71 | 0 | OHL | 0.1549 | 0.3841 | 0.0865 | 126 | 117 | 101 | 117
SFEE1A | SFEE1Q | 0 | 0.27 | Cable | 0.0078 | 0.0293 | 0.3538 | 47 | 47 | 47 | 47
SFEE1B | SFEG1T | 0.39 | 0 | OHL | 0.0353 | 0.0876 | 0.0197 | 126 | 117 | 101 | 117
SFEE1B | SFER11 | 1.71 | 0 | OHL | 0.1549 | 0.3841 | 0.0865 | 126 | 117 | 101 | 117
SFEE1B | SFEE1R | 0 | 0.29 | Cable | 0.0083 | 0.0315 | 0.38 | 47 | 47 | 47 | 47
SFEG1S | SFEV1S | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEG1T | SFEV1T | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135
SFEM1Q | SFER11 | 2.06 | 1.04 | Composite | 0.3817 | 0.5437 | 1.8732 | 133 | 124 | 106 | 124
SFEM1R | SFER11 | 2.06 | 1.04 | Composite | 0.3817 | 0.5437 | 1.8732 | 133 | 124 | 106 | 124
SGRX2- | TEAL21 | 0 | 0.228 | Cable | 0.0008 | 0.0046 | 1.18 | 419 | 419 | 419 | 419
SGRX2- | TEAL21 | 0 | 0.183 | Cable | 0.0006 | 0.0037 | 0.95 | 419 | 419 | 419 | 419
SGRX2- | TEAL21 | 0 | 0.738 | Cable | 0.0025 | 0.015 | 3.83 | 419 | 419 | 419 | 419
SLOY1L | SLOY11 | 0.62 | 0.91 | Composite | 0.0839 | 0.2241 | 1.1472 | 122 | 112 | 106 | 112
SLOY1M | SLOY11 | 0.62 | 0.92 | Composite | 0.0842 | 0.225 | 1.1594 | 122 | 112 | 106 | 112
SLOY1N | SLOY11 | 0.63 | 0.83 | Composite | 0.0823 | 0.2189 | 1.0496 | 122 | 112 | 106 | 112
SLOY1P | SLOY11 | 0.63 | 0.87 | Composite | 0.0835 | 0.2226 | 1.0986 | 122 | 112 | 106 | 112
SPIT21 | THUS21 | 12.1 | 0 | OHL | 0.0644 | 0.6433 | 2.6136 | 967 | 929 | 862 | 929
SPIT21 | THUS21 | 12.1 | 0 | OHL | 0.0644 | 0.6433 | 2.6136 | 967 | 929 | 862 | 929
STRI1A | SFER11 | 6.3 | 0 | OHL | 0.5709 | 1.4151 | 0.3187 | 126 | 117 | 101 | 117
STRI1A | STRI1Q | 7.9 | 0 | OHL | 0.7158 | 1.7746 | 0.3996 | 126 | 117 | 101 | 117
STRI1B | SFER11 | 6.3 | 0 | OHL | 0.5709 | 1.4151 | 0.3187 | 126 | 117 | 101 | 117
STRI1B | STRI1R | 7.9 | 0 | OHL | 0.7158 | 1.7746 | 0.3996 | 126 | 117 | 101 | 117
TARL1B | TARL1K | 34.6 | 0 | OHL | 3.1352 | 7.7721 | 1.7503 | 133 | 124 | 106 | 124
TARL1A | TARL1J | 34.6 | 0 | OHL | 3.1352 | 7.7721 | 1.7503 | 133 | 124 | 106 | 124
TAYN1A | TAYN1R | 6.3 | 0 | OHL | 0.797 | 1.4188 | 0.3175 | 99 | 92 | 79 | 92
TEAL21 | WFIB2- | 38.8 | 0 | OHL | 0.175 | 1.5935 | 10.6476 | 1096 | 1029 | 924 | 1029
THSC2- | THUS21 | 0 | 0.35 | Cable | 0.0021 | 0.0075 | 1.2268 | 100 | 100 | 100 | 100
WIOW1Q | WOHI1R | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147
WIOW1R | WOHI1Q | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147

## B-2-1b
B-2-1b - SPT Circuits for 2025/26
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
AGSF4- | AYRS4- | 0 | 0.1 | Cable | 0.0001 | 0.0013 | 1.1119 | 1247 | 1247 | 1247 | 1247
AREC1- | MAHI1- | 7.615 | 1.613 | Composite | 0.4363 | 1.668 | 2.5345 | 214 | 195 | 195 | 195
AREC3- | GLAP3- | 10.79 | 5.931 | Composite | 10.6428 | 36.9228 | 0.6748 | 40 | 38 | 38 | 38
AUCH2- | MAHI2- | 14.5 | 0 | OHL | 0.109 | 0.8301 | 2.9503 | 570 | 570 | 570 | 570
AUCW1- | HADH1- | 0 | 18 | Cable | 1.83 | 3.88 | 0.96 | 140 | 140 | 140 | 140
AUCW1- | MAYB1- | 0 | 0.07 | Cable | 0 | 0.009 | 0.0682 | 140 | 140 | 140 | 140
AYR-2Q | COYW2S | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 1190 | 1190 | 1190 | 1190
AYR-2R | COYW2T | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 955 | 955 | 955 | 955
AYRS4- | HUNE4- | 0 | 0.9 | Cable | 0.0005 | 0.012 | 10.0073 | 1247 | 1247 | 1247 | 1247
BAGA1Q | BONN1- | 18.3 | 0 | OHL | 0.716 | 3.8726 | 0.9882 | 171 | 152 | 152 | 152
BAGA1Q | DRCR1Q | 4.71 | 3.39 | Composite | 0.5756 | 1.4393 | 2.8779 | 146 | 146 | 146 | 146
BAGA1R | BONN1- | 18.4 | 0 | OHL | 0.72 | 3.8943 | 0.9935 | 171 | 152 | 152 | 152
BAGA1R | DRCR1R | 4.71 | 3.38 | Composite | 0.5752 | 1.4382 | 2.8701 | 146 | 146 | 146 | 146
BAIN1Q | BONN1- | 7.02 | 0.08 | Composite | 0.2761 | 1.4801 | 0.4755 | 114 | 114 | 114 | 114
BAIN1R | BONN1- | 7.02 | 0.28 | Composite | 0.2797 | 1.4992 | 0.7089 | 114 | 114 | 114 | 114
BENB1- | BENB1T | 2.5 | 0 | OHL | 0.1875 | 0.5505 | 0.1315 | 167 | 160 | 148 | 160
BENB1T | BLCW1- | 32.15 | 0.9 | Composite | 1.1801 | 6.5296 | 3.3413 | 199 | 191 | 178 | 191
BENB1T | NECU1B | 4 | 0 | OHL | 0.1038 | 0.7722 | 0.2394 | 482 | 460 | 420 | 460
BERW1Q | ECCL1- | 21.54 | 0.31 | Composite | 1.622 | 4.903 | 1.5274 | 132 | 123 | 106 | 123
BERW1R | ECCL1- | 21.54 | 0.27 | Composite | 1.6213 | 4.8991 | 1.4716 | 132 | 123 | 106 | 123
BLAH1- | DUNH1Q | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 418 | 386 | 386 | 386
BLAH1- | DUNH1R | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 466 | 430 | 418 | 430
BLAH1- | GLGL1Q | 12.6 | 0.375 | Composite | 0.4832 | 2.7239 | 1.1395 | 297 | 281 | 258 | 281
BLAH1- | GLGL1R | 12.6 | 0.375 | Composite | 0.4832 | 2.7239 | 1.1395 | 297 | 281 | 258 | 281
BLAH3B | PLOE3- | 0 | 1.01 | Cable | 0.2795 | 0.8831 | 0.1185 | 40 | 38 | 38 | 38
BLAH3B | PLOE3- | 0 | 1.01 | Cable | 0.2795 | 0.8831 | 0.1185 | 40 | 38 | 38 | 38
BLCW3- | BLKS3- | 0 | 2.801 | Cable | 0.3875 | 1.2246 | 0.6574 | 61.2 | 61.2 | 61.2 | 61.2
BLKL1- | WISH1- | 5.33 | 6.13 | Composite | 0.6542 | 1.8052 | 6.2962 | 161 | 154 | 140 | 154
BLLX1- | LINM1Q | 12.85 | 5.24 | Composite | 1.1339 | 3.1699 | 7.5599 | 132 | 123 | 106 | 123
BONB2J | DENN2- | 19.894 | 0 | OHL | 0.054 | 0.7739 | 5.8126 | 1500 | 1500 | 1500 | 1500
BONB4- | DENN4- | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2976 | 2570 | 2570 | 2508 | 2570
BONN1- | CUMB1Q | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN1- | CUMB1R | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN1- | DENN1- | 8.08 | 0.3 | parallelComposite | 0.1878 | 0.4755 | 1.1901 | 240 | 234 | 202 | 234
BONN1- | STIR1S | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219
BONN1- | STIR1T | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219
BONN2A | DENN2- | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647
BRAP1- | ERSK1Q | 3.17 | 5.4 | Composite | 0.4479 | 1.0975 | 12.4447 | 121 | 110 | 106 | 110
BRAP1- | ERSK1R | 3.45 | 6.23 | Composite | 0.4955 | 1.1727 | 12.9637 | 102 | 79 | 79 | 79
BRAP1- | GOVA1R | 0 | 6.13 | Cable | 0.2168 | 0.45 | 11.0073 | 125 | 113 | 110 | 113
BRAP1- | PAIS1R | 4.52 | 2.19 | Composite | 0.1309 | 0.9964 | 3.6706 | 274 | 274 | 274 | 274
BROT1- | COAL1- | 0 | 3.2 | Cable | 0.0261 | 0.2614 | 5.959 | 293 | 293 | 293 | 293
BROT1- | LINM1Q | 5.774 | 0 | OHL | 0.1373 | 1.3023 | 0.2972 | 266 | 266 | 266 | 266
BROX1Q | CURR1A | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123
BROX1R | CURR1B | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123
BUSB2- | GIFF2Q | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | GIFF2R | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240
BUSB2- | NEIL2- | 20.24 | 0 | OHL | 0.0856 | 0.8267 | 5.625 | 1120 | 1060 | 990 | 1060
BUSB2- | STHA2A | 15.14 | 0 | OHL | 0.064 | 0.6181 | 4.2097 | 1050 | 965 | 880 | 965
CAFA1Q | KEOO1- | 2.58 | 0 | OHL | 0.2337 | 0.5239 | 0.1455 | 132 | 123 | 106 | 123
CATY1Q | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107
CATY1R | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107
CCSS1- | COAL1- | 0 | 6.97 | Cable | 0.10961 | 0.60003 | 11.4841 | 210 | 210 | 210 | 210
CCSS1- | GAWH1Q | 0 | 2.6 | Cable | 0.0409 | 0.2238 | 4.2839 | 210 | 210 | 210 | 210
CCSS3- | CUMH3- | 0 | 2.3 | Cable | 0.3182 | 1.0055 | 0.5398 | 56 | 56 | 56 | 56
CHAP1- | DUMF1- | 26.9 | 0.18 | Composite | 1.0661 | 6.0867 | 1.6344 | 171 | 155 | 155 | 155
CHAP1- | DUMF1- | 26.9 | 0.125 | Composite | 1.065 | 6.0817 | 1.5576 | 171 | 155 | 155 | 155
CHAP1- | ECCF1J | 6.569 | 0.23 | Composite | 0.6009 | 1.515 | 0.651 | 18 | 18 | 18 | 18
CHAP1- | ECCF1K | 6.569 | 0.185 | Composite | 0.6 | 1.5109 | 0.5882 | 21 | 21 | 21 | 21
CHAP1- | GRNA1- | 12.83 | 0.395 | Composite | 0.7959 | 3.0463 | 1.0623 | 132 | 123 | 106 | 123
CHAP1- | GRNA1- | 12.83 | 0.355 | Composite | 0.7947 | 3.0413 | 1.0234 | 132 | 123 | 106 | 123
CHAP1- | HAKB1- | 14.72 | 0 | OHL | 1.535 | 3.472 | 0.754 | 132 | 123 | 106 | 123
CHAS2Q | DALM2Q | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CHAS2R | DALM2R | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186
CLYM2- | DALM2Q | 4.21 | 0 | OHL | 0.019 | 0.1713 | 1.1692 | 750 | 690 | 630 | 690
CLYM2- | DALM2R | 4.21 | 0.093 | Composite | 0.0193 | 0.1737 | 1.8402 | 695 | 560 | 500 | 560
CLYM2- | EERH2- | 8.75 | 0 | OHL | 0.0197 | 0.3069 | 2.8023 | 1500 | 1500 | 1500 | 1500
CLYM2- | EKIL2Q | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | EKIL2R | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060
CLYM2- | LOAN2- | 54.57 | 0 | OHL | 0.1231 | 1.9141 | 17.477 | 1500 | 1500 | 1500 | 1500
CLYN2Q | ELVA2Q | 0 | 6.2 | Cable | 0.032 | 0.174 | 26.956 | 476 | 415 | 415 | 415
CLYS2R | ELVA2R | 0 | 7.17 | Cable | 0.0445 | 0.1289 | 23.8486 | 291 | 245 | 245 | 245
COAB4- | COAL4- | 0 | 1.85 | Cable | 0.0022 | 0.0171 | 20.83 | 556 | 556 | 556 | 556
COAL1A | LINM1R | 5.774 | 3.14 | Composite | 0.2748 | 1.6606 | 2.8754 | 134 | 123 | 123 | 123
COAL1A | MIDM1- | 0 | 14.08 | Cable | 0.3976 | 0.9139 | 17.3414 | 158 | 146 | 146 | 146
COAL1B | CCSS1- | 0 | 6.97 | Cable | 0.10961 | 0.60003 | 11.4841 | 210 | 210 | 210 | 210
COAL1B | CUMW1- | 0 | 11.266 | Cable | 0.3166 | 0.7287 | 15.4075 | 120 | 120 | 120 | 120
COAL1B | DONO1- | 0 | 4.48 | Cable | 0.0874 | 0.4114 | 6.2289 | 211 | 190 | 190 | 190
COAL1B | KYPE1- | 0 | 17.09 | Cable | 0.3286 | 1.5387 | 24.4568 | 194 | 180 | 180 | 180
COAL4- | ELVA4- | 26.71 | 0 | OHL | 0.0467 | 0.5062 | 15.9918 | 2210 | 2130 | 1980 | 2130
COAL4- | STHA4B | 21.73 | 0 | OHL | 0.038 | 0.4118 | 13.0101 | 2210 | 2130 | 1980 | 2130
COAT2Q | NEAR2Q | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156
COAT2R | NEAR2R | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156
COCK2- | KAIM2- | 18.29 | 0 | OHL | 0.0779 | 0.756 | 5.0669 | 1120 | 1060 | 990 | 1060
COCK2- | SMEA2- | 9.51 | 0 | OHL | 0.0405 | 0.3931 | 2.6346 | 1120 | 1060 | 990 | 1060
COCK4Q | ECCL4A | 65.9 | 0 | OHL | 0.135 | 1.4191 | 35.4794 | 1120 | 1060 | 990 | 1060
COCK4R | ECCL4B | 65.89 | 0 | OHL | 0.135 | 1.4189 | 35.4739 | 1120 | 1060 | 990 | 1060
COYL1- | COYT1T | 4.37 | 0.27 | Composite | 0.4027 | 1.0118 | 0.5089 | 132 | 123 | 106 | 123
COYL1- | MAYT1T | 9.14 | 0.57 | Composite | 0.8423 | 2.157 | 1.0619 | 132 | 123 | 106 | 123
COYL2- | COYW2S | 1.29 | 0.08 | Composite | 0.0057 | 0.0515 | 0.4645 | 1500 | 1500 | 1500 | 1500
COYL2- | COYW2T | 1.32 | 0 | OHL | 0.0058 | 0.0522 | 0.3778 | 1500 | 1500 | 1500 | 1500
COYL2- | MAHI2- | 49.5 | 0 | OHL | 0.3612 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1490 | 1430 | 1320 | 1430
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1490 | 1430 | 1320 | 1430
COYT1T | KILS1- | 15.215 | 4.815 | Composite | 1.4768 | 3.99 | 7.6706 | 132 | 123 | 106 | 123
COYT1T | MAYB1- | 17.666 | 0.28 | Composite | 1.6159 | 4.1178 | 1.1779 | 132 | 123 | 106 | 123
COYW2S | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500
COYW2T | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500
CRDY3A | EWEH3- | 4.736 | 0.35 | Composite | 3.8899 | 14.1591 | 0.06 | 45 | 39 | 39 | 39
CRDY3B | EWEH3- | 4.775 | 0.35 | Composite | 3.9211 | 14.2732 | 0.0602 | 45 | 39 | 39 | 39
CROO1Q | NEIL1- | 12.65 | 0.22 | Composite | 0.477 | 2.7203 | 0.9904 | 229 | 211 | 183 | 211
CROO1R | NEIL1- | 12.65 | 0.23 | Composite | 0.4772 | 2.7212 | 1.0043 | 229 | 211 | 183 | 211
CRUA2Q | DALL2- | 8.16 | 0.4 | Composite | 0.0346 | 0.3435 | 4.3204 | 283 | 283 | 283 | 283
CRUA2R | DALL2- | 8.16 | 0.4 | Composite | 0.0346 | 0.3435 | 4.3204 | 283 | 283 | 283 | 283
CRYR1A | WESE1- | 0 | 3.989 | Cable | 0.0559 | 0.3473 | 5.1163 | 155 | 155 | 155 | 155
CRYR4- | FALL4- | 13.86 | 0 | OHL | 0.0184 | 0.2733 | 8.179 | 2470 | 2350 | 2150 | 2350
CRYR4- | TORN4- | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 935 | 785 | 785 | 785
CUPA1Q | LEVT1Q | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142
CUPA1R | LEVT1R | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142
CURR1A | GORG1Q | 1.49 | 5.8 | Composite | 0.261 | 0.9656 | 5.1127 | 111 | 100 | 92 | 100
CURR1A | LING1Q | 8.323 | 5.205 | Composite | 0.7926 | 2.2632 | 6.4813 | 132 | 123 | 106 | 123
CURR1B | GORG1R | 1.49 | 5.78 | Composite | 0.2603 | 0.9634 | 5.0953 | 111 | 100 | 92 | 100
CURR1B | LING1R | 8.323 | 5.335 | Composite | 0.7972 | 2.2773 | 6.5941 | 132 | 123 | 106 | 123
CURR2- | GRMO2- | 42.2 | 0 | OHL | 0.1916 | 1.7399 | 11.6642 | 1090 | 1030 | 925 | 1030
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1380 | 1320 | 1230 | 1320
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1380 | 1320 | 1230 | 1320
CURR2- | KINC2- | 55.76 | 0 | OHL | 0.2531 | 2.2958 | 15.4272 | 1090 | 1030 | 925 | 1030
CURR2- | SIGH2Q | 1.54 | 1.7 | Composite | 0.0174 | 0.1034 | 6.0397 | 180 | 180 | 180 | 180
CURR2- | SIGH2R | 1.54 | 1.67 | Composite | 0.0172 | 0.1027 | 5.9404 | 180 | 180 | 180 | 180
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 570 | 570 | 570 | 570
DALL2- | WIYH2- | 78.15 | 0 | OHL | 0.3305 | 3.192 | 21.732 | 570 | 570 | 570 | 570
DALM1- | SANX1Q | 0 | 5.16 | Cable | 0.1457 | 0.1955 | 6.7791 | 181 | 164 | 164 | 164
DALM1- | SANX1R | 0 | 5.78 | Cable | 0.1632 | 0.2189 | 7.5936 | 181 | 164 | 164 | 164
DENN2- | LAMB2- | 31.991 | 0 | OHL | 0.1442 | 1.3015 | 8.8844 | 955 | 885 | 760 | 885
DENN2- | LAMB2T | 31.991 | 0 | OHL | 0.1442 | 1.3015 | 8.8844 | 955 | 880 | 760 | 885
DENN2- | LOAN2- | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DENN2- | LOAN2T | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DESA1Q | NECU1- | 6.4 | 4.3 | Composite | 0.5652 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160
DEVM1- | ERSK1Q | 16.97 | 0 | OHL | 1.0312 | 3.6645 | 0.9113 | 213 | 202 | 185 | 202
DEVM1- | SPAV1Q | 7.63 | 0 | OHL | 0.5726 | 1.7268 | 0.3878 | 107 | 107 | 101 | 107
DEVM1- | SPAV1R | 7.51 | 0 | OHL | 0.5636 | 1.699 | 0.3818 | 107 | 107 | 101 | 107
DEVM4- | NEIL4R | 28.474 | 0 | OHL | 0.048 | 0.5603 | 16.965 | 2000 | 1920 | 1790 | 1920
DEVM4- | WIYH4Q | 28.908 | 0 | OHL | 0.0485 | 0.5525 | 17.5384 | 1120 | 1060 | 990 | 1060
DEVO1- | STIR1T | 5.8 | 5.816 | Composite | 0.3236 | 1.8724 | 7.2413 | 164 | 130 | 130 | 130
DEVO1- | WFIE1B | 31.8 | 0 | OHL | 2.8944 | 7.5329 | 1.5454 | 162 | 154 | 141 | 154
DEWP2Q | WHHO2Q | 0 | 2.48 | Cable | 0.0159 | 0.0559 | 7.7539 | 276 | 240 | 240 | 240
DEWP2R | WHHO2R | 0 | 2.55 | Cable | 0.0164 | 0.0575 | 7.9728 | 276 | 240 | 240 | 240
DONO3A | HAGH3- | 0 | 8.25 | Cable | 1.1413 | 3.6069 | 1.9363 | 60 | 60 | 60 | 60
DRUM2Q | WIYH2- | 2.46 | 0.29 | Composite | 0.0113 | 0.1081 | 3.8932 | 120 | 120 | 120 | 120
DRUM2R | WIYH2- | 2.46 | 0 | OHL | 0.0111 | 0.1001 | 0.6832 | 120 | 120 | 120 | 120
DUMF1- | TONG1Q | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUNB1Q | DUNB1S | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 232 | 198 | 188 | 198
DUNB1Q | INWI1Q | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 115 | 104 | 104 | 104
DUNB1R | DUNB1T | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 232 | 198 | 188 | 198
DUNB1R | INWI1R | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 115 | 104 | 104 | 104
DUNE1- | GALA1- | 23.64 | 0 | OHL | 2.1456 | 5.5767 | 1.1477 | 164 | 151 | 127 | 151
DUNE1- | SMEA1- | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 154 | 131 | 127 | 131
DUNE3- | KEIH3- | 0 | 4.746 | Cable | 5.1628 | 4.7962 | 0.3798 | 21 | 20 | 20 | 20
DUNE3- | POGB3- | 0 | 3.809 | Cable | 4.4533 | 3.8497 | 0.3048 | 21 | 20 | 20 | 20
DUNE3- | TODD3- | 0 | 6.07 | Cable | 2.245 | 5.682 | 0.73 | 42 | 42 | 42 | 42
DUNF1Q | INKE1Q | 7.58 | 0.09 | Composite | 0.6938 | 1.7769 | 0.5496 | 132 | 122 | 106 | 122
DUNF1Q | MOSM1A | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215
DUNF1R | INKE1R | 7.58 | 0.09 | Composite | 0.6938 | 1.7769 | 0.5496 | 132 | 122 | 106 | 122
DUNF1R | MOSM1B | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215
DUNH1Q | DUNH1S | 0 | 0.336 | Cable | 0.0168 | 0.037 | 0.2759 | 159 | 147 | 147 | 147
DUNH1Q | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458
DUNH1R | DUNH1T | 0 | 0.372 | Cable | 0.0186 | 0.0409 | 0.3054 | 159 | 147 | 147 | 147
DUNH1R | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458
EAST1Q | GLLE1- | 1.69 | 0 | OHL | 0.1536 | 0.3503 | 0.094 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 31.37 | 0 | OHL | 2.8482 | 7.3807 | 1.5285 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 30.94 | 0 | OHL | 2.8144 | 7.1441 | 1.5364 | 132 | 123 | 106 | 123
ECCL4A | ECCL4C | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4A | TORN4- | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4B | ECCL4D | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771
ECCL4B | TORN4- | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4C | STWB4Q | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770
ECCL4D | STWB4R | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770
EERH2- | LOAN2- | 45.82 | 0 | OHL | 0.1034 | 1.6072 | 14.6747 | 1500 | 1500 | 1500 | 1500
EERH2- | NEAR2Q | 15.46 | 0 | OHL | 0.0705 | 0.6545 | 4.1829 | 950 | 885 | 760 | 885
EKIL2Q | EKIL2S | 5.17 | 0 | OHL | 0.0138 | 0.1834 | 1.6594 | 865 | 825 | 750 | 825
EKIL2Q | STHA2A | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIL2R | EKIL2T | 5.17 | 0.108 | Composite | 0.0141 | 0.186 | 2.1213 | 480 | 405 | 405 | 405
EKIL2R | STHA2B | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965
EKIL3A | EKIL3B | 0 | 0 | Series Reactor | 0.5744 | 108.498 | 0 | 30 | 30 | 30 | 30
EKIS2- | NEIL2- | 29.58 | 0 | OHL | 0.1251 | 1.2082 | 8.2207 | 1110 | 1030 | 885 | 1030
EKIS2- | STHA2B | 5.8 | 0 | OHL | 0.0245 | 0.2366 | 1.614 | 1050 | 965 | 880 | 965
EKIS2- | WLEE2- | 0 | 6 | Cable | 0.034 | 0.101 | 25.635 | 378 | 378 | 378 | 378
EKIS2- | WLEX2- | 0 | 16.68 | Cable | 0.088 | 0.346 | 70.948 | 340 | 340 | 340 | 340
ELDE1Q | JOHN1Q | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 149 | 149 | 149 | 149
ELDE1Q | NEIL1- | 3.82 | 0.18 | Composite | 0.1517 | 0.8271 | 0.4569 | 229 | 211 | 183 | 211
ELDE1R | JOHN1R | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 149 | 149 | 149 | 149
ELDE1R | NEIL1- | 3.82 | 0.23 | Composite | 0.1523 | 0.8319 | 0.5267 | 229 | 211 | 183 | 211
ELVA3A | PRST3A | 1.01 | 0 | OHL | 0.8089 | 2.9543 | 0.004 | 49 | 45 | 39 | 45
ELVA4- | GRNA4C | 65.54 | 0 | OHL | 0.1155 | 1.2673 | 38.8356 | 2210 | 2130 | 1980 | 2130
ELVA4- | MOFF4- | 23.5 | 0 | OHL | 0.0414 | 0.4544 | 13.9258 | 2210 | 2130 | 1980 | 2130
ELVA4- | STHA4A | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
ENHI1- | NECU1C | 0 | 5.47 | Cable | 0.157 | 0.5337 | 6.0483 | 90 | 90 | 90 | 90
ESST1- | PART1Q | 0 | 6.9 | Cable | 0.137 | 0.641 | 9.143 | 210 | 200 | 190 | 200
ESST1- | WIYH1- | 0 | 3.59 | Cable | 0.0711 | 0.3255 | 5.0111 | 233 | 200 | 200 | 200
ESST1Q | PART1R | 0 | 6.84 | Cable | 0.136 | 0.635 | 9.062 | 203 | 190 | 190 | 190
ESST1Q | WIYH1- | 0 | 3.16 | Cable | 0.178 | 0.334 | 7.691 | 203 | 190 | 190 | 190
EWEH1Q | GRNA1- | 15.9 | 0.36 | Composite | 1.2138 | 3.4754 | 1.4335 | 295 | 295 | 295 | 295
FALL4- | SMEA4R | 31.1 | 0 | OHL | 0.0414 | 0.6133 | 18.3526 | 2520 | 2400 | 2190 | 2400
FASI1A | HAWI1- | 19.11 | 0 | OHL | 1.7249 | 4.5353 | 0.9303 | 133 | 124 | 107 | 124
FASI1A | JUNV1- | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 199 | 191 | 178 | 191
FASI1B | HAWI1- | 19.11 | 0 | OHL | 1.7249 | 4.5353 | 0.9303 | 132 | 123 | 106 | 123
FASI1B | JUNV1A | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 199 | 191 | 178 | 191
FINN1Q | PART1Q | 0 | 2.813 | Cable | 0.0563 | 0.1582 | 4.0035 | 171 | 152 | 152 | 152
FINN1R | PART1R | 0 | 2.845 | Cable | 0.057 | 0.16 | 4.0491 | 171 | 152 | 152 | 152
GALA1- | HAWI1B | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
GARB1Q | HELE1Q | 15.313 | 0 | OHL | 1.3875 | 3.4126 | 0.7803 | 132 | 123 | 106 | 123
GARB1R | STLE1Q | 26.909 | 0 | OHL | 2.4383 | 5.997 | 1.3713 | 132 | 123 | 106 | 123
GARB1S | GARE1S | 5.03 | 0 | OHL | 0.4558 | 1.1211 | 0.2564 | 132 | 123 | 106 | 123
GARB1T | GARE1T | 5.061 | 0 | OHL | 0.4586 | 1.1279 | 0.2579 | 132 | 123 | 106 | 123
GARE1S | WHTL1S | 1.68 | 0 | OHL | 0.2125 | 0.3513 | 0.0919 | 100 | 94 | 80 | 94
GARE1S | WIYH1- | 35.082 | 0.33 | Composite | 3.1938 | 7.8537 | 2.4208 | 109 | 105 | 101 | 105
GARE1T | WHTL1T | 1.67 | 0 | OHL | 0.2112 | 0.3492 | 0.0913 | 100 | 94 | 80 | 94
GARE1T | WIYH1- | 34.74 | 0.162 | Composite | 3.1552 | 7.7595 | 2.0813 | 109 | 105 | 101 | 105
GAWH3- | HAHA3- | 0 | 5.07 | Cable | 1.7086 | 4.8419 | 0.5551 | 36 | 34 | 34 | 34
GLGL1Q | SAKN1- | 0 | 9 | Cable | 0.2541 | 0.5842 | 11.0847 | 166 | 166 | 166 | 166
GLGL3- | SNQR3- | 0 | 2.3 | Cable | 0.6364 | 2.0111 | 0.2699 | 30 | 30 | 30 | 30
GLGL3- | WHLL3- | 0 | 1.2 | Cable | 0.332 | 1.5811 | 0.1408 | 30 | 30 | 30 | 30
GLLE1- | KEOO1- | 7.68 | 0 | OHL | 0.6969 | 1.6787 | 0.405 | 132 | 123 | 106 | 123
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7434 | 7.134 | 1.4605 | 125 | 113 | 102 | 113
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.7434 | 7.134 | 1.4605 | 125 | 113 | 102 | 113
GLLE1- | TONG1- | 33.1 | 0 | OHL | 3.39 | 7.678 | 1.662 | 132 | 123 | 106 | 123
GLLU1Q | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLLU1R | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 57 | 57 | 57 | 57
GLNI1- | MOSM1A | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 265 | 246 | 212 | 246
GLNI1- | MOSM1B | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 265 | 246 | 212 | 246
GLNI1- | REDH1- | 10.547 | 0 | OHL | 0.9555 | 2.3056 | 0.552 | 161 | 154 | 141 | 154
GLNI1- | WFIE1B | 7.11 | 0 | OHL | 0.5359 | 1.6524 | 0.3546 | 264 | 246 | 212 | 246
GLRB2- | GLRO2- | 14.68 | 0 | OHL | 0.0664 | 0.6181 | 3.956 | 1090 | 1030 | 925 | 1030
GLRO2- | WFIE2- | 12.08 | 0 | OHL | 0.0547 | 0.5102 | 3.2488 | 1090 | 1030 | 925 | 1030
GORG1Q | TELR1Q | 0 | 4.6 | Cable | 0.1299 | 0.2986 | 6.0432 | 72 | 72 | 72 | 72
GORG1R | TELR1R | 0 | 4.6 | Cable | 0.1299 | 0.2986 | 6.0432 | 72 | 72 | 72 | 72
GOVA1Q | HAGR1Q | 0 | 4.04 | Cable | 0.2097 | 0.252 | 6.0812 | 70 | 64 | 64 | 64
GOVA1Q | PAIS1Q | 4.52 | 4.03 | Composite | 0.2635 | 1.0894 | 8.2673 | 125 | 113 | 110 | 113
GOVA1R | HAGR1R | 0 | 4.11 | Cable | 0.187 | 0.225 | 3.587 | 69 | 64 | 64 | 64
GRMO2- | KINC2- | 14.96 | 0 | OHL | 0.068 | 0.6184 | 4.1277 | 1050 | 965 | 880 | 965
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.017 | 0.047 | 0.066 | 1000 | 1000 | 1000 | 1000
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.012 | 0.035 | 0.049 | 1000 | 1000 | 1000 | 1000
GRNA1- | JUNV1- | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191
GRNA1- | JUNV1A | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191
GRNA4- | GRNA4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
GRNA4- | HAKB4B | 1.97 | 0 | OHL | 0.0035 | 0.0381 | 1.1674 | 2210 | 2130 | 1980 | 2130
HAKB4- | MOFF4C | 43.79 | 0 | OHL | 0.0772 | 0.8467 | 25.9494 | 2210 | 2130 | 1980 | 2130
HARE1- | MOFF1- | 0 | 15.33 | Cable | 0.3071 | 0.8622 | 21.8179 | 184 | 184 | 184 | 184
HARR3- | KYPE3A | 0 | 0.5 | Cable | 0.0692 | 0.2186 | 0.1174 | 40 | 38 | 38 | 38
HELE1R | WIYH1- | 24.799 | 0.182 | Composite | 2.2553 | 5.5463 | 1.6125 | 109 | 105 | 101 | 105
HOLM1- | HOLM1T | 0 | 0.28 | Cable | 0.0025 | 0.0233 | 0.5242 | 293 | 293 | 293 | 293
HOLM1- | SHRG1T | 8 | 0 | OHL | 0.6078 | 1.7331 | 0.4228 | 365 | 360 | 350 | 360
HOLM1T | KEOO1- | 10.16 | 0 | OHL | 0.4101 | 2.0583 | 0.5825 | 132 | 123 | 106 | 123
HOLM1T | NECU1B | 16.35 | 0 | OHL | 0.4243 | 3.1565 | 0.9785 | 482 | 460 | 420 | 460
HUCS4- | HUNE4- | 0 | 0.665 | Cable | 0.0003 | 0.0089 | 7.3943 | 1444 | 1444 | 1444 | 1444
HUCS4- | HUNE4- | 0 | 0.675 | Cable | 0.0003 | 0.009 | 7.5055 | 1444 | 1444 | 1444 | 1444
HUER1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUER1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
HUER1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
HUER4- | HUNE4- | 0 | 0.26 | Cable | 0.0001 | 0.0011 | 0.7554 | 2770 | 2770 | 2770 | 2770
HUER4- | HUNE4- | 0 | 0.18 | Cable | 0.0001 | 0.0007 | 0.523 | 2770 | 2770 | 2770 | 2770
HUNE4- | HUNN4A | 0 | 0.259 | Cable | 0.0008 | 0.0027 | 1.7445 | 607 | 607 | 607 | 607
HUNE4- | HUNN4B | 0 | 0.177 | Cable | 0.0005 | 0.0019 | 1.1922 | 607 | 607 | 607 | 607
HUNE4- | KILS4- | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUNE4- | KILS4T | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930
HUNE4- | NEIL4Q | 35.43 | 0 | OHL | 0.0706 | 0.7289 | 20.0655 | 1390 | 1280 | 1110 | 1280
HUNE4- | NEIL4R | 35.43 | 0 | OHL | 0.0706 | 0.7289 | 20.0655 | 1390 | 1280 | 1110 | 1280
HUNF1Q | KILW1R | 12.85 | 3.06 | Composite | 0.6044 | 3.1854 | 6.863 | 146 | 146 | 145 | 146
HUNF1R | SACO1R | 8.572 | 3.04 | Composite | 0.4215 | 2.2374 | 6.6019 | 146 | 146 | 145 | 146
HUNN2A | HUNN2C | 0 | 3.356 | Cable | 0.0212 | 0.1068 | 11.7957 | 240 | 240 | 240 | 240
HUNN2B | HUNN2D | 0 | 3.413 | Cable | 0.0216 | 0.1087 | 11.9781 | 240 | 240 | 240 | 240
INVB2A | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVB2B | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000
INVR2- | WIYH2- | 55.6 | 0 | OHL | 0.2351 | 2.2709 | 15.4613 | 570 | 570 | 570 | 570
INWI1Q | TORN1- | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 115 | 104 | 104 | 104
INWI1R | TORN1- | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 115 | 104 | 104 | 104
JUNA1T | KILW1Q | 12.418 | 0 | OHL | 0.4909 | 2.779 | 0.643 | 146 | 146 | 146 | 146
JUNA1T | SACO1Q | 8.14 | 0 | OHL | 0.3086 | 1.8332 | 0.4224 | 151 | 151 | 151 | 151
JUNB1- | JUNV1- | 1 | 0 | OHL | 6e-06 | 5.7e-05 | 0 | 1000 | 1000 | 1000 | 1000
JUNB1A | JUNV1A | 1 | 0 | OHL | 0 | 0.0001 | 0 | 2286 | 2286 | 2286 | 2286
KAIM2- | SMEA2- | 8.78 | 0 | OHL | 0.0374 | 0.3629 | 2.4323 | 1190 | 1190 | 1190 | 1190
KAIM2- | WHHO2Q | 0 | 6.455 | Cable | 0.0415 | 0.1456 | 20.1821 | 276 | 240 | 240 | 240
KAIM2- | WHHO2R | 0 | 6.297 | Cable | 0.0405 | 0.1421 | 19.6881 | 276 | 240 | 240 | 240
KAIM3- | KAIM3A | 0 | 0 | Series Reactor | 0.0625 | 13.5546 | 0 | 120 | 120 | 120 | 120
KAIM3- | KAIM3B | 0 | 0 | Series Reactor | 0.0624 | 13.55 | 0 | 120 | 120 | 120 | 120
KIER1Q | WIYH1- | 2.089 | 4.183 | Composite | 0.3881 | 0.9293 | 7.6166 | 100 | 80 | 60 | 80
KIER1R | WIYH1- | 2.089 | 4.095 | Composite | 0.3833 | 0.9197 | 7.4586 | 100 | 80 | 60 | 80
KILB1Q | WIYH1- | 0 | 3.38 | Cable | 0.098 | 0.209 | 4.333 | 139 | 126 | 113 | 126
KILB1R | WIYH1- | 0 | 3.29 | Cable | 0.115 | 0.199 | 8.02 | 139 | 126 | 113 | 126
KILG2- | MAHI2- | 0 | 14 | Cable | 0.0719 | 0.2998 | 53.9497 | 352 | 290 | 290 | 290
KILS1- | MEAD1- | 12.57 | 0 | OHL | 0.874 | 2.581 | 2.166 | 162 | 154 | 141 | 154
KILS2- | KILT2Q | 3.56 | 0.29 | Composite | 0.0175 | 0.154 | 2.0858 | 204 | 177 | 177 | 177
KILS2- | KILT2R | 3.56 | 0.33 | Composite | 0.0178 | 0.1548 | 2.24 | 204 | 177 | 177 | 177
KILS4- | STHA4A | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920
KILS4T | STHA4B | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920
KILW1Q | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146
KILW1R | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146
KINB2J | KINC2- | 10.71 | 0 | OHL | 0.0482 | 0.4368 | 2.969 | 1090 | 1030 | 925 | 1030
KINB2K | KINC2- | 10.68 | 0 | OHL | 0.0386 | 0.4264 | 3.0603 | 1090 | 1030 | 925 | 1030
KINC2- | LOAN2Q | 4.28 | 0 | OHL | 0.0186 | 0.1855 | 1.1454 | 765 | 620 | 620 | 620
KINC2- | LOAN2R | 4.28 | 0 | OHL | 0.0186 | 0.1855 | 1.1454 | 765 | 620 | 620 | 620
LAMB2- | LAMB2T | 0.001 | 0 | OHL | 0 | 0 | 0 | 1120 | 1060 | 990 | 1060
LAMB2- | PORD2Q | 3.94 | 0 | OHL | 0.0182 | 0.1701 | 1.0531 | 955 | 885 | 760 | 885
LAMB2- | PORD2R | 3.94 | 0.177 | Composite | 0.0192 | 0.1721 | 2.1551 | 300 | 300 | 300 | 300
LAMB2- | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 955 | 955 | 880 | 955
LAMB2T | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1120 | 1060 | 990 | 1060
LEVE1Q | LEVT1Q | 2.16 | 0 | OHL | 0.1957 | 0.4852 | 0.1093 | 143 | 142 | 128 | 142
LEVE1R | LEVT1R | 2.26 | 0 | OHL | 0.2048 | 0.5083 | 0.1143 | 143 | 142 | 128 | 142
LEVT1Q | REDH1- | 8.61 | 0 | OHL | 0.7803 | 1.9339 | 0.4357 | 143 | 142 | 128 | 142
LEVT1R | WFIE1B | 18.707 | 0 | OHL | 1.588 | 4.18 | 0.9537 | 143 | 142 | 128 | 142
LOAN2- | LOAN2Q | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2R | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2S | 0 | 0.174 | Cable | 0.0004 | 0.0039 | 1.5626 | 760 | 620 | 620 | 620
LOAN2- | LOAN2S | 0 | 0.174 | Cable | 0.0004 | 0.0039 | 1.5626 | 760 | 620 | 620 | 620
LOAN2- | LOAN2T | 0.025 | 0 | OHL | 0 | 0 | 0 | 1500 | 1500 | 1500 | 1500
LOAN2- | MOSM2- | 31.496 | 0.174 | Composite | 0.1429 | 1.3311 | 11.6006 | 1090 | 1030 | 925 | 1030
LOAN2S | MOSM2- | 31.496 | 0 | OHL | 0.1426 | 1.3291 | 8.4753 | 1090 | 1030 | 925 | 1030
LOAN2T | WFIE2- | 29.209 | 0 | OHL | 0.1316 | 1.2106 | 7.9335 | 1090 | 1030 | 925 | 1030
MAHI3- | TRLO3- | 8.722 | 5.5 | Composite | 12.1114 | 32.1139 | 0.6017 | 40 | 30 | 30 | 30
MAYB1- | MAYT1T | 12.59 | 0.31 | Composite | 1.1567 | 3.0101 | 0.9444 | 132 | 123 | 106 | 123
MEAD1- | MEAD1Q | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MEAD1- | MEAD1R | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100
MINN3- | MOFF3A | 0 | 12.34 | Cable | 4.1636 | 17.1281 | 1.314 | 31 | 29 | 29 | 29
MOFF4- | MOFF4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771
MOSH1Q | MOSM1A | 0 | 1.03 | Cable | 0.048 | 0.063 | 2.012 | 132 | 123 | 106 | 123
MOSH1R | MOSM1B | 0 | 0.96 | Cable | 0.044 | 0.057 | 1.826 | 132 | 123 | 106 | 123
MOSM2- | WFIE2- | 8.243 | 0 | OHL | 0.0378 | 0.3641 | 2.1507 | 1090 | 1030 | 925 | 1030
NEAR2Q | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 885 | 760 | 885
NEAR2R | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 285 | 285 | 285 | 285
NEAR3A | NEAR3B | 0 | 0 | Series Reactor | 0.5744 | 108.4985 | 0 | 30 | 30 | 30 | 30
NECU1B | OHLL1- | 0 | 3 | Cable | 0.0534 | 0.2861 | 3.5006 | 180 | 180 | 180 | 180
NECU1C | NOKY1- | 0 | 1.3 | Cable | 0.0084 | 0.0773 | 2.2771 | 240 | 240 | 240 | 240
NECU1C | SOKY1- | 0 | 4.2 | Cable | 0.0458 | 0.2435 | 7.265 | 242 | 223 | 192 | 223
NEIL1- | NEIL1C | 0 | 0.32 | Cable | 0 | 0.0126 | 0 | 416 | 389 | 389 | 389
NEIL1- | PAIS1Q | 8.29 | 0.29 | Composite | 0.1643 | 1.4877 | 1.704 | 268 | 268 | 268 | 268
NEIL1- | PAIS1R | 8.31 | 0.31 | Composite | 0.1648 | 1.493 | 1.7861 | 268 | 268 | 268 | 268
NEIL2- | NEIL2C | 0 | 0.2 | Cable | 0.0007 | 0.003 | 1.492 | 1140 | 945 | 945 | 945
NEIL2- | NEIL2D | 0 | 0.2 | Cable | 0.0002 | 0.0028 | 2.4328 | 500 | 500 | 500 | 500
NEIL2- | WIYH2R | 25.453 | 0 | OHL | 0.1093 | 1.0873 | 6.9047 | 1120 | 1060 | 990 | 1060
NOKY1- | NECU1- | 0 | 1.3 | Cable | 0.0084 | 0.0773 | 2.2771 | 261 | 261 | 261 | 261
PAIS1Q | PAIS1S | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425
PAIS1R | PAIS1T | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425
POOB2Q | SHRU2Q | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2Q | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300
POOB2R | SHRU2R | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270
POOB2R | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300
PORD2Q | WGEO2Q | 0 | 1.83 | Cable | 0.017 | 0.056 | 12.236 | 305 | 198 | 198 | 198
PORD2R | WGEO2R | 0 | 2.15 | Cable | 0.014 | 0.049 | 10.691 | 305 | 198 | 198 | 198
RAVE3S | WISH3S | 0 | 4.1 | Cable | 0.9601 | 1.9766 | 0.01 | 32 | 32 | 32 | 32
RAVE3T | WISH3T | 0 | 4.1 | Cable | 0.9601 | 1.9766 | 0.01 | 32 | 32 | 32 | 32
REDH1- | WFIE1A | 10.097 | 0 | OHL | 0.8077 | 2.2461 | 0.5179 | 157 | 152 | 141 | 152
SMEA4Q | STHA4B | 73.37 | 0 | OHL | 0.1593 | 1.4873 | 41.7375 | 900 | 760 | 760 | 760
SMEA4Q | TORN4- | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 900 | 760 | 760 | 760
SMEA4R | WISH4- | 61.77 | 0 | OHL | 0.1344 | 1.2615 | 34.9418 | 1390 | 1280 | 1110 | 1280
STHA4A | WISH4- | 11.6 | 0 | OHL | 0.0233 | 0.2267 | 6.8043 | 2000 | 1920 | 1790 | 1920
STIR1S | WFIE1A | 37.6 | 5.816 | Composite | 3.218 | 9.4053 | 8.7867 | 162 | 154 | 141 | 154
STLE1R | WIYH1- | 12.892 | 0.291 | Composite | 1.1813 | 2.9041 | 1.2141 | 109 | 105 | 101 | 105
WFIB2- | WFIE2- | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 1090 | 1030 | 925 | 1030
WHTB1S | WHTL1S | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94
WHTB1T | WHTL1T | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94
WIYH2- | WIYH2R | 0 | 0 | Series Reactor | 0.005 | 1.5 | 0 | 1000 | 1000 | 1000 | 1000

## B-2-1c
B-2-1c - NGET Circuits for 2025/26
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
ABHA4A | EXET41 | 48.785 | 0 | OHL | 0.0778 | 0.9831 | 27.9792 | 2078 | 2078 | 2078 | 2078
ABHA4A | LAGA41 | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327
ABHA4B | EXET41 | 49.051 | 0 | OHL | 0.0783 | 0.9885 | 28.1313 | 2423 | 2327 | 2168 | 2327
ABHA4B | LAGA41 | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327
ABTH21 | COWT2A | 13.318 | 0 | OHL | 0.0503 | 0.5449 | 3.758 | 932 | 879 | 790 | 879
ABTH21 | PYLE21 | 35.388 | 0 | OHL | 0.1819 | 1.4523 | 9.9528 | 932 | 879 | 790 | 879
ABTH21 | TREM21 | 46.451 | 0 | OHL | 0.2267 | 2.1393 | 11.8321 | 682 | 629 | 538 | 629
ABTH21 | UPPB21 | 26.996 | 0 | OHL | 0.1234 | 1.1426 | 7.3237 | 955 | 882 | 762 | 882
ABTH21 | UPPB22 | 27.035 | 0.547 | Composite | 0.1245 | 1.1595 | 13.2801 | 772 | 772 | 595 | 595
ALDW21 | BRIN21 | 17.961 | 0 | OHL | 0.1442 | 0.7628 | 4.8487 | 626 | 591 | 535 | 591
ALDW21 | WMEL21 | 8.96 | 0 | OHL | 0.0409 | 0.3891 | 2.3695 | 955 | 882 | 762 | 882
ALVE4A | INDQ41 | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284
ALVE4A | TAUN41 | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284
ALVE4B | INDQ41 | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.209 | 1389 | 1284 | 1108 | 1284
ALVE4B | TAUN42 | 73.298 | 0 | OHL | 0.117 | 1.4771 | 42.0372 | 1389 | 1284 | 1108 | 1284
AMEM4A | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2009 | 1911 | 1746 | 1911
AMEM4A | IVER4A | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 1852 | 1741 | 1624 | 1741
AMEM4B | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2032 | 1933 | 1766 | 1933
AMEM4B | IVER4B | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2032 | 1933 | 1766 | 1933
AXMI41 | CHIC4A | 30.7 | 8.552 | Composite | 0.0364 | 0.588 | 235.173 | 2779 | 2568 | 2217 | 2568
AXMI41 | EXET41 | 36.184 | 0 | OHL | 0.0393 | 0.6293 | 23.853 | 2779 | 2568 | 2217 | 2568
BAGB21 | MAGA21 | 12.629 | 1.389 | parallel Composite | 0.0435 | 0.5216 | 17.0509 | 1204 | 1115 | 1018 | 1115
BAGB21 | SWAN21 | 18.21 | 1.439 | parallel Composite | 0.0625 | 0.7488 | 19.1165 | 1548 | 1548 | 1431 | 1431
BARK21 | REBR22 | 10.879 | 0 | OHL | 0.0411 | 0.4451 | 3.0706 | 1129 | 1081 | 1000 | 1081
BARK22 | REBR21 | 10.854 | 0 | OHL | 0.041 | 0.4441 | 3.0636 | 1205 | 1127 | 1044 | 1127
BARK41 | CHUE4A | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | CHUE4B | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048
BARK41 | WHAM41 | 9.662 | 0.124 | Composite | 0.0156 | 0.1915 | 10.4541 | 2009 | 1909 | 1710 | 1909
BARK41 | WHAM41 | 9.662 | 0 | OHL | 0.0155 | 0.191 | 5.6429 | 2009 | 1911 | 1746 | 1911
BARK41 | WTHU4A | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BARK41 | WTHU4B | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911
BEDD21 | CHSI21 | 17.836 | 0.286 | Composite | 0.068 | 0.7365 | 7.9729 | 944 | 882 | 762 | 835
BEDD21 | WIMB21 | 8.5 | 0.968 | Composite | 0.0409 | 0.3915 | 11.7005 | 859 | 827 | 623 | 694
BEDD22 | CHSI21 | 17.836 | 0.137 | Composite | 0.0677 | 0.7328 | 6.4221 | 762 | 762 | 662 | 662
BEDD23 | WIMB2A | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 995 | 930 | 728 | 806
BEDD4A | ROWD42 | 0 | 10.1 | Cable | 0.0071 | 0.1292 | 121.8435 | 1309 | 1309 | 1309 | 1309
BEDD4B | ROWD41 | 0 | 10.1 | Cable | 0.0069 | 0.1275 | 124.3819 | 1417 | 1417 | 1220 | 1294
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882
BESW21 | FECK21 | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 882 | 762 | 882
BESW21 | OCKH21 | 56.939 | 0.731 | Composite | 0.2318 | 2.4208 | 22.7971 | 819 | 819 | 638 | 638
BICF41 | SPLN41 | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3156 | 3032 | 2823 | 3032
BICF41 | WALP41 | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3189 | 3063 | 2853 | 3063
BICF41 | WBUR41 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BICF41 | WBUR42 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882
BIRK21 | LISD2A | 0 | 12.891 | Cable | 0.0271 | 0.2978 | 125.0427 | 817 | 817 | 739 | 739
BISW21 | FECK21 | 22.83 | 0 | OHL | 0.0938 | 0.9633 | 6.2301 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 24.226 | 0 | OHL | 0.0932 | 1.0024 | 6.7545 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 27.111 | 0 | OHL | 0.1054 | 1.1236 | 7.5448 | 955 | 882 | 762 | 882
BISW21 | PENN21 | 30.172 | 0 | OHL | 0.1233 | 1.2726 | 8.2379 | 1040 | 1031 | 762 | 762
BLYT21 | STEW21 | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 682 | 629 | 538 | 629
BLYT21 | STEW21 | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 682 | 629 | 538 | 629
BLYT21 | TYNE21 | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1360 | 1310 | 1220 | 1310
BLYT21 | TYNE2A | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1360 | 1310 | 1220 | 1310
BLYT41 | MEDB4A | 26.636 | 0.121 | Composite | 0.0426 | 0.514 | 18.0175 | 2199 | 2092 | 1911 | 2092
BLYT41 | MEDB4B | 26.636 | 0.49 | Composite | 0.0429 | 0.5194 | 24.1171 | 2199 | 2092 | 1911 | 2092
BODE41 | GWYN4A | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1056 | 1056 | 980 | 980
BODE41 | GWYN4B | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2771 | 2695 | 2510 | 2695
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 3102 | 2935 | 2765 | 2935
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 3102 | 2935 | 2765 | 2935
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8862 | 3102 | 2935 | 2765 | 2935
BOTW41 | CHIL41 | 7.479 | 0 | OHL | 0.0066 | 0.1285 | 5.027 | 3341 | 3160 | 2971 | 3160
BOTW41 | LOVE41 | 14.672 | 0 | OHL | 0.013 | 0.252 | 9.8617 | 3341 | 3160 | 2971 | 3160
BRAI4A | BRFO41 | 48.267 | 0 | OHL | 0.0449 | 0.8314 | 32.312 | 3326 | 3326 | 3317 | 3326
BRAI4A | BULL41 | 12.343 | 0 | OHL | 0.0121 | 0.2133 | 8.2257 | 3066 | 2830 | 2418 | 2830
BRAI4B | PELH41 | 65.942 | 0 | OHL | 0.0648 | 1.1396 | 43.9331 | 2779 | 2568 | 2217 | 2568
BRAI4B | RAYL41 | 33.03 | 0 | OHL | 0.0346 | 0.5732 | 21.8572 | 2779 | 2568 | 2217 | 2568
BRAW21 | ELLA21 | 16.802 | 0.081 | Composite | 0.0769 | 0.7134 | 5.4384 | 762 | 762 | 619 | 619
BRAW21 | KIRK21 | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 762 | 762 | 619 | 619
BRAW21 | MONF21 | 51.155 | 0 | OHL | 0.095 | 1.8583 | 16.2816 | 1204 | 1115 | 1018 | 1115
BRAW4A | PADI41 | 59.3 | 0 | OHL | 0.0635 | 1.078 | 37.8431 | 2470 | 2350 | 2146 | 2350
BRED21 | MACC21 | 19.612 | 0 | OHL | 0.0663 | 0.7981 | 5.5762 | 948 | 882 | 753 | 753
BRED21 | SMAN21 | 10.004 | 5.629 | parallel Composite | 0.0513 | 0.4604 | 46.762 | 865 | 865 | 749 | 749
BRED21 | STAL21 | 15.054 | 0 | OHL | 0.0665 | 0.6343 | 4.1113 | 1093 | 1031 | 925 | 1031
BRFO41 | LEIS4A | 42.357 | 0 | OHL | 0.046 | 0.7367 | 27.9223 | 2779 | 2569 | 2217 | 2569
BRFO41 | PELH41 | 69.301 | 0 | OHL | 0.0655 | 1.1949 | 46.3271 | 3102 | 2935 | 2765 | 2935
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRFO41 | SIZE41 | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 1590 | 1500 | 1346 | 1500
BRFO41 | NORM41 | 61.576 | 0.1 | Composite | 0.0983 | 1.242 | 37.3151 | 1590 | 1500 | 1346 | 1500
BRIM2A | TOTT23 | 7.437 | 0.311 | Composite | 0.0345 | 0.3234 | 5.3982 | 1085 | 1031 | 925 | 1031
BRIM2A | WALX22 | 5.865 | 0 | OHL | 0.0268 | 0.2482 | 1.5911 | 1093 | 1031 | 925 | 1031
BRIM2B | TOTT22 | 7.305 | 0.393 | Composite | 0.0341 | 0.3201 | 6.2537 | 1085 | 1031 | 925 | 1031
BRIM2B | WALX22 | 5.997 | 0 | OHL | 0.0274 | 0.2538 | 1.6269 | 1093 | 1031 | 925 | 1031
BRIM2C | TOTT24 | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1085 | 1031 | 925 | 1031
BRIM2C | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIM2D | TOTT21 | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1085 | 1031 | 925 | 1031
BRIM2D | WALX21 | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIN21 | CHTE21 | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 934 | 934 | 753 | 753
BRIN21 | JORD21 | 13.257 | 1.489 | Composite | 0.0647 | 0.5918 | 16.0432 | 557 | 557 | 499 | 499
BRIN21 | NORL2A | 13.257 | 2.845 | Composite | 0.0708 | 0.6085 | 24.8202 | 419 | 419 | 381 | 381
BRIN21 | TEMP21 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN21 | TEMP22 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882
BRIN22 | CHTE21 | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1204 | 1115 | 1018 | 1115
BRIN22 | THUR21 | 5.704 | 0 | OHL | 0.0599 | 0.2384 | 1.5621 | 626 | 591 | 535 | 591
BRIN22 | TINP21 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 955 | 882 | 762 | 882
BRIN22 | TINP22 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 955 | 882 | 762 | 882
BRIN41 | THOM41 | 36.285 | 0 | OHL | 0.0394 | 0.6315 | 23.9068 | 2518 | 2395 | 2188 | 2395
BRIN41 | THOM42 | 36.302 | 0 | OHL | 0.0394 | 0.6318 | 23.9168 | 2545 | 2421 | 2211 | 2421
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6724 | 87.0663 | 2779 | 2568 | 2217 | 2245
BRLE41 | DIDC41 | 37.691 | 5.7 | parallel Composite | 0.0419 | 0.6719 | 134.3668 | 2277 | 2277 | 2037 | 2037
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2569 | 2217 | 2569
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.019 | 0.3053 | 11.5725 | 2779 | 2569 | 2217 | 2569
BRLE41 | MELK41 | 81.569 | 0 | OHL | 0.1052 | 1.5315 | 50.3377 | 1389 | 1284 | 1108 | 1284
BRLE41 | MELK41 | 82.134 | 0 | OHL | 0.1052 | 1.5315 | 50.3377 | 1389 | 1284 | 1108 | 1284
BRLE41 | WWEY4A | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092
BRLE41 | WWEY4B | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092
BRWA41 | BRWA4A | 4.371 | 0 | OHL | 0.0079 | 0.087 | 2.5326 | 2030 | 1930 | 1770 | 1930
BRWA42 | BRWA4B | 4 | 0.462 | Composite | 0.0076 | 0.085 | 7.3611 | 2030 | 1930 | 1770 | 1930
BRWA4A | SHUR41 | 14.02 | 0 | OHL | 0.0218 | 0.269 | 8.4136 | 3100 | 3050 | 2960 | 3050
BRWA4B | SHUR41 | 14.02 | 0 | OHL | 0.0218 | 0.269 | 8.4136 | 411 | 411 | 380 | 380
BULL41 | RAYL41 | 20.646 | 0 | OHL | 0.0224 | 0.3591 | 13.6101 | 2779 | 2569 | 2217 | 2569
BURW41 | PELH41 | 42.782 | 0 | OHL | 0.0379 | 0.7348 | 28.7545 | 3326 | 3159 | 2971 | 3159
BURW41 | PELH41 | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3035 | 2876 | 2238 | 2515
BURW41 | WALP41 | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3326 | 3160 | 2971 | 3160
BURW41 | WALP41 | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3326 | 3160 | 2971 | 3160
BUSH21 | DRAK21 | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 1204 | 1115 | 1018 | 1115
BUSH21 | PENN21 | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1038 | 1038 | 762 | 762
BUSH21 | WIEN2B | 5.197 | 4.318 | Composite | 0.0311 | 0.3404 | 48.3427 | 762 | 762 | 681 | 681
BUST21 | NECH21 | 2.648 | 7.619 | Composite | 0.026 | 0.3163 | 76.3606 | 725 | 713 | 599 | 635
BUST21 | NECH21 | 2.648 | 7.648 | Composite | 0.026 | 0.3169 | 76.528 | 725 | 713 | 599 | 635
BUST4A | DRAK41 | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8026 | 1203 | 1203 | 1103 | 1119
BUST4B | DRAK41 | 34.537 | 0 | OHL | 0.0375 | 0.6007 | 22.7664 | 2779 | 2568 | 2217 | 2568
CANT41 | CLEH41 | 14.7 | 0 | OHL | 0.0229 | 0.282 | 8.8214 | 3102 | 3048 | 2853 | 3048
CANT41 | KEMS4A | 28.2 | 0 | OHL | 0.0439 | 0.5411 | 16.9228 | 3102 | 2935 | 2765 | 2935
CANT41 | RICH41 | 20.72 | 0 | OHL | 0.033 | 0.4092 | 12.1374 | 2038 | 2038 | 1801 | 1801
CANT41 | RICH41 | 20.72 | 0 | OHL | 0.033 | 0.4092 | 12.1374 | 2038 | 2038 | 1801 | 1801
CANT41 | SELL4C | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3102 | 3048 | 2958 | 3048
CANT41 | SELL4D | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3103 | 3048 | 2959 | 3048
CAPE1A | INCE11 | 0 | 1 | Cable | 0.2226 | 2.0652 | 0.992 | 258 | 258 | 240 | 240
CAPE1B | INCE11 | 0 | 1 | Cable | 0.2204 | 2.0451 | 0.999 | 240 | 240 | 240 | 240
CAPE4A | CONQ41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160
CAPE4A | FROD41 | 18.404 | 0 | OHL | 0.0199 | 0.2926 | 13.3521 | 2889 | 2748 | 2418 | 2748
CAPE4B | CONQ41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160
CAPE4B | FROD41 | 18.315 | 0 | OHL | 0.0198 | 0.2912 | 13.2878 | 2890 | 2749 | 2418 | 2749
CARE21 | COWT2A | 27.881 | 0 | OHL | 0.1533 | 1.4488 | 6.2406 | 682 | 629 | 538 | 629
CARE21 | USKM2B | 19.94 | 0 | OHL | 0.1096 | 1.0362 | 4.4651 | 682 | 629 | 538 | 629
CARR21 | SMAN21 | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 835 | 665 | 665
CARR21 | SMAN21 | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 835 | 665 | 665
CARR41 | DAIN41 | 2.545 | 0 | OHL | 0.0043 | 0.0496 | 1.5076 | 2169 | 2084 | 1940 | 2084
CARR41 | DAIN41 | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9782 | 3102 | 3048 | 2958 | 3048
CARR41 | KEAR41 | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2212 | 2125 | 1979 | 2125
CARR41 | PEWO4A | 56.9 | 0 | OHL | 0.0988 | 1.1179 | 33.4404 | 2169 | 2084 | 1940 | 2084
CARR4A | DAIN41 | 2.063 | 0 | OHL | 0.0035 | 0.0404 | 1.2165 | 1500 | 1500 | 1500 | 1500
CARR4B | DAIN41 | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 1553 | 1553 | 1553 | 1553
CELL41 | DAIN41 | 53.412 | 2.31 | parallel Composite | 0.0842 | 1.0304 | 76.9149 | 2508 | 2508 | 2300 | 2300
CELL41 | DRAK41 | 45.012 | 0 | OHL | 0.0719 | 0.8656 | 27.0675 | 2397 | 2302 | 2144 | 2302
CELL41 | DRAK41 | 45.712 | 0 | OHL | 0.073 | 0.8791 | 27.4871 | 2397 | 2302 | 2144 | 2302
CELL41 | MACC41 | 31.617 | 0 | OHL | 0.0494 | 0.6065 | 18.9844 | 3102 | 3048 | 2958 | 3048
CHIC41 | EXET41 | 67.12 | 8.8 | Composite | 0.0759 | 1.2212 | 258.3265 | 2779 | 2568 | 2217 | 2568
CHIC41 | MANN41 | 53.913 | 0 | OHL | 0.0585 | 0.9377 | 35.5401 | 3065 | 2829 | 2418 | 2829
CHIC4A | MANN41 | 54.066 | 0 | OHL | 0.0587 | 0.9404 | 35.6406 | 3065 | 2829 | 2418 | 2829
CHIL41 | FAWL41 | 0 | 3.73 | Cable | 0.0037 | 0.0235 | 56.9944 | 970 | 928 | 800 | 928
CHIL41 | FAWL41 | 0 | 3.69 | Cable | 0.0037 | 0.0232 | 56.3832 | 970 | 928 | 800 | 928
CHIL41 | LOVE41 | 22.379 | 0.315 | Composite | 0.0201 | 0.389 | 20.2483 | 1109 | 1109 | 901 | 901
CHSI21 | WWEY21 | 15.318 | 0 | OHL | 0.0519 | 0.6229 | 4.351 | 1316 | 1213 | 1104 | 1213
CHSI21 | WWEY22 | 15.347 | 0 | OHL | 0.052 | 0.6241 | 4.3592 | 1316 | 1213 | 1104 | 1213
CHTE21 | HIGM21 | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1381 | 1339 | 1258 | 1339
CHTE21 | HIGM21 | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1381 | 1381 | 1375 | 1381
CHUE4A | TILB41 | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2827 | 2827 | 2591 | 2591
CHUE4A | WTHU4D | 2.419 | 0 | OHL | 0.0038 | 0.0488 | 1.378 | 3102 | 3048 | 2958 | 3048
CHUE4B | TILB41 | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2924 | 2924 | 2591 | 2591
CHUE4B | WTHU4C | 2.581 | 0 | OHL | 0.004 | 0.0519 | 1.4744 | 3102 | 3048 | 2958 | 3048
CILF2A | UPPB21 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF2B | UPPB22 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882
CILF41 | IMPP41 | 25.119 | 0 | OHL | 0.0273 | 0.4396 | 16.4758 | 2779 | 2568 | 2217 | 2568
CILF41 | RASS41 | 26.901 | 0 | OHL | 0.03 | 0.5141 | 16.2899 | 2779 | 2568 | 2217 | 2568
CILF41 | RHIG41 | 25.011 | 0 | OHL | 0.0275 | 0.4568 | 15.8083 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN41 | 61.595 | 0 | OHL | 0.0668 | 1.0713 | 40.6034 | 2779 | 2568 | 2217 | 2568
CILF41 | SWAN42 | 61.655 | 0 | OHL | 0.0669 | 1.0724 | 40.6428 | 3180 | 3000 | 2692 | 3000
CILF41 | WHSO4A | 35.208 | 0 | OHL | 0.0383 | 0.6151 | 23.1262 | 2779 | 2568 | 2217 | 2568
CITR41 | PUDM41 | 0 | 7.29 | Cable | 0.0066 | 0.0598 | 131.22 | 1282 | 1136 | 984 | 1136
CITR41 | SJOW41 | 0 | 7.243 | Cable | 0.0065 | 0.0594 | 130.374 | 1282 | 1136 | 984 | 1136
CITR41 | SJOW41 | 0 | 6.776 | Cable | 0.0061 | 0.0556 | 121.968 | 1282 | 1136 | 984 | 1136
CITR41 | WHAM4B | 0 | 9.39 | Cable | 0.0085 | 0.077 | 169.02 | 1282 | 1136 | 984 | 1136
CLEH41 | KEMS4B | 13.5 | 0 | OHL | 0.021 | 0.259 | 8.1013 | 3102 | 3048 | 2853 | 3048
CONQ41 | DAIN41 | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 3102 | 3048 | 2853 | 3048
CONQ41 | DAIN41 | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 3102 | 3048 | 2853 | 3048
CONQ41 | FLIB41 | 0 | 3.495 | Cable | 0.0022 | 0.05 | 43.9195 | 1438 | 1438 | 1389 | 1389
CONQ41 | FLIB41 | 0 | 3.388 | Cable | 0.0022 | 0.0485 | 42.5749 | 1438 | 1438 | 1389 | 1389
CONQ41 | GWYN4A | 30.217 | 0.21 | Composite | 0.0003 | 0.0053 | 0.2221 | 2665 | 2561 | 2384 | 2561
CONQ41 | GWYN4B | 30.217 | 0.21 | Composite | 0.0003 | 0.0053 | 0.2221 | 2665 | 2561 | 2384 | 2561
CONQ41 | TREU4A | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2397 | 2302 | 2144 | 2302
CONQ41 | TREU4B | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2212 | 2125 | 1979 | 2125
COSO41 | RAYL41 | 13.913 | 0 | OHL | 0.0217 | 0.2698 | 8.2601 | 3075 | 2876 | 2663 | 2876
COSO41 | TILB4B | 12.363 | 0 | OHL | 0.0193 | 0.24 | 7.3306 | 3075 | 2876 | 2663 | 2876
COTT41 | KEAD4C | 34.628 | 0 | OHL | 0.0419 | 0.6393 | 21.7427 | 2750 | 2750 | 2663 | 2750
COTT41 | KEAD4D | 34.479 | 0 | OHL | 0.0417 | 0.6365 | 21.651 | 2750 | 2550 | 2380 | 2550
COTT41 | MARH4B | 100.853 | 0 | OHL | 0.1677 | 1.9593 | 59.8778 | 2009 | 1912 | 1746 | 1912
COTT41 | RYHA4A | 76.891 | 0 | OHL | 0.0008 | 0.0141 | 0.4865 | 3326 | 3326 | 3317 | 3326
COTT41 | STAY41 | 27.788 | 0.5 | parallel Composite | 0.0504 | 0.5522 | 21.6211 | 2213 | 2126 | 1980 | 2052
COTT42 | RYHA4B | 76.816 | 0 | OHL | 0.0846 | 1.4085 | 48.5917 | 2807 | 2696 | 2511 | 2696
COTT42 | STAY41 | 27.698 | 0 | OHL | 0.0441 | 0.5297 | 16.7334 | 2212 | 2125 | 1979 | 2125
COTT42 | WBUR42 | 6.76 | 0 | OHL | 0.0102 | 0.1298 | 4.0622 | 3326 | 3160 | 2971 | 3160
COVE21 | NECH21 | 30.715 | 0 | OHL | 0.0715 | 1.1726 | 9.309 | 1204 | 1115 | 1018 | 1115
COVE21 | RATS2A | 64.863 | 0.5 | Composite | 0.2171 | 2.6384 | 23.342 | 1000 | 1000 | 1000 | 1000
COWL41 | CULJ4A | 6.496 | 0 | OHL | 0.0085 | 0.1266 | 3.8528 | 2771 | 2568 | 2217 | 2568
COWL41 | DIDC41 | 11.503 | 0 | OHL | 0.0151 | 0.2242 | 6.8223 | 2779 | 2568 | 2217 | 2568
COWL41 | ECLA41 | 36.086 | 0 | OHL | 0.0376 | 0.6259 | 23.8903 | 2779 | 2569 | 2219 | 2569
COWL41 | LEIB4A | 52.28 | 0 | OHL | 0.0518 | 0.904 | 34.7923 | 2779 | 2568 | 2217 | 2568
COWL41 | MITY41 | 100.105 | 2.092 | Composite | 0.1418 | 1.8493 | 98.0711 | 1180 | 1132 | 877 | 979
COWL41 | WALH41 | 89.553 | 2.092 | Composite | 0.113 | 1.6366 | 92.0801 | 1180 | 1132 | 877 | 979
COWT2A | PYLE21 | 22.6 | 0 | OHL | 0.1334 | 0.9291 | 6.3441 | 932 | 879 | 790 | 879
CREB21 | HEDO21 | 19.648 | 0 | OHL | 0.0544 | 0.7327 | 6.0951 | 1749 | 1664 | 1520 | 1664
CREB22 | SAEN21 | 20.412 | 0 | OHL | 0.0566 | 0.7611 | 6.3321 | 1749 | 1664 | 1520 | 1664
CREB41 | GART4A | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3075 | 2876 | 2663 | 2876
CREB41 | GART4B | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3326 | 3159 | 2971 | 3159
CREB41 | THTO41 | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3075 | 2876 | 2663 | 2876
CREB41 | THTO42 | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3075 | 2876 | 2663 | 2876
CULJ4A | DIDC41 | 4.898 | 0 | OHL | 0.0064 | 0.0955 | 2.905 | 2771 | 2568 | 2217 | 2568
DAIN41 | MACC41 | 33.593 | 2.4 | parallel Composite | 0.0535 | 0.6504 | 66.7805 | 2397 | 2302 | 2144 | 2300
DAMC41 | KINO41 | 0 | 0.919 | Cable | 0.0001 | 0.0005 | 2.6467 | 1528 | 1528 | 1528 | 1528
DIDC41 | DIDC41 | 0 | 0 | Series Reactor | 0.0063 | 0.5 | 0 | 2640 | 2640 | 2640 | 2640
DINO41 | PENT41 | 0 | 10.762 | Cable | 0.0075 | 0.1184 | 215.24 | 1604 | 1604 | 1557 | 1557
DINO41 | PENT41 | 4.545 | 7.305 | Composite | 0.0093 | 0.1892 | 94.6439 | 1623 | 1623 | 1571 | 1571
DINO41 | PENT41 | 0 | 10.605 | Cable | 0.0056 | 0.153 | 133.2664 | 916 | 916 | 710 | 710
DRAK41 | HAMH41 | 29.434 | 0 | OHL | 0.0534 | 0.5857 | 17.0575 | 2009 | 1911 | 1746 | 1911
DRAK41 | OLDB4A | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1169 | 1169 | 1068 | 1068
DRAK41 | RATS41 | 32.907 | 0 | OHL | 0.0582 | 0.6532 | 19.1262 | 2009 | 1911 | 1746 | 1911
DRAK41 | RUGE41 | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2009 | 1911 | 1746 | 1911
DRAK41 | WILE41 | 16.937 | 0 | OHL | 0.0308 | 0.337 | 9.8147 | 2009 | 1911 | 1746 | 1911
DRAX41 | DRAX42 | 0 | 0 | Series Reactor | 0.006 | 2 | 0 | 1320 | 1320 | 1320 | 1320
DRAX41 | EGGB42 | 11.188 | 0.64 | Composite | 0.0128 | 0.2017 | 30.2999 | 2089 | 2089 | 1878 | 1878
DRAX41 | FENW4A | 13.443 | 0 | OHL | 0.0146 | 0.2338 | 8.8618 | 3180 | 3000 | 2692 | 3000
DRAX41 | THTO42 | 22.579 | 0 | OHL | 0.0198 | 0.3877 | 15.2046 | 3075 | 2876 | 2663 | 2876
DRAX42 | EGGB41 | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2973 | 2778 | 2447 | 2778
DRAX42 | THOM41 | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 3102 | 3048 | 2958 | 2993
DRAX42 | THTO41 | 22.579 | 0 | OHL | 0.0198 | 0.3877 | 15.2046 | 3075 | 2876 | 2663 | 2876
DUNG41 | NINF41 | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3065 | 2829 | 2418 | 2829
DUNG41 | NINF41 | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3066 | 2830 | 2418 | 2830
DUNG41 | SELL4E | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 3066 | 2830 | 2418 | 2830
DUNG41 | SELL4F | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 3066 | 2830 | 2418 | 2830
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 524 | 518 | 401 | 401
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 525 | 426 | 426
EALI21 | WISD2A | 0 | 6.075 | Cable | 0.0121 | 0.1391 | 61.5397 | 750 | 750 | 735 | 735
EASO41 | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
EASO4A | RYHA4B | 58.95 | 0 | OHL | 0.0523 | 1.0125 | 39.6215 | 3326 | 3160 | 2971 | 3160
EASO4B | RYHA4A | 58.769 | 0 | OHL | 0.0521 | 1.0094 | 39.5003 | 2779 | 2569 | 2217 | 2569
EASO4B | WYMO41 | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
ECLA41 | LEIB4B | 15.985 | 0 | OHL | 0.014 | 0.2745 | 10.7642 | 3326 | 3160 | 2971 | 3160
ECLA41 | PAFB4A | 44.72 | 0 | OHL | 0.0814 | 0.8898 | 25.9172 | 2009 | 1911 | 1746 | 1911
ECLA41 | PAFB4B | 44.886 | 0 | OHL | 0.0817 | 0.8931 | 26.0131 | 2009 | 1911 | 1746 | 1911
EGGB41 | MONF4A | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1970 | 1970 | 1970 | 1970
EGGB41 | ROCH4A | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1239 | 1239 | 1122 | 1122
EGGB41 | THOM41 | 28.07 | 0.197 | Composite | 0.0281 | 0.4884 | 21.9218 | 2217 | 2217 | 1801 | 1801
EGGB42 | FERR4A | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2779 | 2568 | 2217 | 2568
EGGB42 | MONF41 | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2779 | 2568 | 2217 | 2568
EGGB42 | STSB4B | 48.084 | 0 | OHL | 0.0459 | 0.8295 | 32.1013 | 2779 | 2568 | 2217 | 2568
ELLA21 | FERR22 | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1324 | 1260 | 1151 | 1260
ELLA21 | KIRK21 | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 762 | 762 | 619 | 619
ELLA21 | STAL21 | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 882 | 762 | 882
ELST12 | HEND11 | 0 | 1 | Cable | 0.081 | 0.634 | 16.01 | 299 | 275 | 218 | 275
ELST21 | MILH2A | 6.375 | 6.338 | Composite | 0.0548 | 0.3963 | 55.677 | 524 | 524 | 430 | 430
ELST21 | MILH2B | 6.375 | 6.282 | Composite | 0.0546 | 0.3952 | 55.2004 | 524 | 524 | 430 | 430
ELST21 | WARL21 | 59.208 | 0.261 | Composite | 0.2449 | 2.4665 | 19.2619 | 762 | 762 | 619 | 619
ELST21 | WATS21 | 5.398 | 0.399 | Composite | 0.0254 | 0.2396 | 5.8016 | 762 | 762 | 619 | 619
ELST22 | WARL21 | 59.244 | 0.59 | Composite | 0.2456 | 2.4772 | 22.8481 | 762 | 762 | 619 | 619
ELST22 | WATS22 | 5.398 | 0.222 | Composite | 0.0251 | 0.2347 | 3.8776 | 762 | 762 | 619 | 619
ELST41 | ELST4A | 0.1 | 0 | Series Reactor | 0 | 0 | 0 | 2000 | 2000 | 2000 | 2000
ELST41 | ELST4A | 0.1 | 0 | OHL | 0 | 0 | 0 | 2000 | 2000 | 2000 | 2000
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 1732 | 1663 | 1732
ELST4A | SUND41 | 34.834 | 0 | OHL | 0.0646 | 0.6825 | 20.4656 | 3102 | 3048 | 2958 | 3048
ELST4B | SUND42 | 34.706 | 0 | OHL | 0.0646 | 0.6803 | 20.3822 | 1590 | 1500 | 1346 | 1500
ENDE41 | PAFB4A | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | PAFB4B | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911
ENDE41 | RATS41 | 36.941 | 0 | OHL | 0.0399 | 0.5872 | 26.8034 | 2779 | 2568 | 2217 | 2568
ENDE41 | RATS41 | 36.873 | 0 | OHL | 0.0398 | 0.5862 | 26.7543 | 2779 | 2568 | 2217 | 2568
EXET41 | TAUN41 | 38.147 | 0 | OHL | 0.0694 | 0.759 | 22.1074 | 2009 | 1911 | 1746 | 1911
EXET41 | TAUN42 | 38.107 | 0 | OHL | 0.0693 | 0.7582 | 22.0842 | 2009 | 1911 | 1746 | 1911
FAWL41 | MANN41 | 61.115 | 0 | OHL | 0.066 | 1.0014 | 43.0253 | 2779 | 2568 | 2217 | 2568
FAWL41 | MAWO41 | 18.639 | 0 | OHL | 0.0214 | 0.3062 | 13.1667 | 2423 | 2327 | 2167 | 2327
FECK41 | HAMH41 | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2009 | 1911 | 1746 | 1911
FECK41 | IRON41 | 66.123 | 0 | OHL | 0.123 | 1.3148 | 38.3377 | 2009 | 1911 | 1746 | 1911
FECK41 | MITY41 | 78.649 | 0 | OHL | 0.1527 | 1.5677 | 45.4527 | 1967 | 1874 | 1712 | 1874
FECK41 | WALH41 | 67.986 | 0 | OHL | 0.1237 | 1.3527 | 39.4005 | 1967 | 1875 | 1712 | 1875
FENW4A | KEAD42 | 42.517 | 0 | parallel OHL | 0.0198 | 0.2161 | 24.6399 | 3075 | 2876 | 2663 | 2876
FENW4A | THOM42 | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2009 | 1911 | 1746 | 1911
FERR21 | FERR2B | 0 | 0.285 | Cable | 0.0018 | 0.0044 | 1.9295 | 380 | 380 | 380 | 380
FERR21 | FERR2C | 0.586 | 0 | OHL | 0.0013 | 0.0216 | 0.1825 | 1381 | 1307 | 1227 | 1307
FERR21 | MONF21 | 4.485 | 0 | OHL | 0.0103 | 0.1651 | 1.3966 | 1372 | 1307 | 1207 | 1307
FERR21 | SKLG21 | 20.033 | 0.685 | Composite | 0.0991 | 0.9874 | 9.8077 | 865 | 823 | 752 | 823
FERR22 | FERR2C | 0.554 | 0.16 | Composite | 0.002 | 0.0234 | 1.3262 | 1031 | 1031 | 981 | 981
FERR2A | FERR2B | 0.416 | 0 | OHL | 0.0019 | 0.0176 | 0.1129 | 525 | 495 | 445 | 495
FERR2A | FERR2B | 0.416 | 0 | OHL | 0.0019 | 0.0176 | 0.1129 | 525 | 495 | 445 | 495
FERR2A | MONF22 | 3.922 | 0 | OHL | 0.009 | 0.1444 | 1.2212 | 1204 | 1115 | 1018 | 1115
FERR2B | FERR2C | 0 | 0.816 | Cable | 0.0027 | 0.0204 | 6.0881 | 435 | 435 | 395 | 395
FERR2B | FERR2C | 0 | 0.726 | Cable | 0.0024 | 0.0182 | 5.4162 | 435 | 435 | 395 | 395
FERR2B | SKLG21 | 19.545 | 0.56 | Composite | 0.0975 | 0.9671 | 8.7544 | 865 | 823 | 752 | 823
FFES21 | TRAW21 | 7.291 | 0.133 | Composite | 0.0771 | 0.3081 | 2.8868 | 551 | 512 | 442 | 512
FFES22 | TRAW21 | 7.358 | 0 | OHL | 0.0772 | 0.3075 | 2.0153 | 551 | 512 | 442 | 512
FIDF21 | FIDF21 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF21 | FIDF21 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750
FIDF21 | FROD21 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF21 | FROD22 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213
FIDF21 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FIDF21 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3140 | 3086 | 2999 | 3086
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3140 | 3086 | 2999 | 3086
FOUR21 | HARK24 | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 854 | 795 | 700 | 795
FOUR21 | STEW21 | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 854 | 795 | 700 | 795
FROD41 | ROCK41 | 1.197 | 0 | OHL | 0.0022 | 0.0238 | 0.6917 | 1100 | 1100 | 1100 | 1100
GART4A | HUMR41 | 37.372 | 0 | OHL | 0.0413 | 0.7015 | 23.0779 | 3156 | 3032 | 2823 | 3032
GART4A | KEAD43 | 5.711 | 0 | OHL | 0.0062 | 0.0993 | 3.7642 | 3075 | 2876 | 2663 | 2876
GART4B | KEAD41 | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3326 | 3256 | 2978 | 3256
GART4B | KILL41 | 34.462 | 0 | OHL | 0.038 | 0.6467 | 21.2883 | 3156 | 3032 | 2823 | 3032
GRAI41 | GRAI41 | 0 | 0 | Series Reactor | 0.0027 | 2.3091 | 0 | 2002 | 2002 | 2002 | 2002
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570
GRAI41 | KINO41 | 11.507 | 0.8 | parallel Composite | 0.0126 | 0.2028 | 18.5632 | 3326 | 3159 | 2633 | 2813
GRAI41 | TILB41 | 26.642 | 2.049 | Composite | 0.0304 | 0.4847 | 57.4011 | 2003 | 2003 | 1939 | 2003
GREN41 | MARH4A | 28.74 | 0 | OHL | 0.0485 | 0.5616 | 16.9528 | 2514 | 2439 | 2314 | 2439
GREN41 | MARH4B | 28.56 | 0 | OHL | 0.0482 | 0.5581 | 16.8451 | 2009 | 1912 | 1746 | 1912
GREN41 | MARV4A | 26 | 0 | OHL | 0.0473 | 0.5173 | 15.0681 | 2009 | 1911 | 1746 | 1911
GREN41 | MARV4B | 26 | 0 | OHL | 0.0473 | 0.5173 | 15.0681 | 2009 | 1911 | 1746 | 1911
GRIW41 | KEAD41 | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3075 | 2876 | 2663 | 2876
GRIW41 | SHBA41 | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2720 | 2484 | 2720
GRST2A | LACK2A | 1.016 | 0 | OHL | 0.0046 | 0.0441 | 0.2687 | 1175 | 1119 | 1023 | 1119
GRST2A | LACK2B | 1.016 | 0.138 | Composite | 0.0049 | 0.0464 | 1.7453 | 1129 | 1119 | 1000 | 1000
GRST2A | WILT2A | 0 | 0.73 | Cable | 0.0026 | 0.0111 | 4.5883 | 207 | 196 | 183 | 196
GRST2A | WILT2B | 0 | 0.741 | Cable | 0.0027 | 0.0112 | 4.6575 | 207 | 198 | 185 | 198
GRST2B | LACK2B | 0.63 | 0.08 | Composite | 0.003 | 0.0287 | 1.0226 | 1129 | 1119 | 1000 | 1000
GRST2B | LACK2C | 0.63 | 0.162 | Composite | 0.0032 | 0.03 | 1.9 | 1129 | 1119 | 1000 | 1000
GRST2B | WILT2C | 0 | 0.399 | Cable | 0.0014 | 0.006 | 2.5079 | 198 | 198 | 180 | 180
GRST2B | WILT2D | 0 | 0.389 | Cable | 0.0014 | 0.0059 | 2.445 | 206 | 204 | 190 | 204
GWYN4A | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
GWYN4B | PENT41 | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
HACK2A | TOTT2B | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 1093 | 1031 | 926 | 1031
HACK2B | TOTT2A | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 1093 | 1031 | 926 | 1031
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1770 | 1730 | 1600 | 1730
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1770 | 1730 | 1600 | 1730
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729
HAKB1- | HARK13 | 1 | 0 | OHL | 0.7047 | 2.0317 | 0.451 | 132 | 123 | 106 | 123
HAKB4- | HARK41 | 9.857 | 0 | OHL | 0.0176 | 0.1957 | 5.7308 | 2213 | 2126 | 1980 | 2126
HAKB4B | HARK41 | 9.857 | 0 | OHL | 0.0176 | 0.1957 | 5.7308 | 2170 | 2084 | 1941 | 2084
HAMB4A | HEYS41 | 25.85 | 0 | OHL | 0.0229 | 0.444 | 17.3733 | 3326 | 3299 | 3098 | 3299
HAMB4A | PEWO41 | 19.698 | 0.752 | parallel Composite | 0.0308 | 0.3917 | 24.9792 | 2473 | 2473 | 2189 | 2189
HAMB4A | STAH4A | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 240 | 240 | 240
HAMB4B | HEYS41 | 26.02 | 0 | OHL | 0.0231 | 0.4469 | 17.4871 | 3326 | 3326 | 3152 | 3326
HAMB4B | PEWO41 | 19.698 | 0.592 | parallel Composite | 0.0308 | 0.3911 | 20.9006 | 2473 | 2473 | 2189 | 2189
HAMB4B | STAH4B | 3.926 | 0 | OHL | 0.0085 | 0.0806 | 2.1967 | 240 | 240 | 240 | 240
HAMH2A | NECH21 | 10.439 | 0 | OHL | 0.0239 | 0.3843 | 3.2511 | 1362 | 1285 | 1202 | 1285
HAMH41 | WILE41 | 84.14 | 0.7 | Composite | 0.1249 | 1.6005 | 76.5151 | 2009 | 1912 | 1746 | 1912
HARK13 | JUNV1- | 1 | 0 | OHL | 1.1033 | 2.8058 | 0.6023 | 132 | 123 | 106 | 123
HARK21 | HARK22 | 0 | 0 | SSSC | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
HARK21 | HARK22 | 0 | 0 | SSSC | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
HARK23 | STEW21 | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 774 | 774 | 676 | 676
HARK41 | HUTT41 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2663 | 2771
HARK41 | HUTT42 | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771
HARM21 | HATL21 | 13.983 | 0 | OHL | 0.0472 | 0.5702 | 3.9648 | 1093 | 1031 | 925 | 1031
HARM21 | HAWP21 | 17.287 | 0 | OHL | 0.0584 | 0.7033 | 4.9126 | 1204 | 1115 | 1018 | 1115
HATL21 | HAWP2A | 31.443 | 0 | OHL | 0.1066 | 1.2811 | 8.9228 | 1093 | 1031 | 926 | 1031
HATL21 | SALH21 | 7.794 | 0 | OHL | 0.0327 | 0.3353 | 2.0878 | 1381 | 1279 | 1157 | 1279
HATL21 | TODP21 | 18.314 | 0 | OHL | 0.0678 | 0.7732 | 4.9952 | 1381 | 1279 | 1157 | 1279
HAWP21 | HAWP22 | 0 | 0.256 | Cable | 0.0005 | 0.0057 | 2.7392 | 908 | 874 | 720 | 801
HAWP22 | NORT21 | 30.238 | 0.203 | Composite | 0.0715 | 1.131 | 11.4977 | 1381 | 1381 | 1285 | 1381
HAWP22 | OFFE21 | 9.514 | 0 | OHL | 0.0435 | 0.4027 | 2.5811 | 1176 | 1119 | 1024 | 1119
HAWP2A | WBOL21 | 17.721 | 0 | OHL | 0.0008 | 0.0075 | 0.0481 | 1176 | 1119 | 1024 | 1119
HAWP4A | NORT41 | 30.157 | 0 | OHL | 0.0335 | 0.531 | 19.6771 | 2545 | 2421 | 2211 | 2421
HEDO21 | SAES21 | 1.371 | 0 | OHL | 0.0038 | 0.0511 | 0.4252 | 1749 | 1664 | 1520 | 1664
HEYS41 | MIDL41 | 0.9 | 0 | OHL | 0.0008 | 0.0155 | 0.6049 | 3326 | 3160 | 2971 | 3160
HEYS41 | QUER4B | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3299 | 3098 | 3299
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1770 | 1730 | 1600 | 1730
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1770 | 1730 | 1600 | 1730
HIGM21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591
HIGM41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0247 | 0.2903 | 13.416 | 2212 | 2125 | 1979 | 2125
HIGM4A | STOB41 | 40.547 | 0 | OHL | 0.0738 | 0.8067 | 23.4963 | 2147 | 2056 | 1904 | 2056
HINP41 | MELK41 | 86.136 | 0 | OHL | 0.1564 | 1.7133 | 49.9342 | 2009 | 1911 | 1746 | 1911
HINP41 | SAFO42 | 26.58 | 8.94 | Composite | 0.0421 | 0.5573 | 218.3267 | 2009 | 1911 | 1746 | 1911
HINP41 | SEAB41 | 57.813 | 8.99 | Composite | 0.0765 | 1.1045 | 239.9146 | 2009 | 1911 | 1746 | 1911
HINP41 | SHUR41 | 1.2 | 0 | OHL | 0.0019 | 0.0235 | 0.7057 | 3103 | 3048 | 2959 | 3048
HINP41 | SHUR41 | 1.213 | 0 | OHL | 0.002 | 0.024 | 0.707 | 3103 | 3048 | 2959 | 3048
HUMR41 | KILL41 | 2.879 | 0 | OHL | 0.0032 | 0.0543 | 1.7706 | 2771 | 2771 | 2771 | 2771
HURS21 | LITT2A | 5.164 | 2.841 | Composite | 0.0536 | 0.2993 | 17.9365 | 844 | 837 | 761 | 774
HURS21 | LITT2B | 5.14 | 2.771 | Composite | 0.0527 | 0.2963 | 17.5227 | 867 | 837 | 761 | 798
HURS21 | NEWX21 | 0 | 21.864 | Cable | 0.0437 | 0.5007 | 221.4823 | 890 | 882 | 704 | 784
HURS21 | NEWX21 | 0 | 21.106 | Cable | 0.0422 | 0.4833 | 213.8038 | 890 | 882 | 704 | 784
HUTT41 | HUTT41 | 0 | 0 | Series Capacitor | 0 | 0.5114 | 0 | 2771 | 2771 | 2771 | 2771
HUTT41 | HUTT41 | 0 | 0 | Series Reactor | 0 | 0.0702 | 0 | 2472 | 2472 | 2472 | 2472
HUTT41 | QUER4A | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
HUTT41 | QUER4B | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048
HUTT42 | HUTT42 | 0 | 0 | Series Capacitor | 0 | 0.5114 | 0 | 2771 | 2771 | 2771 | 2771
HUTT42 | HUTT42 | 0 | 0 | Series Reactor | 0 | 0.0702 | 0 | 2472 | 2472 | 2472 | 2472
IMPP41 | MELK41 | 78.775 | 3.913 | Composite | 0.0882 | 1.4129 | 130.2038 | 1424 | 1424 | 1424 | 1424
INDQ41 | LAND41 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 2199 | 2092 | 1911 | 2092
INDQ41 | LAND42 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 1389 | 1284 | 1108 | 1284
IROA11 | OLDS12 | 1 | 0 | OHL | 0.298 | 2.366 | 3.453 | 452 | 423 | 365 | 372
IROA12 | OLDS12 | 1 | 0 | OHL | 0.297 | 2.361 | 2.693 | 457 | 424 | 366 | 372
IROA21 | MELK2A | 33.683 | 0.38 | Composite | 0.1862 | 1.7591 | 10.7703 | 581 | 581 | 524 | 524
IROA21 | MELK2B | 33.683 | 0.951 | Composite | 0.1877 | 1.7704 | 15.6295 | 581 | 581 | 524 | 524
IROA21 | WHSO2A | 34.621 | 0 | OHL | 0.2033 | 1.4667 | 9.4554 | 750 | 750 | 715 | 750
IROA21 | WHSO2B | 34.555 | 0 | OHL | 0.2034 | 1.4638 | 9.4375 | 750 | 750 | 715 | 750
IRON41 | LEGA4B | 62.073 | 0 | OHL | 0.0991 | 1.1937 | 37.3273 | 2002 | 2002 | 2002 | 2002
IRON41 | PENN4A | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9851 | 1389 | 1284 | 1108 | 1284
IRON41 | PENN4B | 24.617 | 0 | OHL | 0.0488 | 0.491 | 14.2132 | 1590 | 1500 | 1346 | 1500
IRON41 | RUGE41 | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9045 | 1389 | 1284 | 1108 | 1284
IRON41 | SHRE4A | 15.129 | 0 | OHL | 0.0242 | 0.2909 | 9.0977 | 2397 | 2302 | 2144 | 2302
IVER21 | NHYD2A | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381
IVER21 | WWEY22 | 25.652 | 0.342 | Composite | 0.0975 | 1.059 | 10.9579 | 960 | 960 | 839 | 839
IVER22 | NHYD2B | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381
IVER22 | WATS21 | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 776 | 776 | 631 | 631
IVER22 | WATS22 | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 776 | 776 | 631 | 631
IVER2A | LALE21 | 17.186 | 0.402 | Composite | 0.0656 | 0.7143 | 9.2206 | 841 | 841 | 665 | 665
JORD21 | NORL2B | 0 | 2.843 | Cable | 0.0109 | 0.0719 | 20.1177 | 419 | 419 | 381 | 381
KEAD42 | WBUR42 | 28.425 | 0 | OHL | 0.0252 | 0.4882 | 19.1053 | 3326 | 3249 | 3098 | 3249
KEAD43 | KEAD44 | 0 | 0 | SSSC | 0 | 0.25 | 0 | 3326 | 3159 | 2971 | 3159
KEAD43 | KILL41 | 41.067 | 0 | OHL | 0.0403 | 0.7345 | 26.6033 | 3060 | 2931 | 2715 | 2931
KEAD43 | WBUR41 | 28.266 | 0 | OHL | 0.0251 | 0.4855 | 18.9987 | 3326 | 3159 | 2971 | 3159
KEAR21 | WHGA21 | 14.509 | 0.241 | Composite | 0.0667 | 0.6208 | 6.5558 | 835 | 835 | 665 | 665
KEAR21 | WHGA21 | 14.509 | 0.129 | Composite | 0.0665 | 0.6177 | 5.3384 | 213 | 213 | 289 | 289
KEAR41 | PADI41 | 39.101 | 0 | OHL | 0.0567 | 0.7296 | 24.2055 | 2169 | 2084 | 1940 | 2084
KEMS41 | LOFI4A | 38.035 | 0 | OHL | 0.0594 | 0.7324 | 22.7265 | 3102 | 2935 | 2765 | 2935
KEMS41 | LOFI4B | 37.572 | 0 | OHL | 0.0587 | 0.7235 | 22.4507 | 3102 | 2935 | 2765 | 2935
KENG41 | SJOW41 | 0 | 4.769 | Cable | 0.0032 | 0.0564 | 52.0546 | 1770 | 1730 | 1600 | 1730
KENG41 | SJOW41 | 0 | 4.769 | Cable | 0.0032 | 0.0564 | 52.0546 | 1770 | 1730 | 1600 | 1730
KENG41 | WIMB41 | 0 | 12.329 | Cable | 0.0085 | 0.1557 | 134.5735 | 1770 | 1730 | 1600 | 1730
KENG41 | WIMB41 | 0 | 12.2 | Cable | 0.0084 | 0.1541 | 133.1654 | 1770 | 1730 | 1600 | 1730
KENG41 | WISD41 | 0 | 2.939 | Cable | 0.002 | 0.0347 | 32.0798 | 1770 | 1730 | 1600 | 1730
KENG41 | WISD42 | 0 | 2.989 | Cable | 0.002 | 0.0353 | 32.6255 | 1770 | 1730 | 1600 | 1730
KIBY21 | LISD21 | 0 | 10.239 | Cable | 0.0173 | 0.2966 | 60.8154 | 762 | 762 | 698 | 698
KIBY21 | LISD21 | 0 | 9.518 | Cable | 0.0228 | 0.2008 | 86.3283 | 762 | 762 | 619 | 619
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339
KIBY21 | WASF2A | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1521 | 1461 | 1360 | 1461
KIBY21 | WASF2B | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1521 | 1461 | 1360 | 1461
KILL41 | SHBA41 | 17.05 | 0 | OHL | 0.0179 | 0.3134 | 10.7556 | 2860 | 2720 | 2484 | 2720
KINO41 | NFLE41 | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3102 | 2935 | 2692 | 2935
KINO41 | SING41 | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2889 | 2748 | 2510 | 2748
KINO41 | TILB41 | 15.478 | 1.835 | Composite | 0.0181 | 0.2893 | 46.9053 | 2003 | 2003 | 1948 | 1948
KIRK2A | SKLG21 | 0 | 8.608 | Cable | 0.0146 | 0.2402 | 93.5689 | 762 | 762 | 619 | 619
KITW21 | OLDB21 | 7.704 | 0.597 | Composite | 0.0301 | 0.3318 | 8.6639 | 667 | 667 | 619 | 619
KITW21 | OLDB2A | 8.278 | 0.222 | Composite | 0.0317 | 0.3449 | 4.7492 | 772 | 772 | 619 | 619
KNAR21 | MONF21 | 38.531 | 0.141 | Composite | 0.2716 | 1.7712 | 11.0429 | 551 | 513 | 443 | 513
KNAR21 | POPP21 | 49.192 | 0 | OHL | 0.3299 | 2.3254 | 12.2192 | 551 | 512 | 442 | 512
LACK21 | TODP21 | 5.955 | 0 | OHL | 0.0196 | 0.2454 | 1.6636 | 1408 | 1332 | 1251 | 1332
LACK41 | SALH41 | 10.108 | 0.25 | Composite | 0.016 | 0.1998 | 10.4648 | 1831 | 1739 | 1588 | 1739
LACK41 | THTO41 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030
LACK41 | THTO42 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030
LAGA41 | LAND41 | 21.224 | 0 | OHL | 0.0339 | 0.4081 | 12.7626 | 2423 | 2327 | 2168 | 2327
LAGA41 | LAND42 | 21.355 | 0 | OHL | 0.0341 | 0.4108 | 12.8374 | 2423 | 2327 | 2168 | 2327
LALE21 | WWEY2A | 8.395 | 0 | OHL | 0.0317 | 0.3434 | 2.3695 | 1316 | 1213 | 1104 | 1213
LEGA41 | TREU4A | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA41 | TREU4B | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720
LEGA4A | SHRE4A | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2295 | 2002 | 2002 | 2002 | 2002
LEIB4A | SUND42 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIB4B | SUND41 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568
LEIS11 | SIZE11 | 0 | 2.149 | Cable | 0.0196 | 0.2155 | 4.8028 | 301 | 301 | 243 | 243
LEIS11 | SIZE11 | 0 | 2.148 | Cable | 0.0195 | 0.2154 | 4.8006 | 301 | 301 | 243 | 243
LEIS11 | SIZE1A | 0 | 1.65 | Cable | 0.015 | 0.1655 | 3.6876 | 301 | 301 | 243 | 243
LEIS11 | SIZE1B | 0 | 1.65 | Cable | 0.015 | 0.1655 | 3.6876 | 301 | 301 | 243 | 243
LEIS4A | SIZE41 | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2779 | 2569 | 2217 | 2569
LHOR4B | NINF41 | 23.2 | 0 | OHL | 0.0252 | 0.4035 | 15.2937 | 3102 | 2935 | 2765 | 2935
LISD21 | LISD2A | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 750 | 740 | 740
LITT41 | LOFI4A | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3103 | 3048 | 2959 | 3048
LITT41 | LOFI4B | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3103 | 3048 | 2959 | 3048
LITT41 | WTHU4E | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815
LITT41 | WTHU4F | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815
LOFI4A | ROWD4A | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500
LOFI4B | ROWD4B | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500
LOVE41 | NURS41 | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2771 | 2568 | 2217 | 2568
LOVE41 | NURS4A | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2779 | 2568 | 2217 | 2568
MACC41 | STAL4B | 31.196 | 0 | OHL | 0.057 | 0.6101 | 18.4203 | 1710 | 1627 | 1488 | 1627
MAGA21 | PYLE21 | 6.238 | 0 | OHL | 0.0211 | 0.2537 | 1.7667 | 1204 | 1115 | 1018 | 1115
MANN41 | NURS4A | 39.823 | 0 | OHL | 0.043 | 0.6631 | 27.5672 | 2779 | 2568 | 2217 | 2568
MARH41 | MARH4A | 0 | 0 | Zero Length | 0 | 0 | 0 | 2860 | 2860 | 2860 | 2860
MARH42 | MARH4B | 0 | 0 | Zero Length | 0 | 0 | 0 | 2860 | 2860 | 2860 | 2860
MARH4A | STAY41 | 73.027 | 0 | OHL | 0.0012 | 0.0143 | 0.4307 | 2514 | 2439 | 2314 | 2439
MARV4A | SUND41 | 13.75 | 0 | OHL | 0.025 | 0.2736 | 7.9687 | 2009 | 1911 | 1746 | 1911
MARV4B | SUND42 | 13.955 | 1 | Composite | 0.0254 | 0.2777 | 8.0872 | 2009 | 1911 | 1746 | 1911
MAWO41 | NURS41 | 7.441 | 0 | OHL | 0.0093 | 0.1281 | 5.0417 | 2423 | 2327 | 2167 | 2327
MEDB4A | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326
MEDB4A | STWB4R | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326
MEDB4B | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326
MEDB4B | STWB4Q | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326
MELK41 | MITY41 | 28.101 | 0 | OHL | 0.0511 | 0.5591 | 16.2853 | 2105 | 2016 | 1867 | 2016
MELK41 | MITY41 | 28.052 | 0 | OHL | 0.051 | 0.5581 | 16.257 | 2105 | 2016 | 1867 | 2016
MELK41 | SAFO41 | 85.26 | 8.94 | Composite | 0.1484 | 1.7246 | 252.3421 | 2009 | 1912 | 1746 | 1912
MELK41 | SEAB41 | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2545 | 2421 | 2211 | 2421
MIDL41 | QUER4A | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3326 | 3159 | 2971 | 3159
MONF22 | POPP21 | 37.84 | 0 | OHL | 0.208 | 2.0034 | 8.337 | 682 | 629 | 538 | 629
MONF41 | PADI41 | 87.851 | 0 | OHL | 0.0885 | 1.5682 | 57.0689 | 2518 | 2395 | 2188 | 2395
NECT41 | NECT41 | 0 | 0.129 | Cable | 0.0001 | 0.0016 | 1.6211 | 1940 | 1940 | 1940 | 1940
NECT41 | NECT4A | 0 | 0 | Zero Length | 0 | 0 | 0 | 1364 | 1364 | 1250 | 1250
NECT41 | NECT4B | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159
NECT4A | NORM41 | 35.652 | 0 | OHL | 0.0316 | 0.6124 | 23.9626 | 3326 | 3326 | 3317 | 3326
NECT4A | WALP41 | 43.459 | 0 | OHL | 0.0385 | 0.7464 | 29.2107 | 3326 | 3326 | 3317 | 3326
NECT4B | NORM41 | 35.652 | 0 | OHL | 0.0316 | 0.6124 | 23.9626 | 3326 | 3258 | 3060 | 3258
NECT4B | WALP41 | 43.459 | 0 | OHL | 0.0385 | 0.7464 | 29.2107 | 3326 | 3160 | 2971 | 3160
NEEP21 | PITS21 | 0.851 | 3.975 | Composite | 0.0214 | 0.1378 | 26.8236 | 419 | 419 | 381 | 381
NEEP21 | SHEC21 | 0.851 | 4.428 | Composite | 0.0234 | 0.1494 | 29.8542 | 419 | 419 | 381 | 381
NEEP4A | STSB4B | 12.801 | 0 | OHL | 0.0276 | 0.2627 | 7.1402 | 2779 | 2568 | 2217 | 2568
NEWX41 | WIMB41 | 0 | 12.688 | Cable | 0.0087 | 0.1697 | 102.5891 | 1100 | 1100 | 1100 | 1100
NFLE41 | SING41 | 5.941 | 0 | OHL | 0.0093 | 0.114 | 3.5652 | 2889 | 2748 | 2510 | 2748
NFLE41 | WTHU4A | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NFLE41 | WTHU4B | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907
NORL2A | SHEC21 | 0 | 4.372 | Cable | 0.0192 | 0.1119 | 29.2487 | 419 | 419 | 381 | 381
NORL2B | PITS21 | 0 | 10.751 | Cable | 0.0473 | 0.2752 | 71.9242 | 419 | 419 | 381 | 381
NORM11 | NOTR11 | 1 | 0 | OHL | 0.236 | 0.778 | 0.315 | 265 | 246 | 212 | 246
NORM12 | NOTR12 | 1 | 0 | OHL | 0.2362 | 0.778 | 0.3149 | 346 | 290 | 265 | 290
NORT21 | SALH21 | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1381 | 1293 | 1197 | 1293
NORT41 | OSBA41 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | OSBA42 | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | SALH42 | 12.206 | 0 | OHL | 0.022 | 0.2492 | 6.888 | 2009 | 1912 | 1746 | 1912
NORT41 | SPEN41 | 21.134 | 0 | OHL | 0.0276 | 0.4062 | 12.7287 | 2545 | 2421 | 2211 | 2421
NORT41 | SPEN42 | 21.134 | 0 | OHL | 0.0276 | 0.4062 | 12.7287 | 2545 | 2421 | 2211 | 2421
NORW11 | NOTR11 | 1 | 0 | OHL | 0.236 | 0.778 | 0.315 | 265 | 246 | 212 | 246
NORW12 | NOTR12 | 1 | 0 | OHL | 0.2362 | 0.778 | 0.3149 | 346 | 290 | 265 | 290
OCKH21 | OLDB2A | 5.46 | 0 | OHL | 0.0208 | 0.2294 | 1.4988 | 1416 | 1339 | 1258 | 1339
OCKH21 | WIEN2A | 4.623 | 0.283 | Composite | 0.0216 | 0.202 | 4.2819 | 672 | 672 | 599 | 599
OCKH2A | WIEN2B | 4.67 | 0 | OHL | 0.0213 | 0.1977 | 1.2665 | 760 | 760 | 760 | 760
OFFE21 | WBOL21 | 8.207 | 0 | OHL | 0.0327 | 0.3406 | 2.2784 | 1176 | 1115 | 1018 | 1115
OSBA41 | THTO43 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2779 | 2568 | 2217 | 2568
OSBA42 | THTO41 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 2779 | 2568 | 2217 | 2568
PADI41 | PEWO4B | 37.608 | 0 | OHL | 0.0556 | 0.7049 | 23.1779 | 2169 | 2084 | 1940 | 2084
PELH41 | RYEH4A | 23.015 | 0 | OHL | 0.025 | 0.4003 | 15.1704 | 2779 | 2568 | 2217 | 2568
PELH41 | RYEH4B | 23.439 | 0 | OHL | 0.0254 | 0.4077 | 15.4489 | 2779 | 2569 | 2217 | 2569
PELH41 | SUND42 | 45.13 | 0 | OHL | 0.0487 | 0.752 | 31.2185 | 3180 | 3000 | 2692 | 3000
PELH41 | WYMO41 | 26.856 | 0 | OHL | 0.029 | 0.4469 | 18.6034 | 2771 | 2771 | 2692 | 2771
PEMB41 | SWAN41 | 84.697 | 0 | OHL | 0.0919 | 1.4731 | 55.833 | 2779 | 2568 | 2217 | 2568
PEMB41 | SWAN41 | 83.975 | 0 | OHL | 0.0911 | 1.4606 | 55.3574 | 2779 | 2568 | 2217 | 2568
PEMB41 | SWAN42 | 84.57 | 0 | OHL | 0.0918 | 1.4709 | 55.7496 | 2779 | 2568 | 2217 | 2568
PEMB41 | WALH41 | 217.727 | 5.468 | parallel Composite | 0.2376 | 3.8305 | 206.6595 | 2779 | 2568 | 2217 | 2568
PENT41 | TRAW41 | 45.1 | 6.308 | Composite | 0.0638 | 0.9671 | 131.0985 | 1769 | 1633 | 1401 | 1633
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568
PEWO21 | PEWO2A | 0 | 0 | SSSC | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
PEWO22 | PEWO2B | 0 | 0 | SSSC | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
PEWO21 | WASF2A | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1521 | 1461 | 1360 | 1461
PEWO22 | WASF2B | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1521 | 1461 | 1360 | 1461
PEWO41 | QUER4A | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3102 | 3048 | 2853 | 3048
PEWO41 | QUER4B | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3102 | 3048 | 2853 | 3048
PITS21 | TEMP21 | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 419 | 419 | 381 | 381
PITS21 | WIBA21 | 0 | 2.324 | Cable | 0.0077 | 0.0581 | 17.337 | 439 | 439 | 381 | 381
PUDM41 | WHAM4A | 0 | 2.17 | Cable | 0.002 | 0.0178 | 39.06 | 1282 | 1136 | 984 | 1136
PYLE21 | PYLE21 | 0 | 0.1 | Cable | 0.0001 | 0.0025 | 0.676 | 1416 | 1339 | 1258 | 1339
PYLE21 | PYLE21 | 0 | 0.25 | Cable | 0.0004 | 0.0063 | 1.69 | 1416 | 1339 | 1258 | 1339
RASS41 | WALH41 | 72.788 | 5.269 | parallel Composite | 0.0799 | 1.2848 | 109.6557 | 2779 | 2568 | 2217 | 2568
RATS41 | STAY4A | 43.662 | 0 | OHL | 0.0794 | 0.8687 | 25.3035 | 2147 | 2057 | 1905 | 2057
RATS41 | STOB41 | 24.492 | 0.179 | Composite | 0.0446 | 0.4882 | 20.1119 | 2147 | 2056 | 1904 | 2056
RATS41 | WILE41 | 21.748 | 0.216 | Composite | 0.0397 | 0.435 | 16.174 | 1309 | 1309 | 1067 | 1067
RATS41 | WILE41 | 21.684 | 0 | OHL | 0.0394 | 0.4314 | 12.5666 | 2009 | 1911 | 1746 | 1911
RAYL41 | TILB4A | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 3102 | 2935 | 2765 | 2935
REBR21 | TOTT23 | 3.305 | 9.678 | parallel Composite | 0.0166 | 0.2027 | 106.1327 | 1205 | 1127 | 1044 | 1127
REBR22 | TOTT24 | 3.305 | 11.448 | parallel Composite | 0.0174 | 0.2151 | 125.3726 | 1205 | 1127 | 1044 | 1127
RHIG41 | SWAN41 | 34.34 | 0 | OHL | 0.0373 | 0.5973 | 22.6374 | 2779 | 2568 | 2217 | 2568
ROCH21 | STAL21 | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1324 | 1260 | 1151 | 1260
ROCH21 | WHGA21 | 11.489 | 0.257 | Composite | 0.053 | 0.4934 | 5.9105 | 841 | 841 | 665 | 665
ROCH21 | WHGA21 | 11.489 | 0.238 | Composite | 0.0529 | 0.4929 | 5.7039 | 419 | 419 | 404 | 404
RYEH41 | RYEH4B | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0903 | 2779 | 2569 | 2217 | 2569
RYEH41 | WALX4A | 5.324 | 0 | OHL | 0.0058 | 0.0926 | 3.5096 | 2779 | 2568 | 2217 | 2568
RYEH4A | RYEH43 | 0.264 | 0 | OHL | 0.0004 | 0.0051 | 0.1585 | 2779 | 2569 | 2217 | 2569
RYEH4A | WALX4B | 5.461 | 0 | OHL | 0.0059 | 0.095 | 3.6 | 2779 | 2568 | 2217 | 2568
RYEH4B | RYEH42 | 0.215 | 0 | OHL | 0.0003 | 0.0041 | 0.1291 | 2779 | 2569 | 2217 | 2569
SAEN21 | SAES21 | 0.484 | 0 | OHL | 0.0013 | 0.018 | 0.1501 | 1749 | 1664 | 1520 | 1664
SAFO41 | SEAB41 | 31.28 | 0 | OHL | 0.0345 | 0.5479 | 20.4859 | 3190 | 3060 | 2850 | 3060
SALH41 | SALH42 | 0 | 0 | SSSC | 0 | 1.25 | 0 | 2217 | 2217 | 2217 | 2217
SEAB41 | SEAB4A | 0.03 | 0 | OHL | 0 | 0.0006 | 0.018 | 2545 | 2421 | 2211 | 2421
SEAB41 | WHSO4A | 30.426 | 3.89 | Composite | 0.0374 | 0.5858 | 97.4265 | 1424 | 1424 | 1424 | 1424
SELL4A | SELL4A | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 1860 | 1860 | 1860 | 1860
SELL4A | SELL4C | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642
SELL4A | SELL4D | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642
SELL4A | SELL4E | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642
SELL4A | SELL4F | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642
SELL4B | SELL4C | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3159 | 2971 | 3159
SELL4B | SELL4D | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3326 | 3326 | 3326
SELL4B | SELL4E | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3159 | 2971 | 3159
SELL4B | SELL4F | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3159 | 2971 | 3159
SHRE4A | SHRE4B | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 240 | 240 | 240 | 240
SHUR41 | SHUR41 | 0 | 0 | Series Reactor | 0 | 2 | 0 | 2400 | 2400 | 2400 | 2400
SHUR41 | TAUN41 | 27 | 0 | OHL | 0.0487 | 0.5369 | 15.6574 | 2213 | 2126 | 1980 | 2126
SHUR41 | TAUN42 | 27 | 0 | OHL | 0.0487 | 0.5369 | 15.6574 | 2213 | 2126 | 1980 | 2126
SPEN41 | STEW41 | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2470 | 2350 | 2146 | 2350
SPEN42 | STEW41 | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2470 | 2350 | 2146 | 2350
SPLN41 | WALP41 | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3189 | 3063 | 2853 | 3063
SSHI22 | TYNE2A | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1247 | 1180 | 1065 | 1180
SSHI22 | WBOL21 | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1176 | 1119 | 1024 | 1119
STAL4A | THOM41 | 69.271 | 6.952 | Composite | 0.0721 | 1.2648 | 151.7118 | 1442 | 1442 | 1314 | 1314
STAL4B | STSB4A | 26.581 | 7.031 | Composite | 0.0345 | 0.532 | 124.2199 | 1436 | 1436 | 1308 | 1308
STEN11 | STES11 | 1 | 0 | OHL | 0.0266 | 0.1193 | 0.1077 | 198 | 198 | 181 | 181
SUND41 | WYMO41 | 18.156 | 0 | OHL | 0.0196 | 0.302 | 12.5826 | 3048 | 3000 | 2692 | 3000
SWAN41 | SWAN4B | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 3048 | 3048 | 2971 | 3048
SWAN42 | SWAN4A | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 1389 | 1284 | 1108 | 1284
TEMP22 | WIBA21 | 0 | 3.607 | Cable | 0.0159 | 0.0923 | 24.1308 | 421 | 421 | 381 | 381
THOM21 | WMEL21 | 23.791 | 0.947 | Composite | 0.1105 | 1.0548 | 15.8849 | 764 | 764 | 698 | 698
THOM2A | WMEL21 | 24.413 | 0.8 | Composite | 0.1126 | 1.0793 | 10.588 | 955 | 882 | 762 | 882
THUR21 | THUR2A | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 551 | 512 | 442 | 512
THUR2A | WMEL21 | 16.348 | 0 | OHL | 0.0746 | 0.7099 | 4.3235 | 955 | 882 | 762 | 882
TILB21 | WARL21 | 13.065 | 0 | OHL | 0.0597 | 0.553 | 3.5441 | 1175 | 1119 | 1023 | 1119
TILB21 | WARL21 | 12.897 | 0 | OHL | 0.059 | 0.5459 | 3.4987 | 1175 | 1119 | 1023 | 1119
TILB41 | TILB4A | 0.058 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3102 | 3048 | 2958 | 3048
TILB41 | TILB4B | 0.059 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3102 | 3048 | 2853 | 3048
TOTT2A | TOTT22 | 0 | 0 | Zero Length | 0 | 0 | 0 | 904 | 904 | 904 | 904
TOTT2A | TOTT24 | 0 | 0 | Zero Length | 0 | 0 | 0 | 950 | 950 | 830 | 830
TOTT2B | TOTT21 | 0 | 0 | Zero Length | 0 | 0 | 0 | 904 | 904 | 904 | 904
TOTT2B | TOTT23 | 0 | 0 | Zero Length | 0 | 0 | 0 | 950 | 950 | 830 | 830
TRAW41 | TREU4A | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TRAW41 | TREU4B | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TREM21 | USKM2A | 15.048 | 0 | OHL | 0.0854 | 0.7095 | 3.7487 | 695 | 641 | 548 | 641
TYNE21 | WBOL21 | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1131 | 1052 | 912 | 1052
USKM11 | USKM12 | 0 | 0 | Series Reactor | 0.25 | 20 | 0 | 90 | 90 | 90 | 90
USKM21 | USKM2A | 0.692 | 0 | OHL | 0.0038 | 0.036 | 0.1546 | 695 | 642 | 548 | 642
USKM21 | USKM2B | 0.391 | 0 | OHL | 0.0039 | 0.0167 | 0.1052 | 682 | 629 | 538 | 629
USKM21 | WHSO21 | 5.841 | 0 | OHL | 0.0345 | 0.2401 | 1.6394 | 1005 | 956 | 874 | 956
USKM21 | WHSO22 | 5.849 | 0 | OHL | 0.0345 | 0.2405 | 1.6417 | 1005 | 956 | 873 | 956
USKM2A | WHSO21 | 5.562 | 0 | OHL | 0.0306 | 0.289 | 1.2455 | 695 | 641 | 548 | 641
USKM2B | WHSO22 | 5.851 | 0 | OHL | 0.0322 | 0.304 | 1.3103 | 682 | 629 | 538 | 629
WBUR41 | WBUR42 | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 1500 | 1500 | 1500 | 1500
WHSO41 | WHSO4A | 0.077 | 0 | OHL | 0.0001 | 0.0013 | 0.0506 | 2780 | 2570 | 2220 | 2570
WIMB21 | WIMB2A | 0 | 0 | Zero Length | 0 | 0 | 0 | 995 | 930 | 728 | 806
WTHU4C | WTHU4E | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400
WTHU4D | WTHU4F | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400

## B-2-1d
B-2-1d - OFTO Transmission Circuits for 2025/26
OFTO | Wind Farm | Node 1 | Node 2 | OHL Length(km) | Cable Length(km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA) | Voltage (kV)
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSO11 | BOSW11 | 0 | 29.45 | Cable | 1.634 | 2.451 | 25.197 | 106 | 132
TC Beatrice OFTO Limited | Beatrice Offshore Wind Farm | BEIW21 | BEIW22 | 0 | 1.315 | Cable | 0.033 | 0.014 | 4.119 | 321 | 220
|  | BEIW21 | BEAT21 | 0 | 89.2 | Cable | 0.822 | 2.262 | 291.875 | 321 | 220
|  | BEIW22 | BEAT22 | 0 | 89.2 | Cable | 0.822 | 2.262 | 291.875 | 321 | 220
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BODE41 | BBWO41 | 0 | 0.6 | Cable | 0.0009 | 0.0064 | 5.1271 | 277 | 400
|  | BBWO21 | BBWW21 | 0 | 34.622 | Cable | 0.3875 | 0.9335 | 103.7511 | 277 | 220
DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank A Offshore Wind Farm | DBAOD | DBAWD | 0 | 205 | Cable | 0.0024 | 0 | 0 | 1940 | ±320
|  | CREB41 | DBAO41 | 0 | 1.6 | Cable | 5.9e-06 | 8e-05 | 0.3796 | 2044 | 400
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDW11 | DUDO11 | 0 | 89.3 | Cable | 1.816 | 6.8182 | 110.6693 | 172 | 132
|  | DUDW12 | DUDO12 | 0 | 89.3 | Cable | 1.816 | 6.8182 | 110.6693 | 172 | 132
East Anglia One Limited | East Anglia Offshore Wind Farm | BRFO41 | BRST41 | 0 | 0.47 | Cable | 0.001209 | 0.0059617 | 3.8508 | 369 | 400
|  | BRFO41 | BRST42 | 0 | 0.47 | Cable | 0.001209 | 0.0059617 | 3.8508 | 369 | 400
|  | BRST21 | EAAW21 | 0 | 122.358 | Cable | 0.77153 | 3.2715 | 411.04 | 344 | 220
|  | BRST22 | EAAW22 | 0 | 122.358 | Cable | 0.77153 | 3.2715 | 411.04 | 344 | 220
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GALO11 | LEIS11 | 0 | 0.28 | Cable | 0.01 | 0.03 | 0.38 | 208 | 132
|  | GALO12 | LEIS11 | 0 | 0.28 | Cable | 0.01 | 0.03 | 0.38 | 208 | 132
|  | GALO11 | GANW11 | 0 | 45.8 | Cable | 1.23 | 2.83 | 58.38 | 180.6 | 132
|  | GALO12 | GANW12 | 0 | 45.8 | Cable | 1.23 | 2.83 | 58.38 | 180.6 | 132
Greater Gabbard OFTO Plc | Greater Gabbard Offshore Wind Farm | GGON11 | LEIS11 | 0 | 0 | Cable | 0 | 0 | 0 | 180 | 132
|  | GGON12 | LEIS11 | 0 | 0 | Cable | 0 | 0 | 0 | 180 | 132
|  | GGON13 | LEIS11 | 0 | 0 | Cable | 0 | 0 | 0 | 180 | 132
|  | GREG11 | GGON11 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GREG12 | GGON12 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GREG13 | GGON13 | 0 | 45 | Cable | 1.04 | 3.17 | 59.93 | 180 | 132
|  | GREG12 | GREG14 | 0 | 17 | Cable | 0.36 | 1.07 | 20.5 | 150 | 132
TC Gunfleet Sands OFTO Limited | Gunfleet Sands Offshore Wind Farm | CLTO11 | GUNS11 | 0 | 12.789 | Cable | 0.3254 | 0.8061 | 15.5518 | 158 | 132
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | GWYO11 | GWBW11 | 0 | 33.3 | Cable | 0.973 | 2.5403 | 37.6879 | 149 | 132
|  | GWYO11 | GWBW12 | 0 | 33.3 | Cable | 0.973 | 2.5403 | 37.6879 | 149 | 132
|  | GWYO12 | GWAW11 | 0 | 30.3 | Cable | 0.8763 | 2.3371 | 34.6335 | 149 | 132
|  | GWYO12 | GWAW12 | 0 | 30.3 | Cable | 0.8763 | 2.3371 | 34.6335 | 149 | 132
Diamond Transmission Partners Hornsea One Limited | Hornsea One Offshore Wind Farm | KILL41 | HOWA41 | 0 | 0.52 | Cable | 0.000387 | 0.007298 | 5.7608 | 1328 | 400
|  | KILL41 | HOWA41 | 0 | 0.5 | Cable | 0.000387 | 0.007298 | 5.7608 | 1328 | 400
|  | HOWA21 | HOWR2A | 0 | 105.1 | Cable | 0.68384 | 3.2701 | 292.1283 | 380 | 220
|  | HOWR2A | HOWW2A | 0 | 66.2 | Cable | 0.4924 | 1.6413 | 175.1469 | 380 | 220
|  | HOWA21 | HOWR2A | 0 | 104.9 | Cable | 0.69628 | 3.1955 | 303.8973 | 380 | 220
|  | HOWR2A | HOWW2B | 0 | 72.2 | Cable | 0.47736 | 1.7155 | 203.0972 | 380 | 220
|  | HOWA21 | HOWR2A | 0 | 104.7 | Cable | 0.6809 | 3.2601 | 291.07 | 380 | 220
|  | HOWR2A | HOWW2C | 0 | 85 | Cable | 0.63223 | 2.1074 | 224.8866 | 380 | 220
|  | HOWW2A | HOWW2B | 0 | 12.3 | Cable | 0.15756 | 0.30496 | 34.5997 | 364 | 220
|  | HOWW2B | HOWW2C | 0 | 13.9 | Cable | 0.17806 | 0.34463 | 39.1004 | 364 | 220
Breesea Limited | Hornsea Two Offshore Wind Farm | KILL41 | HOWB41 | 0 | 0.315 | Cable | 0.0002 | 0.004 | 3.7 | 935 | 400
|  | KILL41 | HOWB41 | 0 | 0.315 | Cable | 0.0002 | 0.004 | 3.7 | 935 | 400
|  | HOWB21 | HOWR2B | 0 | 103.7 | Cable | 0.59 | 2.69 | 338.42 | 415 | 220
|  | HOWR2B | HOWW2D | 0 | 60.2 | Cable | 0.4 | 1.5 | 165.42 | 412 | 220
|  | HOWB21 | HOWR2B | 0 | 103.55 | Cable | 0.59 | 2.69 | 337.97 | 415 | 220
|  | HOWR2B | HOWW2D | 0 | 61.6 | Cable | 0.42 | 1.52 | 169.26 | 412 | 220
|  | HOWB21 | HOWR2B | 0 | 103.4 | Cable | 0.59 | 2.69 | 382.85 | 415 | 220
|  | HOWR2B | HOWW2D | 0 | 62.2 | Cable | 0.42 | 1.54 | 170.9 | 412 | 220
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HUMO11 | HUMW11 | 0 | 39 | Cable | 1.417 | 3.447 | 46.189 | 121 | 132
|  | HUMO12 | HUMW12 | 0 | 39 | Cable | 1.417 | 3.447 | 46.189 | 121 | 132
|  | HUMO21 | HEDO21 | 0 | 0 | Cable | 0 | 0 | 0 | 121 | 132
|  | HUMO22 | HEDO21 | 0 | 0 | Cable | 0 | 0 | 0 | 121 | 132
TC Lincs OFTO Limited | Lincs Offshore Windfarm | LINO41 | WALP41 | 0 | 0.13 | Cable | 9.43e-05 | 0.001641 | 1.6336 | 492 | 400
|  | LINO11 | LINO13 | 0 | 0.129 | Cable | 0.000178 | 0.002903 | 1.4914 | 301 | 132
|  | LINO12 | LINO14 | 0 | 0.078 | Cable | 0.000108 | 0.001755 | 0.90176 | 301 | 132
|  | LINO13 | LINS11 | 0 | 60 | Cable | 2.0442 | 4.3446 | 69.5405 | 152 | 132
|  | LINO14 | LINS12 | 0 | 60 | Cable | 2.0442 | 4.3446 | 69.5405 | 152 | 132
Blue Transmission London Array Limited | London Array Offshore Wind Farm | CLEH41 | LONO4A | 0 | 0.08 | Cable | 0.00021 | 0.00052 | 0.76413 | 360 | 400
|  | CLEH41 | LONO4B | 0 | 0.13 | Cable | 0.00034125 | 0.000845 | 1.2417 | 360 | 400
|  | LONO11 | LOAW11 | 0 | 53.798 | Cable | 1.5829 | 2.9755 | 73.1044 | 167 | 150
|  | LONO12 | LOYW11 | 0 | 53.848 | Cable | 1.5837 | 2.9776 | 73.1539 | 167 | 150
|  | LONO13 | LOAW12 | 0 | 52.657 | Cable | 1.5488 | 2.9125 | 71.5816 | 167 | 150
|  | LONO14 | LOYW12 | 0 | 52.682 | Cable | 1.5492 | 2.9137 | 71.6099 | 167 | 150
Moray East Offshore Wind Limited | Moray East Offshore Wind Farm | MOWE21 | MORO21 | 0 | 90.69 | Cable | 0.632 | 2.405 | 284.21 | 312 | 220
|  | MOWE22 | MORO22 | 0 | 97.8 | Cable | 0.632 | 2.405 | 304.75 | 312 | 220
|  | MOWE23 | MORO23 | 0 | 91.48 | Cable | 0.632 | 2.405 | 286.49 | 312 | 220
|  | NEDE4K | MORF41 | 0 | 0.06 | Cable | 0.0027 | 0.001 | 0.27 | 398 | 275
|  | NEDE4K | MORF42 | 0 | 0.1 | Cable | 0.0043 | 0.002 | 0.42 | 398 | 275
Moray East Offshore Wind Limited | Moray East Offshore Wind Farm | NEDE4K | MORF43 | 0 | 0.15 | Cable | 0.001 | 0.003 | 0.67 | 398 | 275
MORAY WEST OFTO LIMITED | Moray West Offshore Wind Farm | MOWW2A | MOWO21 | 0 | 29 | Cable | 0.10961 | 0.79111 | 133.6478 | 440 | 220
|  | MOWW22 | MOWO22 | 0 | 29 | Cable | 0.10961 | 0.79111 | 133.6478 | 440 | 220
|  | MOWW21 | MOWW2A | 0 | 49 | Cable | 0.3341 | 1.0428 | 175.8342 | 440 | 220
|  | MOWW2B | MOWW22 | 0 | 51 | Cable | 0.3477 | 1.0853 | 183.0111 | 440 | 220
NEART NA GAOITHE OFFSHORE WIND LIMITED | Neart na Gaoithe Offshore Wind Farm | CRYR4- | NNGO41 | 0 | 0.58 | Cable | 0.0015 | 0.0059 | 0 | 245 | 400
|  | CRYR4- | NNGO42 | 0 | 0.58 | Cable | 0.0015 | 0.0059 | 0 | 245 | 400
|  | NNGO21 | NNGW21 | 0 | 50.659 | Cable | 0.7591 | 1.4011 | 0.006 | 230 | 220
|  | NNGO22 | NNGW22 | 0 | 50.917 | Cable | 0.7592 | 1.4081 | 0.0006 | 230 | 220
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMO11 | ORMW11 | 0 | 44.3 | Cable | 0.7323 | 3.104 | 46.68 | 158 | 132
Diamond Transmission Partners RB Limited | Race Bank Offshore Wind Farm | RACW22 | RACO22 | 0 | 82.5 | Cable | 0.487 | 2.1111 | 247.8447 | 302 | 220
|  | RACW21 | RACO21 | 0 | 83.5 | Cable | 0.4934 | 2.1359 | 250.7489 | 302 | 220
|  | WALP41 | RACO41 | 0 | 0.1 | Cable | 0.0001 | 0.0011 | 0.8093 | 450 | 400
|  | WALP41 | RACO42 | 0 | 0.1 | Cable | 0.0001 | 0.0011 | 0.8093 | 450 | 400
|  | RACW21 | RACW22 | 0 | 6.7 | Cable | 0.0433 | 0.1661 | 19.4582 | 302 | 220
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | BOLN41 | TWNE41 | 0 | 0.602 | Cable | 0.0028 | 0.0042 | 4.4179 | 411 | 400
|  | BOLN41 | TWNE42 | 0 | 0.764 | Cable | 0.0036 | 0.0053 | 5.6068 | 411 | 400
|  | TWNE11 | RAMW11 | 0 | 42.35 | Cable | 0.7285 | 1.9531 | 75.9552 | 210 | 150
|  | TWNE12 | RAMW12 | 0 | 42.29 | Cable | 0.7275 | 1.9502 | 75.842 | 210 | 150
TC Robin Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | RREW11 | 0 | 14.4 | Cable | 0.78 | 1.17 | 12.06 | 103 | 132
| Robin Rigg West Offshore Wind Farm | RORW11 | RRWW11 | 0 | 14.4 | Cable | 0.78 | 1.17 | 12.06 | 103 | 132
Seagreen Wind Energy Limited | Seagreen One Wind Farm | SGRO21 | SGRW21 | 0 | 84.1 | Cable | 0.61407 | 2.1131 | 283.19 | 362 | 220
|  | SGRO22 | SGRW22 | 0 | 84.1 | Cable | 0.61407 | 2.1131 | 283.19 | 362 | 220
|  | SGRO22 | SGRW22 | 0 | 84.1 | Cable | 0.61407 | 2.1131 | 283.19 | 362 | 220
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW11 | SALL11 | 0 | 44.8 | Cable | 1.0219 | 3.6202 | 55.2715 | 178 | 132
|  | SSBW11 | SALL12 | 0 | 42.9 | Cable | 0.9695 | 3.4676 | 53.1915 | 178 | 132
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW11 | THOW11 | 0 | 28.89 | Cable | 0.9305 | 1.9682 | 33.0484 | 155 | 132
|  | THAW12 | THOW12 | 0 | 28.89 | Cable | 0.9305 | 1.9682 | 33.0484 | 155 | 132
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNO22 | TKNW21 | 0 | 107.8 | Cable | 0.57 | 3.15 | 313 | 427 | 220
|  | TKNO21 | TKNE21 | 0 | 106.8 | Cable | 0.56 | 3.13 | 310 | 427 | 220
|  | BICF41 | TKNO41 | 0 | 2.01 | Cable | 0.004 | 0.02 | 18.6 | 505 | 400
|  | BICF41 | TKNO42 | 0 | 1.78 | Cable | 0.004 | 0.02 | 16.5 | 505 | 400
Diamond Transmission Partners Walney Extension Limited | Walney Extension Offshore Wind Farm | WOWE21 | WACW21 | 0 | 80.1 | Cable | 0.9432 | 1.99 | 251.59 | 347 | 220
|  | WADW21 | WACW21 | 0 | 22.9 | Cable | 0.4826 | 0.6719 | 50.0868 | 220 | 220
|  | WOWE22 | WADW21 | 0 | 66 | Cable | 0.7713 | 1.6434 | 207.5336 | 347 | 220
|  | MIDL41 | WOWE41 | 0 | 0.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
|  | MIDL41 | WOWE42 | 0 | 0.3 | Cable | 0.0015 | 0.0023 | 2.7143 | 470 | 400
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAO11 | WAAO1A | 0 | 2.9 | Cable | 0.076045 | 0.13688 | 3.5539 | 192 | 132
|  | WAAO1A | WAAW11 | 0 | 43.7 | Cable | 1.2943 | 2.3298 | 55.0577 | 164 | 132
Blue Transmission Walney 2 OFTO Limited | Walney 2 Offshore Wind Farm | WABO11 | WABO1A | 0 | 5.23 | Cable | 0.15 | 0.27 | 6.384 | 192 | 132
|  | WABO1A | WABW11 | 0 | 44.13 | Cable | 1.266 | 2.279 | 53.869 | 164 | 132
WoDS Transmission plc | West of Duddon Sands Offshore Wind Farm | WDSW11 | WDSO11 | 0 | 42.075 | Cable | 0.663 | 1.9978 | 69.3823 | 209 | 155
|  | WDSW12 | WDSO12 | 0 | 42.075 | Cable | 0.663 | 1.9978 | 69.3823 | 209 | 155
|  | HEYS41 | WDSO41 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
|  | HEYS41 | WDSO42 | 0 | 0.225 | Cable | 0.0004 | 0.0024 | 1.7417 | 346 | 400
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERO11 | WERW11 | 0 | 25.8335 | Cable | 0.2949 | 1.4823 | 45.7125 | 140 | 150
|  | HEDO21 | WERO21 | 0 | 0.368 | Cable | 0.003 | 0.0122 | 1.2704 | 256.7809 | 275
|  | HEDO21 | WERO22 | 0 | 0.329 | Cable | 0.0027 | 0.0109 | 1.1357 | 256.7809 | 275

## B-2-2a
B-2-2a - SHE Transmission Circuit Changes 2026/27 to 2033/34
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
CHAR1S | GLAG1S | 2026 | Change | 1.4 | 2.395 | Composite | 0.1389 | 0.5114 | 3.2329 | 113 | 105 | 105 | 105
CHAR1T | GLAG1N | 2026 | Change | 1.4 | 2.395 | Composite | 0.1389 | 0.5114 | 3.2329 | 113 | 105 | 105 | 105
CLAY1Q | REDM1Q | 2026 | Change | 0 | 4.8 | Cable | 0.1508 | 0.2841 | 6.9377 | 120 | 120 | 120 | 120
CLAY1T | REDM1R | 2026 | Change | 0 | 4.8 | Cable | 0.1508 | 0.2841 | 6.9377 | 120 | 120 | 120 | 120
ELGI1Q | KEIT11 | 2026 | Change | 27.4 | 1 | Composite | 1.3811 | 6.056 | 3.0895 | 242 | 229 | 209 | 229
ELGI1R | KEIT11 | 2026 | Change | 27.4 | 1 | Composite | 1.3786 | 6.0376 | 2.991 | 242 | 229 | 209 | 229
ERRO11 | ERRO1B | 2026 | Addition | 0 | 0.2 | Cable | 0 | 0 | 0.0001 | 22861 | 22861 | 22861 | 22861
ERRO11 | ERRO1A | 2026 | Addition | 0 | 0.2 | Cable | 0 | 0 | 0.0001 | 22861 | 22861 | 22861 | 22861
GARB1Q | SLOY11 | 2026 | Change | 14.9 | 0.13 | Composite | 0.7524 | 3.549 | 0.9158 | 148 | 139 | 139 | 139
GARB1R | SLOY11 | 2026 | Change | 14.9 | 0.15 | Composite | 0.7535 | 3.5502 | 0.9437 | 148 | 140 | 140 | 140
GARB1S | SLOY11 | 2026 | Change | 14.9 | 0.12 | Composite | 0.7514 | 3.5485 | 0.9018 | 153 | 147 | 147 | 147
GARB1T | SLOY11 | 2026 | Change | 14.9 | 0.16 | Composite | 0.754 | 3.5508 | 0.9576 | 148 | 140 | 140 | 140
GLFA1- | KEIT11 | 2026 | Change | 29.6 | 1 | Composite | 2.7101 | 6.9191 | 2.8576 | 126 | 117 | 101 | 117
GREM1J | KERG11 | 2026 | Addition | 10.2 | 10.7 | Composite | 0.5896 | 2.9812 | 20.0181 | 242 | 229 | 209 | 229
GREM1K | KERG11 | 2026 | Addition | 11.1 | 9.6 | Composite | 0.6262 | 3.0796 | 18.0693 | 242 | 229 | 209 | 229
ABED11 | DUNM1A | 2028 | Addition | 5 | 0 | OHL | 0.2495 | 1.0387 | 0.2799 | 195 | 181 | 157 | 181
ABNE1R | GRIF1T | 2028 | Change | 34.95 | 8.62 | Composite | 3.4267 | 8.7981 | 11.9578 | 133 | 123 | 106 | 123
AIGA1Q | KIOR1A | 2028 | Removed | 2.39 | 0.32 | Composite | 0.2456 | 0.6107 | 0.137 | 132.6 | 123.5 | 106.3 | 123.5
AIGN11 | KIOR1A | 2028 | Addition | 2.71 | 0.43 | Composite | 0.2588 | 0.6721 | 0.7025 | 133 | 123 | 106 | 123
ALYT21 | TEAL21 | 2028 | Change | 16.2 | 0 | OHL | 0.0638 | 0.675 | 4.5064 | 1615 | 1558 | 1458 | 1558
ALYT21 | TEAL21 | 2028 | Change | 16.2 | 0 | OHL | 0.0638 | 0.675 | 4.5064 | 1615 | 1558 | 1458 | 1558
ALYT41 | FETT41 | 2028 | Change | 67.41 | 0 | OHL | 0.1222 | 1.1964 | 42.8402 | 2349 | 2266 | 2120 | 2266
ALYT41 | FETT41 | 2028 | Change | 67.41 | 0 | OHL | 0.1222 | 1.1964 | 42.8402 | 2349 | 2266 | 2120 | 2266
ALYT41 | KINB4J | 2028 | Change | 70.04 | 0 | OHL | 0.127 | 1.2431 | 44.5116 | 2349 | 2266 | 2120 | 2266
ALYT41 | KINB4K | 2028 | Change | 70.04 | 0 | OHL | 0.127 | 1.2431 | 44.5116 | 2349 | 2266 | 2120 | 2266
ANSN2- | CRDH21 | 2028 | Addition | 20.25 | 0 | OHL | 0.0752 | 0.8961 | 5.35 | 1543 | 1477 | 1372 | 1477
ANSN2- | CRMU21 | 2028 | Addition | 24.95 | 0 | OHL | 0.0927 | 1.1041 | 6.5918 | 1543 | 1477 | 1372 | 1477
ANSU1- | INVE11 | 2028 | Removed | 11.35 | 0 | OHL | 0.1783 | 1.8641 | 0.7847 | 741 | 709 | 658 | 709
ANSU1- | PORA1A | 2028 | Removed | 24.95 | 0 | OHL | 0.3919 | 4.0977 | 1.725 | 741 | 709 | 658 | 709
ARBR1R | TEAL11 | 2028 | Removed | 23.2 | 0 | OHL | 1.6542 | 5.1082 | 1.201 | 133 | 123 | 106 | 123
ARBR1R | TEAS1- | 2028 | Addition | 18.2 | 0 | OHL | 1.4586 | 4.0482 | 0.9315 | 133 | 123 | 106 | 123
BEAU11 | CULL1A | 2028 | Change | 12.7 | 1.54 | Composite | 1.1793 | 3.0706 | 3.1444 | 133 | 123 | 106 | 123
BEAU11 | KIOR1A | 2028 | Change | 0 | 1.5 | Cable | 0.0242 | 0.1264 | 2.4508 | 203 | 203 | 203 | 203
BEAU11 | KNOC11 | 2028 | Change | 17.1 | 1.09 | Composite | 1.5776 | 3.9235 | 2.3223 | 133 | 133 | 133 | 133
BEAU11 | KNOC11 | 2028 | Change | 17.1 | 1 | Composite | 1.5748 | 3.9177 | 2.2076 | 133 | 133 | 133 | 133
BEAU4- | FAUG41 | 2028 | Change | 48.6 | 0 | OHL | 0.0632 | 0.9322 | 29.3196 | 2771 | 2674 | 2480 | 2674
BEIB11 | COGA11 | 2028 | Addition | 0.05 | 1 | Composite | 0.0182 | 0.0792 | 1.5199 | 228 | 228 | 228 | 228
BONB2J | BRCW2K | 2028 | Change | 10.1 | 0 | OHL | 0.0278 | 0.415 | 2.8741 | 1905 | 1839 | 1705 | 1839
BONB4- | MELG41 | 2028 | Change | 126.483 | 0 | OHL | 0.1637 | 2.4049 | 76.9816 | 2771 | 2674 | 2480 | 2674
BRCW2J | KINA21 | 2028 | Change | 59.185 | 0 | OHL | 0.163 | 2.4317 | 16.8418 | 1905 | 1839 | 1705 | 1839
BUMU1Q | CHAR11 | 2028 | Change | 42.2 | 0 | OHL | 3.8318 | 9.6079 | 2.1174 | 133 | 123 | 106 | 123
CASS1Q | DLCH11 | 2028 | Addition | 26.21 | 0 | OHL | 2.3764 | 6.262 | 1.2538 | 133 | 123 | 106 | 123
CASS1Q | DLCH11 | 2028 | Removed | 26.21 | 0 | OHL | 2.3762 | 6.2502 | 1.2558 | 133 | 123 | 106 | 123
CHLS11 | DLCH11 | 2028 | Addition | 10.5 | 0 | OHL | 0.524 | 2.1813 | 0.5877 | 242 | 229 | 209 | 229
CLAC1Q | INVE11 | 2028 | Change | 8.4 | 0 | OHL | 0.7621 | 1.911 | 0.4216 | 126 | 117 | 101 | 117
CLAC1Q | SLOY11 | 2028 | Change | 13.05 | 1.37 | Composite | 1.2548 | 2.9741 | 2.584 | 133 | 123 | 106 | 123
CLOI11 | MELG11 | 2028 | Addition | 7.2 | 2.3 | Composite | 0.3092 | 1.812 | 3.8565 | 228 | 228 | 228 | 228
COGA1- | COGA11 | 2028 | Addition | 6.9 | 0 | OHL | 0.3444 | 1.4334 | 0.3862 | 242 | 229 | 209 | 229
COGA1- | FARI1J | 2028 | Removed | 13.9 | 4.11 | Composite | 0.7576 | 3.1671 | 6.9378 | 228 | 228 | 228 | 228
COGA11 | FARI1J | 2028 | Addition | 7 | 4.11 | Composite | 0.4132 | 1.7337 | 6.5516 | 228 | 228 | 228 | 228
CONN2Q | LOCB21 | 2028 | Change | 76.34 | 0 | OHL | 0.4749 | 3.8965 | 16.5501 | 702 | 665 | 599 | 665
CONN2R | GORW2- | 2028 | Change | 47.76 | 0 | OHL | 0.2976 | 2.4553 | 10.3104 | 702 | 665 | 599 | 665
CRAI11 | KINT11 | 2028 | Change | 16.4 | 1.37 | Composite | 0.8406 | 3.7374 | 3.022 | 203 | 203 | 203 | 203
CRAI11 | KINT11 | 2028 | Change | 16.4 | 1.36 | Composite | 0.8405 | 3.7363 | 3.0062 | 203 | 203 | 203 | 203
CRAI11 | TARL1A | 2028 | Change | 4.7 | 0 | OHL | 0.4283 | 1.1171 | 0.2279 | 133 | 123 | 106 | 123
CRAI11 | TARL1A | 2028 | Change | 4.7 | 0 | OHL | 0.4283 | 1.1171 | 0.2279 | 133 | 123 | 106 | 123
CRAR1R | INVE11 | 2028 | Removed | 22.58 | 0 | OHL | 0.3547 | 3.7085 | 1.5611 | 741 | 709 | 658 | 709
CRAR1R | PORA11 | 2028 | Removed | 13.72 | 0 | OHL | 0.2155 | 2.2533 | 0.9486 | 741 | 709 | 658 | 709
CRAS2- | CRDH21 | 2028 | Addition | 31.48 | 0 | OHL | 0.1169 | 1.393 | 8.317 | 1543 | 1477 | 1372 | 1477
CRAS2- | CRMU21 | 2028 | Addition | 13.72 | 0 | OHL | 0.051 | 0.6071 | 3.6248 | 1543 | 1477 | 1372 | 1477
CRDH11 | FERO1A | 2028 | Addition | 6.21 | 0 | OHL | 0.7891 | 1.47 | 0.3018 | 99 | 92 | 79 | 92
CRDH11 | NANT1A | 2028 | Addition | 4.98 | 0 | OHL | 0.6328 | 1.1789 | 0.242 | 99 | 92 | 79 | 92
CRDH21 | DALB2A | 2028 | Addition | 13.5 | 0 | OHL | 0.0501 | 0.5974 | 3.5667 | 1543 | 1477 | 1372 | 1477
CRDH21 | DALB2B | 2028 | Addition | 13.5 | 0 | OHL | 0.0501 | 0.5974 | 3.5667 | 1543 | 1477 | 1372 | 1477
CRMU21 | CRSN21 | 2028 | Addition | 44.7 | 0 | OHL | 0.1673 | 1.9767 | 11.8097 | 1543 | 1477 | 1372 | 1477
CRMU21 | CRSN21 | 2028 | Addition | 44.7 | 0 | OHL | 0.1673 | 1.9767 | 11.8097 | 1543 | 1477 | 1372 | 1477
CRSN11 | CRSS11 | 2028 | Addition | 0 | 1 | Cable | 0 | 0 | 0.0005 | 22861 | 22861 | 22861 | 22861
CRSN11 | CRSS11 | 2028 | Addition | 0 | 1 | Cable | 0 | 0 | 0.0005 | 22861 | 22861 | 22861 | 22861
CRSS11 | HICL11 | 2028 | Addition | 0 | 3.9 | Cable | 0.0702 | 0.546 | 4.68 | 158 | 158 | 158 | 158
CRSS11 | PORA1A | 2028 | Removed | 44.7 | 0 | OHL | 0.7021 | 7.3414 | 3.0905 | 741 | 709 | 658 | 709
CRSS12 | PORA11 | 2028 | Removed | 44.7 | 0 | OHL | 0.7021 | 7.3414 | 3.0905 | 741 | 709 | 658 | 709
DLCH11 | LAIR1Q | 2028 | Change | 4.52 | 0 | OHL | 0.41 | 1.0761 | 0.2172 | 133 | 123 | 106 | 123
DLCH11 | LAIS1A | 2028 | Addition | 3.7 | 0 | OHL | 0.0854 | 0.743 | 0.2125 | 464 | 446 | 414 | 446
DLCH11 | LOCB11 | 2028 | Removed | 17 | 0.83 | Composite | 0.4024 | 3.4774 | 2.4655 | 373 | 373 | 373 | 373
DONW21 | DOUN21 | 2028 | Addition | 0 | 0.35 | Cable | 0.0009 | 0.0064 | 2.004 | 585 | 585 | 585 | 585
DONW21 | FINS21 | 2028 | Addition | 0 | 66.749 | Cable | 0.6535 | 1.5542 | 164.8261 | 224 | 224 | 224 | 224
DUNM1- | DUNM1A | 2028 | Addition | 2.76 | 0 | OHL | 0.1377 | 0.5734 | 0.1545 | 242 | 229 | 209 | 229
DUNM1- | FARI1K | 2028 | Removed | 6 | 4.07 | Composite | 0.3635 | 1.5267 | 6.5106 | 228 | 228 | 228 | 228
DUNM1A | FARI1K | 2028 | Addition | 3.24 | 4.07 | Composite | 0.2257 | 0.9533 | 6.3561 | 228 | 228 | 228 | 228
DYCE1J | KINT11 | 2028 | Change | 10.17 | 1.9 | Composite | 0.7474 | 2.4256 | 3.5243 | 145 | 131 | 116 | 131
DYCE1K | KINT11 | 2028 | Change | 10.17 | 1.9 | Composite | 0.5381 | 2.4328 | 3.529 | 203 | 203 | 203 | 203
FARI2J | FOYE2- | 2028 | Change | 8.4 | 0 | OHL | 0.0491 | 0.3665 | 2.2471 | 934 | 881 | 791 | 881
FARI2J | KNOC21 | 2028 | Change | 14.9 | 0 | OHL | 0.0871 | 0.6501 | 3.986 | 934 | 881 | 791 | 881
FARI2K | FOYE2- | 2028 | Change | 8.4 | 0 | OHL | 0.0491 | 0.3665 | 2.2471 | 934 | 881 | 791 | 881
FARI2K | KNOC21 | 2028 | Change | 14.9 | 0 | OHL | 0.0871 | 0.6501 | 3.986 | 934 | 881 | 791 | 881
FASN2R | FAUG2R | 2028 | Change | 25.4 | 0 | OHL | 0.0707 | 1.0666 | 7.0845 | 1905 | 1839 | 1705 | 1839
FAUG11 | FWIL1A | 2028 | Change | 8.5 | 0.25 | Composite | 0.5918 | 1.9651 | 0.8738 | 255 | 247 | 237 | 247
FAUG11 | FWIL1R | 2028 | Change | 43.4 | 0.17 | Composite | 3.0094 | 9.9692 | 2.4696 | 255 | 247 | 237 | 247
FAUG11 | GLDO1G | 2028 | Change | 0 | 7.539 | Cable | 0.2512 | 0.8622 | 7.5701 | 120 | 120 | 120 | 120
FAUG11 | GLEN1- | 2028 | Change | 11.29 | 0.36 | Composite | 0.7827 | 2.6487 | 0.5499 | 270 | 265 | 260 | 265
FAUG11 | MILW1A | 2028 | Change | 12.19 | 0.34 | Composite | 0.845 | 2.8607 | 0.5933 | 270 | 265 | 260 | 265
FAUG2Q | TUMM2J | 2028 | Change | 77.2 | 0 | OHL | 0.2105 | 3.0631 | 22.3618 | 1905 | 1839 | 1705 | 1839
FAUG41 | MELG41 | 2028 | Change | 24.01 | 0 | OHL | 0.0313 | 0.4663 | 14.4552 | 2771 | 2674 | 2480 | 2674
FERO1- | FERO1A | 2028 | Addition | 5.1 | 0 | OHL | 0.6451 | 1.1203 | 0.2657 | 99 | 92 | 79 | 92
FERO1- | TAYN1A | 2028 | Removed | 5.1 | 0 | OHL | 0.6451 | 1.1203 | 0.2657 | 99 | 92 | 79 | 92
FERO1A | TAYN1R | 2028 | Addition | 6.3 | 0 | OHL | 0.8006 | 1.4914 | 0.3062 | 99 | 92 | 79 | 92
FETT41 | KINT41 | 2028 | Change | 32.21 | 0 | OHL | 0.0584 | 0.5717 | 20.47 | 2349 | 2266 | 2120 | 2266
FETT41 | KINT41 | 2028 | Change | 32.21 | 0 | OHL | 0.0584 | 0.5717 | 20.47 | 2349 | 2266 | 2120 | 2266
FRAS1Q | STRI1A | 2028 | Change | 10.1 | 0 | OHL | 0.9205 | 2.4007 | 0.4898 | 126 | 117 | 101 | 117
FRAS1R | STRI1B | 2028 | Change | 10.1 | 0 | OHL | 0.9205 | 2.4007 | 0.4898 | 126 | 117 | 101 | 117
FWIL1A | FWIL1Q | 2028 | Change | 34.9 | 0 | OHL | 2.4185 | 8.0087 | 1.7399 | 255 | 247 | 237 | 247
GLRB2- | TEAL21 | 2028 | Change | 38.8 | 0 | OHL | 0.1582 | 1.3783 | 12.2465 | 1911 | 1870 | 1828 | 1870
INVE11 | NANT1A | 2028 | Removed | 15.1 | 0 | OHL | 1.9103 | 3.4005 | 0.7609 | 99 | 92 | 79 | 92
INVE11 | SLOY11 | 2028 | Change | 21.4 | 1.28 | Composite | 2.0092 | 4.9655 | 2.8547 | 126 | 117 | 101 | 117
INVE11 | TAYN1A | 2028 | Removed | 16.29 | 0 | OHL | 2.0608 | 3.6685 | 0.8208 | 99 | 92 | 79 | 92
KEIC1- | KEIT11 | 2028 | Addition | 0 | 0.31 | Cable | 0.0043 | 0.0315 | 0.4989 | 160 | 160 | 160 | 160
KEIC1- | KEIT11 | 2028 | Removed | 0 | 0.31 | Cable | 0.0043 | 0.0315 | 0.4989 | 160 | 160 | 160 | 160
KINA21 | TUMM2K | 2028 | Change | 4.008 | 0 | OHL | 0.011 | 0.1647 | 1.1405 | 1905 | 1839 | 1705 | 1839
KINT11 | TARL1A | 2028 | Change | 15.55 | 0.12 | Composite | 1.6395 | 3.6453 | 0.9505 | 112 | 104 | 90 | 104
KINT21 | PERS2R | 2028 | Change | 28.2 | 0 | OHL | 0.1285 | 1.2228 | 7.4248 | 1096 | 1029 | 924 | 1029
LAIS11 | LAIS1A | 2028 | Addition | 0 | 0.6 | Cable | 0.0125 | 0.046 | 0.8214 | 112 | 112 | 112 | 112
LAIS1A | LOCB11 | 2028 | Addition | 13.3 | 0.83 | Composite | 0.317 | 2.7344 | 2.2529 | 373 | 373 | 373 | 373
PEHE21 | PERS2Q | 2028 | Change | 47.6 | 0 | OHL | 0.216 | 2.0277 | 12.6919 | 1096 | 1029 | 924 | 1029
PEHG1A | PEHG1Q | 2028 | Change | 1.8 | 0 | OHL | 0.0907 | 0.4113 | 0.0918 | 242 | 229 | 209 | 229
PEHG1A | SFER1K | 2028 | Change | 6.1 | 0 | OHL | 0.3073 | 1.3939 | 0.3112 | 242 | 229 | 209 | 229
PEHG1B | PEHG1R | 2028 | Change | 1.8 | 0 | OHL | 0.0907 | 0.4113 | 0.0918 | 242 | 229 | 209 | 229
PEHG1B | SFER1J | 2028 | Change | 6.1 | 0 | OHL | 0.3073 | 1.3939 | 0.3112 | 242 | 229 | 209 | 229
PORA11 | PORA1R | 2028 | Removed | 6.14 | 0 | OHL | 0.7766 | 1.383 | 0.3092 | 99 | 92 | 79 | 92
PORA1A | PORA1Q | 2028 | Removed | 6.14 | 0 | OHL | 0.7766 | 1.383 | 0.3092 | 99 | 92 | 79 | 92
SFEE1A | SFEG1S | 2028 | Change | 0.39 | 0 | OHL | 0.0354 | 0.0911 | 0.0192 | 126 | 117 | 101 | 117
SFEE1A | SFER11 | 2028 | Change | 1.71 | 0 | OHL | 0.1554 | 0.3995 | 0.0842 | 126 | 117 | 101 | 117
SFEE1B | SFEG1T | 2028 | Change | 0.39 | 0 | OHL | 0.0354 | 0.0911 | 0.0192 | 126 | 117 | 101 | 117
SFEE1B | SFER11 | 2028 | Change | 1.71 | 0 | OHL | 0.1554 | 0.3995 | 0.0842 | 126 | 117 | 101 | 117
SFER11 | STRI1A | 2028 | Change | 6.3 | 0 | OHL | 0.5742 | 1.4974 | 0.3055 | 126 | 117 | 101 | 117
SFER11 | STRI1B | 2028 | Change | 6.3 | 0 | OHL | 0.5742 | 1.4974 | 0.3055 | 126 | 117 | 101 | 117
STRI1A | STRI1Q | 2028 | Change | 7.9 | 0 | OHL | 0.72 | 1.8777 | 0.3831 | 126 | 117 | 101 | 117
STRI1B | STRI1R | 2028 | Change | 7.9 | 0 | OHL | 0.72 | 1.8777 | 0.3831 | 126 | 117 | 101 | 117
STRW1- | STWO11 | 2028 | Addition | 4.25 | 0 | OHL | 0.1344 | 0.928 | 0.226 | 336 | 320 | 290 | 320
TARL1A | TARL1J | 2028 | Change | 34.6 | 0 | OHL | 3.1392 | 7.8715 | 1.7364 | 133 | 123 | 106 | 123
TARL1A | TARL1K | 2028 | Change | 34.6 | 0 | OHL | 3.1392 | 7.8715 | 1.7364 | 133 | 123 | 106 | 123
TAYN1A | TAYN1R | 2028 | Removed | 6.3 | 0 | OHL | 0.797 | 1.4188 | 0.3175 | 99 | 92 | 79 | 92
TEAL11 | TEAS1- | 2028 | Addition | 5 | 0 | OHL | 0.1956 | 1.06 | 0.2695 | 183 | 160 | 149 | 160
TEAL21 | WFIB2- | 2028 | Change | 38.8 | 0 | OHL | 0.1582 | 1.3783 | 12.2465 | 1911 | 1870 | 1828 | 1870
ACHE11 | SHIN11 | 2030 | Addition | 16 | 1.5 | Composite | 0.8441 | 3.4638 | 2.6691 | 126 | 126 | 126 | 126
ALYT21 | TEAL21 | 2030 | Removed | 16.2 | 0 | OHL | 0.0638 | 0.675 | 4.5064 | 1615 | 1558 | 1458 | 1558
ALYT22 | TEAL21 | 2030 | Removed | 16.2 | 0 | OHL | 0.0638 | 0.675 | 4.5064 | 1615 | 1558 | 1458 | 1558
ALYT41 | EMMO41 | 2030 | Addition | 16.2 | 0 | OHL | 0.0301 | 0.3193 | 9.5731 | 2349 | 2266 | 2120 | 2266
ALYT41 | EMMO41 | 2030 | Addition | 16.2 | 0 | OHL | 0.0301 | 0.3193 | 9.5731 | 2349 | 2266 | 2120 | 2266
ARMO1- | DUGR1Q | 2030 | Change | 14 | 0 | OHL | 0.6987 | 2.9084 | 0.7836 | 195 | 181 | 157 | 181
BALA11 | HARI1- | 2030 | Addition | 32.5 | 0 | OHL | 1.622 | 6.7516 | 1.8191 | 242 | 229 | 209 | 229
BALA11 | LEWI11 | 2030 | Addition | 26 | 0 | OHL | 1.2976 | 5.4013 | 1.4553 | 242 | 229 | 209 | 229
BALA11 | MUAI11 | 2030 | Addition | 13 | 0 | OHL | 0.6488 | 2.7007 | 0.7276 | 242 | 229 | 209 | 229
BANN21 | SPIT21 | 2030 | Addition | 0 | 1.9 | Cable | 0.0008 | 0.0234 | 20.2491 | 1560 | 1560 | 1560 | 1560
BANN21 | SPIT21 | 2030 | Addition | 0 | 1.9 | Cable | 0.0008 | 0.0234 | 20.2491 | 1560 | 1560 | 1560 | 1560
BANN41 | BANN4A | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0005 | 69275 | 69275 | 69275 | 69275
BANN4A | BANN41 | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0005 | 69275 | 69275 | 69275 | 69275
BANN41 | CAAI41 | 2030 | Addition | 97 | 0 | OHL | 0.0854 | 1.7387 | 63.6096 | 2771 | 2771 | 2771 | 2771
BANN41 | CAAI41 | 2030 | Addition | 97 | 0 | OHL | 0.0854 | 1.7387 | 63.6096 | 2771 | 2771 | 2771 | 2771
BANN41 | OWPL41 | 2030 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
BANN41 | OWPL41 | 2030 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
BEAU11 | KNOC11 | 2030 | Removed | 17.1 | 1.09 | Composite | 1.5776 | 3.9235 | 2.3223 | 133 | 133 | 133 | 133
BEAU11 | KNOC11 | 2030 | Removed | 17.1 | 1 | Composite | 1.5748 | 3.9177 | 2.2076 | 133 | 133 | 133 | 133
BEAU11 | SHIN11 | 2030 | Change | 58.62 | 4.25 | Composite | 5.4645 | 13.5151 | 8.045 | 126 | 117 | 101 | 117
BEAU11 | SHIN11 | 2030 | Change | 58.62 | 4.28 | Composite | 5.4653 | 13.5178 | 8.0848 | 133 | 123 | 106 | 123
BEAU21 | FASN2Q | 2030 | Removed | 25.3 | 0 | OHL | 0.0687 | 0.9878 | 7.3866 | 1905 | 1839 | 1705 | 1839
BEAU21 | FYRI2J | 2030 | Change | 29 | 1.5 | Composite | 0.1822 | 1.5002 | 14.8807 | 780 | 750 | 700 | 750
BEAU21 | FYRI2K | 2030 | Change | 29 | 1.5 | Composite | 0.1822 | 1.5002 | 14.8807 | 780 | 750 | 700 | 750
BEAU4- | FAUG41 | 2030 | Removed | 48.6 | 0 | OHL | 0.0632 | 0.9322 | 29.3196 | 2771 | 2674 | 2480 | 2674
BEAU4- | FNLN41 | 2030 | Addition | 5 | 0 | OHL | 0.0064 | 0.0923 | 3.0885 | 2771 | 2674 | 2480 | 2674
BEAU4A | FNLN41 | 2030 | Addition | 5 | 0 | OHL | 0.0064 | 0.0923 | 3.0885 | 2771 | 2674 | 2480 | 2674
BERB2Q | BLHI21 | 2030 | Removed | 46.26 | 0 | OHL | 0.2661 | 1.8527 | 13.0844 | 934 | 881 | 791 | 881
BERB2Q | CLGO2K | 2030 | Addition | 0.46 | 0 | OHL | 0.0026 | 0.0184 | 0.1301 | 934 | 881 | 791 | 881
BERB2Q | KNOC21 | 2030 | Change | 36.1 | 7 | Composite | 0.2407 | 1.7715 | 51.223 | 931 | 881 | 791 | 881
BERB2R | CLGO2J | 2030 | Addition | 0.46 | 0 | OHL | 0.0026 | 0.0184 | 0.1301 | 934 | 881 | 791 | 881
BERB2R | KNOC21 | 2030 | Addition | 39.98 | 7 | Composite | 0.2407 | 1.7715 | 51.223 | 931 | 881 | 791 | 881
BING11 | FASN1A | 2030 | Addition | 0 | 8 | Cable | 0.1832 | 0.6763 | 10.9478 | 186 | 186 | 186 | 186
BING11 | FASN1B | 2030 | Addition | 0 | 8 | Cable | 0.1832 | 0.6763 | 10.9478 | 186 | 186 | 186 | 186
BING11 | TOSY11 | 2030 | Addition | 16.5 | 0 | OHL | 1.4948 | 3.5249 | 0.885 | 133 | 123 | 106 | 123
BING41 | FAUG41 | 2030 | Addition | 25.4 | 0 | OHL | 0.0335 | 0.5057 | 14.9584 | 2771 | 2674 | 2480 | 2674
BING41 | FNLN41 | 2030 | Addition | 20.3 | 0 | OHL | 0.026 | 0.3746 | 12.5394 | 2771 | 2674 | 2480 | 2674
BLEX1- | FAUG11 | 2030 | Addition | 14.4 | 5.2 | Composite | 0.9604 | 3.3019 | 10.1655 | 120 | 120 | 120 | 120
BLGH11 | CRDH11 | 2030 | Addition | 10 | 0.5 | Composite | 0.5095 | 2.1158 | 1.2442 | 112 | 112 | 112 | 112
BLHI11 | ELCH11 | 2030 | Addition | 24.3 | 1.7 | Composite | 1.2395 | 5.1652 | 3.9393 | 228 | 228 | 228 | 228
BLHI21 | CLGO2K | 2030 | Addition | 44.72 | 0 | OHL | 0.2573 | 1.7911 | 12.6489 | 934 | 881 | 791 | 881
BLHI4Q | FNLN41 | 2030 | Addition | 110 | 0 | OHL | 0.0968 | 1.9717 | 72.1346 | 2771 | 2771 | 2771 | 2771
BLHI4Q | GRNS41 | 2030 | Addition | 60.37 | 0 | OHL | 0.0545 | 1.0838 | 39.5705 | 2771 | 2771 | 2771 | 2771
BLHI4R | FNLN41 | 2030 | Addition | 110 | 0 | OHL | 0.0968 | 1.9717 | 72.1346 | 2771 | 2771 | 2771 | 2771
BLHI4R | GRNS41 | 2030 | Addition | 60.37 | 0 | OHL | 0.0545 | 1.0838 | 39.5705 | 2771 | 2771 | 2771 | 2771
BONB2J | BRCW2K | 2030 | Removed | 10.1 | 0 | OHL | 0.0278 | 0.415 | 2.8741 | 1905 | 1839 | 1705 | 1839
BONB4- | MELG41 | 2030 | Change | 125.99 | 0 | OHL | 0.163 | 2.3924 | 76.7317 | 2771 | 2674 | 2480 | 2674
BONB4A | CMBS41 | 2030 | Addition | 10 | 0 | OHL | 0.013 | 0.1942 | 6.0205 | 2771 | 2674 | 2480 | 2674
BRCW11 | CMBS11 | 2030 | Addition | 0 | 0.1 | Cable | 0.0011 | 0.0058 | 0.18 | 319 | 319 | 319 | 319
BRCW11 | CMBS11 | 2030 | Addition | 0 | 0.1 | Cable | 0.0011 | 0.0058 | 0.18 | 319 | 319 | 319 | 319
BRCW2J | KINA21 | 2030 | Removed | 59.185 | 0 | OHL | 0.163 | 2.4317 | 16.8418 | 1905 | 1839 | 1705 | 1839
BROA1A | BROA11 | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0001 | 22861 | 22861 | 22861 | 22861
BROA1B | BROA11 | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0001 | 22861 | 22861 | 22861 | 22861
BROA11 | EDIN11 | 2030 | Change | 28 | 15.131 | Composite | 0.7241 | 6.7434 | 60.6017 | 414 | 400 | 366 | 400
BROA11 | EDIN11 | 2030 | Addition | 28 | 15.158 | Composite | 0.7242 | 6.7445 | 60.7071 | 414 | 400 | 366 | 400
BROA11 | FAUG11 | 2030 | Addition | 82 | 9 | Composite | 1.9634 | 18.4101 | 39.5248 | 414 | 400 | 366 | 400
BROA11 | QUOI1Q | 2030 | Change | 63 | 0 | OHL | 1.4777 | 13.8822 | 3.3538 | 421 | 400 | 366 | 400
BROR1A | DUBE1- | 2030 | Change | 34.58 | 4 | Composite | 3.2792 | 8.1349 | 6.4872 | 126 | 117 | 101 | 117
CAAD1Q | TNGF11 | 2030 | Addition | 13.5 | 6.25 | Composite | 0.4933 | 3.5174 | 12.766 | 301 | 301 | 301 | 301
CAAD1R | CNBH1A | 2030 | Addition | 13.5 | 0.65 | Composite | 0.4356 | 3.1059 | 1.9531 | 301 | 301 | 301 | 301
CAAI11 | DLCH11 | 2030 | Addition | 17 | 1.2 | Composite | 0.4068 | 3.5057 | 3.1292 | 373 | 373 | 373 | 373
CAAI11 | LAIS1A | 2030 | Addition | 13.3 | 1.2 | Composite | 0.3214 | 2.7627 | 2.9167 | 373 | 373 | 373 | 373
CAAI41 | FNLN41 | 2030 | Addition | 75 | 0 | OHL | 0.066 | 1.3443 | 49.1827 | 2771 | 2771 | 2771 | 2771
CAAI41 | FNLN41 | 2030 | Addition | 75 | 0 | OHL | 0.066 | 1.3443 | 49.1827 | 2771 | 2771 | 2771 | 2771
CLAT1- | INVE11 | 2030 | Addition | 9.18 | 0 | OHL | 0.8329 | 2.0884 | 0.4607 | 126 | 117 | 101 | 117
CLAT1- | SLOY11 | 2030 | Addition | 12.22 | 1.28 | Composite | 1.1766 | 2.8765 | 2.394 | 126 | 117 | 101 | 117
CLGO11 | OURA1- | 2030 | Addition | 9 | 1 | Composite | 0.4772 | 1.9582 | 1.8275 | 149 | 149 | 149 | 149
CLGO2J | DAAS2- | 2030 | Addition | 12.77 | 0 | OHL | 0.0735 | 0.5137 | 3.6019 | 934 | 881 | 791 | 881
CMBS41 | KINA41 | 2030 | Addition | 59.8 | 0 | OHL | 0.0779 | 1.1613 | 36.0025 | 2771 | 2674 | 2480 | 2674
CONN11 | STCS11 | 2030 | Addition | 12 | 0.76 | Composite | 0.2087 | 2.0271 | 1.9014 | 200 | 200 | 200 | 200
CONN11 | STRW1- | 2030 | Removed | 12 | 1.11 | Composite | 0.6221 | 2.5859 | 2.1934 | 200 | 200 | 200 | 200
CONN1J | KRKN11 | 2030 | Addition | 1.5 | 0.5 | Composite | 0.0853 | 0.3535 | 0.7694 | 200 | 200 | 200 | 200
CONN1J | STCS11 | 2030 | Addition | 12 | 0.76 | Composite | 0.2087 | 2.0271 | 1.9014 | 200 | 200 | 200 | 200
CONN2Q | LOCB21 | 2030 | Change | 75.34 | 1 | Composite | 0.4702 | 3.8704 | 22.034 | 702 | 665 | 599 | 665
CRAI11 | WOHI1Q | 2030 | Change | 0 | 3.75 | Cable | 0.0937 | 0.3188 | 4.3125 | 160 | 160 | 160 | 160
CRAI11 | WOHI1R | 2030 | Change | 0 | 3.75 | Cable | 0.0937 | 0.3188 | 4.3125 | 160 | 160 | 160 | 160
CRDH11 | LAFD11 | 2030 | Addition | 7.5 | 0.5 | Composite | 0.3883 | 1.6023 | 1.0818 | 149 | 149 | 149 | 149
CRSN11 | CRSS11 | 2030 | Change | 0 | 1 | Cable | 0.011 | 0.058 | 1.8001 | 319 | 319 | 319 | 319
CRSN11 | CRSS11 | 2030 | Change | 0 | 1 | Cable | 0.011 | 0.058 | 1.8001 | 319 | 319 | 319 | 319
CULL1A | DEAW1- | 2030 | Change | 5.2 | 3.8 | Composite | 0.5786 | 1.5375 | 5.2886 | 133 | 123 | 106 | 123
DAAS2- | KNOC21 | 2030 | Removed | 60.22 | 0 | OHL | 0.3465 | 2.4118 | 17.033 | 934 | 881 | 791 | 881
DELL11 | MELG11 | 2030 | Addition | 7.2 | 8.1 | Composite | 0.4004 | 2.2113 | 12.656 | 228 | 228 | 228 | 228
DLCH11 | LAIS1A | 2030 | Addition | 3.7 | 0 | OHL | 0.0854 | 0.743 | 0.2125 | 464 | 446 | 414 | 446
DLCH11 | LAIS1A | 2030 | Removed | 3.7 | 0 | OHL | 0.0854 | 0.743 | 0.2125 | 464 | 446 | 414 | 446
DLCH11 | LOCB11 | 2030 | Removed | 17 | 0.92 | Composite | 0.4035 | 3.4843 | 2.6269 | 373 | 373 | 373 | 373
DOUN11 | OWFD11 | 2030 | Addition | 0 | 1 | Cable | 0.0205 | 0.0848 | 1.3486 | 190 | 190 | 190 | 190
DUDH1Q | GLAG1S | 2030 | Removed | 0 | 1.95 | Cable | 0.0585 | 0.115 | 2.73 | 124 | 124 | 124 | 124
DUDH1Q | MILC1T | 2030 | Removed | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 131 | 131 | 131
DUDH1R | GLAG1N | 2030 | Removed | 0 | 1.95 | Cable | 0.0585 | 0.115 | 2.73 | 124 | 124 | 124 | 124
DUDH1R | MILC1V | 2030 | Removed | 0 | 4.8 | Cable | 0.255 | 0.442 | 5.304 | 131 | 131 | 131 | 131
DUGR1Q | EDIN11 | 2030 | Change | 9 | 0 | OHL | 0.4492 | 1.8697 | 0.5037 | 195 | 181 | 157 | 181
DUNO1Q | WHTB1S | 2030 | Change | 18.1 | 0 | OHL | 0.906 | 4.3138 | 0.8885 | 242 | 229 | 209 | 229
DUNO1R | WHTB1T | 2030 | Change | 18.1 | 0 | OHL | 0.906 | 4.3138 | 0.8885 | 242 | 229 | 209 | 229
DYCE1J | KINT11 | 2030 | Change | 10.17 | 1.9 | Composite | 0.5381 | 2.4328 | 3.5291 | 203 | 203 | 203 | 203
DYCE1K | KINT11 | 2030 | Change | 10.17 | 1.9 | Composite | 0.5381 | 2.4328 | 3.5291 | 203 | 203 | 203 | 203
EDIN1A | EDIN11 | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0001 | 22861 | 22861 | 22861 | 22861
EDIN1B | EDIN11 | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0001 | 22861 | 22861 | 22861 | 22861
EDIN11 | GLUE1- | 2030 | Addition | 0 | 2.8 | Cable | 0.0166 | 0.214 | 5.0189 | 348 | 348 | 348 | 348
ELGI1Q | KEIT11 | 2030 | Change | 22.9 | 5.5 | parallel Composite | 1.2154 | 5.4442 | 10.2417 | 242 | 229 | 209 | 229
ELGI1R | KEIT11 | 2030 | Change | 22.9 | 5.5 | parallel Composite | 1.2129 | 5.4258 | 10.1433 | 242 | 229 | 209 | 229
EMMO21 | TEAL21 | 2030 | Addition | 0 | 1 | Cable | 0.0004 | 0.0123 | 10.6574 | 1560 | 1560 | 1560 | 1560
EMMO21 | TEAL21 | 2030 | Addition | 0 | 1 | Cable | 0.0004 | 0.0123 | 10.6574 | 1560 | 1560 | 1560 | 1560
EMMO21 | TEAL21 | 2030 | Addition | 0 | 1 | Cable | 0.0004 | 0.0123 | 10.6574 | 1560 | 1560 | 1560 | 1560
EMMO41 | GLRB4- | 2030 | Addition | 38.8 | 0 | OHL | 0.0747 | 0.6444 | 26.2939 | 2780 | 2720 | 2660 | 2720
EMMO41 | HURL41 | 2030 | Addition | 59 | 0 | OHL | 0.0519 | 1.0575 | 38.6904 | 2771 | 2771 | 2771 | 2771
EMMO41 | HURL41 | 2030 | Addition | 59 | 0 | OHL | 0.0519 | 1.0575 | 38.6904 | 2771 | 2771 | 2771 | 2771
EMMO41 | WFIB4- | 2030 | Addition | 38.8 | 0 | OHL | 0.0747 | 0.6444 | 26.2939 | 2780 | 2720 | 2660 | 2720
ERRO11 | KINA1A | 2030 | Addition | 0 | 4 | Cable | 0.0186 | 0.1613 | 13.9908 | 240 | 240 | 240 | 240
ERRO11 | KINA1B | 2030 | Addition | 0 | 4 | Cable | 0.0186 | 0.1613 | 13.9908 | 240 | 240 | 240 | 240
ERRO11 | TUMM1J | 2030 | Removed | 0 | 1.33 | Cable | 0.0137 | 0.0977 | 2.5681 | 301 | 301 | 301 | 301
ERRO11 | TUMM1K | 2030 | Removed | 0 | 1.3 | Cable | 0.0134 | 0.0955 | 2.5101 | 301 | 301 | 301 | 301
FASN2R | FAUG2R | 2030 | Removed | 25.4 | 0 | OHL | 0.0707 | 1.0666 | 7.0845 | 1905 | 1839 | 1705 | 1839
FAUG11 | FWIL1A | 2030 | Removed | 8.5 | 0.25 | Composite | 0.5918 | 1.9651 | 0.8738 | 255 | 247 | 237 | 247
FAUG11 | FWIL1R | 2030 | Removed | 43.4 | 0.17 | Composite | 3.0094 | 9.9692 | 2.4696 | 255 | 247 | 237 | 247
FAUG11 | QUOI1Q | 2030 | Change | 19 | 9 | Composite | 0.4857 | 4.5279 | 36.1711 | 414 | 400 | 366 | 400
FAUG2Q | TUMM2J | 2030 | Removed | 77.2 | 0 | OHL | 0.2105 | 3.0631 | 22.3618 | 1905 | 1839 | 1705 | 1839
FAUG41 | FAUG42 | 2030 | Addition | 0 | 0.721 | Cable | 0 | 0 | 0.0036 | 69275 | 69275 | 69275 | 69275
FAUG42 | FAUG41 | 2030 | Addition | 0 | 0.721 | Cable | 0 | 0 | 0.0036 | 69275 | 69275 | 69275 | 69275
FAUG41 | FNLN41 | 2030 | Addition | 45.7 | 0 | OHL | 0.0595 | 0.8803 | 27.4978 | 2771 | 2674 | 2480 | 2674
FAUG41 | KINA41 | 2030 | Addition | 80.2 | 0 | OHL | 0.1034 | 1.5032 | 49.164 | 2771 | 2674 | 2480 | 2674
FAUG41 | LOCL41 | 2030 | Addition | 8.5 | 0 | OHL | 0.0112 | 0.1692 | 5.0055 | 2771 | 2674 | 2480 | 2674
FAUG41 | LOCL41 | 2030 | Addition | 8.5 | 0 | OHL | 0.0112 | 0.1692 | 5.0055 | 2771 | 2674 | 2480 | 2674
FETT11 | GLDY11 | 2030 | Addition | 20.75 | 0.75 | Composite | 1.0476 | 4.3929 | 2.3431 | 203 | 203 | 203 | 203
FINS11 | HEST11 | 2030 | Addition | 31.4 | 12.3 | Composite | 1.8244 | 7.5539 | 18.6206 | 200 | 200 | 200 | 200
FNLN41 | FNLN4A | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0005 | 69275 | 69275 | 69275 | 69275
FNLN41 | FNLN4A | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0005 | 69275 | 69275 | 69275 | 69275
FOYE2- | LKEM21 | 2030 | Addition | 0 | 7.5 | Cable | 0.0177 | 0.2328 | 44.3686 | 850 | 850 | 850 | 850
FWIL1A | INGA1Q | 2030 | Removed | 2.4 | 0.13 | Composite | 0.2176 | 0.5738 | 0.1148 | 133 | 123 | 106 | 123
FWIL1R | LOCL11 | 2030 | Addition | 34.9 | 0 | OHL | 2.4235 | 8.1468 | 1.7136 | 255 | 247 | 237 | 247
GARV11 | LOCB11 | 2030 | Addition | 0 | 4 | Cable | 0.0283 | 0.1548 | 13.5231 | 444 | 444 | 444 | 444
GILB11 | HOME11 | 2030 | Addition | 0 | 0.5 | Cable | 0.015 | 0.0295 | 0.7 | 124 | 124 | 124 | 124
GILB11 | MEYG11 | 2030 | Addition | 0 | 0.1 | Cable | 0.0011 | 0.0058 | 0.18 | 319 | 319 | 319 | 319
GILB11 | MEYG11 | 2030 | Addition | 0 | 0.1 | Cable | 0.0011 | 0.0058 | 0.18 | 319 | 319 | 319 | 319
GILB11 | MEYG11 | 2030 | Addition | 0 | 0.1 | Cable | 0.0011 | 0.0058 | 0.18 | 319 | 319 | 319 | 319
GILB11 | SLCK11 | 2030 | Addition | 7 | 0.5 | Composite | 0.3644 | 1.4837 | 1.0918 | 124 | 124 | 124 | 124
GILB11 | THUS11 | 2030 | Addition | 13.1 | 10 | Composite | 0.3664 | 3.6507 | 18.6221 | 348 | 348 | 348 | 348
GILB11 | THUS11 | 2030 | Addition | 13.1 | 10 | Composite | 0.3664 | 3.6507 | 18.6221 | 348 | 348 | 348 | 348
GLAG1N | STNG11 | 2030 | Addition | 0 | 2.76 | Cable | 0.0828 | 0.1628 | 3.864 | 124 | 124 | 124 | 124
GLAG1S | STNG11 | 2030 | Addition | 0 | 2.76 | Cable | 0.0828 | 0.1628 | 3.864 | 124 | 124 | 124 | 124
GLRB2- | TEAL21 | 2030 | Removed | 38.8 | 0 | OHL | 0.1582 | 1.3783 | 12.2465 | 1911 | 1870 | 1828 | 1870
GREM1J | KERG11 | 2030 | Removed | 10.2 | 10.7 | Composite | 0.5896 | 2.9812 | 20.0181 | 242 | 229 | 209 | 229
GREM1J | MSHL11 | 2030 | Addition | 0 | 1.7 | Cable | 0.0128 | 0.137 | 3.0897 | 286 | 286 | 286 | 286
GRNS41 | LOSD41 | 2030 | Addition | 22.39 | 0 | OHL | 0.0202 | 0.4019 | 14.6759 | 2771 | 2771 | 2771 | 2771
GRNS41 | LOSD41 | 2030 | Addition | 22.39 | 0 | OHL | 0.0202 | 0.4019 | 14.6759 | 2771 | 2771 | 2771 | 2771
GRNS41 | NEDE41 | 2030 | Addition | 0 | 3 | Cable | 0.002 | 0.0164 | 33.651 | 1299 | 1299 | 1299 | 1299
GRNS41 | NEDE41 | 2030 | Addition | 0 | 3 | Cable | 0.002 | 0.0164 | 33.651 | 1299 | 1299 | 1299 | 1299
GRNS41 | NEDE41 | 2030 | Addition | 0 | 3 | Cable | 0.002 | 0.0164 | 33.651 | 1299 | 1299 | 1299 | 1299
GRNV41 | NEDE41 | 2030 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
HEBW11 | LEWI11 | 2030 | Addition | 1.9 | 0.6 | Composite | 0.1027 | 0.444 | 1.0917 | 242 | 229 | 209 | 229
HURL41 | KINT41 | 2030 | Addition | 41 | 0 | OHL | 0.0361 | 0.7349 | 26.8865 | 2771 | 2771 | 2771 | 2771
HURL41 | KINT41 | 2030 | Addition | 41 | 0 | OHL | 0.0361 | 0.7349 | 26.8865 | 2771 | 2771 | 2771 | 2771
INGA1Q | LOCL11 | 2030 | Addition | 2.4 | 0.13 | Composite | 0.2276 | 0.5838 | 0.1247 | 133 | 123 | 106 | 123
INVE11 | SLOY11 | 2030 | Removed | 21.4 | 1.28 | Composite | 2.0092 | 4.9655 | 2.8547 | 126 | 117 | 101 | 117
KERG11 | MSHL11 | 2030 | Addition | 10.2 | 9 | Composite | 0.5768 | 2.8442 | 16.9284 | 242 | 229 | 209 | 229
KINA21 | TUMM2K | 2030 | Removed | 4.008 | 0 | OHL | 0.011 | 0.1647 | 1.1405 | 1905 | 1839 | 1705 | 1839
KINT21 | PEHE21 | 2030 | Change | 50.4 | 0 | OHL | 0.1934 | 1.8928 | 15.1047 | 1615 | 1558 | 1458 | 1558
KINT21 | PERS2R | 2030 | Change | 28.2 | 0 | OHL | 0.1095 | 1.1114 | 8.1774 | 1615 | 1558 | 1458 | 1558
KINT21 | TEAL21 | 2030 | Change | 99.1 | 1.5 | Composite | 0.5402 | 5.0779 | 30.918 | 695 | 643 | 548 | 643
KINT21 | TEAL21 | 2030 | Change | 99.1 | 1.5 | Composite | 0.5402 | 5.0779 | 30.918 | 695 | 643 | 548 | 643
KION11 | KIOR1A | 2030 | Addition | 0 | 0.28 | Cable | 0.0079 | 0.0247 | 0.3707 | 149 | 149 | 149 | 149
KIOR1- | KIOR1A | 2030 | Removed | 0.48 | 0.21 | Composite | 0.0435 | 0.1149 | 0.023 | 133 | 123 | 106 | 123
KNOC21 | LOCA2- | 2030 | Addition | 0 | 9 | Cable | 0.0244 | 0.1645 | 51.5317 | 585 | 585 | 585 | 585
LAIS1A | LOCB11 | 2030 | Removed | 13.3 | 0.83 | Composite | 0.317 | 2.7344 | 2.2529 | 373 | 373 | 373 | 373
LEWI11 | STOR1Q | 2030 | Addition | 0 | 1 | Cable | 0.0522 | 0.0608 | 1.395 | 148 | 148 | 148 | 148
LEWI11 | STOR1R | 2030 | Addition | 0 | 1 | Cable | 0.0522 | 0.0608 | 1.395 | 148 | 148 | 148 | 148
LEWI41 | LEWI4A | 2030 | Addition | 0 | 0.35 | Cable | 0 | 0 | 0.0018 | 69275 | 69275 | 69275 | 69275
LEWI41 | LEWI4A | 2030 | Addition | 0 | 0.35 | Cable | 0 | 0 | 0.0018 | 69275 | 69275 | 69275 | 69275
LOCB11 | MYBS1Q | 2030 | Change | 81.3 | 4.38 | Composite | 7.5233 | 18.6631 | 9.3536 | 126 | 117 | 101 | 117
LOCB11 | SHIN11 | 2030 | Change | 8.5 | 2.5 | Composite | 0.2264 | 1.9323 | 4.9633 | 373 | 373 | 373 | 373
LOCB11 | SHIN11 | 2030 | Change | 8.5 | 2.5 | Composite | 0.2264 | 1.9323 | 4.9633 | 373 | 373 | 373 | 373
LOCB21 | STRB2- | 2030 | Change | 17.9 | 1 | Composite | 0.1126 | 0.9278 | 9.6078 | 780 | 750 | 700 | 750
LOSD41 | LOSD4A | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0005 | 69275 | 69275 | 69275 | 69275
LOSD41 | LOSD4A | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0005 | 69275 | 69275 | 69275 | 69275
LOSD41 | NEDE41 | 2030 | Addition | 24.5 | 0 | OHL | 0.049 | 0.4825 | 14.0885 | 1995 | 1926 | 1787 | 1926
LOSD41 | NEDE41 | 2030 | Addition | 24.5 | 0 | OHL | 0.049 | 0.4825 | 14.0885 | 1995 | 1926 | 1787 | 1926
LOSD41 | PEHE41 | 2030 | Addition | 8 | 0 | OHL | 0.016 | 0.1575 | 4.6003 | 1995 | 1926 | 1787 | 1926
LOSD41 | PEHE41 | 2030 | Addition | 8 | 0 | OHL | 0.016 | 0.1575 | 4.6003 | 1995 | 1926 | 1787 | 1926
MILC1T | STNG11 | 2030 | Addition | 0 | 5.43 | Cable | 0.2739 | 0.4792 | 6.186 | 130 | 130 | 130 | 130
MILC1V | STNG11 | 2030 | Addition | 0 | 5.43 | Cable | 0.2843 | 0.4796 | 6.4379 | 130 | 130 | 130 | 130
NEDE41 | PEHE41 | 2030 | Removed | 30.04 | 0 | OHL | 0.0601 | 0.5916 | 17.2743 | 1995 | 1926 | 1787 | 1926
NEDE41 | PEHE41 | 2030 | Removed | 30.04 | 0 | OHL | 0.0601 | 0.5916 | 17.2743 | 1995 | 1926 | 1787 | 1926
PEHE21 | PERS2Q | 2030 | Change | 47.6 | 0 | OHL | 0.1839 | 1.8396 | 13.9931 | 1615 | 1558 | 1458 | 1558
PEHE4A | PEHE41 | 2030 | Addition | 0 | 0.63 | Cable | 0.0004 | 0.0081 | 18.672 | 1170 | 1170 | 1170 | 1170
PEHE4A | PEHE41 | 2030 | Addition | 0 | 0.61 | Cable | 0.0004 | 0.0092 | 19.28 | 1170 | 1170 | 1170 | 1170
PEHG1A | SALM1C | 2030 | Addition | 3 | 0 | OHL | 0.1504 | 0.7133 | 0.1478 | 242 | 229 | 209 | 229
PEHG1A | SFER1K | 2030 | Removed | 6.1 | 0 | OHL | 0.3073 | 1.3939 | 0.3112 | 242 | 229 | 209 | 229
PEHG1B | SALM1D | 2030 | Addition | 3 | 0 | OHL | 0.1504 | 0.7133 | 0.1478 | 242 | 229 | 209 | 229
PEHG1B | SFER1J | 2030 | Removed | 6.1 | 0 | OHL | 0.3073 | 1.3939 | 0.3112 | 242 | 229 | 209 | 229
SALM1A | SALM1D | 2030 | Addition | 2 | 0 | OHL | 0.1002 | 0.4755 | 0.0986 | 242 | 229 | 209 | 229
SALM1B | SALM1C | 2030 | Addition | 2 | 0 | OHL | 0.1002 | 0.4755 | 0.0986 | 242 | 229 | 209 | 229
SALM1C | SFER1K | 2030 | Addition | 3.1 | 0 | OHL | 0.1554 | 0.737 | 0.1528 | 242 | 229 | 209 | 229
SALM1D | SFER1J | 2030 | Addition | 3.1 | 0 | OHL | 0.1554 | 0.737 | 0.1528 | 242 | 229 | 209 | 229
STCS11 | STRW1- | 2030 | Addition | 0 | 0.35 | Cable | 0.0073 | 0.0293 | 0.4798 | 200 | 200 | 200 | 200
STCS11 | STSO11 | 2030 | Addition | 4.25 | 6 | Composite | 0.2531 | 1.1361 | 4.9198 | 200 | 200 | 200 | 200
STRW1- | STWO11 | 2030 | Addition | 4.25 | 0 | OHL | 0.135 | 0.9627 | 0.2198 | 336 | 320 | 290 | 320
STRW1- | STWO11 | 2030 | Removed | 4.25 | 0 | OHL | 0.1344 | 0.928 | 0.226 | 336 | 320 | 290 | 320
TEAL21 | WFIB2- | 2030 | Removed | 38.8 | 0 | OHL | 0.1582 | 1.3783 | 12.2465 | 1911 | 1870 | 1828 | 1870
ACHE11 | SHIN11 | 2033 | Removed | 16 | 1.5 | Composite | 0.8441 | 3.4638 | 2.6691 | 126 | 126 | 126 | 126
ACHE11 | SOYK11 | 2033 | Addition | 15 | 1.5 | Composite | 0.7942 | 3.256 | 2.6131 | 126 | 126 | 126 | 126
ARBR1A | ARBR1Q | 2033 | Change | 14.5 | 0 | OHL | 0.7239 | 3.1785 | 0.7618 | 242 | 229 | 209 | 229
ARBR1A | BREC1R | 2033 | Removed | 26.1 | 0 | OHL | 2.7415 | 6.2598 | 1.2479 | 112 | 104 | 90 | 104
ARBR1A | TEAL11 | 2033 | Change | 8.7 | 0 | OHL | 0.4343 | 1.9071 | 0.4571 | 242 | 229 | 209 | 229
ARBR1R | TEAS1- | 2033 | Change | 18.2 | 0 | OHL | 0.9086 | 3.9895 | 0.9562 | 242 | 229 | 209 | 229
AYRE41 | BANN41 | 2033 | Addition | 0 | 1 | Cable | 0.0008 | 0.0102 | 9.5504 | 500 | 500 | 500 | 500
AYRE41 | BANN41 | 2033 | Addition | 0 | 1 | Cable | 0.0008 | 0.0102 | 9.5504 | 500 | 500 | 500 | 500
BEAU21 | FYRI2J | 2033 | Removed | 29 | 1.5 | Composite | 0.1822 | 1.5002 | 14.8807 | 780 | 750 | 700 | 750
BEAU21 | FYRI2K | 2033 | Removed | 29 | 1.5 | Composite | 0.1822 | 1.5002 | 14.8807 | 780 | 750 | 700 | 750
BEAU21 | KIWF21 | 2033 | Addition | 10 | 0 | OHL | 0.0631 | 0.5505 | 2.0375 | 780 | 750 | 700 | 750
BEAU21 | KIWF21 | 2033 | Addition | 10 | 0 | OHL | 0.0631 | 0.5505 | 2.0375 | 780 | 750 | 700 | 750
BELK41 | HURL41 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
BELK41 | HURL41 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
BEWF1- | YELL11 | 2033 | Addition | 0 | 1.1 | Cable | 0.0235 | 0.0937 | 1.5296 | 213 | 213 | 213 | 213
BLHI21 | NCCS21 | 2033 | Change | 9 | 0 | OHL | 0.0518 | 0.3605 | 2.5456 | 934 | 881 | 791 | 881
BLHI21 | NCCS21 | 2033 | Change | 9 | 0 | OHL | 0.0518 | 0.3605 | 2.5456 | 934 | 881 | 791 | 881
BONB4- | COIM41 | 2033 | Addition | 112.99 | 0 | OHL | 0.1463 | 2.1525 | 68.7016 | 2771 | 2674 | 2480 | 2674
BONB4- | MELG41 | 2033 | Removed | 125.99 | 0 | OHL | 0.163 | 2.3924 | 76.7317 | 2771 | 2674 | 2480 | 2674
BREC1Q | BRID1J | 2033 | Removed | 5.1 | 0 | OHL | 0.5358 | 1.1593 | 0.2548 | 112 | 104 | 90 | 104
BREC1Q | FIDD11 | 2033 | Removed | 29.85 | 0.55 | Composite | 3.1469 | 6.4992 | 2.3331 | 112 | 104 | 90 | 104
BREC1R | BRID1K | 2033 | Removed | 5.1 | 0 | OHL | 0.5358 | 1.1593 | 0.2548 | 112 | 104 | 90 | 104
BRID1J | NECS11 | 2033 | Addition | 5.1 | 0 | OHL | 0.2547 | 1.1223 | 0.2667 | 242 | 229 | 209 | 229
BRID1K | NECS11 | 2033 | Addition | 5.1 | 0 | OHL | 0.2547 | 1.1223 | 0.2667 | 242 | 229 | 209 | 229
BUCH41 | PEHE41 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
CAAD1R | CNBH11 | 2033 | Change | 13.5 | 1.3 | Composite | 0.4423 | 3.1537 | 3.2082 | 301 | 301 | 301 | 301
CAIN2- | KINT21 | 2033 | Removed | 41.08 | 0 | OHL | 0.2363 | 1.6453 | 11.6193 | 934 | 881 | 791 | 881
CAIN3J | NCCS3- | 2033 | Addition | 0 | 1 | Cable | 0.0001 | 0.0001 | 0 | 5715 | 5715 | 5715 | 5715
CALO41 | GRNS41 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
CALO41 | GRNS41 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
CENS11 | KERG11 | 2033 | Addition | 0 | 8.5 | Cable | 0.0587 | 0.7194 | 15.8196 | 320 | 320 | 320 | 320
CENS11 | KERG11 | 2033 | Addition | 0 | 8.5 | Cable | 0.0587 | 0.7194 | 15.8196 | 320 | 320 | 320 | 320
CENS11 | KERG11 | 2033 | Addition | 0 | 8.5 | Cable | 0.0587 | 0.7194 | 15.8196 | 320 | 320 | 320 | 320
CENS21 | NORS21 | 2033 | Addition | 12 | 3 | Composite | 0.1423 | 0.993 | 13.7755 | 461 | 461 | 461 | 461
CENS21 | NORS21 | 2033 | Addition | 12 | 3 | Composite | 0.1423 | 0.993 | 13.7755 | 461 | 461 | 461 | 461
COGL41 | COGL4J | 2033 | Addition | 0 | 6 | Cable | 0.017 | 0.0448 | 51.1565 | 930 | 930 | 930 | 930
COGL41 | COGL4K | 2033 | Addition | 0 | 6 | Cable | 0.017 | 0.0448 | 51.1565 | 930 | 930 | 930 | 930
COGL4J | LOCL41 | 2033 | Addition | 3.5 | 0 | OHL | 0.0046 | 0.0697 | 2.0611 | 2771 | 2674 | 2480 | 2674
COGL4K | LOCL41 | 2033 | Addition | 3.5 | 0 | OHL | 0.0046 | 0.0697 | 2.0611 | 2771 | 2674 | 2480 | 2674
COIM41 | EABA41 | 2033 | Addition | 0 | 15 | Cable | 0.0095 | 0.1922 | 444.5714 | 1170 | 1170 | 1170 | 1170
COIM41 | EABA41 | 2033 | Addition | 0 | 15 | Cable | 0.0095 | 0.2272 | 474.0984 | 1170 | 1170 | 1170 | 1170
COIM41 | FAUG41 | 2033 | Addition | 37.01 | 0 | OHL | 0.0479 | 0.7062 | 22.4853 | 2771 | 2674 | 2480 | 2674
COIM41 | KINA41 | 2033 | Addition | 43.19 | 0 | OHL | 0.0554 | 0.797 | 26.6787 | 2771 | 2674 | 2480 | 2674
COIM41 | MELG41 | 2033 | Addition | 13 | 0 | OHL | 0.0167 | 0.2399 | 8.0302 | 2771 | 2674 | 2480 | 2674
COUA1A | COUA1N | 2033 | Removed | 14.6 | 0 | OHL | 0.7289 | 3.1936 | 0.7686 | 242 | 229 | 209 | 229
COUA1A | COUA1Q | 2033 | Addition | 13.6 | 0 | OHL | 0.679 | 2.9749 | 0.716 | 242 | 229 | 209 | 229
COUA1B | COUA1R | 2033 | Addition | 13.6 | 0 | OHL | 0.679 | 2.9749 | 0.716 | 242 | 229 | 209 | 229
COUA1B | COUA1S | 2033 | Removed | 14.6 | 0 | OHL | 0.7289 | 3.1936 | 0.7686 | 242 | 229 | 209 | 229
COUA1N | COUA1Q | 2033 | Addition | 1 | 0 | OHL | 0.0499 | 0.2187 | 0.0526 | 242 | 229 | 209 | 229
COUA1R | COUA1S | 2033 | Addition | 1 | 0 | OHL | 0.0499 | 0.2187 | 0.0526 | 242 | 229 | 209 | 229
CRDH11 | FERO1A | 2033 | Change | 6.21 | 0 | OHL | 0.0998 | 1.1643 | 0.3867 | 741 | 709 | 658 | 709
CRDH11 | NANT1A | 2033 | Change | 4.98 | 0 | OHL | 0.08 | 0.9339 | 0.3101 | 741 | 709 | 658 | 709
CWIN41 | NEMA41 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
CWIN41 | NEMA41 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
EDAY11 | FINS11 | 2033 | Addition | 14.9 | 21 | Composite | 1.4026 | 4.4909 | 29.5809 | 189 | 200 | 200 | 200
ELGI11 | KEIT11 | 2033 | Change | 22.9 | 5.5 | Composite | 1.2154 | 5.4442 | 10.2417 | 242 | 229 | 209 | 229
ELGI11 | KEIT11 | 2033 | Change | 22.9 | 5.5 | Composite | 1.2129 | 5.4258 | 10.1433 | 242 | 229 | 209 | 229
EMMO4A | EMMO41 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
EMMO4A | EMMO41 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.005 | 69275 | 69275 | 69275 | 69275
FAUG41 | KINA41 | 2033 | Removed | 80.2 | 0 | OHL | 0.1034 | 1.5032 | 49.164 | 2771 | 2674 | 2480 | 2674
FERO1A | TAYN1R | 2033 | Change | 6.3 | 0 | OHL | 0.1012 | 1.1814 | 0.3922 | 741 | 709 | 658 | 709
FETT11 | FIDD1Q | 2033 | Addition | 5 | 3 | Composite | 0.3212 | 1.4328 | 4.3535 | 186 | 186 | 186 | 186
FETT11 | FIDD1R | 2033 | Addition | 5 | 3 | Composite | 0.3212 | 1.4328 | 4.3535 | 186 | 186 | 186 | 186
FIDD1Q | TARL1A | 2033 | Removed | 25 | 0.55 | Composite | 2.6452 | 6.016 | 2.2253 | 112 | 104 | 90 | 104
FOYE2- | FOYE2J | 2033 | Change | 0 | 0.85 | Cable | 0.0056 | 0.0161 | 3.4319 | 319 | 319 | 319 | 319
FYRI2J | KIWF21 | 2033 | Addition | 20.5 | 0 | OHL | 0.1294 | 1.1285 | 4.1769 | 780 | 750 | 700 | 750
FYRI2K | KIWF21 | 2033 | Addition | 20.5 | 0 | OHL | 0.1294 | 1.1285 | 4.1769 | 780 | 750 | 700 | 750
GRNS41 | STMR41 | 2033 | Addition | 0 | 0.5 | Cable | 0.0003 | 0.0106 | 5.7552 | 1596 | 1596 | 1596 | 1596
GRNS41 | STMR41 | 2033 | Addition | 0 | 0.5 | Cable | 0.0003 | 0.0106 | 5.7552 | 1596 | 1596 | 1596 | 1596
KINM4A | NEMA41 | 2033 | Addition | 11.1 | 0 | OHL | 0.0207 | 0.2186 | 6.5322 | 2349 | 2266 | 2120 | 2266
KINM4B | PEHE41 | 2033 | Addition | 23.8 | 0 | OHL | 0.0443 | 0.4687 | 14.006 | 2349 | 2266 | 2120 | 2266
KINT21 | NECS21 | 2033 | Addition | 64.1 | 1.5 | Composite | 0.3502 | 3.2974 | 23.0192 | 695 | 643 | 548 | 643
KINT21 | NECS21 | 2033 | Addition | 64.1 | 1.5 | Composite | 0.3502 | 3.2974 | 23.0192 | 695 | 643 | 548 | 643
KINT21 | PEHE21 | 2033 | Removed | 50.4 | 0 | OHL | 0.1934 | 1.8928 | 15.1047 | 1615 | 1558 | 1458 | 1558
KINT21 | PERS2R | 2033 | Removed | 28.2 | 0 | OHL | 0.1095 | 1.1114 | 8.1774 | 1615 | 1558 | 1458 | 1558
KINT21 | TEAL21 | 2033 | Removed | 99.1 | 1.5 | Composite | 0.5402 | 5.0779 | 30.918 | 695 | 643 | 548 | 643
KINT21 | TEAL21 | 2033 | Removed | 99.1 | 1.5 | Composite | 0.5402 | 5.0779 | 30.918 | 695 | 643 | 548 | 643
KINT41 | NEMA41 | 2033 | Addition | 15.5 | 0 | OHL | 0.0281 | 0.2751 | 9.8286 | 2349 | 2266 | 2120 | 2266
KINT41 | NEMA41 | 2033 | Addition | 15.5 | 0 | OHL | 0.0281 | 0.2751 | 9.8286 | 2349 | 2266 | 2120 | 2266
KIWF21 | KIWF2A | 2033 | Addition | 25 | 0 | OHL | 0.1579 | 1.3763 | 5.0938 | 702 | 665 | 599 | 665
KIWF21 | KIWF2B | 2033 | Addition | 25 | 0 | OHL | 0.1579 | 1.3763 | 5.0938 | 702 | 665 | 599 | 665
LEWI41 | NPIC41 | 2033 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0005 | 69275 | 69275 | 69275 | 69275
LEWI41 | NPIC41 | 2033 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0005 | 69275 | 69275 | 69275 | 69275
LEWI41 | TLSK41 | 2033 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0005 | 69275 | 69275 | 69275 | 69275
LEWI41 | TLSK41 | 2033 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0.0005 | 69275 | 69275 | 69275 | 69275
LOCL41 | LOFA41 | 2033 | Addition | 24.5 | 1 | Composite | 0.061 | 0.4235 | 49.6198 | 350 | 350 | 350 | 350
LOSD11 | SINC11 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.0005 | 22861 | 22861 | 22861 | 22861
LOSD11 | SINC11 | 2033 | Addition | 0 | 1 | Cable | 0 | 0 | 0.0005 | 22861 | 22861 | 22861 | 22861
LOSD4A | LOSD41 | 2033 | Addition | 0 | 1 | Cable | 0.0006 | 0.0128 | 29.6381 | 1170 | 1170 | 1170 | 1170
LOSD4A | LOSD41 | 2033 | Addition | 0 | 1 | Cable | 0.0006 | 0.0151 | 31.6066 | 1170 | 1170 | 1170 | 1170
LOSD41 | PEHE41 | 2033 | Change | 8 | 0 | OHL | 0.0067 | 0.1269 | 5.6906 | 3464 | 3464 | 3326 | 3464
LOSD41 | PEHE41 | 2033 | Change | 8 | 0 | OHL | 0.0067 | 0.1269 | 5.6906 | 3464 | 3464 | 3326 | 3464
LUNH21 | NECS21 | 2033 | Addition | 0 | 1 | Cable | 0.01 | 0.024 | 6.22 | 400 | 400 | 400 | 400
LUNH21 | NECS21 | 2033 | Addition | 0 | 1 | Cable | 0.01 | 0.024 | 6.22 | 400 | 400 | 400 | 400
NANT1- | NANT1A | 2033 | Change | 4.1 | 0 | OHL | 0.2058 | 0.9331 | 0.2098 | 242 | 229 | 209 | 229
NANT1A | TAYN1Q | 2033 | Change | 7.6 | 0 | OHL | 0.1221 | 1.4246 | 0.4733 | 741 | 709 | 658 | 709
NECS21 | OSSI21 | 2033 | Addition | 0 | 1 | Cable | 0.0004 | 0.0123 | 10.6574 | 1560 | 1560 | 1560 | 1560
NECS21 | TEAL21 | 2033 | Addition | 35 | 0 | OHL | 0.19 | 1.7805 | 7.8988 | 695 | 643 | 548 | 643
NECS21 | TEAL21 | 2033 | Addition | 35 | 0 | OHL | 0.19 | 1.7805 | 7.8988 | 695 | 643 | 548 | 643
NEMA1Q | PERS11 | 2033 | Addition | 12.7 | 0 | OHL | 0.298 | 3.1604 | 0.5988 | 464 | 446 | 414 | 446
NEMA1R | PERS11 | 2033 | Addition | 12.7 | 0 | OHL | 0.298 | 3.1604 | 0.5988 | 464 | 446 | 414 | 446
NEMA41 | PEHE41 | 2033 | Addition | 34.9 | 0 | OHL | 0.065 | 0.6873 | 20.5382 | 2349 | 2266 | 2120 | 2266
NORS21 | YELL21 | 2033 | Addition | 0 | 19.5 | Cable | 0.1568 | 0.7048 | 67.3595 | 461 | 461 | 461 | 461
NWGL4- | PEHE41 | 2033 | Addition | 0 | 1 | Cable | 0.0003 | 0.0106 | 46.242 | 1600 | 1600 | 1600 | 1600
PEHE21 | PERS2Q | 2033 | Removed | 47.6 | 0 | OHL | 0.1839 | 1.8396 | 13.9931 | 1615 | 1558 | 1458 | 1558
SHIN11 | SOYK11 | 2033 | Addition | 1 | 0 | OHL | 0.0499 | 0.2077 | 0.056 | 242 | 229 | 209 | 229
TEAL11 | TEAS1- | 2033 | Change | 5 | 0 | OHL | 0.2496 | 1.096 | 0.2627 | 242 | 229 | 209 | 229

## B-2-2b
B-2-2b - SPT Circuit Changes 2026/27 to 2033/34
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
CURR2- | SIGH2Q | 2026 | Change | 1.54 | 1.7 | Composite | 0.0169 | 0.1036 | 6.0402 | 180 | 180 | 180 | 180
CURR2- | SIGH2R | 2026 | Change | 1.54 | 1.67 | Composite | 0.0168 | 0.103 | 5.941 | 180 | 180 | 180 | 180
DUNF1Q | INKE1Q | 2026 | Change | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122
DUNF1R | INKE1R | 2026 | Change | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122
KILS2- | KILT2Q | 2026 | Change | 3.56 | 0.29 | Composite | 0.0165 | 0.1465 | 2.1425 | 204 | 177 | 177 | 177
KILS2- | KILT2R | 2026 | Change | 3.56 | 0.33 | Composite | 0.0168 | 0.1474 | 2.2967 | 204 | 177 | 177 | 177
AREX1- | AREX1A | 2028 | Addition | 0 | 1.7 | Cable | 0.048 | 0.1103 | 2.0938 | 85 | 85 | 85 | 85
AREX1A | CHMO1T | 2028 | Addition | 4.7 | 0 | OHL | 0.3571 | 1.0182 | 0.2484 | 284 | 278 | 270 | 278
AREX1A | MAHI1B | 2028 | Addition | 7.5 | 0.5 | Composite | 0.5731 | 1.6545 | 1.2722 | 365 | 365 | 365 | 365
AYR-2Q | OLDT2- | 2028 | Addition | 0 | 2.37 | Cable | 0.0058 | 0.042 | 12.3876 | 776 | 776 | 776 | 776
AYRS4- | HBES4- | 2028 | Addition | 0 | 0.1 | Cable | 0.0001 | 0.0013 | 1.1119 | 2770 | 2770 | 2770 | 2770
BROX1Q | DRUR1- | 2028 | Addition | 0 | 1.3 | Cable | 0.0373 | 0.1268 | 1.4374 | 134 | 134 | 134 | 134
CHMO1- | CHMO1T | 2028 | Addition | 0.3 | 0 | OHL | 0.0225 | 0.066 | 0.0158 | 167 | 160 | 148 | 160
CHMO1T | STOC1- | 2028 | Addition | 5.9 | 0 | OHL | 0.4426 | 1.2993 | 0.3103 | 167 | 160 | 148 | 160
CLAW1- | DESA1Q | 2028 | Addition | 6.4 | 2.3 | Composite | 0.5256 | 1.6179 | 3.5471 | 167 | 160 | 147 | 160
CLAW1- | NECU1- | 2028 | Addition | 0 | 2.21 | Cable | 0.0438 | 0.2004 | 3.0848 | 182 | 182 | 182 | 182
COAL1A | KENN1- | 2028 | Addition | 16 | 3.4 | Composite | 1.2963 | 3.7441 | 5.0291 | 140 | 140 | 140 | 140
COAL4- | REDS4- | 2028 | Addition | 11 | 0 | OHL | 0.0192 | 0.2085 | 6.5859 | 2210 | 2210 | 2210 | 2210
COAN4- | REDS4- | 2028 | Addition | 11 | 0 | OHL | 0.0192 | 0.2085 | 6.5859 | 2210 | 2210 | 2210 | 2210
COAN4- | STHA4A | 2028 | Addition | 21.79 | 0 | OHL | 0.0381 | 0.413 | 13.045 | 2210 | 2210 | 2210 | 2210
COBA4- | COAN4- | 2028 | Addition | 0 | 2.5 | Cable | 0.0017 | 0.032 | 27.7981 | 1247 | 1247 | 1247 | 1247
COYL2- | CRCK2- | 2028 | Addition | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1110 | 1110 | 1110
CRCK2- | MAHI2- | 2028 | Addition | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1110 | 1110 | 1110
DAER1- | MOFF1A | 2028 | Addition | 6.1 | 6.8 | Composite | 0.6601 | 1.7847 | 8.6959 | 133 | 124 | 107 | 124
DALB2A | DALL2- | 2028 | Addition | 5.7 | 0 | OHL | 0.0241 | 0.2328 | 1.5851 | 1380 | 1320 | 1230 | 1320
DALB2B | WIYH2- | 2028 | Addition | 72.45 | 0 | OHL | 0.3064 | 2.9592 | 20.1469 | 1380 | 1320 | 1230 | 1320
ELVA4- | REDS4- | 2028 | Addition | 15.77 | 0 | OHL | 0.0276 | 0.2989 | 9.4418 | 2210 | 2130 | 1980 | 2130
ELVA4- | REDS4- | 2028 | Addition | 15.77 | 0 | OHL | 0.0276 | 0.2989 | 9.4418 | 2210 | 2130 | 1980 | 2130
EWEH1Q | HORI1- | 2028 | Addition | 6 | 0 | OHL | 0.4507 | 1.3202 | 0.316 | 199 | 191 | 178 | 191
FASI1A | HAWI1D | 2028 | Addition | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124
FASI1B | HAWI1C | 2028 | Addition | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124
FIGS2- | KINC2- | 2028 | Addition | 0 | 0.7 | Cable | 0.0018 | 0.0075 | 5.395 | 352 | 352 | 352 | 352
GALA1- | HAWI1- | 2028 | Addition | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160
GALA1- | HAWI1- | 2028 | Addition | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160
GBRN1- | NECU1C | 2028 | Addition | 8 | 0.4 | Composite | 0.609 | 1.7878 | 0.8495 | 167 | 167 | 167 | 167
GLGL1- | SANQ1- | 2028 | Addition | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 283 | 283 | 283 | 283
GLLE1- | WNUK1- | 2028 | Addition | 17 | 0.5 | Composite | 1.2996 | 3.7201 | 1.6799 | 200 | 200 | 200 | 200
HLND1- | WISH1- | 2028 | Addition | 17 | 1.01 | Composite | 1.3056 | 3.8061 | 2.1392 | 167 | 160 | 148 | 160
HUNE1- | HUNF1Q | 2028 | Addition | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUNE1- | JUNA1T | 2028 | Addition | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
HUNF1R | HUNE1- | 2028 | Addition | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
KILW1A | KILW1Q | 2028 | Addition | 0 | 1.23 | Cable | 0.0347 | 0.0798 | 1.5149 | 181 | 164 | 164 | 164
KILW1R | LYLS1- | 2028 | Addition | 0 | 0.6 | Cable | 0.0169 | 0.0389 | 0.739 | 164 | 164 | 164 | 164
KINB4J | KINN4- | 2028 | Addition | 8.8 | 0 | OHL | 0.0181 | 0.1864 | 4.8531 | 2000 | 1920 | 1790 | 1920
KINB4K | KINN4- | 2028 | Addition | 8.8 | 0 | OHL | 0.0181 | 0.1864 | 4.8531 | 2000 | 1920 | 1790 | 1920
KINC2- | KINN2A | 2028 | Addition | 1.9 | 0 | OHL | 0.0083 | 0.0851 | 0.4956 | 1100 | 1100 | 1100 | 1100
KINC2- | KINN2B | 2028 | Addition | 1.9 | 0 | OHL | 0.0083 | 0.0851 | 0.4956 | 1100 | 1100 | 1100 | 1100
LOAN2- | DEBS2- | 2028 | Addition | 0 | 4 | Cable | 0.0081 | 0.1105 | 24.3285 | 820 | 736 | 674 | 736
LORG1- | SHRG1T | 2028 | Addition | 10 | 0 | OHL | 0.7598 | 2.1663 | 0.5285 | 284 | 284 | 284 | 284
MOFF1- | SCOP1- | 2028 | Addition | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293
MOFF1A | SCOP1A | 2028 | Addition | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293
NECU1B | OHLL1- | 2028 | Addition | 0 | 3 | Cable | 0.0534 | 0.2861 | 3.5006 | 180 | 180 | 180 | 180
NEIL1- | SERG1- | 2028 | Addition | 0 | 1.98 | Cable | 0.0559 | 0.1285 | 2.4386 | 200 | 200 | 200 | 200
NLAN2- | NEAR2Q | 2028 | Addition | 0 | 2 | Cable | 0.0102 | 0.0284 | 16.7258 | 695 | 695 | 500 | 695
REDS1A | REDS1Q | 2028 | Addition | 0 | 0.2 | Cable | 0.0056 | 0.013 | 0.2463 | 134 | 134 | 134 | 134
REDS1A | REDS1R | 2028 | Addition | 0 | 0.2 | Cable | 0.0056 | 0.013 | 0.2463 | 134 | 134 | 134 | 134
REDS1A | SPRB1- | 2028 | Addition | 18 | 0 | OHL | 1.3662 | 4.0108 | 0.9183 | 284 | 278 | 270 | 278
REDS1A | SPRB1- | 2028 | Addition | 18 | 0 | OHL | 1.3662 | 4.0108 | 0.9183 | 284 | 278 | 270 | 278
REDS3A | HRCR3A | 2028 | Addition | 0 | 18 | Cable | 4.1157 | 15.3565 | 2.3237 | 80 | 80 | 80 | 80
SMEA4Q | WISH4- | 2028 | Addition | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2770 | 2730 | 2660 | 2730
STHA4B | WISH4- | 2028 | Addition | 11.6 | 0 | OHL | 0.0243 | 0.2192 | 7.0076 | 2770 | 2730 | 2660 | 2730
BAGA1Q | BONN1- | 2028 | Change | 18.3 | 0 | OHL | 0.6862 | 3.8983 | 0.9904 | 242 | 223 | 192 | 223
BAGA1R | BONN1- | 2028 | Change | 18.4 | 0 | OHL | 0.69 | 3.9202 | 0.9957 | 242 | 223 | 192 | 223
BENB1T | BLCW1- | 2028 | Change | 32.15 | 0.9 | Composite | 1.1801 | 6.5296 | 3.3413 | 199 | 199 | 199 | 199
BLAH1- | GLGL1- | 2028 | Change | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 297 | 297 | 297 | 297
BLAH1- | GLGL1- | 2028 | Change | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 297 | 297 | 297 | 297
BRAP1- | ERSK1R | 2028 | Change | 3.17 | 5.4 | Composite | 0.4467 | 1.0763 | 12.4479 | 102 | 102 | 102 | 102
CHAP1- | GRNA1- | 2028 | Change | 12.83 | 0.35 | Composite | 0.7983 | 3.0495 | 1.0029 | 198 | 186 | 168 | 186
CHAP1- | HAKB1- | 2028 | Change | 14.72 | 0 | OHL | 0.78187 | 3.1313 | 0.80314 | 242 | 225 | 194 | 225
CRYR4- | FALL4- | 2028 | Change | 13.86 | 0 | OHL | 0.0182 | 0.2732 | 8.1821 | 2473 | 2349 | 2148 | 2349
CRYR4- | TORN4- | 2028 | Change | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 1415 | 1415 | 1415 | 1415
DEVM4- | WIYH4Q | 2028 | Change | 28.65 | 0 | OHL | 0.0545 | 0.5243 | 17.916 | 1390 | 1280 | 1110 | 1280
ELDE1Q | NEIL1- | 2028 | Change | 3.82 | 0.18 | Composite | 0.1455 | 0.8324 | 0.4574 | 229 | 211 | 183 | 211
ELDE1R | NEIL1- | 2028 | Change | 3.82 | 0.23 | Composite | 0.1461 | 0.8373 | 0.5271 | 229 | 211 | 183 | 211
ELVA4- | GRNA4C | 2028 | Change | 65.54 | 0 | OHL | 0.1406 | 1.3109 | 37.3092 | 2770 | 2770 | 2770 | 2770
ELVA4- | MOFF4- | 2028 | Change | 23.5 | 0 | OHL | 0.0504 | 0.47 | 13.3784 | 2770 | 2770 | 2770 | 2770
GLLE1- | NETS1- | 2028 | Change | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278
GLLE1- | NETS1- | 2028 | Change | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278
GRNA4- | HAKB4B | 2028 | Change | 1.97 | 0 | OHL | 0.0035 | 0.0381 | 1.1674 | 2370 | 2370 | 2370 | 2370
HAKB4- | MOFF4C | 2028 | Change | 43.79 | 0 | OHL | 0.0772 | 0.8467 | 25.9494 | 2370 | 2370 | 2370 | 2370
LAMB2- | WIYH2- | 2028 | Change | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9716 | 1380 | 1320 | 1230 | 1320
LAMB2T | WIYH2- | 2028 | Change | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1380 | 1320 | 1230 | 1320
MOSM2- | WFIE2- | 2028 | Change | 8.243 | 0 | OHL | 0.0378 | 0.3641 | 2.1507 | 1090 | 1090 | 1090 | 1090
NEAR2Q | WISH2- | 2028 | Change | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 955 | 955 | 955
SMEA4Q | TORN4- | 2028 | Change | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 1360 | 1280 | 1280 | 1280
BRAP1- | ERSK1Q | 2028 | Removed | 3.17 | 5.4 | Composite | 0.4479 | 1.0975 | 12.4447 | 121 | 110 | 106 | 110
COAL4- | ELVA4- | 2028 | Removed | 26.71 | 0 | OHL | 0.0467 | 0.5062 | 15.9918 | 2210 | 2130 | 1980 | 2130
COYL2- | MAHI2- | 2028 | Removed | 49.5 | 0 | OHL | 0.3612 | 2.813 | 10.0797 | 1110 | 1090 | 1060 | 1090
DALL2- | WIYH2- | 2028 | Removed | 78.15 | 0 | OHL | 0.3305 | 3.192 | 21.732 | 570 | 570 | 570 | 570
DESA1Q | NECU1C | 2028 | Removed | 6.4 | 4.3 | Composite | 0.5652 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160
ELVA4- | STHA4A | 2028 | Removed | 48.56 | 0 | OHL | 0.085 | 0.9204 | 29.0717 | 2210 | 2130 | 1980 | 2130
FASI1A | HAWI1- | 2028 | Removed | 19.11 | 0 | OHL | 1.7249 | 4.5353 | 0.9303 | 133 | 124 | 107 | 124
FASI1B | HAWI1- | 2028 | Removed | 19.11 | 0 | OHL | 1.7249 | 4.5353 | 0.9303 | 132 | 123 | 106 | 123
GALA1- | HAWI1B | 2028 | Removed | 23.55 | 0 | OHL | 1.211 | 2.684 | 7.57 | 132 | 122 | 106 | 122
HUER1- | HUNF1Q | 2028 | Removed | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146
HUER1- | HUNF1R | 2028 | Removed | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146
HUER1- | JUNA1T | 2028 | Removed | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175
KINB2J | KINC2- | 2028 | Removed | 10.703 | 0 | OHL | 0.0482 | 0.4365 | 2.9693 | 1090 | 1030 | 925 | 1030
KINB2K | KINC2- | 2028 | Removed | 10.68 | 0 | OHL | 0.0386 | 0.4264 | 3.0603 | 830 | 800 | 800 | 800
SMEA4Q | STHA4B | 2028 | Removed | 73.37 | 0 | OHL | 0.1593 | 1.4873 | 41.7375 | 900 | 760 | 760 | 760
AYRS4- | HESF4- | 2030 | Addition | 0 | 0.1 | Cable | 0.0001 | 0.0013 | 1.1119 | 2770 | 2770 | 2770 | 2770
BANR1- | HAZE1T | 2030 | Addition | 17.1 | 0 | OHL | 0.9083 | 3.6376 | 0.933 | 242 | 232 | 214 | 232
BENB1T | KEOO1Q | 2030 | Addition | 20.25 | 0 | OHL | 0.5256 | 3.9095 | 1.2119 | 482 | 460 | 420 | 460
BILS4- | BRNX4- | 2030 | Addition | 0 | 1 | Cable | 0.0005 | 0.0134 | 11.1192 | 831 | 831 | 831 | 831
BLCW1- | GNSH1- | 2030 | Addition | 1.8 | 0 | OHL | 0.1352 | 0.3961 | 0.0948 | 167 | 160 | 148 | 160
BODI1- | REDS1C | 2030 | Addition | 0 | 1.6 | Cable | 0.0254 | 0.1197 | 2.5007 | 200 | 185 | 175 | 185
BONB4A | DENN4- | 2030 | Addition | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2977 | 2570 | 2570 | 2508 | 2570
BONN2- | CUMB2- | 2030 | Addition | 10.89 | 0 | OHL | 0.0474 | 0.4987 | 2.7708 | 1380 | 1320 | 1230 | 1320
BONN2- | DENN2T | 2030 | Addition | 3.25 | 0 | OHL | 0.0141 | 0.1488 | 0.8269 | 1380 | 1320 | 1230 | 1320
BONN4- | KINN4- | 2030 | Addition | 19.1 | 0 | OHL | 0.0238 | 0.331 | 12.5409 | 2778 | 2736 | 2667 | 2736
BONN4- | WISH4- | 2030 | Addition | 40.36 | 0 | OHL | 0.0862 | 0.837 | 22.708 | 2770 | 2730 | 2660 | 2730
BREE1- | CLAW1- | 2030 | Addition | 6.5 | 0 | OHL | 0.4883 | 1.4302 | 0.3423 | 199 | 191 | 178 | 191
BRNX4- | ECCL4B | 2030 | Addition | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2470 | 2350 | 2150 | 2350
BRNX4- | SMEA4Q | 2030 | Addition | 54.32 | 0 | OHL | 0.0716 | 1.0582 | 32.3337 | 2473 | 2349 | 2148 | 2349
BRNX4- | TOCS4A | 2030 | Addition | 0 | 4.5 | Cable | 0.0012 | 0.0243 | 112.6449 | 1074 | 1074 | 1074 | 1074
BRNX4- | TORN4- | 2030 | Addition | 0 | 2.1 | Cable | 0.0005 | 0.014 | 46.7008 | 1040 | 900 | 900 | 900
BRNX4- | TORN4- | 2030 | Addition | 0 | 1.94 | Cable | 0.0005 | 0.013 | 43.1426 | 945 | 800 | 800 | 800
BRNX4Q | CRYR4- | 2030 | Addition | 9.36 | 0 | OHL | 0.012 | 0.1717 | 5.799 | 2522 | 2397 | 2189 | 2397
BRNX4Q | TORN4- | 2030 | Addition | 0 | 1.97 | Cable | 0.002 | 0.0326 | 38.612 | 935 | 785 | 785 | 785
BRNX4R | ECCL4A | 2030 | Addition | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2470 | 2350 | 2150 | 2350
BRNX4R | TORN4- | 2030 | Addition | 0 | 1.94 | Cable | 0.0019 | 0.0321 | 38.024 | 900 | 760 | 760 | 760
BUSB2- | WESL2- | 2030 | Addition | 0 | 0.3 | Cable | 0.0003 | 0.0085 | 1.5767 | 1500 | 1500 | 1500 | 1500
CHAP1- | CPCR1- | 2030 | Addition | 0 | 0.85 | Cable | 0.0134 | 0.0732 | 1.4005 | 180 | 180 | 180 | 180
CHAP1- | OFOA1T | 2030 | Addition | 24.82 | 0.18 | Composite | 0.984 | 5.6173 | 1.5274 | 171 | 155 | 155 | 155
CLFO1- | CURR1A | 2030 | Addition | 27 | 1.6 | Composite | 2.1169 | 6.0497 | 3.3907 | 133 | 124 | 107 | 124
CLYM4- | DENN4- | 2030 | Addition | 33.63 | 0 | OHL | 0.0359 | 0.5576 | 22.7874 | 2780 | 2570 | 2220 | 2570
COCK4Q | GALN4- | 2030 | Addition | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060
COCK4R | GALN4- | 2030 | Addition | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060
COLD1- | ECCL1- | 2030 | Addition | 0.4 | 0 | OHL | 0.0186 | 0.024 | 0.109 | 200 | 200 | 200 | 200
CONL2Q | GLRO2- | 2030 | Addition | 2.14 | 0 | OHL | 0.0099 | 0.0977 | 0.5452 | 1096 | 1029 | 924 | 1029
CONL2R | GLRO2- | 2030 | Addition | 2.14 | 0 | OHL | 0.0099 | 0.0977 | 0.5452 | 1096 | 1029 | 924 | 1029
CONL4- | GLRB4- | 2030 | Addition | 12.54 | 0 | OHL | 0.0261 | 0.2255 | 7.8748 | 2770 | 2730 | 2660 | 2730
CONL4- | WFIE4- | 2030 | Addition | 9.94 | 0 | OHL | 0.0207 | 0.1787 | 6.242 | 2770 | 2730 | 2660 | 2730
CRAG4- | KILS4T | 2030 | Addition | 0 | 2.6 | Cable | 0.006 | 0.0216 | 20.1263 | 410 | 410 | 410 | 410
CRCK3A | KNCR3- | 2030 | Addition | 0 | 2.5 | Cable | 0.3459 | 1.093 | 0.5868 | 40 | 38 | 38 | 38
CREA1- | CLOU1- | 2030 | Addition | 0 | 2 | Cable | 0.039 | 0.1837 | 2.7807 | 211 | 211 | 211 | 211
CREA1- | GLGL1B | 2030 | Addition | 0 | 1.44 | Cable | 0.0407 | 0.0935 | 1.7735 | 181 | 164 | 164 | 164
CRFO1- | REDS1D | 2030 | Addition | 0 | 1.65 | Cable | 0.0135 | 0.1348 | 3.0726 | 293 | 293 | 293 | 293
CRUA2S | CRUA2A | 2030 | Addition | 0 | 0.4 | Cable | 0.0021 | 0.0086 | 1.5414 | 352 | 352 | 352 | 352
CRUA2T | CRUA2B | 2030 | Addition | 0 | 0.4 | Cable | 0.0021 | 0.0086 | 1.5414 | 352 | 352 | 352 | 352
CUMB2- | NEAR2S | 2030 | Addition | 6.11 | 0 | OHL | 0.0266 | 0.2798 | 1.5546 | 1380 | 1320 | 1230 | 1320
DEBS2- | KINC2- | 2030 | Addition | 4.28 | 5 | Composite | 0.0285 | 0.3247 | 31.5405 | 820 | 736 | 674 | 736
DENN2- | DENN2T | 2030 | Addition | 1 | 0 | OHL | 0 | 0 | 0 | 4763 | 4763 | 4763 | 4763
DENN2- | EERH2- | 2030 | Addition | 24.88 | 0 | OHL | 0.0561 | 0.8727 | 7.9683 | 1500 | 1500 | 1500 | 1500
DENN2- | GARC2- | 2030 | Addition | 0 | 1.97 | Cable | 0.004 | 0.0544 | 11.9818 | 889 | 889 | 889 | 889
DENN2T | KINC2- | 2030 | Addition | 17.75 | 0 | OHL | 0.04 | 0.6226 | 5.6848 | 1910 | 1770 | 1520 | 1770
DENN4- | KINN4- | 2030 | Addition | 16.1 | 0 | OHL | 0.0178 | 0.273 | 10.7108 | 2550 | 2420 | 2210 | 2420
DENN4- | KINN4- | 2030 | Addition | 16.1 | 0 | OHL | 0.0178 | 0.273 | 10.7108 | 2550 | 2420 | 2210 | 2420
DENN4- | LAMB4T | 2030 | Addition | 32.18 | 0 | OHL | 0.0661 | 0.6818 | 17.786 | 2000 | 1920 | 1790 | 1920
DUMF1- | OFOA1T | 2030 | Addition | 2.08 | 0 | OHL | 0.0822 | 0.4694 | 0.1069 | 229 | 212 | 183 | 212
DUNE1- | GALN1Q | 2030 | Addition | 13.34 | 3.025 | Composite | 0.3835 | 2.6741 | 5.246 | 482 | 460 | 420 | 460
DUNE1- | GALN1R | 2030 | Addition | 13.34 | 3.025 | Composite | 0.3835 | 2.6741 | 5.246 | 482 | 460 | 420 | 460
EAST1Q | GLLE1- | 2030 | Addition | 1.5 | 0.3 | Composite | 0.1236 | 0.3498 | 0.4484 | 133 | 124 | 107 | 124
ECCL1- | GALA1- | 2030 | Addition | 30.58 | 0 | OHL | 1.6249 | 6.7325 | 1.5989 | 242 | 232 | 214 | 232
ECCL1- | GALN1Q | 2030 | Addition | 37.86 | 0 | OHL | 1.7993 | 8.0292 | 2.0633 | 242 | 232 | 214 | 232
ECCL4A | GALN4- | 2030 | Addition | 30.4 | 0 | OHL | 0.0623 | 0.6546 | 16.3668 | 2000 | 1920 | 1790 | 1920
ECCL4B | GALN4- | 2030 | Addition | 30.4 | 0 | OHL | 0.0623 | 0.6546 | 16.3668 | 2000 | 1920 | 1790 | 1920
EERH2T | NEAR2S | 2030 | Addition | 7.74 | 0 | OHL | 0.033 | 0.3199 | 2.1442 | 1380 | 1320 | 1230 | 1320
EERH2T | NEAR2T | 2030 | Addition | 7.74 | 0 | OHL | 0.033 | 0.3199 | 2.1442 | 1380 | 1320 | 1230 | 1320
ELVA1- | NLEI1- | 2030 | Addition | 14 | 0 | OHL | 0.7436 | 2.9782 | 0.7639 | 226 | 216 | 200 | 216
EUCH1- | LORG1- | 2030 | Addition | 3.5 | 0 | OHL | 0.2629 | 0.7701 | 0.1843 | 167 | 160 | 148 | 160
FALL1Q | NEWL1- | 2030 | Addition | 3.5 | 2.55 | Composite | 0.2579 | 0.9101 | 3.3316 | 181 | 164 | 164 | 164
GALA1- | GALN1R | 2030 | Addition | 7.72 | 0 | OHL | 0.1978 | 1.3968 | 0.4869 | 482 | 460 | 420 | 460
GARC2- | PLEC2- | 2030 | Addition | 0 | 1.2 | Cable | 0.0062 | 0.0257 | 4.6243 | 445 | 445 | 445 | 445
GHPS1B | GLGL1B | 2030 | Addition | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 12 | 12 | 11 | 12
GHPS1B | GLGL1B | 2030 | Addition | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 12 | 12 | 11 | 12
GHPS1B | LETH1- | 2030 | Addition | 0 | 3 | Cable | 0.0404 | 0.2597 | 9.3604 | 200 | 200 | 200 | 200
GLGL3- | GLMU3- | 2030 | Addition | 0 | 10 | Cable | 2.7669 | 8.7439 | 1.1735 | 40 | 38 | 38 | 38
GLLE1- | GLLE1A | 2030 | Addition | 16.55 | 0 | OHL | 1.0058 | 3.644 | 0.8645 | 234 | 225 | 209 | 225
GLLE1- | HOLM1T | 2030 | Addition | 18.58 | 0 | OHL | 0.479 | 3.4684 | 1.142 | 482 | 460 | 420 | 460
GLLE1A | TONG1- | 2030 | Addition | 16.55 | 0 | OHL | 1.0058 | 3.644 | 0.8645 | 234 | 225 | 209 | 225
GLLE1B | TONG1- | 2030 | Addition | 16.55 | 0 | OHL | 1.0058 | 3.644 | 0.8645 | 234 | 225 | 209 | 225
GLLU1R | NETS1- | 2030 | Addition | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 57 | 57 | 57 | 57
GNSH1- | KEOO1Q | 2030 | Addition | 10.1 | 0.9 | Composite | 0.7816 | 2.2655 | 2.0167 | 272 | 231 | 231 | 231
HALB1T | HALB1- | 2030 | Addition | 0.08 | 0 | OHL | 0.0042 | 0.017 | 0.0044 | 226 | 216 | 200 | 216
HALB1T | MOSM1B | 2030 | Addition | 6.6 | 0 | OHL | 0.5008 | 1.4589 | 0.3393 | 215 | 215 | 198 | 215
HAZE1- | HAZE1T | 2030 | Addition | 1.75 | 0 | OHL | 0.1313 | 0.3854 | 0.092 | 112 | 112 | 112 | 112
HAZE1T | REDS1A | 2030 | Addition | 0 | 7.48 | Cable | 0.5334 | 1.5447 | 1.3203 | 112 | 112 | 112 | 112
HOLM1T | QUAN1- | 2030 | Addition | 6 | 0 | OHL | 0.4559 | 1.2998 | 0.3171 | 284 | 278 | 270 | 278
KEOO1- | KEOO1Q | 2030 | Addition | 3 | 0 | OHL | 0.0779 | 0.5792 | 0.1795 | 482 | 460 | 420 | 460
KINC2- | KLBG2- | 2030 | Addition | 0 | 0.7 | Cable | 0.0036 | 0.015 | 2.6975 | 352 | 352 | 352 | 352
KINN4- | MOSM4- | 2030 | Addition | 36.996 | 0 | OHL | 0.0718 | 0.6743 | 23.0985 | 2770 | 2730 | 2660 | 2730
KINN4- | WFIE4- | 2030 | Addition | 34.639 | 0 | OHL | 0.0667 | 0.6224 | 21.8425 | 2770 | 2730 | 2660 | 2730
KNOK1- | MAHI1C | 2030 | Addition | 2.5 | 0.5 | Composite | 0.1407 | 0.5692 | 0.9179 | 241 | 230 | 210 | 230
KNSH1- | ARFO1- | 2030 | Addition | 7 | 0 | OHL | 0.5259 | 1.5402 | 0.3686 | 199 | 191 | 178 | 191
KNSH1- | GLLU1Q | 2030 | Addition | 4 | 0 | OHL | 0.3653 | 0.9499 | 0.1945 | 49 | 49 | 49 | 49
KNSH1- | NETS1- | 2030 | Addition | 18 | 0 | OHL | 1.6438 | 4.2747 | 0.8752 | 198 | 186 | 168 | 186
LAMB4T | WIYH4Q | 2030 | Addition | 17.88 | 0 | OHL | 0.0357 | 0.3452 | 10.5184 | 2000 | 1920 | 1790 | 1920
LMEP1- | GLLE1B | 2030 | Addition | 0 | 1.6 | Cable | 0.0357 | 0.1487 | 1.4206 | 352 | 352 | 352 | 352
MONB1A | SACO1S | 2030 | Addition | 0 | 0.2 | Cable | 0.0056 | 0.013 | 0.2463 | 181 | 164 | 164 | 164
MONB1B | SACO1T | 2030 | Addition | 0 | 0.2 | Cable | 0.0056 | 0.013 | 0.2463 | 181 | 164 | 164 | 164
MOSM4- | WFIE4- | 2030 | Addition | 8.243 | 0 | OHL | 0.0174 | 0.1577 | 4.9523 | 2770 | 2730 | 2660 | 2730
NEAR2- | NEAR2T | 2030 | Addition | 7.6 | 0 | OHL | 0.0331 | 0.3408 | 1.9829 | 1380 | 1320 | 1230 | 1320
NEAR2Q | LEGR2- | 2030 | Addition | 0 | 0.2 | Cable | 0.001 | 0.0043 | 0.7707 | 370 | 370 | 370 | 370
OFOA1- | OFOA1T | 2030 | Addition | 20 | 0 | OHL | 1.5025 | 4.4007 | 1.0533 | 167 | 160 | 148 | 160
OLDH4- | BRNX4- | 2030 | Addition | 0 | 0.95 | Cable | 0.0005 | 0.0127 | 10.5633 | 533 | 533 | 533 | 533
REDS4- | GHPS4- | 2030 | Addition | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926
REDS4- | GHPS4- | 2030 | Addition | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926
SACO1S | SACO1Q | 2030 | Addition | 4.07 | 0 | OHL | 0.1543 | 0.9166 | 0.2112 | 151 | 151 | 151 | 151
SACO1T | SACO1R | 2030 | Addition | 4.07 | 0 | OHL | 0.1543 | 0.9166 | 0.2112 | 146 | 146 | 145 | 146
SHRG1T | SHRG1- | 2030 | Addition | 1.01 | 0 | OHL | 0.0759 | 0.2222 | 0.0532 | 133 | 124 | 107 | 124
WFIB4- | WFIE4- | 2030 | Addition | 22.48 | 0 | OHL | 0.0468 | 0.4042 | 14.1168 | 2770 | 2730 | 2660 | 2730
WHIF4Q | WIYH4Q | 2030 | Addition | 0 | 1.1 | Cable | 0.0013 | 0.0102 | 12.3854 | 813 | 813 | 813 | 813
WHIF4R | WIYH4Q | 2030 | Addition | 0 | 1.1 | Cable | 0.0013 | 0.0102 | 12.3854 | 813 | 813 | 813 | 813
BLAH1- | GLGL1A | 2030 | Change | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 297 | 281 | 258 | 281
BLAH1- | GLGL1A | 2030 | Change | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 297 | 281 | 258 | 281
BRAP1- | ERSK1R | 2030 | Change | 2.03 | 6.4 | Composite | 0.2508 | 1.0434 | 9.0367 | 156 | 156 | 156 | 156
CAFA1Q | KEOO1- | 2030 | Change | 2.58 | 0 | OHL | 0.198 | 0.5682 | 0.1357 | 135 | 126 | 110 | 126
CHAP1- | GRNA1- | 2030 | Change | 12.83 | 0.355 | Composite | 0.7981 | 3.0459 | 1.0231 | 132 | 123 | 106 | 123
COAL1A | KENN1- | 2030 | Change | 16 | 3.4 | Composite | 1.2963 | 3.7441 | 5.0291 | 140 | 124 | 124 | 124
COAL4- | REDS4- | 2030 | Change | 11 | 0 | OHL | 0.0235 | 0.2158 | 6.3256 | 2770 | 2770 | 2770 | 2770
COAL4- | STHA4B | 2030 | Change | 21.73 | 0 | OHL | 0.0463 | 0.4262 | 12.4959 | 2770 | 2770 | 2770 | 2770
COAN4- | REDS4- | 2030 | Change | 11 | 0 | OHL | 0.0235 | 0.2158 | 6.3256 | 2770 | 2770 | 2770 | 2770
COAN4- | STHA4A | 2030 | Change | 21.79 | 0 | OHL | 0.0465 | 0.4275 | 12.5295 | 2770 | 2770 | 2770 | 2770
COYL2- | CRCK2- | 2030 | Change | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090
CRCK2- | MAHI2- | 2030 | Change | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090
DALL2- | INVR2- | 2030 | Change | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 1380 | 1320 | 1230 | 1320
DENN2- | LAMB2- | 2030 | Change | 31.991 | 0 | OHL | 0.1391 | 1.4345 | 8.3553 | 1380 | 1320 | 1230 | 1320
DEVM4- | WIYH4Q | 2030 | Change | 28.908 | 0 | OHL | 0.0485 | 0.5525 | 17.5384 | 2000 | 1920 | 1790 | 1920
DUNF1R | HALB1T | 2030 | Change | 3.86 | 0 | OHL | 0.2051 | 0.8375 | 0.2048 | 215 | 215 | 198 | 215
ELVA4- | REDS4- | 2030 | Change | 15.77 | 0 | OHL | 0.0336 | 0.3093 | 9.0686 | 2770 | 2770 | 2770 | 2770
ELVA4- | REDS4- | 2030 | Change | 15.77 | 0 | OHL | 0.0336 | 0.3093 | 9.0686 | 2770 | 2770 | 2770 | 2770
GLGL1B | SANQ1- | 2030 | Change | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 283 | 277 | 269 | 277
GLLE1- | GLLE1B | 2030 | Change | 16.55 | 0 | OHL | 1.0058 | 3.644 | 0.8645 | 234 | 225 | 209 | 225
GLLE1- | KEOO1- | 2030 | Change | 7.68 | 0 | OHL | 0.1961 | 1.3641 | 0.4896 | 482 | 445 | 385 | 445
GORG1Q | TELR1Q | 2030 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 72 | 72 | 72 | 72
GORG1R | TELR1R | 2030 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 72 | 72 | 72 | 72
GRNA4- | HAKB4B | 2030 | Change | 1.97 | 0 | OHL | 0.0042 | 0.0394 | 1.1215 | 2770 | 2770 | 2770 | 2770
HAKB4- | MOFF4C | 2030 | Change | 43.79 | 0 | OHL | 0.0939 | 0.8758 | 24.9293 | 2770 | 2770 | 2770 | 2770
HUNF1R | SACO1T | 2030 | Change | 4.502 | 3.04 | Composite | 0.2672 | 1.3209 | 6.3907 | 146 | 146 | 145 | 146
JUNA1T | SACO1S | 2030 | Change | 4.07 | 0 | OHL | 0.1543 | 0.9166 | 0.2112 | 151 | 151 | 151 | 151
JUNB1- | JUNV1- | 2030 | Change | 1 | 0 | OHL | 0 | 0.0001 | 0 | 2286 | 2286 | 2286 | 2286
KINC2- | KINN2A | 2030 | Change | 1.9 | 0 | OHL | 0.0043 | 0.0666 | 0.6085 | 1390 | 1280 | 1110 | 1280
KINC2- | KINN2B | 2030 | Change | 0 | 1.9 | Cable | 0.0025 | 0.0212 | 18.0563 | 660 | 660 | 595 | 660
LORG1- | SHRG1T | 2030 | Change | 10 | 0 | OHL | 0.7598 | 2.1663 | 0.5285 | 284 | 279 | 270 | 279
NEAR2- | WISH2- | 2030 | Change | 15.76 | 0 | OHL | 0.0685 | 0.7067 | 4.1118 | 1380 | 1320 | 1230 | 1320
NEIL1- | SERG1- | 2030 | Change | 0 | 1.98 | Cable | 0.0559 | 0.1285 | 2.4386 | 200 | 185 | 175 | 185
BENB1T | BLCW1- | 2030 | Removed | 32.15 | 0.9 | Composite | 1.1801 | 6.5296 | 3.3413 | 199 | 199 | 199 | 199
BONB2J | DENN2- | 2030 | Removed | 19.894 | 0 | OHL | 0.054 | 0.7739 | 5.8126 | 1500 | 1500 | 1500 | 1500
BONN1- | CUMB1Q | 2030 | Removed | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN1- | CUMB1R | 2030 | Removed | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135
BONN2A | DENN2- | 2030 | Removed | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647
BONN2B | DENN2- | 2030 | Removed | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647
CHAP1- | DUMF1- | 2030 | Removed | 26.9 | 0.18 | Composite | 1.0661 | 6.0867 | 1.6344 | 171 | 155 | 155 | 155
CLYM2- | LOAN2- | 2030 | Removed | 54.57 | 0 | OHL | 0.1231 | 1.9141 | 17.477 | 1500 | 1500 | 1500 | 1500
COCK4Q | ECCL4A | 2030 | Removed | 65.9 | 0 | OHL | 0.135 | 1.4191 | 35.4794 | 1120 | 1060 | 990 | 1060
COCK4R | ECCL4B | 2030 | Removed | 65.89 | 0 | OHL | 0.135 | 1.4189 | 35.4739 | 1120 | 1060 | 990 | 1060
CRYR4- | TORN4- | 2030 | Removed | 9.36 | 1.97 | Composite | 0.0144 | 0.2171 | 44.1355 | 1415 | 1415 | 1415 | 1415
DENN2- | LAMB2T | 2030 | Removed | 31.991 | 0 | OHL | 0.1442 | 1.3015 | 8.8844 | 955 | 885 | 760 | 885
DENN2- | LOAN2- | 2030 | Removed | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DENN2- | LOAN2T | 2030 | Removed | 21.59 | 0 | OHL | 0.0498 | 0.7694 | 6.8256 | 1500 | 1500 | 1500 | 1500
DUMF1- | TONG1Q | 2030 | Removed | 43.58 | 0 | OHL | 4.447 | 10.71 | 2.18 | 132 | 123 | 106 | 123
DUNE1- | GALA1- | 2030 | Removed | 23.64 | 0 | OHL | 2.1456 | 5.5767 | 1.1477 | 164 | 151 | 127 | 151
DUNE1- | SMEA1- | 2030 | Removed | 17.838 | 0.621 | Composite | 1.098 | 3.6602 | 1.7709 | 154 | 131 | 127 | 131
EAST1Q | GLLE1- | 2030 | Removed | 1.69 | 0 | OHL | 0.1536 | 0.3503 | 0.094 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 2030 | Removed | 31.37 | 0 | OHL | 2.8482 | 7.3807 | 1.5285 | 132 | 123 | 106 | 123
ECCL1- | GALA1- | 2030 | Removed | 30.94 | 0 | OHL | 2.8144 | 7.1441 | 1.5364 | 132 | 123 | 106 | 123
ECCL4A | TORN4- | 2030 | Removed | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
ECCL4B | TORN4- | 2030 | Removed | 34.2 | 2.1 | Composite | 0.0447 | 0.6543 | 67.6758 | 2330 | 1840 | 1840 | 1840
EERH2- | LOAN2- | 2030 | Removed | 45.82 | 0 | OHL | 0.1034 | 1.6072 | 14.6747 | 1500 | 1500 | 1500 | 1500
EERH2- | NEAR2Q | 2030 | Removed | 15.46 | 0 | OHL | 0.0705 | 0.6545 | 4.1829 | 950 | 885 | 760 | 885
GLLE1- | WNUK1- | 2030 | Removed | 17 | 0.5 | Composite | 1.2996 | 3.7201 | 1.6799 | 200 | 200 | 200 | 200
GLLU1Q | NETS1- | 2030 | Removed | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49
GLLU1R | NETS1- | 2030 | Removed | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 57 | 57 | 57 | 57
GLRB2- | GLRO2- | 2030 | Removed | 14.68 | 0 | OHL | 0.0664 | 0.6181 | 3.956 | 1090 | 1030 | 925 | 1030
GLRO2- | WFIE2- | 2030 | Removed | 12.08 | 0 | OHL | 0.0547 | 0.5102 | 3.2488 | 1090 | 1030 | 925 | 1030
HOLM1T | KEOO1- | 2030 | Removed | 10.16 | 0 | OHL | 0.4101 | 2.0583 | 0.5825 | 132 | 123 | 106 | 123
KINC2- | LOAN2Q | 2030 | Removed | 4.28 | 0 | OHL | 0.0186 | 0.1855 | 1.1454 | 765 | 620 | 620 | 620
KINC2- | LOAN2R | 2030 | Removed | 4.28 | 0 | OHL | 0.0186 | 0.1855 | 1.1454 | 765 | 620 | 620 | 620
LAMB2- | LAMB2T | 2030 | Removed | 0.001 | 0 | OHL | 0 | 0 | 0 | 1120 | 1060 | 990 | 1060
LAMB2T | WIYH2- | 2030 | Removed | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9691 | 1380 | 1320 | 1230 | 1320
LOAN2- | DEBS2- | 2030 | Removed | 0 | 4 | Cable | 0.0081 | 0.1105 | 24.3285 | 820 | 736 | 674 | 736
LOAN2- | LOAN2Q | 2030 | Removed | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2R | 2030 | Removed | 0 | 0 | Series Reactor | 0.0047 | 1.9355 | 0 | 620 | 620 | 620 | 620
LOAN2- | LOAN2S | 2030 | Removed | 0 | 0.174 | Cable | 0.0004 | 0.0039 | 1.5626 | 760 | 760 | 760 | 760
LOAN2- | LOAN2S | 2030 | Removed | 0 | 0.174 | Cable | 0.0004 | 0.0039 | 1.5626 | 760 | 760 | 760 | 760
LOAN2- | LOAN2T | 2030 | Removed | 0.025 | 0 | OHL | 0 | 0 | 0 | 1500 | 1500 | 1500 | 1500
LOAN2S | MOSM2- | 2030 | Removed | 31.496 | 0 | OHL | 0.1426 | 1.3291 | 8.4753 | 1090 | 1090 | 1090 | 1090
LOAN2T | WFIE2- | 2030 | Removed | 29.209 | 0 | OHL | 0.1316 | 1.2106 | 7.9335 | 1090 | 1030 | 925 | 1030
MOSM2- | WFIE2- | 2030 | Removed | 8.243 | 0 | OHL | 0.0378 | 0.3641 | 2.1507 | 1090 | 1090 | 1090 | 1090
NEAR2Q | WISH2- | 2030 | Removed | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 955 | 955 | 955
SMEA4Q | TORN4- | 2030 | Removed | 54.32 | 1.94 | Composite | 0.0742 | 1.1033 | 70.0791 | 1360 | 1280 | 1280 | 1280
BONN1- | BONN1R | 2033 | Addition | 0 | 0 | OHL | 0 | 0 | 0 | 240 | 240 | 240 | 240
BONN1- | BONN1S | 2033 | Addition | 0 | 0 | OHL | 0 | 0 | 0 | 240 | 240 | 240 | 240
BONN1R | DENN1- | 2033 | Addition | 4.04 | 0.3 | Composite | 0.3745 | 0.8399 | 0.6219 | 240 | 240 | 240 | 240
BONN1R | STIR1S | 2033 | Addition | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 240 | 240 | 240 | 240
BONN1S | DENN1A | 2033 | Addition | 4.04 | 0.3 | Composite | 0.3745 | 0.8399 | 0.6219 | 240 | 240 | 240 | 240
BONN1S | STIR1T | 2033 | Addition | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 240 | 240 | 240 | 240
COAN1Q | COAN1- | 2033 | Addition | 0 | 0.5 | Cable | 0.0099 | 0.0149 | 0.6569 | 200 | 185 | 175 | 185
COAN1Q | KIRH1- | 2033 | Addition | 8.36 | 0 | OHL | 0.4477 | 1.9686 | 0.415 | 176 | 176 | 176 | 176
COAN1R | COAN1- | 2033 | Addition | 0 | 0.5 | Cable | 0.0099 | 0.0149 | 0.6569 | 200 | 185 | 175 | 185
COAN1R | KIRH1- | 2033 | Addition | 8.36 | 0 | OHL | 0.4477 | 1.9686 | 0.415 | 176 | 176 | 176 | 176
COLD1T | COLD1- | 2033 | Addition | 0 | 0.68 | Cable | 0.0192 | 0.0441 | 0.8375 | 134 | 123 | 123 | 123
ENHI3- | MONQ3- | 2033 | Addition | 7 | 0 | OHL | 8.424 | 21.315 | 0.0269 | 34 | 32 | 28 | 32
GRNA4- | WESS4- | 2033 | Addition | 0 | 0.4 | Cable | 0.0002 | 0.0053 | 4.4477 | 575 | 575 | 575 | 575
HARB4Q | SMEA4Q | 2033 | Addition | 33.44 | 0 | OHL | 0.0711 | 0.6639 | 19.4885 | 2770 | 2730 | 2660 | 2730
HARB4Q | WISH4- | 2033 | Addition | 28.33 | 0 | OHL | 0.0602 | 0.5625 | 16.5105 | 2770 | 2730 | 2660 | 2730
HARB4R | SMEA4R | 2033 | Addition | 33.44 | 0 | OHL | 0.0711 | 0.6639 | 19.4885 | 2770 | 2730 | 2660 | 2730
HARB4R | WISH4- | 2033 | Addition | 28.33 | 0 | OHL | 0.0602 | 0.5625 | 16.5105 | 2770 | 2730 | 2660 | 2730
HILB1- | MOSM1Q | 2033 | Addition | 0 | 3.5 | Cable | 0.0286 | 0.2859 | 6.5177 | 293 | 293 | 293 | 293
HUNE4- | KEPP4T | 2033 | Addition | 1 | 0.3 | Composite | 0.0022 | 0.0246 | 3.8943 | 1243 | 1243 | 1243 | 1243
HUNP4- | KEPP4T | 2033 | Addition | 2.4 | 0 | OHL | 0.0049 | 0.0494 | 1.3404 | 2000 | 1920 | 1790 | 1920
LALE1- | COLD1T | 2033 | Addition | 3.77 | 0 | OHL | 0.2828 | 0.8302 | 0.1983 | 167 | 160 | 148 | 160
MAHI2- | WMHL2- | 2033 | Addition | 0 | 6 | Cable | 0.0064 | 0.1695 | 31.5334 | 575 | 575 | 575 | 575
MOFF4- | BTCK4- | 2033 | Addition | 0.01 | 0 | OHL | 0 | 0 | 0 | 6928 | 6928 | 6928 | 6928
MOFF4- | BTCK4- | 2033 | Addition | 0.01 | 0 | OHL | 0 | 0 | 0 | 6928 | 6928 | 6928 | 6928
MOIL2- | AUCH2- | 2033 | Addition | 12.21 | 0 | OHL | 0.0528 | 0.5275 | 3.2843 | 1372 | 1324 | 1228 | 1324
MOIL2- | AUCH2- | 2033 | Addition | 12.21 | 0 | OHL | 0.0528 | 0.5275 | 3.2843 | 1372 | 1324 | 1228 | 1324
TORN4- | THRN4- | 2033 | Addition | 0 | 1.05 | Cable | 0.0003 | 0.007 | 23.3504 | 1040 | 900 | 900 | 900
TORN4Q | THRN4- | 2033 | Addition | 0 | 0.89 | Cable | 0.0002 | 0.0059 | 19.7922 | 945 | 800 | 800 | 800
WFIE4- | WFIE4A | 2033 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0 | 2770 | 2770 | 2770 | 2770
BANK4- | ECCL4A | 2033 | Change | 0.3 | 0 | OHL | 0 | 0 | 0 | 2000 | 1920 | 1790 | 1920
BRNX4- | THRN4- | 2033 | Change | 0 | 1.05 | Cable | 0.0003 | 0.007 | 23.3504 | 1040 | 900 | 900 | 900
BRNX4- | THRN4- | 2033 | Change | 0 | 1.05 | Cable | 0.0003 | 0.007 | 23.3504 | 945 | 800 | 800 | 800
COAL4- | REDS4- | 2033 | Change | 11 | 0 | OHL | 0.0192 | 0.2085 | 6.5859 | 2210 | 2130 | 1980 | 2130
COAL4- | STHA4B | 2033 | Change | 21.73 | 0 | OHL | 0.038 | 0.4118 | 13.0101 | 2210 | 2130 | 1980 | 2130
COAN4- | REDS4- | 2033 | Change | 11 | 0 | OHL | 0.0192 | 0.2085 | 6.5859 | 2210 | 2130 | 1980 | 2130
COAN4- | STHA4A | 2033 | Change | 21.79 | 0 | OHL | 0.0381 | 0.413 | 13.045 | 2210 | 2130 | 1980 | 2130
ELVA4- | REDS4- | 2033 | Change | 15.77 | 0 | OHL | 0.0276 | 0.2989 | 9.4418 | 2210 | 2130 | 1980 | 2130
GORG1Q | TELR1Q | 2033 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 24 | 24 | 24 | 24
GORG1R | TELR1R | 2033 | Change | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 24 | 24 | 24 | 24
JUNB1- | JUNV1- | 2033 | Change | 1 | 0 | OHL | 0 | 0.0001 | 0 | 1000 | 1000 | 1000 | 1000
KINB4J | KINN4- | 2033 | Change | 8.8 | 0 | OHL | 0.0188 | 0.1808 | 5.0001 | 2410 | 2320 | 2160 | 2320
KINB4K | KINN4- | 2033 | Change | 8.8 | 0 | OHL | 0.0188 | 0.1808 | 5.0001 | 2410 | 2320 | 2160 | 2320
BONN1- | DENN1- | 2033 | Removed | 8.08 | 0.3 | Composite | 0.1876 | 0.4239 | 1.241 | 244 | 214 | 214 | 214
BONN1- | STIR1S | 2033 | Removed | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219
BONN1- | STIR1T | 2033 | Removed | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219
SMEA4Q | WISH4- | 2033 | Removed | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2770 | 2730 | 2660 | 2730
SMEA4R | WISH4- | 2033 | Removed | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2770 | 2730 | 2660 | 2730
WFIB2- | WFIE2- | 2033 | Removed | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 1090 | 1030 | 925 | 1030

## B-2-2c
B-2-2c - NGET Circuit Changes 2026/27 to 2033/34
Node1 | Node2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA)
BENR41 | NEWX41 | 2026 | Addition | 0 | 4.14 | Cable | 0.0206 | 0.0555 | 50.9843 | 1100 | 1100 | 1100 | 1100
BENR41 | WIMB41 | 2026 | Addition | 0 | 8.318 | Cable | 0.0415 | 0.1115 | 102.4365 | 1250 | 1250 | 1250 | 1250
BIGG41 | EASO41 | 2026 | Addition | 16.5 | 0 | OHL | 0.0146 | 0.2834 | 11.0904 | 2779 | 2569 | 2217 | 2568
BIGG41 | WYMO41 | 2026 | Addition | 18.772 | 0 | OHL | 0.0166 | 0.3224 | 12.6175 | 2779 | 2568 | 2217 | 2568
BOLN41 | LHOR4A | 2026 | Addition | 28.1 | 0 | OHL | 0.0305 | 0.4887 | 18.5239 | 3102 | 2935 | 2765 | 2935
BOLN41 | LOVE41 | 2026 | Change | 64.961 | 0 | OHL | 0.0576 | 1.1158 | 43.6626 | 3102 | 2935 | 2765 | 2935
BOLN41 | LOVE41 | 2026 | Change | 64.774 | 0 | OHL | 0.0574 | 1.1125 | 43.5374 | 3326 | 3326 | 3320 | 3326
BRAI4B | RAYL41 | 2026 | Change | 33.03 | 0 | OHL | 0.0325 | 0.5709 | 22.0036 | 2779 | 2568 | 2217 | 2568
BRFO41 | DISS4A | 2026 | Addition | 31.4 | 0.1 | Composite | 0.0279 | 0.5404 | 23.1059 | 3326 | 3160 | 2971 | 3160
BRFO41 | DISS4B | 2026 | Addition | 31.4 | 0.1 | Composite | 0.0279 | 0.5404 | 23.1059 | 3326 | 3160 | 2971 | 3160
BRLE41 | FLEE41 | 2026 | Change | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3326 | 3326 | 3320 | 3326
BRLE41 | FLEE41 | 2026 | Change | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3326 | 3326 | 3320 | 3326
BRLE41 | MELK41 | 2026 | Change | 77.5 | 4.4 | Composite | 0.1014 | 1.4812 | 154.8346 | 2830 | 2770 | 2680 | 2770
BRLE41 | MELK41 | 2026 | Change | 78.24 | 4.4 | Composite | 0.1024 | 1.4951 | 155.2907 | 2830 | 2770 | 2680 | 2770
BRWA4A | MELK41 | 2026 | Addition | 77.004 | 0 | OHL | 0.1367 | 1.519 | 45.0376 | 2009 | 1912 | 1746 | 1912
BRWA4B | MELK41 | 2026 | Addition | 76.264 | 0 | OHL | 0.1356 | 1.5048 | 44.5913 | 2009 | 1912 | 1746 | 1912
BULL41 | RAYL41 | 2026 | Change | 20.646 | 0 | OHL | 0.0203 | 0.3568 | 13.7565 | 3326 | 3326 | 3320 | 3326
CILF41 | RASS41 | 2026 | Change | 26.901 | 0 | OHL | 0.0296 | 0.4899 | 17.0456 | 2779 | 2568 | 2217 | 2568
CONQ41 | GWYN4B | 2026 | Change | 30.217 | 0.21 | Composite | 0.0273 | 0.5204 | 25.4825 | 2830 | 2770 | 2680 | 2770
CONQ42 | GWYN4A | 2026 | Change | 30.217 | 0.21 | Composite | 0.0273 | 0.5204 | 25.4825 | 2830 | 2770 | 2680 | 2770
COWL41 | ECLA41 | 2026 | Change | 36.086 | 0 | OHL | 0.032 | 0.6198 | 24.255 | 3326 | 3326 | 3317 | 3326
COWL41 | FARM41 | 2026 | Addition | 11.228 | 2.092 | Composite | 0.0139 | 0.226 | 41.9824 | 1180 | 1132 | 877 | 979
COWL41 | FARM41 | 2026 | Addition | 11.228 | 2.092 | Composite | 0.0139 | 0.226 | 41.9824 | 1180 | 1132 | 877 | 979
COWL41 | LEIB4A | 2026 | Change | 52.28 | 0 | OHL | 0.0462 | 0.8979 | 35.1591 | 3326 | 3326 | 3320 | 3326
COWL41 | MITY41 | 2026 | Removed | 100.105 | 2.092 | Composite | 0.1418 | 1.8493 | 98.0711 | 1180 | 1132 | 877 | 979
COWL41 | WALH41 | 2026 | Removed | 89.553 | 2.092 | Composite | 0.113 | 1.6366 | 92.0801 | 1180 | 1132 | 877 | 979
CREB41 | THTO42 | 2026 | Change | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3326 | 3326 | 3320 | 3326
DINO41 | PENT41 | 2026 | Change | 0 | 10.762 | Cable | 0.0057 | 0.1552 | 135.2393 | 1604 | 1604 | 1557 | 1557
DISS4A | NORM41 | 2026 | Addition | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3160 | 2971 | 3160
DISS4A | YAXL41 | 2026 | Addition | 0.05 | 0 | OHL | 0 | 0.0009 | 0.0336 | 3326 | 3326 | 3317 | 3326
DISS4B | NORM41 | 2026 | Addition | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3160 | 2971 | 3160
DISS4B | YAXL41 | 2026 | Addition | 0.05 | 0 | OHL | 0 | 0.0009 | 0.0336 | 3326 | 3326 | 3317 | 3326
DRAK41 | RATS41 | 2026 | Change | 32.907 | 0 | OHL | 0.0566 | 0.6488 | 19.2536 | 2009 | 1911 | 1746 | 1911
DRAK41 | WILE41 | 2026 | Change | 16.937 | 0 | OHL | 0.0285 | 0.3306 | 10.0005 | 3100 | 3050 | 3050 | 3050
EASO41 | WYMO41 | 2026 | Change | 35.272 | 0 | OHL | 0.0313 | 0.6058 | 23.7078 | 3326 | 3326 | 3320 | 3326
EASO41 | WYMO41 | 2026 | Removed | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
EASO41 | WYMO41 | 2026 | Change | 35.272 | 0 | OHL | 0.0313 | 0.6058 | 23.7078 | 3326 | 3326 | 3320 | 3326
EASO41 | WYMO41 | 2026 | Removed | 35.272 | 0 | OHL | 0.0383 | 0.6135 | 23.2517 | 2779 | 2568 | 2217 | 2568
FARM41 | MITY41 | 2026 | Addition | 88.877 | 0 | OHL | 0.1144 | 1.6098 | 56.5224 | 2170 | 2170 | 1940 | 2170
FARM41 | WALH41 | 2026 | Addition | 78.325 | 0 | OHL | 0.0991 | 1.4105 | 50.0977 | 2170 | 2080 | 1940 | 2080
FAWL41 | MANN41 | 2026 | Change | 61.115 | 0 | OHL | 0.0583 | 1.0223 | 42.2225 | 2779 | 2568 | 2217 | 2568
FECK41 | MITY41 | 2026 | Change | 78.649 | 0 | OHL | 0.1392 | 1.5543 | 45.8863 | 1967 | 1874 | 1712 | 1874
GRAI41 | KINO41 | 2026 | Removed | 11.507 | 0.8 | Composite | 0.0126 | 0.2028 | 18.5632 | 3326 | 3159 | 2633 | 2813
GRAI41 | TILB41 | 2026 | Change | 26.858 | 2.049 | Composite | 0.0306 | 0.4885 | 57.5433 | 2003 | 2003 | 1939 | 2003
GRAI41 | WAEN41 | 2026 | Addition | 1.948 | 0 | OHL | 0.0021 | 0.0339 | 1.2841 | 3326 | 3160 | 2633 | 2813
HAMB4A | STAH4A | 2026 | Change | 3.926 | 0 | OHL | 0.007 | 0.078 | 2.2826 | 1970 | 1870 | 1710 | 1870
HAMB4B | STAH4B | 2026 | Change | 3.926 | 0 | OHL | 0.007 | 0.078 | 2.2826 | 1970 | 1870 | 1710 | 1870
HAMH41 | WILE41 | 2026 | Change | 84.14 | 0.7 | Composite | 0.1244 | 1.599 | 76.5606 | 2009 | 1912 | 1746 | 1912
HAWP22 | NORT21 | 2026 | Change | 27.949 | 0.203 | Composite | 0.0668 | 1.0519 | 10.749 | 1381 | 1381 | 1285 | 1381
HAWP4A | NORT41 | 2026 | Change | 27.868 | 0 | OHL | 0.0313 | 0.4936 | 18.0929 | 2545 | 2421 | 2211 | 2421
HINP41 | MELK41 | 2026 | Removed | 86.136 | 0 | OHL | 0.1564 | 1.7133 | 49.9342 | 2009 | 1911 | 1746 | 1911
HINP41 | SAFO41 | 2026 | Addition | 26.58 | 8.94 | Composite | 0.0421 | 0.5573 | 218.3267 | 2009 | 1911 | 1770 | 1911
HINP41 | SAFO42 | 2026 | Change | 26.571 | 8.99 | Composite | 0.0421 | 0.5575 | 219.45 | 2009 | 1912 | 1746 | 1912
HURS21 | NEWX21 | 2026 | Change | 0 | 18.499 | Cable | 0.1952 | 0.5245 | 107.6787 | 1200 | 1200 | 1200 | 1200
HURS21 | NEWX21 | 2026 | Change | 0 | 18.357 | Cable | 0.1937 | 0.5204 | 106.8521 | 1200 | 1200 | 1200 | 1200
HYLC21 | OFFE21 | 2026 | Addition | 6.65 | 0 | OHL | 0.0304 | 0.2815 | 1.8041 | 1176 | 1115 | 940 | 1018
HYLC21 | WBOL21 | 2026 | Addition | 1.557 | 0 | OHL | 0.0071 | 0.0659 | 0.4224 | 1176 | 1115 | 940 | 1018
KEAD43 | KEAD43 | 2026 | Addition | 0 | 0 | Series Reactor | 0.0015 | 0.5 | 0 | 2640 | 2640 | 2640 | 2640
KINO41 | WAEN41 | 2026 | Addition | 9.683 | 0.8 | parallel Composite | 0.0107 | 0.171 | 17.3608 | 3326 | 3160 | 2633 | 2813
LEIB4A | SUND42 | 2026 | Change | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 3326 | 3326 | 3320 | 3326
LLFG41 | PEMB41 | 2026 | Addition | 55.98 | 0 | OHL | 0.0607 | 0.9737 | 36.9025 | 2779 | 2568 | 2217 | 2568
LLFG41 | PEMB41 | 2026 | Addition | 55.88 | 0 | OHL | 0.0606 | 0.9719 | 36.8368 | 2779 | 2568 | 2217 | 2568
LLFG41 | SWAN41 | 2026 | Addition | 28 | 0 | OHL | 0.0304 | 0.487 | 18.458 | 2779 | 2568 | 2217 | 2568
LLFG41 | WALH41 | 2026 | Addition | 161.956 | 5.468 | parallel Composite | 0.1766 | 2.8363 | 170.6498 | 2779 | 2568 | 2217 | 2568
MANN41 | NURS4A | 2026 | Change | 39.823 | 0 | OHL | 0.0353 | 0.684 | 26.7664 | 3326 | 3326 | 3320 | 3326
MARV41 | MARV4A | 2026 | Addition | 0.145 | 0 | OHL | 0.0003 | 0.0029 | 0.0839 | 2009 | 1912 | 1746 | 1912
MARV41 | MARV4B | 2026 | Addition | 0.077 | 0 | OHL | 0.0001 | 0.0015 | 0.0446 | 2009 | 1912 | 1746 | 1912
MELK41 | SAFO41 | 2026 | Removed | 85.26 | 8.94 | Composite | 0.1484 | 1.7246 | 252.3421 | 2009 | 1912 | 1746 | 1912
NECT41 | NECT41 | 2026 | Removed | 0 | 0.129 | Cable | 0.0001 | 0.0016 | 1.6211 | 1940 | 1940 | 1940 | 1940
NECT41 | NECT4A | 2026 | Removed | 0 | 0 | Zero Length | 0 | 0 | 0 | 1364 | 1364 | 1250 | 1250
NECT41 | NECT4B | 2026 | Removed | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159
NECT41 | NORM41 | 2026 | Addition | 35.621 | 0 | OHL | 0.0316 | 0.6118 | 23.9417 | 3326 | 3326 | 3317 | 3326
NECT41 | NORM41 | 2026 | Addition | 35.621 | 0 | OHL | 0.0316 | 0.6118 | 23.9417 | 3326 | 3258 | 3060 | 3258
NECT41 | WALP41 | 2026 | Addition | 43.23 | 0 | OHL | 0.0383 | 0.7425 | 29.057 | 3326 | 3160 | 2971 | 3160
NECT41 | WALP41 | 2026 | Addition | 43.23 | 0 | OHL | 0.0383 | 0.7425 | 29.057 | 3326 | 3326 | 3317 | 3326
NECT4A | NORM41 | 2026 | Removed | 35.652 | 0 | OHL | 0.0316 | 0.6124 | 23.9626 | 3326 | 3326 | 3317 | 3326
NECT4A | WALP41 | 2026 | Removed | 43.459 | 0 | OHL | 0.0385 | 0.7464 | 29.2107 | 3326 | 3326 | 3317 | 3326
NECT4B | NORM41 | 2026 | Removed | 35.652 | 0 | OHL | 0.0316 | 0.6124 | 23.9626 | 3326 | 3258 | 3060 | 3258
NECT4B | WALP41 | 2026 | Removed | 43.459 | 0 | OHL | 0.0385 | 0.7464 | 29.2107 | 3326 | 3160 | 2971 | 3160
PEMB41 | SWAN41 | 2026 | Removed | 83.975 | 0 | OHL | 0.0911 | 1.4606 | 55.3574 | 2779 | 2568 | 2217 | 2568
PEMB41 | WALH41 | 2026 | Removed | 217.727 | 5.468 | Composite | 0.2376 | 3.8305 | 206.6595 | 2779 | 2568 | 2217 | 2568
PITS21 | TEMP21 | 2026 | Removed | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 419 | 419 | 381 | 381
PITS21 | WIBA21 | 2026 | Change | 0 | 2.7 | Cable | 0.0041 | 0.0722 | 16.0368 | 530 | 530 | 445 | 530
SAFO41 | SEAB4A | 2026 | Change | 31.28 | 0 | OHL | 0.0345 | 0.5479 | 20.4859 | 3028 | 2909 | 2712 | 2909
SAFO42 | SEAB41 | 2026 | Addition | 31.242 | 0 | OHL | 0.0344 | 0.5471 | 20.4646 | 3028 | 2909 | 2712 | 2909
TEMP21 | TEMP22 | 2026 | Addition | 0 | 0 | Series Reactor | 0 | 0 | 0 | 953 | 953 | 953 | 953
TEMP21 | TEMP22 | 2026 | Addition | 0 | 0 | Series Reactor | 0 | 0 | 0 | 953 | 953 | 953 | 953
TEMP22 | WIBA21 | 2026 | Change | 0 | 3.3 | Cable | 0.0051 | 0.0882 | 19.6006 | 530 | 530 | 445 | 530
ABHA41 | LAGA41 | 2028 | Change | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327
ABHA42 | LAGA41 | 2028 | Change | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327
BARK41 | WHAM41 | 2028 | Change | 9.662 | 0 | OHL | 0.0151 | 0.191 | 5.623 | 3100 | 3050 | 2960 | 3050
BARK41 | WHAM41 | 2028 | Change | 9.662 | 0.124 | Composite | 0.0151 | 0.1915 | 10.4342 | 3100 | 3050 | 2960 | 3050
BENR41 | NEWX41 | 2028 | Change | 0 | 4.14 | Cable | 0.0021 | 0.0555 | 50.9843 | 1100 | 1100 | 1100 | 1100
BENR41 | WIMB41 | 2028 | Change | 0 | 8.318 | Cable | 0.0041 | 0.1115 | 102.4365 | 1250 | 1250 | 1250 | 1250
BESW21 | FECK21 | 2028 | Change | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 882 | 762 | 882
BESW21 | OCKH21 | 2028 | Change | 56.939 | 0.731 | Composite | 0.2318 | 2.4208 | 22.7971 | 819 | 819 | 638 | 638
BISW21 | FECK21 | 2028 | Change | 22.83 | 0 | OHL | 0.09 | 0.9539 | 6.2893 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 2028 | Change | 24.226 | 0 | OHL | 0.0923 | 1.0003 | 6.768 | 955 | 882 | 762 | 882
BISW21 | KITW21 | 2028 | Change | 27.111 | 0 | OHL | 0.1043 | 1.1209 | 7.5619 | 955 | 882 | 762 | 882
BISW21 | PENN21 | 2028 | Change | 30.172 | 0 | OHL | 0.1181 | 1.2598 | 8.3183 | 1040 | 1031 | 762 | 762
BRAI4A | BRFO41 | 2028 | Change | 48.267 | 0 | OHL | 0.0428 | 0.829 | 32.4419 | 3326 | 3326 | 3317 | 3326
BRAI4A | BULL41 | 2028 | Change | 12.343 | 0 | OHL | 0.0109 | 0.212 | 8.2953 | 3066 | 2830 | 2418 | 2830
BRAI4B | BULL41 | 2028 | Addition | 12.384 | 0 | OHL | 0.011 | 0.2127 | 8.3227 | 3326 | 3326 | 3320 | 3326
BRAI4B | PELH42 | 2028 | Change | 65.942 | 0 | OHL | 0.0585 | 1.1326 | 44.3214 | 3326 | 3326 | 3320 | 3326
BRAI4B | RAYL41 | 2028 | Removed | 33.03 | 0 | OHL | 0.0358 | 0.5745 | 21.774 | 2779 | 2568 | 2217 | 2568
BRAW21 | KIRK21 | 2028 | Change | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 762 | 762 | 619 | 619
BRED21 | MACC21 | 2028 | Change | 19.612 | 0 | OHL | 0.0663 | 0.7981 | 5.5762 | 948 | 882 | 753 | 753
BRFO41 | YAXL4A | 2028 | Removed | 31.4 | 0.1 | Composite | 0.0279 | 0.5404 | 23.1059 | 3326 | 3160 | 2971 | 3160
BRFO41 | YAXL4B | 2028 | Removed | 31.4 | 0.1 | Composite | 0.0279 | 0.5404 | 23.1059 | 3326 | 3160 | 2971 | 3160
BRFO41 | KILA41 | 2028 | Addition | 36 | 0 | OHL | 0.0391 | 0.6261 | 23.7317 | 2779 | 2568 | 2217 | 2568
BRFO41 | KILA41 | 2028 | Addition | 36 | 0 | OHL | 0.0391 | 0.6261 | 23.7317 | 2779 | 2568 | 2217 | 2568
BRFO41 | PELH41 | 2028 | Change | 69.301 | 0 | OHL | 0.0614 | 1.1903 | 46.5796 | 3102 | 2935 | 2765 | 2935
BRFO41 | SIZE41 | 2028 | Removed | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRFO41 | SIZE41 | 2028 | Removed | 43.167 | 0 | OHL | 0.0468 | 0.7508 | 28.4562 | 2779 | 2568 | 2217 | 2568
BRFO41 | YAXT41 | 2028 | Addition | 31.516 | 0.1 | Composite | 0.0279 | 0.5413 | 21.1839 | 3326 | 3160 | 2971 | 3160
BRFO41 | YAXT42 | 2028 | Addition | 31.516 | 0.1 | Composite | 0.0279 | 0.5413 | 21.1839 | 3326 | 3160 | 2971 | 3160
BRIM2A | TOTT21 | 2028 | Change | 7.437 | 0.311 | Composite | 0.025 | 0.3106 | 5.4901 | 2130 | 2030 | 2030 | 2100
BRIM2A | WALX21 | 2028 | Change | 5.865 | 0 | OHL | 0.0193 | 0.2381 | 1.6636 | 2130 | 2030 | 2030 | 2100
BRIM2B | TOTT22 | 2028 | Change | 7.305 | 0.393 | Composite | 0.0247 | 0.3075 | 6.344 | 2130 | 2030 | 2030 | 2100
BRIM2B | WALX22 | 2028 | Change | 5.997 | 0 | OHL | 0.0198 | 0.2434 | 1.701 | 2130 | 2030 | 2030 | 2100
BRIM2C | TOTT24 | 2028 | Removed | 7.455 | 0.235 | Composite | 0.0344 | 0.3223 | 4.5788 | 1085 | 1031 | 925 | 1031
BRIM2C | WALX21 | 2028 | Removed | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIM2D | TOTT21 | 2028 | Removed | 7.455 | 0.384 | Composite | 0.0347 | 0.3264 | 6.1984 | 1085 | 1031 | 925 | 1031
BRIM2D | WALX21 | 2028 | Removed | 5.97 | 0 | OHL | 0.0273 | 0.2528 | 1.6211 | 1093 | 1031 | 925 | 1031
BRIM4C | HACK41 | 2028 | Addition | 13.209 | 0.527 | Composite | 0.0207 | 0.257 | 20.907 | 3100 | 3050 | 2960 | 3050
BRIM4C | WALX41 | 2028 | Addition | 5.97 | 0 | OHL | 0.0093 | 0.1145 | 3.5827 | 3100 | 3050 | 2960 | 3050
BRIM4D | HACK41 | 2028 | Addition | 13.209 | 0.676 | Composite | 0.0207 | 0.258 | 24.5769 | 3100 | 3050 | 2960 | 3050
BRIM4D | WALX41 | 2028 | Addition | 5.97 | 0 | OHL | 0.0093 | 0.1145 | 3.5827 | 3100 | 3050 | 2960 | 3050
BRWA4A | MELK41 | 2028 | Removed | 77.004 | 0 | OHL | 0.1367 | 1.519 | 45.0374 | 2009 | 1911 | 2850 | 1911
BRWA4B | MELK41 | 2028 | Removed | 76.264 | 0 | OHL | 0.1356 | 1.5048 | 44.5915 | 2009 | 2009 | 2850 | 2009
BULL41 | RAYL41 | 2028 | Addition | 20.646 | 0 | OHL | 0.0183 | 0.3546 | 13.8771 | 3326 | 3326 | 3320 | 3326
BULL41 | RAYL41 | 2028 | Change | 20.646 | 0 | OHL | 0.0183 | 0.3546 | 13.8771 | 3326 | 3326 | 3320 | 3326
BUSH21 | DRAK21 | 2028 | Change | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 1204 | 1115 | 1018 | 1115
BUSH21 | PENN21 | 2028 | Change | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1038 | 1038 | 762 | 762
CARR21 | SMAN21 | 2028 | Change | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 835 | 665 | 665
CARR21 | SMAN21 | 2028 | Change | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 835 | 665 | 665
CARR41 | DAIN41 | 2028 | Change | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9776 | 3102 | 3048 | 2958 | 3048
CARR41 | DAIN41 | 2028 | Change | 2.545 | 0 | OHL | 0.0043 | 0.0496 | 1.5076 | 2169 | 2084 | 1940 | 2084
CARR41 | KEAR41 | 2028 | Change | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2212 | 2125 | 1979 | 2125
CARR41 | PEWO41 | 2028 | Change | 56.9 | 0 | OHL | 0.0988 | 1.1179 | 33.4404 | 2169 | 2084 | 1940 | 2084
CARR42 | DAIN41 | 2028 | Change | 2.063 | 0 | OHL | 0.0035 | 0.0404 | 1.2165 | 1500 | 1500 | 1500 | 1500
CELL41 | CELL41 | 2028 | Addition | 0 | 0 | Series Compensation | 0 | 0.375 | 0 | 2420 | 2420 | 2420 | 2420
CELL41 | CELL41 | 2028 | Addition | 0 | 0 | Series Compensation | 0 | 0.375 | 0 | 2420 | 2420 | 2420 | 2420
CELL41 | CELL42 | 2028 | Addition | 0 | 0 | Series Compensation | 0 | 0.375 | 0 | 2420 | 2420 | 2420 | 2420
CELL41 | CELL43 | 2028 | Addition | 0 | 0 | Series Compensation | 0 | 0.375 | 0 | 2420 | 2420 | 2420 | 2420
CELL41 | DAIN41 | 2028 | Change | 53.412 | 2.31 | parallel Composite | 0.0842 | 1.0304 | 76.9149 | 2508 | 2508 | 2300 | 2300
CELL41 | DRAK41 | 2028 | Change | 45.012 | 0 | OHL | 0.0719 | 0.8656 | 27.0675 | 2420 | 2420 | 2420 | 2420
CELL41 | DRAK41 | 2028 | Change | 45.712 | 0 | OHL | 0.073 | 0.8791 | 27.4871 | 2420 | 2420 | 2420 | 2420
CELL41 | MACC41 | 2028 | Change | 31.617 | 0 | OHL | 0.0494 | 0.6065 | 18.9844 | 3102 | 3048 | 2958 | 3048
CILF41 | IMPP41 | 2028 | Change | 25.119 | 0 | OHL | 0.0223 | 0.4309 | 16.9054 | 3326 | 3326 | 3320 | 3326
CILF41 | WHSO4A | 2028 | Change | 35.208 | 0 | OHL | 0.0312 | 0.6042 | 23.6862 | 3326 | 3326 | 3320 | 3326
CONQ41 | TREU4B | 2028 | Change | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2212 | 2125 | 1979 | 2125
CONQ42 | TREU4A | 2028 | Change | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2397 | 2302 | 2144 | 2302
COTT41 | MARH4B | 2028 | Change | 100.853 | 0 | OHL | 0.1677 | 1.9593 | 59.8778 | 2009 | 1912 | 1746 | 1912
COTT41 | RYHA41 | 2028 | Change | 76.891 | 0 | OHL | 0.0846 | 1.4096 | 48.6457 | 3326 | 3326 | 3317 | 3326
COTT41 | STAY41 | 2028 | Change | 27.788 | 0.5 | parallel Composite | 0.0504 | 0.5522 | 21.6211 | 2213 | 2126 | 1980 | 2052
COTT42 | RYHA42 | 2028 | Change | 76.816 | 0 | OHL | 0.0846 | 1.4085 | 48.5917 | 2807 | 2696 | 2511 | 2696
COTT42 | WBUR42 | 2028 | Change | 6.76 | 0 | OHL | 0.0102 | 0.1298 | 4.0622 | 3326 | 3160 | 2971 | 3160
COVE21 | NECH21 | 2028 | Change | 30.715 | 0 | OHL | 0.0715 | 1.1726 | 9.309 | 1204 | 1115 | 1018 | 1115
COVE21 | RATS2A | 2028 | Change | 64.863 | 0.5 | Composite | 0.2171 | 2.6384 | 23.342 | 1000 | 1000 | 1000 | 1000
COWL41 | CULJ4B | 2028 | Addition | 6.874 | 0 | OHL | 0.009 | 0.134 | 4.077 | 2810 | 2700 | 2510 | 2700
COWL41 | DIDC41 | 2028 | Removed | 11.503 | 0 | OHL | 0.0151 | 0.2242 | 6.8223 | 2779 | 2568 | 2217 | 2568
COWL41 | FARM41 | 2028 | Change | 11.228 | 2.092 | Composite | 0.0127 | 0.2093 | 58.9278 | 2830 | 2770 | 2680 | 2770
COWL41 | FARM41 | 2028 | Change | 11.228 | 2.092 | Composite | 0.0127 | 0.2093 | 58.9278 | 2170 | 2170 | 1940 | 2170
CREB41 | WANB41 | 2028 | Addition | 0 | 0.2 | Cable | 0 | 0.0013 | 4.926 | 2750 | 2750 | 2750 | 2750
CREB41 | WANB41 | 2028 | Addition | 0 | 0.25 | Cable | 0 | 0.0011 | 9.2363 | 3326 | 3320 | 3320 | 3320
CREB42 | THTO42 | 2028 | Change | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3326 | 3326 | 3320 | 3326
CREB42 | WANB42 | 2028 | Addition | 0 | 0.03 | Cable | 0 | 0.0001 | 1.1084 | 3326 | 3320 | 3320 | 3320
CUJT41 | CULJ41 | 2028 | Addition | 0.457 | 0 | OHL | 0.0006 | 0.0089 | 0.2702 | 2771 | 2568 | 2217 | 2568
CULJ41 | CULJ4B | 2028 | Addition | 0.1 | 0.6 | Composite | 0.0003 | 0.006 | 14.8372 | 2810 | 2700 | 2510 | 2700
CULJ4B | DIDC42 | 2028 | Addition | 4.629 | 0 | OHL | 0.0061 | 0.0902 | 2.7453 | 2810 | 2700 | 2510 | 2700
DAIN41 | MACC41 | 2028 | Change | 33.593 | 2.4 | parallel Composite | 0.0535 | 0.6504 | 66.7805 | 2397 | 2302 | 2144 | 2300
DINO41 | PENT41 | 2028 | Change | 4.545 | 7.305 | Composite | 0.0093 | 0.1892 | 94.6439 | 1623 | 1623 | 1571 | 1571
NORM41 | YAXL4A | 2028 | Removed | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3160 | 2971 | 3160
NORM41 | YAXL4B | 2028 | Removed | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3160 | 2971 | 3160
DISS4A | YAXL41 | 2028 | Removed | 0.05 | 0 | OHL | 0 | 0.0009 | 0.0336 | 3326 | 3160 | 2971 | 3160
DISS4B | YAXL41 | 2028 | Removed | 0.05 | 0 | OHL | 0 | 0.0009 | 0.0336 | 3326 | 3160 | 2971 | 3160
DRAK41 | HAMH41 | 2028 | Change | 29.434 | 0 | OHL | 0.0534 | 0.5857 | 17.0575 | 2009 | 1911 | 1746 | 1911
DRAK41 | OLDB4A | 2028 | Change | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1169 | 1169 | 1068 | 1068
DRAK41 | RATS41 | 2028 | Change | 32.907 | 0 | OHL | 0.0566 | 0.6488 | 19.2536 | 2009 | 1911 | 1746 | 1911
DRAK41 | RUGE41 | 2028 | Change | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2009 | 1911 | 1746 | 1911
DRAK41 | WILE41 | 2028 | Change | 16.937 | 0 | OHL | 0.0285 | 0.3306 | 10.0005 | 3100 | 3050 | 3050 | 3050
DRAX41 | EGGB41 | 2028 | Change | 11.188 | 0.64 | Composite | 0.0126 | 0.2026 | 23.0231 | 2691 | 2691 | 2394 | 2394
DRAX42 | EGGB42 | 2028 | Change | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2973 | 2778 | 2447 | 2778
DRAX42 | THOM41 | 2028 | Change | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 2981 | 2867 | 2248 | 2505
EGGB41 | MONF42 | 2028 | Addition | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 2780 | 2570 | 2220 | 2570
EGGB41 | MONF4A | 2028 | Removed | 10.37 | 0 | OHL | 0.0113 | 0.1804 | 6.836 | 1970 | 1970 | 1970 | 1970
EGGB41 | ROCH4A | 2028 | Change | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1239 | 1239 | 1122 | 1122
ELLA21 | FERR22 | 2028 | Change | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1324 | 1260 | 1151 | 1260
ELLA21 | KIRK21 | 2028 | Change | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 762 | 762 | 619 | 619
ELLA21 | STAL21 | 2028 | Change | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 882 | 762 | 882
ELST4A | SUND41 | 2028 | Change | 34.834 | 0 | OHL | 0.0646 | 0.6825 | 20.4656 | 3102 | 3048 | 2958 | 3048
ELST4B | SUND42 | 2028 | Change | 34.706 | 0 | OHL | 0.0646 | 0.6803 | 20.3822 | 1590 | 1500 | 1346 | 1500
FECK41 | HAMH41 | 2028 | Change | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2009 | 1911 | 1746 | 1911
FECK41 | HAMH41 | 2028 | Change | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2009 | 1911 | 1746 | 1911
FECK41 | IRON41 | 2028 | Change | 66.123 | 0 | OHL | 0.1101 | 1.2908 | 39.0421 | 3100 | 3050 | 2960 | 3050
FECK41 | MITY41 | 2028 | Change | 78.649 | 0 | OHL | 0.1392 | 1.5543 | 45.8863 | 1967 | 1874 | 1712 | 1874
FENW4A | KEAD42 | 2028 | Change | 42.517 | 0 | parallel OHL | 0.0198 | 0.2161 | 24.6399 | 3420 | 3180 | 1980 | 3180
FENW4A | THOM42 | 2028 | Change | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2009 | 1911 | 1746 | 1911
FERR2B | FERR2C | 2028 | Addition | 0 | 0.726 | Cable | 0.0077 | 0.0206 | 4.2261 | 953 | 953 | 953 | 953
GART4A | WANB42 | 2028 | Change | 32.081 | 0 | OHL | 0.0348 | 0.558 | 21.1475 | 3326 | 3260 | 2980 | 3260
GART4B | WANB41 | 2028 | Change | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3326 | 3260 | 2980 | 3260
GRAI41 | TILB41 | 2028 | Removed | 26.858 | 2.049 | Composite | 0.0306 | 0.4885 | 57.5433 | 2003 | 2003 | 1939 | 2003
GRAI41 | WAEN41 | 2028 | Addition | 1.948 | 0 | OHL | 0.0021 | 0.0339 | 1.2841 | 2003 | 2003 | 1939 | 2003
GREN41 | MARH4A | 2028 | Change | 28.74 | 0 | OHL | 0.0485 | 0.5616 | 16.9528 | 2514 | 2439 | 2314 | 2439
GREN41 | MARH4B | 2028 | Change | 28.56 | 0 | OHL | 0.0482 | 0.5581 | 16.8451 | 2009 | 1912 | 1746 | 1912
GRIW41 | KEAD41 | 2028 | Change | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3075 | 2876 | 2663 | 2876
GRIW41 | SHBA41 | 2028 | Change | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2720 | 2484 | 2720
GWYD41 | TRAW41 | 2028 | Addition | 38.945 | 0 | OHL | 0.0607 | 0.7472 | 23.3708 | 3102 | 3048 | 2958 | 3048
GWYD41 | TRAW41 | 2028 | Addition | 38.945 | 0 | OHL | 0.0607 | 0.7472 | 23.3708 | 3102 | 3048 | 2958 | 3048
GWYD41 | TRAW41 | 2028 | Addition | 38.945 | 0 | OHL | 0.0607 | 0.7472 | 23.3708 | 3102 | 3048 | 2958 | 3048
GWYD41 | TREU4A | 2028 | Addition | 25.073 | 0 | OHL | 0.0391 | 0.4811 | 15.0463 | 3102 | 3048 | 2958 | 3048
GWYD41 | TREU4B | 2028 | Addition | 25.073 | 0 | OHL | 0.0391 | 0.4811 | 15.0463 | 3102 | 3048 | 2958 | 3048
HACK21 | TOTT21 | 2028 | Removed | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 1093 | 1031 | 926 | 1031
HACK22 | TOTT22 | 2028 | Removed | 5.754 | 0.292 | Composite | 0.0268 | 0.2517 | 4.735 | 1093 | 1031 | 926 | 1031
HAKB4- | HARK41 | 2028 | Removed | 9.857 | 0 | OHL | 0.0176 | 0.1957 | 5.7308 | 2213 | 2126 | 1980 | 2126
HAKB4- | HARK41 | 2028 | Addition | 10.107 | 0 | OHL | 0.0184 | 0.2062 | 5.7084 | 2213 | 2126 | 1980 | 2126
HAKB4B | HARG41 | 2028 | Addition | 10.107 | 0 | OHL | 0.0184 | 0.2062 | 5.7084 | 2170 | 2084 | 1941 | 2084
HAKB4B | HARK41 | 2028 | Removed | 9.857 | 0 | OHL | 0.0176 | 0.1957 | 5.7308 | 2170 | 2084 | 1941 | 2084
HAMH41 | WILE41 | 2028 | Change | 84.14 | 0.7 | Composite | 0.1244 | 1.599 | 76.5606 | 2009 | 1912 | 1746 | 1912
HARK12 | JUNB1A | 2028 | Addition | 1 | 0 | OHL | 1.1033 | 2.8058 | 0.6023 | 199 | 191 | 178 | 191
HARK12 | JUNB1A | 2028 | Change | 1 | 0 | OHL | 1.1033 | 2.8058 | 0.6023 | 199 | 191 | 178 | 191
HARK41 | HUTT41 | 2028 | Removed | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2771 | 2771
HARK41 | HUTT41 | 2028 | Addition | 81.544 | 0 | OHL | 0.127 | 1.5659 | 48.8916 | 2771 | 2771 | 2771 | 2771
HARK41 | HUTT41 | 2028 | Removed | 81.444 | 0 | OHL | 0.1269 | 1.564 | 48.8314 | 2771 | 2771 | 2663 | 2771
HARK41 | HUTT41 | 2028 | Addition | 81.544 | 0 | OHL | 0.127 | 1.5659 | 48.8916 | 2771 | 2771 | 2663 | 2771
HATL21 | HAWP21 | 2028 | Change | 31.443 | 0 | OHL | 0.1066 | 1.2811 | 8.9228 | 1093 | 1031 | 926 | 1031
HATL21 | TODP21 | 2028 | Change | 18.314 | 0 | OHL | 0.0678 | 0.7732 | 4.9952 | 1381 | 1279 | 1157 | 1279
HIGM41 | WBUR41 | 2028 | Change | 14.852 | 0.229 | Composite | 0.0247 | 0.2903 | 13.416 | 2212 | 2125 | 1979 | 2125
HINP41 | SAFO41 | 2028 | Change | 26.58 | 8.94 | Composite | 0.0421 | 0.5573 | 218.3267 | 2210 | 2130 | 1980 | 2130
HINP41 | SAFO42 | 2028 | Change | 26.571 | 8.99 | Composite | 0.0421 | 0.5575 | 219.45 | 2210 | 2130 | 1980 | 2130
IMPP41 | MELK41 | 2028 | Change | 78.775 | 3.913 | Composite | 0.0726 | 1.3961 | 131.2081 | 1424 | 1424 | 1424 | 1424
IRON41 | PENN4A | 2028 | Change | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9851 | 1389 | 1284 | 1108 | 1284
IRON41 | PENN4B | 2028 | Change | 24.617 | 0 | OHL | 0.0415 | 0.481 | 14.5223 | 1590 | 1500 | 1346 | 1500
IRON41 | RUGE41 | 2028 | Change | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9045 | 1389 | 1284 | 1108 | 1284
IVER41 | UXBM41 | 2028 | Addition | 0 | 0.2 | Cable | 0.0002 | 0.0023 | 1.9101 | 970 | 970 | 970 | 970
KEAR41 | PADI41 | 2028 | Change | 39.101 | 0 | OHL | 0.0567 | 0.7296 | 24.2055 | 2169 | 2084 | 1940 | 2084
KILA41 | SIZE41 | 2028 | Addition | 7.167 | 0 | OHL | 0.0078 | 0.1247 | 4.7246 | 2779 | 2568 | 2217 | 2568
KILA41 | SIZE41 | 2028 | Addition | 7.167 | 0 | OHL | 0.0078 | 0.1247 | 4.7246 | 2779 | 2568 | 2217 | 2568
KNAR21 | MONF22 | 2028 | Removed | 38.531 | 0.141 | Composite | 0.2749 | 1.7717 | 11.0381 | 551 | 513 | 443 | 513
KNAR21 | POPP21 | 2028 | Removed | 49.192 | 0 | OHL | 0.3266 | 2.325 | 12.2241 | 551 | 512 | 442 | 512
LAGA41 | LAND41 | 2028 | Change | 21.224 | 0 | OHL | 0.0339 | 0.4081 | 12.7626 | 2423 | 2327 | 2168 | 2327
LAGA41 | LAND42 | 2028 | Change | 21.355 | 0 | OHL | 0.0341 | 0.4108 | 12.8374 | 2423 | 2327 | 2168 | 2327
MACC41 | STAL41 | 2028 | Change | 31.196 | 0 | OHL | 0.057 | 0.6101 | 18.4203 | 1710 | 1627 | 1488 | 1627
MAGA21 | PORT21 | 2028 | Addition | 0 | 2 | Cable | 0.0088 | 0.0512 | 13.38 | 550 | 550 | 550 | 550
MAGA21 | PORT21 | 2028 | Addition | 0 | 2 | Cable | 0.0088 | 0.0512 | 13.38 | 550 | 550 | 550 | 550
MARH4A | STAY41 | 2028 | Change | 73.027 | 0 | OHL | 0.1233 | 1.427 | 43.0736 | 2514 | 2439 | 2314 | 2439
MELK41 | SEAB41 | 2028 | Change | 53.558 | 0 | OHL | 0.0507 | 0.9354 | 35.4701 | 2545 | 2421 | 2211 | 2421
MELK41 | WOOL41 | 2028 | Addition | 73.712 | 0 | OHL | 0.1142 | 1.4118 | 44.3162 | 3103 | 3048 | 2959 | 3048
MELK41 | WOOL41 | 2028 | Addition | 72.972 | 0 | OHL | 0.1132 | 1.3978 | 43.8649 | 3103 | 3048 | 2959 | 3048
MONF21 | POPP21 | 2028 | Removed | 37.84 | 0 | OHL | 0.208 | 2.0034 | 8.337 | 682 | 629 | 538 | 629
NEWX41 | WIMB41 | 2028 | Change | 0 | 12.445 | Cable | 0.0062 | 0.1668 | 153.2607 | 1100 | 1100 | 1100 | 1100
NORM41 | YAXT41 | 2028 | Addition | 30.062 | 0 | OHL | 0.0266 | 0.5163 | 20.2066 | 3326 | 3160 | 2971 | 3160
NORM41 | YAXT42 | 2028 | Addition | 30.062 | 0 | OHL | 0.0266 | 0.5163 | 20.2066 | 3326 | 3160 | 2971 | 3160
NORT22 | SALH21 | 2028 | Change | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1381 | 1293 | 1197 | 1293
NORT41 | OSBA41 | 2028 | Removed | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | OSBA42 | 2028 | Removed | 83.839 | 0 | OHL | 0.1132 | 1.593 | 51.0467 | 2009 | 1911 | 1746 | 1911
NORT41 | SALH42 | 2028 | Change | 12.206 | 0 | OHL | 0.022 | 0.2492 | 6.888 | 2009 | 1912 | 1746 | 1912
NORT41 | SHPT41 | 2028 | Addition | 70.453 | 0 | OHL | 0.0887 | 1.3257 | 43.3174 | 2550 | 2420 | 2210 | 2420
NORT41 | SHPT42 | 2028 | Addition | 70.453 | 0 | OHL | 0.0887 | 1.3257 | 43.3174 | 2550 | 2420 | 2210 | 2420
OCKH21 | OLDB22 | 2028 | Change | 5.46 | 0 | OHL | 0.0208 | 0.2294 | 1.4988 | 1416 | 1339 | 1258 | 1339
OSBA41 | SHPT41 | 2028 | Addition | 13.35 | 0 | OHL | 0.0208 | 0.2561 | 8.0113 | 3100 | 3050 | 2960 | 3050
OSBA42 | SHPT42 | 2028 | Addition | 13.35 | 0 | OHL | 0.0208 | 0.2561 | 8.0113 | 3100 | 3050 | 2960 | 3050
OVTO21 | POPP21 | 2028 | Addition | 4.794 | 0.2 | Composite | 0.0258 | 0.2405 | 3.2683 | 680 | 630 | 540 | 630
OVTO21 | POPP21 | 2028 | Addition | 4.677 | 0 | OHL | 0.0248 | 0.2311 | 1.1022 | 680 | 630 | 540 | 630
OVTO21 | TADT2A | 2028 | Addition | 20.523 | 0 | OHL | 0.1005 | 0.8717 | 5.5596 | 1500 | 1420 | 1300 | 1420
OVTO21 | TADT2B | 2028 | Addition | 20.523 | 0 | OHL | 0.1005 | 0.8717 | 5.5596 | 1500 | 1420 | 1300 | 1420
OVTO41 | SHPT41 | 2028 | Addition | 2.761 | 0.2 | Composite | 0.0051 | 0.0581 | 6.4744 | 1500 | 1420 | 1300 | 1420
OVTO42 | SHPT42 | 2028 | Addition | 2.761 | 0 | OHL | 0.005 | 0.0567 | 1.5484 | 1500 | 1420 | 1300 | 1420
PELH41 | RYEH4B | 2028 | Change | 23.439 | 0 | OHL | 0.0208 | 0.4026 | 15.7518 | 3326 | 3326 | 3320 | 3326
PELH41 | SUND42 | 2028 | Removed | 45.13 | 0 | OHL | 0.0487 | 0.7853 | 29.7565 | 3180 | 3000 | 2692 | 3000
PELH41 | WYMO41 | 2028 | Change | 26.856 | 0 | OHL | 0.0291 | 0.4667 | 17.7225 | 2771 | 2771 | 2692 | 2771
PELH42 | RYEH4A | 2028 | Change | 23.015 | 0 | OHL | 0.0204 | 0.3953 | 15.4679 | 3326 | 3326 | 3320 | 3326
PENT41 | TRAW41 | 2028 | Change | 45.1 | 6.308 | Composite | 0.0638 | 0.9671 | 131.0985 | 1769 | 1633 | 1401 | 1633
PERH11 | WYLF11 | 2028 | Addition | 17.554 | 5.4 | Composite | 0.4704 | 4.1792 | 10.2507 | 390 | 390 | 390 | 390
PERH1A | PERH11 | 2028 | Change | 1.592 | 3 | Composite | 0.0687 | 0.5867 | 5.2274 | 390 | 390 | 390 | 390
PURI4A | WOOL41 | 2028 | Addition | 3.292 | 0 | OHL | 0.0036 | 0.056 | 2.2041 | 3103 | 3048 | 2959 | 3048
PURI4B | WOOL41 | 2028 | Addition | 3.292 | 0 | OHL | 0.0036 | 0.056 | 2.2041 | 3103 | 3048 | 2959 | 3048
ROCH21 | STAL21 | 2028 | Change | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1324 | 1260 | 1151 | 1260
RYEH41 | RYEH4B | 2028 | Change | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0921 | 3326 | 3326 | 3320 | 3326
RYEH41 | WALX41 | 2028 | Change | 5.324 | 0 | OHL | 0.0047 | 0.0914 | 3.5785 | 3326 | 3326 | 3320 | 3326
RYEH4A | WALX41 | 2028 | Change | 5.461 | 0 | OHL | 0.0048 | 0.0938 | 3.6706 | 3326 | 3326 | 3320 | 3326
SAFO41 | SEAB41 | 2028 | Change | 31.28 | 0 | OHL | 0.0345 | 0.5479 | 20.4859 | 3028 | 2909 | 2712 | 2909
SAFO42 | SEAB41 | 2028 | Change | 31.242 | 0 | OHL | 0.0344 | 0.5471 | 20.4646 | 3028 | 2909 | 2712 | 2909
SEAB41 | WHSO4A | 2028 | Change | 30.426 | 3.89 | Composite | 0.0329 | 0.5809 | 97.722 | 1424 | 1424 | 1424 | 1424
SSHI21 | SSHI21 | 2028 | Addition | 0 | 0 | Series Compensation | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
SSHI21 | SSHI21 | 2028 | Addition | 0 | 0 | Series Compensation | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
SSHI21 | WBOL21 | 2028 | Addition | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1131 | 1052 | 912 | 1052
SUND41 | WYMO41 | 2028 | Change | 18.156 | 0 | OHL | 0.0197 | 0.3152 | 11.9934 | 3048 | 3000 | 2692 | 3000
SUND42 | WYMO42 | 2028 | Addition | 17.986 | 0 | OHL | 0.0195 | 0.3128 | 11.8561 | 3180 | 3000 | 2692 | 3000
TILB21 | WARL21 | 2028 | Change | 13.065 | 0 | OHL | 0.043 | 0.5303 | 3.7055 | 2130 | 2100 | 2030 | 2100
TILB21 | WARL21 | 2028 | Change | 12.897 | 0 | OHL | 0.0425 | 0.5235 | 3.658 | 2130 | 2100 | 2030 | 2100
TILB41 | WAEN41 | 2028 | Addition | 24.818 | 1.805 | Composite | 0.0282 | 0.4515 | 52.4628 | 2003 | 2003 | 1939 | 2003
TRAW41 | TREU4A | 2028 | Removed | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TRAW41 | TREU4B | 2028 | Removed | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5731 | 3102 | 3048 | 2958 | 3048
TYNE21 | SSHI21 | 2028 | Addition | 6.863 | 0 | OHL | 0.0303 | 0.2915 | 1.8625 | 1131 | 1052 | 912 | 1052
TYNE21 | WBOL21 | 2028 | Removed | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1131 | 1052 | 912 | 1052
WANB41 | WANB42 | 2028 | Addition | 0 | 0 | Series Reactor | 0.0014 | 1 | 0 | 2750 | 2750 | 2750 | 2750
YAXL41 | YAXT41 | 2028 | Addition | 0 | 0.3 | Cable | 0.0001 | 0.002 | 7.389 | 3326 | 3160 | 2971 | 3160
YAXL41 | YAXT42 | 2028 | Addition | 0.1 | 0 | OHL | 0.0001 | 0.0017 | 0.067 | 3326 | 3160 | 2971 | 3160
ALVE41 | INDQ41 | 2030 | Removed | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284
ALVE41 | INDQ41 | 2030 | Addition | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284
ALVE41 | INDQ41 | 2030 | Addition | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.2092 | 1389 | 1284 | 1108 | 1284
ALVE41 | TAUN41 | 2030 | Removed | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284
ALVE41 | TAUN41 | 2030 | Addition | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284
ALVE41 | TAUN42 | 2030 | Addition | 73.437 | 0 | OHL | 0.1172 | 1.4799 | 42.117 | 1389 | 1284 | 1108 | 1284
ALVE42 | INDQ41 | 2030 | Removed | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.209 | 1389 | 1284 | 1108 | 1284
ALVE42 | TAUN42 | 2030 | Removed | 73.298 | 0 | OHL | 0.117 | 1.4771 | 42.0372 | 1389 | 1284 | 1108 | 1284
AMEM41 | ECLA41 | 2030 | Change | 35.315 | 0 | OHL | 0.055 | 0.6776 | 21.1925 | 3100 | 3050 | 2960 | 3050
AMEM41 | IVER41 | 2030 | Removed | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 1852 | 1741 | 1624 | 1741
AMEM41 | UXBM41 | 2030 | Addition | 20.056 | 0 | OHL | 0.0313 | 0.3848 | 12.0356 | 3100 | 3050 | 2960 | 3050
AMEM42 | ECLA41 | 2030 | Change | 35.315 | 0 | OHL | 0.055 | 0.6776 | 21.1925 | 3100 | 3050 | 2960 | 3050
AMEM42 | IVER42 | 2030 | Removed | 20.256 | 0 | OHL | 0.0368 | 0.403 | 11.7392 | 2032 | 1933 | 1766 | 1933
AMEM42 | UXBM41 | 2030 | Addition | 20.056 | 0 | OHL | 0.0313 | 0.3848 | 12.0356 | 3100 | 3050 | 2960 | 3050
AXMI41 | EXET41 | 2030 | Change | 36.184 | 0 | OHL | 0.0404 | 0.6915 | 21.9115 | 3090 | 2960 | 2740 | 2960
BESW21 | FECK21 | 2030 | Change | 35.814 | 0 | OHL | 0.135 | 1.4909 | 9.9087 | 955 | 882 | 762 | 882
BESW21 | OCKH21 | 2030 | Change | 56.939 | 0.731 | Composite | 0.225 | 2.4038 | 22.9039 | 819 | 819 | 638 | 638
BICF41 | SPLN41 | 2030 | Removed | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3156 | 3032 | 2823 | 3032
BICF41 | WALP41 | 2030 | Removed | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3189 | 3063 | 2853 | 3063
BICF41 | WMAA41 | 2030 | Addition | 13.995 | 0 | OHL | 0.0124 | 0.2404 | 9.4066 | 3326 | 3326 | 3326 | 3326
BICF41 | WMAA42 | 2030 | Addition | 13.995 | 0 | OHL | 0.0124 | 0.2404 | 9.4066 | 3326 | 3326 | 3326 | 3326
BIRW41 | CREB42 | 2030 | Addition | 0.7 | 0 | OHL | 0.0006 | 0.012 | 0.4705 | 3326 | 3326 | 3320 | 3326
BIRW41 | THTO42 | 2030 | Addition | 28.971 | 0 | OHL | 0.0257 | 0.4976 | 19.4733 | 3326 | 3326 | 3320 | 3326
BIRW42 | THTO41 | 2030 | Addition | 28.971 | 0 | OHL | 0.0257 | 0.4976 | 19.4733 | 3326 | 3326 | 3320 | 3326
BIRW42 | WANB41 | 2030 | Addition | 0.7 | 0 | OHL | 0.0006 | 0.012 | 0.4705 | 3326 | 3326 | 3320 | 3326
BODE41 | CONQ41 | 2030 | Addition | 30.717 | 0.21 | Composite | 0.0273 | 0.5289 | 25.8244 | 2830 | 2770 | 2680 | 2770
BODE41 | CONQ42 | 2030 | Addition | 30.717 | 0.21 | Composite | 0.0273 | 0.5289 | 25.8244 | 2830 | 2770 | 2680 | 2770
BODE41 | GWYN4A | 2030 | Removed | 0 | 0.8 | Cable | 0.0008 | 0.0094 | 7.6404 | 1056 | 1056 | 980 | 980
BODE41 | GWYN4B | 2030 | Removed | 0.5 | 0 | OHL | 0.0005 | 0.0087 | 0.3284 | 2771 | 2695 | 2510 | 2695
BODE41 | PENT41 | 2030 | Addition | 50.011 | 0 | OHL | 0.0443 | 0.8588 | 33.624 | 3326 | 3326 | 3320 | 3326
BODE41 | PENT41 | 2030 | Addition | 50.011 | 0 | OHL | 0.0443 | 0.8588 | 33.624 | 3326 | 3326 | 3320 | 3326
BRAI4A | BRFO41 | 2030 | Change | 40 | 9 | Composite | 0.0376 | 0.7249 | 366.1773 | 3326 | 3326 | 3320 | 3326
BRAI4B | BRFO43 | 2030 | Addition | 40.091 | 9 | Composite | 0.0377 | 0.7265 | 366.2382 | 3326 | 3326 | 3320 | 3326
BRAI4B | PELH42 | 2030 | Removed | 65.942 | 0 | OHL | 0.0585 | 1.1326 | 44.3214 | 3326 | 3326 | 3320 | 3326
BRFO41 | PELH41 | 2030 | Removed | 69.301 | 0 | OHL | 0.0614 | 1.1903 | 46.5796 | 3102 | 2935 | 2765 | 2935
BRFO41 | TWIN4A | 2030 | Addition | 28.419 | 0 | OHL | 0.0252 | 0.4881 | 19.1016 | 3326 | 3326 | 3317 | 3326
BRFO43 | TWIN4B | 2030 | Addition | 28.419 | 0 | OHL | 0.0252 | 0.4881 | 19.1016 | 3326 | 3326 | 3317 | 3326
BRIN21 | CHTE21 | 2030 | Removed | 22.464 | 0.22 | Composite | 0.0519 | 0.8305 | 9.3505 | 934 | 934 | 753 | 753
BRIN22 | CHTE21 | 2030 | Removed | 22.375 | 0 | OHL | 0.0513 | 0.8236 | 6.9689 | 1204 | 1115 | 1018 | 1115
BRIN41 | LONL41 | 2030 | Addition | 1.2 | 0 | OHL | 0.0013 | 0.0209 | 0.7911 | 2518 | 2395 | 2188 | 2395
BRIN41 | LONL41 | 2030 | Addition | 1.2 | 0 | OHL | 0.0013 | 0.0209 | 0.7911 | 2545 | 2421 | 2211 | 2421
BRIN41 | THOM41 | 2030 | Removed | 36.285 | 0 | OHL | 0.0394 | 0.6315 | 23.9068 | 2518 | 2395 | 2188 | 2395
BRIN41 | THOM42 | 2030 | Removed | 36.302 | 0 | OHL | 0.0394 | 0.6318 | 23.9168 | 2545 | 2421 | 2211 | 2421
BRYN42 | PENI4A | 2030 | Addition | 23.025 | 0 | OHL | 0.0275 | 0.4072 | 15.1794 | 2777 | 2667 | 2484 | 2667
BRYN42 | TRAW41 | 2030 | Addition | 14.06 | 9.443 | Composite | 0.0207 | 0.3041 | 241.8511 | 2777 | 2473 | 2189 | 2189
CHIC41 | EXET41 | 2030 | Change | 67.12 | 8.518 | Composite | 0.077 | 1.2834 | 256.385 | 2779 | 2568 | 2217 | 2568
CHTE21 | HIGM21 | 2030 | Removed | 43.651 | 0 | OHL | 0.1214 | 1.8002 | 12.2369 | 1381 | 1381 | 1375 | 1381
CHTE21 | HIGM21 | 2030 | Removed | 43.792 | 0 | OHL | 0.1218 | 1.806 | 12.2763 | 1381 | 1339 | 1258 | 1339
CHTE41 | HIGB41 | 2030 | Addition | 43.651 | 0 | OHL | 0.0574 | 0.8509 | 25.8889 | 2780 | 2670 | 2480 | 2670
CHTE41 | HIGB42 | 2030 | Addition | 43.792 | 0 | OHL | 0.0576 | 0.8537 | 25.9723 | 2780 | 2670 | 2480 | 2670
CHTE41 | LONL41 | 2030 | Addition | 20.775 | 0 | OHL | 0.0225 | 0.3613 | 13.6946 | 2780 | 2570 | 2220 | 2570
CHTE41 | LONL41 | 2030 | Addition | 20.864 | 0 | OHL | 0.0226 | 0.3629 | 13.753 | 2780 | 2570 | 2220 | 2570
CHUE4A | TILB41 | 2030 | Removed | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2827 | 2827 | 2591 | 2591
CHUE4A | TILN41 | 2030 | Addition | 9.295 | 0 | OHL | 0.0145 | 0.179 | 5.554 | 2827 | 2827 | 2591 | 2591
CHUE4B | TILB41 | 2030 | Removed | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2924 | 2924 | 2591 | 2591
CHUE4B | TILN41 | 2030 | Addition | 9.295 | 0 | OHL | 0.0145 | 0.179 | 5.554 | 2924 | 2924 | 2591 | 2591
CONQ41 | GWYN4B | 2030 | Removed | 30.217 | 0.21 | Composite | 0.0268 | 0.5204 | 25.4825 | 2830 | 2770 | 2680 | 2770
CONQ41 | TREU4B | 2030 | Change | 14.323 | 0 | OHL | 0.0223 | 0.2748 | 8.5952 | 3100 | 3050 | 2960 | 3050
CONQ42 | GWYN4A | 2030 | Removed | 30.217 | 0.21 | Composite | 0.0268 | 0.5204 | 25.4825 | 2830 | 2770 | 2680 | 2770
CONQ42 | TREU4A | 2030 | Change | 14.323 | 0 | OHL | 0.0223 | 0.2748 | 8.5952 | 3100 | 3050 | 2960 | 3050
COTT41 | HIGB42 | 2030 | Addition | 8.291 | 0.25 | Composite | 0.0137 | 0.1608 | 14.1976 | 3100 | 3050 | 2960 | 3050
COTT41 | MARH4B | 2030 | Change | 100.853 | 0 | OHL | 0.1677 | 1.9593 | 59.8778 | 2210 | 2130 | 1980 | 2130
COTT41 | STAY41 | 2030 | Removed | 27.788 | 0.5 | Composite | 0.0504 | 0.5522 | 21.6211 | 2213 | 2126 | 1980 | 2052
COWL41 | ECLA41 | 2030 | Removed | 36.086 | 0 | OHL | 0.032 | 0.6198 | 24.255 | 3326 | 3326 | 3320 | 3326
COWL41 | LEIB4A | 2030 | Removed | 52.28 | 0 | OHL | 0.0462 | 0.8979 | 35.1591 | 3326 | 3326 | 3320 | 3326
COWL41 | QNTN41 | 2030 | Addition | 30.495 | 0.18 | Composite | 0.0271 | 0.525 | 24.9304 | 3326 | 3326 | 3320 | 3326
COWL41 | QNTN42 | 2030 | Addition | 30.495 | 0 | OHL | 0.027 | 0.5238 | 20.497 | 3326 | 3326 | 3320 | 3326
CREB42 | THTO42 | 2030 | Removed | 29.671 | 0 | OHL | 0.0263 | 0.5096 | 19.9438 | 3326 | 3326 | 3320 | 3326
DINO41 | PENI4A | 2030 | Addition | 0 | 6.183 | Cable | 0.005 | 0.0727 | 76.1439 | 1830 | 1623 | 1623 | 1623
DINO41 | PENT41 | 2030 | Removed | 4.545 | 7.305 | Composite | 0.0093 | 0.1892 | 94.6439 | 1623 | 1623 | 1571 | 1571
DRAK41 | HAMH41 | 2030 | Change | 29.434 | 0 | OHL | 0.0495 | 0.5747 | 17.3788 | 3100 | 3050 | 2960 | 3050
DRAK41 | OLDB4A | 2030 | Change | 48.818 | 0.5 | Composite | 0.0896 | 0.9723 | 36.7331 | 1169 | 1169 | 1068 | 1068
DRAX41 | EGGB41 | 2030 | Change | 11.188 | 0.64 | Composite | 0.0114 | 0.1998 | 23.1481 | 2691 | 2691 | 2394 | 2394
DRAX41 | FENW4A | 2030 | Change | 13.443 | 0 | OHL | 0.0119 | 0.2309 | 9.0356 | 3326 | 3160 | 2970 | 3160
DRAX42 | EGGB42 | 2030 | Change | 11.188 | 0 | OHL | 0.0112 | 0.1951 | 7.3991 | 3326 | 3326 | 3320 | 3326
DRAX42 | THOM42 | 2030 | Change | 21.73 | 0 | OHL | 0.0259 | 0.3925 | 13.9349 | 3100 | 3050 | 2960 | 3050
DRAX42 | WREH41 | 2030 | Addition | 0 | 0.5 | Cable | 0.0003 | 0.0045 | 6.1575 | 2120 | 1060 | 1060 | 1060
DRAX42 | WREH42 | 2030 | Addition | 0 | 0.5 | Cable | 0.0003 | 0.0045 | 6.1575 | 2120 | 1060 | 1060 | 1060
ECLA41 | LEIB4B | 2030 | Change | 15.985 | 0 | OHL | 0.0142 | 0.2746 | 10.7442 | 3326 | 3160 | 2971 | 3160
ECLA41 | PAFB4A | 2030 | Change | 44.72 | 0 | OHL | 0.0697 | 0.858 | 26.8364 | 3100 | 3050 | 2960 | 3050
ECLA41 | PAFB4B | 2030 | Change | 44.886 | 0 | OHL | 0.0699 | 0.8612 | 26.9357 | 3100 | 3050 | 2960 | 3050
ECLA41 | QNTN41 | 2030 | Addition | 5.591 | 0.18 | Composite | 0.005 | 0.0972 | 8.1914 | 3326 | 3326 | 3320 | 3326
ELST41 | ELST4B | 2030 | Addition | 0 | 0.1 | Cable | 0 | 0 | 0 | 3100 | 3050 | 2960 | 3050
ELST41 | ELST41 | 2030 | Change | 0 | 0 | Series Reactor | 0.0033 | 0.913 | 0 | 2000 | 2000 | 2000 | 2000
ELST41 | ELST41 | 2030 | Addition | 0 | 0 | Series Reactor | 0.0033 | 0.913 | 0 | 2000 | 2000 | 2000 | 2000
ELST41 | LECH41 | 2030 | Addition | 0 | 0.13 | Cable | 0.0001 | 0.0017 | 1.601 | 1767 | 1732 | 1663 | 1732
ELST41 | LECH42 | 2030 | Addition | 0 | 0.2 | Cable | 0.0001 | 0.0027 | 2.463 | 1767 | 1732 | 1663 | 1732
ELST41 | LECH43 | 2030 | Addition | 0 | 0.18 | Cable | 0.0001 | 0.0024 | 2.2167 | 1767 | 1732 | 1663 | 1732
ELST41 | LECH44 | 2030 | Addition | 0 | 0.14 | Cable | 0.0001 | 0.0019 | 1.7241 | 1767 | 1732 | 1663 | 1732
ELST41 | SJOW41 | 2030 | Addition | 0 | 20 | Cable | 0.0136 | 0.2525 | 246.3008 | 1767 | 1732 | 1100 | 1732
ELST41 | SJOW41 | 2030 | Change | 0 | 20 | Cable | 0.0141 | 0.2451 | 244.29 | 1767 | 1732 | 1663 | 1732
ELST41 | SUND41 | 2030 | Change | 34.834 | 0 | OHL | 0.0543 | 0.6683 | 20.9031 | 3102 | 3048 | 2958 | 3048
ELST41 | SUND42 | 2030 | Change | 34.706 | 0 | OHL | 0.0541 | 0.6659 | 20.8265 | 3100 | 3050 | 2960 | 3050
ENDE41 | PAFB4A | 2030 | Change | 41.13 | 0 | OHL | 0.0616 | 0.7797 | 24.9939 | 3100 | 3050 | 2960 | 3050
ENDE41 | PAFB4B | 2030 | Change | 41.13 | 0 | OHL | 0.0616 | 0.7797 | 24.9939 | 3100 | 3050 | 2960 | 3050
FECK41 | HAMH41 | 2030 | Change | 43.314 | 0 | OHL | 0.0724 | 0.8482 | 25.4947 | 3100 | 3050 | 2960 | 3050
FECK41 | MITY41 | 2030 | Change | 72.186 | 7.5 | Composite | 0.1189 | 1.4401 | 225.4124 | 2830 | 2770 | 2680 | 2770
FECK41 | WALH41 | 2030 | Change | 61.523 | 7.5 | Composite | 0.1009 | 1.2318 | 219.122 | 3100 | 3050 | 2960 | 3050
FENW4A | THOM41 | 2030 | Change | 8.287 | 0 | OHL | 0.014 | 0.1616 | 4.8993 | 2009 | 1911 | 1746 | 1911
GRAI41 | WAEN41 | 2030 | Change | 1.948 | 0 | OHL | 0.0017 | 0.0334 | 1.3118 | 3326 | 3326 | 3320 | 3326
GRAI41 | WAEN41 | 2030 | Change | 1.948 | 0 | OHL | 0.0017 | 0.0334 | 1.3118 | 3326 | 3326 | 3320 | 3326
GREN41 | MARH4B | 2030 | Change | 28.56 | 0 | OHL | 0.0482 | 0.5581 | 16.8451 | 2210 | 2130 | 1980 | 2130
GWYN4A | PENT41 | 2030 | Removed | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
GWYN4B | PENT41 | 2030 | Removed | 49.211 | 0 | OHL | 0.0645 | 0.9572 | 29.2535 | 2779 | 2568 | 2217 | 2568
HAKB4- | HARK41 | 2030 | Change | 10.107 | 0 | OHL | 0.0175 | 0.1997 | 5.8779 | 3180 | 3130 | 3050 | 3130
HAKB4B | HARK41 | 2030 | Change | 10.107 | 0 | OHL | 0.0175 | 0.1997 | 5.8779 | 3180 | 3130 | 3050 | 3130
HARK21 | HARK22 | 2030 | Removed | 0 | 0 | Series Reactor | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
HARK21 | HARK22 | 2030 | Removed | 0 | 0 | Series Capacitor | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
HARK22 | HARK23 | 2030 | Removed | 0 | 0 | Series Capacitor | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
HARK22 | HARK23 | 2030 | Removed | 0 | 0 | Series Reactor | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
HAWP21 | HAWP22 | 2030 | Removed | 0 | 0.256 | Cable | 0.0005 | 0.0057 | 2.7392 | 908 | 874 | 720 | 801
HAWP21 | OFFE21 | 2030 | Addition | 9.514 | 0.08 | Composite | 0.0443 | 0.4049 | 3.0467 | 1180 | 1120 | 1020 | 1120
HAWP22 | NORT21 | 2030 | Removed | 27.949 | 0.203 | Composite | 0.0668 | 1.0519 | 10.749 | 1381 | 1381 | 1285 | 1381
HAWP22 | OFFE21 | 2030 | Removed | 9.514 | 0 | OHL | 0.0435 | 0.4027 | 2.5811 | 1176 | 1119 | 1024 | 1119
HAWP41 | MURT41 | 2030 | Addition | 0 | 1 | Cable | 0.0005 | 0.009 | 12.315 | 2120 | 1060 | 1060 | 1060
HAWP41 | MURT42 | 2030 | Addition | 0 | 1 | Cable | 0.0005 | 0.009 | 12.315 | 2120 | 1060 | 1060 | 1060
HAWP41 | NORT41 | 2030 | Addition | 27.393 | 0 | OHL | 0.0243 | 0.4692 | 18.4688 | 3326 | 3326 | 3320 | 3326
HAWP41 | NORT41 | 2030 | Addition | 27.393 | 0 | OHL | 0.0243 | 0.4692 | 18.4688 | 3326 | 3326 | 3320 | 3326
HAWP4A | NORT41 | 2030 | Removed | 27.868 | 0 | OHL | 0.0313 | 0.4936 | 18.0929 | 2545 | 2421 | 2211 | 2421
HEYS41 | MIDL41 | 2030 | Addition | 0.4 | 0 | OHL | 0.0004 | 0.0069 | 0.2689 | 3326 | 3326 | 3326 | 3326
HEYS41 | QUER4B | 2030 | Removed | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3299 | 3098 | 3299
HIGB41 | STOB41 | 2030 | Addition | 40.547 | 0 | OHL | 0.0656 | 0.7839 | 24.1636 | 3100 | 3050 | 2960 | 3050
HIGB41 | WBUR41 | 2030 | Addition | 14.852 | 0.229 | Composite | 0.0236 | 0.2867 | 17.3644 | 3100 | 3050 | 2960 | 3050
HIGB42 | STAY41 | 2030 | Addition | 21.563 | 0 | OHL | 0.0336 | 0.4137 | 12.9394 | 3100 | 3050 | 2960 | 3050
HIGM21 | THUR2A | 2030 | Removed | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591
HIGM41 | STOB41 | 2030 | Removed | 40.547 | 0 | OHL | 0.0738 | 0.8067 | 23.4963 | 2147 | 2056 | 1904 | 2056
HIGM41 | WBUR41 | 2030 | Removed | 14.852 | 0.229 | Composite | 0.0247 | 0.2903 | 13.416 | 2212 | 2125 | 1979 | 2125
HIMB21 | THUR2A | 2030 | Addition | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591
ICKE21 | IVER22 | 2030 | Addition | 5.055 | 0 | OHL | 0.0218 | 0.2154 | 1.3644 | 1330 | 1330 | 1210 | 1330
ICKE21 | WATS21 | 2030 | Addition | 8.967 | 0.483 | Composite | 0.0411 | 0.3931 | 7.6839 | 1330 | 1330 | 1210 | 1330
ICKE2A | ICKE21 | 2030 | Addition | 0 | 0.1 | Cable | 0.0005 | 0.0014 | 1.1642 | 1400 | 1400 | 1400 | 1400
ICKE2A | IVER22 | 2030 | Addition | 5.055 | 0 | OHL | 0.0218 | 0.2154 | 1.3644 | 1400 | 1400 | 1400 | 1400
ICKE2A | WATS22 | 2030 | Addition | 8.967 | 0.436 | Composite | 0.041 | 0.3918 | 7.173 | 1400 | 1400 | 1400 | 1400
IVER22 | WATS21 | 2030 | Removed | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 776 | 776 | 631 | 631
IVER22 | WATS22 | 2030 | Removed | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 776 | 776 | 631 | 631
IVER41 | UXBM41 | 2030 | Change | 0.2 | 0 | OHL | 0.0003 | 0.0038 | 0.12 | 3100 | 3050 | 2960 | 3050
IVER42 | UXBM41 | 2030 | Addition | 0.2 | 0 | OHL | 0.0003 | 0.0038 | 0.12 | 3100 | 3050 | 2960 | 3050
KINO41 | TILB41 | 2030 | Change | 15.478 | 1.805 | Composite | 0.014 | 0.2778 | 54.8801 | 3326 | 2926 | 2560 | 2926
KINO41 | WAEN41 | 2030 | Change | 9.683 | 0.8 | parallel Composite | 0.0085 | 0.1671 | 36.076 | 3326 | 3160 | 2633 | 2813
LACK41 | SALH41 | 2030 | Change | 10.108 | 0.25 | Composite | 0.0158 | 0.1987 | 12.248 | 3100 | 3050 | 2960 | 3050
LEGA41 | TREU4A | 2030 | Change | 12.119 | 0 | OHL | 0.0107 | 0.2082 | 8.1457 | 3326 | 3326 | 3320 | 3326
LEGA41 | TREU4B | 2030 | Change | 12.119 | 0 | OHL | 0.0107 | 0.2082 | 8.1457 | 3326 | 3326 | 3320 | 3326
LEIB4A | QNTN42 | 2030 | Addition | 21.785 | 0 | OHL | 0.0193 | 0.3742 | 14.6421 | 3326 | 3326 | 3320 | 3326
LONL41 | THOM41 | 2030 | Addition | 35.102 | 0 | OHL | 0.0381 | 0.611 | 23.1258 | 2545 | 2421 | 2211 | 2421
LONL41 | THOM42 | 2030 | Addition | 35.085 | 0 | OHL | 0.0381 | 0.6106 | 23.1157 | 2518 | 2395 | 2188 | 2395
MIDL41 | QUER4B | 2030 | Addition | 9.204 | 0 | OHL | 0.0082 | 0.1581 | 6.1864 | 3326 | 3326 | 3326 | 3326
NECT41 | WALP42 | 2030 | Change | 43.23 | 0.45 | Composite | 0.0384 | 0.7445 | 45.6824 | 3326 | 3160 | 2971 | 3160
NEWX41 | WIMB41 | 2030 | Removed | 0 | 12.445 | Cable | 0.0062 | 0.1668 | 153.2607 | 1100 | 1100 | 1100 | 1100
NORT21 | SALH21 | 2030 | Change | 12.178 | 0 | OHL | 0.0431 | 0.5178 | 3.2966 | 1381 | 1293 | 1197 | 1293
NORT41 | SALH42 | 2030 | Change | 12.206 | 0 | OHL | 0.0204 | 0.2452 | 6.9937 | 3100 | 3050 | 2960 | 3050
NORT41 | SPEN41 | 2030 | Change | 21.134 | 0 | OHL | 0.0276 | 0.4062 | 12.7287 | 2780 | 2670 | 2480 | 2670
NORT41 | SPEN42 | 2030 | Change | 21.134 | 0 | OHL | 0.0276 | 0.4062 | 12.7287 | 2780 | 2670 | 2480 | 2670
PELH41 | TWIN4A | 2030 | Addition | 40.882 | 0 | OHL | 0.0362 | 0.7022 | 27.478 | 3326 | 3326 | 3317 | 3326
PELH42 | TWIN4B | 2030 | Addition | 40.823 | 0 | OHL | 0.0362 | 0.7012 | 27.4385 | 3326 | 3326 | 3317 | 3326
PENI4A | PENT41 | 2030 | Addition | 4.545 | 0 | OHL | 0.0054 | 0.0804 | 2.9963 | 2777 | 2667 | 2484 | 2667
PENT41 | TRAW41 | 2030 | Change | 41.63 | 9.608 | Composite | 0.0537 | 0.7926 | 264.0908 | 2777 | 2473 | 2189 | 2189
RATS41 | STAY41 | 2030 | Change | 43.662 | 0 | OHL | 0.0738 | 0.8516 | 25.8092 | 2147 | 2057 | 1905 | 2057
RATS41 | STOB41 | 2030 | Change | 24.492 | 0.179 | Composite | 0.0414 | 0.4784 | 21.0929 | 3100 | 3050 | 2960 | 3050
SPEN41 | STEW41 | 2030 | Change | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2780 | 2670 | 2480 | 2670
SPEN42 | STEW41 | 2030 | Change | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2780 | 2670 | 2480 | 2670
SPLN41 | WALP41 | 2030 | Removed | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3189 | 3063 | 2853 | 3063
SPLN41 | WMAA41 | 2030 | Addition | 6.02 | 0 | OHL | 0.0067 | 0.1134 | 3.7023 | 3156 | 3156 | 3156 | 3156
SPLN41 | WMAA41 | 2030 | Addition | 6.02 | 0 | OHL | 0.0067 | 0.1134 | 3.7023 | 3156 | 3156 | 3156 | 3156
THTO41 | WANB41 | 2030 | Removed | 29.809 | 0 | OHL | 0.0264 | 0.512 | 20.0362 | 3326 | 3326 | 3320 | 3326
TILB21 | WARL21 | 2030 | Change | 12.865 | 0.2 | Composite | 0.0558 | 0.5433 | 4.7032 | 1175 | 1119 | 1023 | 1119
TILB21 | WARL21 | 2030 | Change | 12.697 | 0.2 | Composite | 0.0553 | 0.5365 | 4.6556 | 1175 | 1119 | 1023 | 1119
TILB41 | TILB41 | 2030 | Addition | 0 | 0 | Series Reactor | 0.0003 | 0.5 | 0 | 2000 | 2000 | 2000 | 2000
TILB41 | TILB41 | 2030 | Addition | 0 | 0 | Series Reactor | 0.0003 | 0.5 | 0 | 2000 | 2000 | 2000 | 2000
TILB41 | TILN41 | 2030 | Addition | 3.75 | 1 | Composite | 0.0062 | 0.0795 | 24.81 | 2827 | 2827 | 2591 | 2591
TILB42 | TILB42 | 2030 | Addition | 0 | 0 | Series Reactor | 0.0003 | 0.5 | 0 | 2000 | 2000 | 2000 | 2000
TILB42 | TILN41 | 2030 | Addition | 3.75 | 0.68 | Composite | 0.0061 | 0.0772 | 17.5878 | 2924 | 2924 | 2591 | 2591
TILB42 | WAEN41 | 2030 | Change | 24.818 | 1.805 | Composite | 0.0222 | 0.4382 | 61.1702 | 3326 | 2926 | 2560 | 2926
TWIN41 | TWIN4A | 2030 | Addition | 0 | 0.2 | Cable | 0.0001 | 0.0027 | 2.463 | 278 | 278 | 278 | 278
TWIN42 | TWIN4B | 2030 | Addition | 0.1 | 0 | OHL | 0.0001 | 0.0019 | 0.0591 | 278 | 278 | 278 | 278
BAYB41 | COTT41 | 2033 | Addition | 99.853 | 0 | OHL | 0.166 | 1.9398 | 59.288 | 2210 | 2130 | 1980 | 2130
BAYB41 | MARH4A | 2033 | Addition | 38 | 0 | OHL | 0.0592 | 0.7291 | 22.8037 | 3100 | 3100 | 3100 | 3100
BAYB41 | MARH4B | 2033 | Addition | 38 | 0 | OHL | 0.0592 | 0.7291 | 22.8037 | 3100 | 3050 | 2960 | 3050
BAYB41 | NERY41 | 2033 | Addition | 27 | 3 | Composite | 0.0247 | 0.4838 | 92.0381 | 3326 | 3326 | 3320 | 3326
BAYB41 | NERY42 | 2033 | Addition | 27 | 3 | Composite | 0.0247 | 0.4838 | 92.0381 | 3326 | 3326 | 3320 | 3326
BAYB41 | STAY41 | 2033 | Addition | 72.027 | 0 | OHL | 0.1216 | 1.4075 | 42.4838 | 3100 | 3100 | 3100 | 3100
BIRW41 | HIGB41 | 2033 | Addition | 90 | 0 | OHL | 0.0798 | 1.5458 | 60.4929 | 3326 | 3326 | 3320 | 3326
BIRW42 | HIGB42 | 2033 | Addition | 90 | 0 | OHL | 0.0798 | 1.5458 | 60.4929 | 3326 | 3326 | 3320 | 3326
BLNE41 | STWT41 | 2033 | Addition | 26.711 | 0 | OHL | 0.0237 | 0.4588 | 17.9521 | 3326 | 3326 | 3320 | 3326
BLNE41 | STWT42 | 2033 | Addition | 26.779 | 0 | OHL | 0.0237 | 0.46 | 17.9977 | 3326 | 3326 | 3320 | 3326
BLYT21 | STEW21 | 2033 | Removed | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 682 | 629 | 538 | 629
BLYT21 | STEW21 | 2033 | Removed | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 682 | 629 | 538 | 629
BRFO42 | EACS41 | 2033 | Addition | 8.9 | 16 | Composite | 0.0118 | 0.2203 | 609.1693 | 3326 | 2850 | 2700 | 2850
BRFO42 | NORM41 | 2033 | Addition | 68.7 | 0 | OHL | 0.0609 | 1.18 | 46.1762 | 3326 | 2850 | 2700 | 2850
BRFO44 | EACS41 | 2033 | Addition | 8.9 | 15.5 | Composite | 0.0116 | 0.2182 | 590.3197 | 3326 | 2850 | 2700 | 2850
BRFO44 | NORM41 | 2033 | Addition | 68.7 | 0 | OHL | 0.0609 | 1.18 | 46.1762 | 3326 | 2850 | 2700 | 2850
BURW41 | PELH42 | 2033 | Change | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3326 | 3140 | 2769 | 3140
BURW41 | WALB41 | 2033 | Addition | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3326 | 3160 | 2971 | 3160
BURW41 | WALB42 | 2033 | Addition | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3326 | 3160 | 2971 | 3160
BURW41 | WALP41 | 2033 | Removed | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3326 | 3160 | 2971 | 3160
BURW41 | WALP42 | 2033 | Removed | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3326 | 3160 | 2971 | 3160
CANT41 | MINS41 | 2033 | Addition | 19.386 | 0 | OHL | 0.0302 | 0.3833 | 11.2842 | 3100 | 3050 | 2960 | 3050
CANT41 | MINS41 | 2033 | Addition | 19.386 | 0 | OHL | 0.0302 | 0.3833 | 11.2842 | 3100 | 3050 | 2960 | 3050
CANT41 | RICH41 | 2033 | Removed | 20.72 | 0 | OHL | 0.033 | 0.4092 | 12.1374 | 2038 | 2038 | 1801 | 1801
CANT41 | RICH41 | 2033 | Removed | 20.72 | 0 | OHL | 0.033 | 0.4092 | 12.1374 | 2038 | 2038 | 1801 | 1801
CARR41 | KEAR41 | 2033 | Change | 13.154 | 0 | OHL | 0.0207 | 0.265 | 7.5449 | 2212 | 2125 | 1979 | 2125
CARR41 | PEWO41 | 2033 | Change | 56.9 | 0 | OHL | 0.0837 | 1.1325 | 33.0539 | 2810 | 2810 | 2810 | 2810
CELL41 | DRAK41 | 2033 | Change | 45.012 | 0 | OHL | 0.0701 | 0.8636 | 27.0114 | 3100 | 3050 | 2960 | 3050
CELL41 | DRAK41 | 2033 | Change | 45.704 | 0 | OHL | 0.0712 | 0.8769 | 27.4254 | 3100 | 3050 | 2960 | 3050
CHIL41 | LOVE41 | 2033 | Change | 22.379 | 0.315 | Composite | 0.0199 | 0.3865 | 22.7998 | 3326 | 3326 | 3320 | 3326
CHTE41 | WILE41 | 2033 | Addition | 64 | 0 | OHL | 0.0567 | 1.0993 | 43.0172 | 3326 | 3326 | 3326 | 3326
CHTE41 | WILE41 | 2033 | Addition | 64 | 0 | OHL | 0.0567 | 1.0993 | 43.0172 | 3326 | 3326 | 3326 | 3326
COTT41 | MARH4B | 2033 | Removed | 100.853 | 0 | OHL | 0.1677 | 1.9593 | 59.8778 | 2210 | 2130 | 1980 | 2130
COTT41 | NERY42 | 2033 | Addition | 76.548 | 0 | OHL | 0.0842 | 1.4033 | 48.4287 | 3326 | 3326 | 3326 | 3326
COTT41 | NERY42 | 2033 | Addition | 76.548 | 0 | OHL | 0.0842 | 1.4033 | 48.4287 | 3326 | 3326 | 3326 | 3326
COTT41 | RYHA41 | 2033 | Removed | 76.891 | 0 | OHL | 0.0846 | 1.4096 | 48.6457 | 3326 | 3326 | 3317 | 3326
COTT42 | COTT42 | 2033 | Addition | 0 | 0 | Series Compensation | 0 | 0.3125 | 0 | 3326 | 3160 | 2971 | 3160
COTT42 | NERY41 | 2033 | Addition | 76.473 | 0 | OHL | 0.0842 | 1.4022 | 48.3747 | 2807 | 2696 | 2511 | 2696
COTT42 | RYHA42 | 2033 | Removed | 76.816 | 0 | OHL | 0.0846 | 1.4085 | 48.5917 | 2807 | 2696 | 2511 | 2696
DRAX41 | THOM41 | 2033 | Change | 21.73 | 0 | OHL | 0.0248 | 0.3899 | 14.0086 | 3100 | 3050 | 2960 | 3050
DRAX41 | THTO42 | 2033 | Change | 22.579 | 0 | OHL | 0.0198 | 0.3877 | 15.2046 | 3326 | 3128 | 2926 | 3128
DRAX42 | THTO41 | 2033 | Change | 22.579 | 0 | OHL | 0.0198 | 0.3877 | 15.2046 | 3326 | 3128 | 2926 | 3128
EACS41 | TILN41 | 2033 | Addition | 81.3 | 4.05 | Composite | 0.0731 | 1.4135 | 207.327 | 3326 | 2850 | 2700 | 2850
EACS41 | TILN41 | 2033 | Addition | 81.3 | 4.05 | Composite | 0.0731 | 1.4135 | 207.327 | 3326 | 2850 | 2700 | 2850
EGGB41 | THOM41 | 2033 | Change | 28.07 | 0.197 | Composite | 0.0298 | 0.5031 | 23.0044 | 2810 | 2700 | 2510 | 2700
EGGB42 | STSB41 | 2033 | Change | 48.084 | 0 | OHL | 0.0477 | 0.8458 | 31.5881 | 2779 | 2568 | 2217 | 2568
EXET41 | TAUN41 | 2033 | Change | 38.147 | 0 | OHL | 0.0594 | 0.7319 | 22.8914 | 3100 | 3050 | 2960 | 3050
EXET41 | TAUN42 | 2033 | Change | 38.107 | 0 | OHL | 0.0594 | 0.7312 | 22.8669 | 3100 | 3050 | 2960 | 3050
FARM41 | WALH41 | 2033 | Change | 78.325 | 0 | OHL | 0.0966 | 1.4037 | 50.2949 | 2170 | 2080 | 1940 | 2080
FENW4A | THOM41 | 2033 | Change | 8.287 | 0 | OHL | 0.0129 | 0.159 | 4.973 | 3100 | 3050 | 2960 | 3050
FOUR21 | HARK24 | 2033 | Removed | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 854 | 795 | 700 | 795
FOUR21 | STEW21 | 2033 | Removed | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 854 | 795 | 700 | 795
GOTH41 | RATS41 | 2033 | Change | 2.814 | 0.216 | Composite | 0.0052 | 0.0574 | 6.9509 | 2009 | 1911 | 1746 | 1911
GREN41 | MARH4B | 2033 | Change | 28.19 | 0 | OHL | 0.0439 | 0.5409 | 16.9168 | 3100 | 3050 | 2960 | 3050
GREN41 | MARV4B | 2033 | Change | 26 | 0 | OHL | 0.0405 | 0.4989 | 15.6025 | 3100 | 3050 | 2960 | 3050
GREN42 | MARH4A | 2033 | Change | 28.37 | 0 | OHL | 0.0442 | 0.5443 | 17.0245 | 3100 | 3050 | 2960 | 3050
GREN42 | MARV4A | 2033 | Change | 26 | 0 | OHL | 0.0405 | 0.4989 | 15.6025 | 3100 | 3050 | 2960 | 3050
GRIW41 | LCNA41 | 2033 | Addition | 34 | 4 | Composite | 0.0321 | 0.6376 | 72.113 | 3326 | 3326 | 3320 | 3326
GRIW41 | LCNA41 | 2033 | Addition | 34 | 4 | Composite | 0.0321 | 0.6376 | 72.113 | 3326 | 3326 | 3320 | 3326
HARK23 | STEW21 | 2033 | Removed | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 774 | 774 | 676 | 676
HINP41 | SHUR41 | 2033 | Change | 1.2 | 0 | OHL | 0.0019 | 0.0235 | 0.7041 | 3100 | 3050 | 2960 | 3050
HINP41 | SHUR41 | 2033 | Change | 1.213 | 0 | OHL | 0.0019 | 0.0238 | 0.7119 | 3100 | 3050 | 2960 | 3050
INGL41 | WALB41 | 2033 | Addition | 0 | 1 | Cable | 0.0005 | 0.009 | 12.315 | 2120 | 1060 | 1060 | 1060
INGL41 | WALB42 | 2033 | Addition | 0 | 1 | Cable | 0.0005 | 0.009 | 12.315 | 2120 | 1060 | 1060 | 1060
INGL42 | WALB41 | 2033 | Addition | 0 | 1 | Cable | 0.0005 | 0.009 | 12.315 | 2120 | 1060 | 1060 | 1060
INGL42 | WALB42 | 2033 | Addition | 0 | 1 | Cable | 0.0005 | 0.009 | 12.315 | 2120 | 1060 | 1060 | 1060
IROA21 | MELK2A | 2033 | Change | 33.683 | 0.38 | Composite | 0.1891 | 1.7623 | 9.7484 | 965 | 925 | 865 | 925
IROA21 | MELK2B | 2033 | Change | 33.683 | 0.951 | Composite | 0.1952 | 1.7785 | 13.072 | 965 | 925 | 865 | 925
IRON41 | LEGA41 | 2033 | Removed | 62.073 | 0 | OHL | 0.0991 | 1.1937 | 37.3273 | 2002 | 2002 | 2002 | 2002
IRON41 | LOWF41 | 2033 | Addition | 42.073 | 0 | OHL | 0.0656 | 0.8072 | 25.2479 | 3100 | 3050 | 2960 | 3050
IRON41 | PENN4A | 2033 | Change | 27.761 | 0 | OHL | 0.0449 | 0.5376 | 16.5164 | 2030 | 1930 | 1770 | 1930
IRON41 | RUGE41 | 2033 | Change | 58.681 | 0 | OHL | 0.1011 | 1.1529 | 34.4359 | 2030 | 1930 | 1770 | 1930
IRON41 | SHRE4A | 2033 | Change | 15.129 | 0 | OHL | 0.0236 | 0.2903 | 9.0789 | 3100 | 3050 | 2960 | 3050
KEAR41 | PADI41 | 2033 | Change | 39.101 | 0 | OHL | 0.0553 | 0.7599 | 23.2874 | 2169 | 2084 | 1940 | 2084
KIBY21 | WASF21 | 2033 | Removed | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1521 | 1461 | 1360 | 1461
KIBY21 | WASF22 | 2033 | Removed | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1521 | 1461 | 1360 | 1461
KILA41 | SAXM41 | 2033 | Addition | 0 | 2 | Cable | 0.0011 | 0.018 | 24.6301 | 1060 | 1060 | 1060 | 1060
KILA41 | SAXM42 | 2033 | Addition | 0 | 2 | Cable | 0.0011 | 0.018 | 24.6301 | 1060 | 1060 | 1060 | 1060
KINO41 | TILB41 | 2033 | Change | 15.478 | 1.805 | Composite | 0.014 | 0.2778 | 54.8801 | 3326 | 2926 | 2560 | 2926
LCNA41 | LCNB41 | 2033 | Addition | 3 | 0 | OHL | 0.0027 | 0.0515 | 2.0164 | 3326 | 3326 | 3320 | 3326
LCNA41 | LCNB41 | 2033 | Addition | 3 | 0 | OHL | 0.0027 | 0.0515 | 2.0164 | 3326 | 3326 | 3326 | 3326
LCNB41 | WMAA41 | 2033 | Addition | 63 | 7 | Composite | 0.0593 | 1.1759 | 128.5503 | 3326 | 3326 | 3320 | 3326
LCNB41 | WMAA42 | 2033 | Addition | 63 | 7 | Composite | 0.0593 | 1.1759 | 128.5503 | 3326 | 3326 | 3320 | 3326
LEGA41 | LOWF41 | 2033 | Addition | 20 | 0 | OHL | 0.0312 | 0.3837 | 12.002 | 3100 | 3050 | 2960 | 3050
LEGA41 | LOWF41 | 2033 | Addition | 20 | 0 | OHL | 0.0312 | 0.3837 | 12.002 | 3100 | 3050 | 2960 | 3050
LEGA41 | SHRE4A | 2033 | Removed | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2295 | 2002 | 2002 | 2002 | 2002
LOWF41 | SHRE4A | 2033 | Addition | 26.944 | 0 | OHL | 0.042 | 0.517 | 16.169 | 3100 | 3050 | 2960 | 3050
MAGA21 | PYLE21 | 2033 | Addition | 0 | 6.2 | Cable | 0.013 | 0.1432 | 60.14 | 1204 | 1115 | 1018 | 1115
MARV4A | SUND41 | 2033 | Change | 13.75 | 0 | OHL | 0.0214 | 0.2638 | 8.2513 | 3100 | 3050 | 2960 | 3050
MARV4B | SUND42 | 2033 | Change | 13.955 | 0 | OHL | 0.0217 | 0.2677 | 8.374 | 3100 | 3050 | 2960 | 3050
MINC41 | MINS41 | 2033 | Addition | 0 | 1 | Cable | 0.0005 | 0.009 | 12.315 | 1060 | 1060 | 1060 | 1060
MINC42 | MINS41 | 2033 | Addition | 0 | 1 | Cable | 0.0005 | 0.009 | 12.315 | 1060 | 1060 | 1060 | 1060
MINS41 | RICH41 | 2033 | Addition | 2.863 | 0 | OHL | 0.0045 | 0.0566 | 1.6665 | 3100 | 3050 | 2960 | 3050
MINS41 | RICH41 | 2033 | Addition | 2.863 | 0 | OHL | 0.0045 | 0.0566 | 1.6665 | 3100 | 3050 | 2960 | 3050
NERY41 | RYHA42 | 2033 | Addition | 0.343 | 0 | OHL | 0.0004 | 0.0063 | 0.217 | 2807 | 2696 | 2511 | 2696
NERY41 | WEMA41 | 2033 | Addition | 27 | 3 | Composite | 0.0247 | 0.4838 | 92.0381 | 3326 | 3326 | 3320 | 3326
NERY42 | RYHA41 | 2033 | Addition | 0.343 | 0 | OHL | 0.0004 | 0.0063 | 0.217 | 3326 | 3326 | 3326 | 3326
NERY42 | WEMA41 | 2033 | Addition | 27 | 3 | Composite | 0.0247 | 0.4838 | 92.0381 | 3326 | 3326 | 3320 | 3326
NORE41 | NORT41 | 2033 | Addition | 0.32 | 0 | OHL | 0.0005 | 0.0064 | 0.1833 | 3100 | 3050 | 2960 | 3050
NORE41 | SALH41 | 2033 | Addition | 11.886 | 0 | OHL | 0.0198 | 0.2388 | 6.8104 | 3100 | 3050 | 2960 | 3050
NORT41 | SALH42 | 2033 | Removed | 12.206 | 0 | OHL | 0.0204 | 0.2452 | 6.9937 | 3100 | 3050 | 2960 | 3050
NORT41 | SHPT41 | 2033 | Change | 70.453 | 0 | OHL | 0.1098 | 1.3518 | 42.2787 | 3100 | 3050 | 2960 | 3050
NORT41 | SHPT42 | 2033 | Change | 70.453 | 0 | OHL | 0.1098 | 1.3518 | 42.2787 | 3100 | 3050 | 2960 | 3050
NORT41 | SPEN41 | 2033 | Change | 21.134 | 0 | OHL | 0.0187 | 0.363 | 14.2051 | 3326 | 3326 | 3326 | 3326
NORT41 | SPEN42 | 2033 | Change | 21.134 | 0 | OHL | 0.0187 | 0.363 | 14.2051 | 3326 | 3326 | 3326 | 3326
PADI41 | PEWO41 | 2033 | Change | 37.608 | 0 | OHL | 0.0475 | 0.7159 | 22.8474 | 2810 | 2810 | 2810 | 2810
SHRE4A | SHRE4B | 2033 | Change | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0332 | 3610 | 3610 | 3610 | 3610
SHUR41 | TAUN41 | 2033 | Change | 27 | 0 | OHL | 0.0421 | 0.518 | 16.2026 | 3100 | 3050 | 2960 | 3050
SHUR41 | TAUN42 | 2033 | Change | 27 | 0 | OHL | 0.0421 | 0.518 | 16.2026 | 3100 | 3050 | 2960 | 3050
SPEN41 | STEW41 | 2033 | Change | 37.795 | 0.126 | Composite | 0.0335 | 0.65 | 27.4412 | 3326 | 3326 | 3326 | 3326
SPEN42 | STEW41 | 2033 | Change | 37.795 | 0 | OHL | 0.0335 | 0.6492 | 25.4037 | 3326 | 3326 | 3326 | 3326
SSHI21 | TYNE2A | 2033 | Change | 4.609 | 1.6 | Composite | 0.0372 | 0.2411 | 10.564 | 1360 | 1310 | 1220 | 1310
STEW41 | STWT41 | 2033 | Addition | 0 | 0.5 | Cable | 0.0001 | 0.0033 | 12.315 | 3326 | 3326 | 3320 | 3326
STEW41 | STWT42 | 2033 | Addition | 0 | 0.5 | Cable | 0.0001 | 0.0033 | 12.315 | 3326 | 3326 | 3320 | 3326
THOM21 | THOM21 | 2033 | Addition | 0 | 0 | Series Compensation | 0 | 2.6446 | 0 | 1524 | 1524 | 1524 | 1524
THTO42 | THTO42 | 2033 | Addition | 0 | 0 | Series Compensation | 0 | 1.25 | 0 | 2217 | 2217 | 2217 | 2217
THUR21 | THUR2A | 2033 | Change | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 675 | 675 | 675 | 675
TIBB41 | TILB41 | 2033 | Addition | 0 | 0.059 | Cable | 0 | 0.0004 | 1.4507 | 2771 | 2771 | 2771 | 2771
TIBB41 | WARL41 | 2033 | Addition | 12.897 | 0 | OHL | 0.0201 | 0.2474 | 7.7391 | 3100 | 3050 | 2960 | 3050
TIBB42 | TILB42 | 2033 | Addition | 0 | 0.059 | Cable | 0 | 0.0004 | 1.4507 | 2771 | 2771 | 2771 | 2771
TIBB42 | WARL41 | 2033 | Addition | 13.065 | 0 | OHL | 0.0204 | 0.2507 | 7.8396 | 3100 | 3050 | 2960 | 3050
TILB21 | WARL21 | 2033 | Removed | 12.865 | 0.2 | Composite | 0.0558 | 0.5433 | 4.7032 | 1175 | 1119 | 1023 | 1119
TILB21 | WARL21 | 2033 | Removed | 12.697 | 0.2 | Composite | 0.0553 | 0.5365 | 4.6556 | 1175 | 1119 | 1023 | 1119
TILB42 | WAEN41 | 2033 | Change | 24.818 | 1.805 | Composite | 0.0221 | 0.4342 | 83.3988 | 3326 | 2926 | 2560 | 2926
TYNE21 | SSHI21 | 2033 | Change | 4.444 | 1.6 | Composite | 0.0365 | 0.2341 | 10.5193 | 1180 | 1120 | 1020 | 1120
WALB41 | WALP41 | 2033 | Addition | 0.25 | 0 | OHL | 0.0002 | 0.0043 | 0.168 | 3326 | 3326 | 3326 | 3326
WALB41 | WMAB41 | 2033 | Addition | 22 | 3 | Composite | 0.0203 | 0.398 | 88.6774 | 3326 | 3326 | 3326 | 3326
WALB42 | WALP42 | 2033 | Addition | 0.25 | 0 | OHL | 0.0002 | 0.0043 | 0.168 | 3326 | 3326 | 3326 | 3326
WALB42 | WMAB41 | 2033 | Addition | 22 | 3 | Composite | 0.0203 | 0.398 | 88.6774 | 3326 | 3326 | 3326 | 3326
WMAA41 | WMAB41 | 2033 | Addition | 0.5 | 0 | OHL | 0.0004 | 0.0086 | 0.3361 | 3326 | 3326 | 3326 | 3326
WMAA42 | WMAB42 | 2033 | Addition | 0.5 | 0 | OHL | 0.0004 | 0.0086 | 0.3361 | 3326 | 3326 | 3326 | 3326

## B-2-2d
B.2.2d - OFTO Circuit Changes 2026/27 to 2033/34
Wind Farm | Node 1 | Node 2 | Year | Status | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Interconnection Type | Rated DC Voltage (kV) | Rated AC Voltage (kV) | Rating (MVA)
Dogger Bank B Offshore Wind Farm | DBBODC | DBBWDC | 2026 | Addition | 0 | 205 | Cable | 0.0024 | 0 | 0 | HVDC | ±320 | 400 | 1940
| DBBO41 | CREB41 | 2026 | Addition | 0 | 1.6 | Cable | 5.9e-06 | 8e-05 | 0.3796 | AC | 400 | 400 | 2044
East Anglia 3A Offshore Wind Farm | BRFO4 Onshore Converter station | EACO4 Offshore Converter station | 2026 | Addition | 0 | 185 | Cable | 0.00124 | 0 | 0 | HVDC | ±320 | 400 | 1320
Hornsea 3A-1 Offshore Wind Farm | NORM41 | HOWC41 | 2026 | Addition | 0 | 1.8 | Cable | TBC | TBC | TBC | AC | N/A | 400 | 1320
| HOWC4X | HOWW4X | 2026 | Addition | 0 | 220 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | 1320
Hornsea 3A-2 Offshore Wind Farm | NORM41 | HOWC42 | 2026 | Addition | 0 | 1.8 | Cable | TBC | TBC | TBC | AC | N/A | 400 | 1320
| HOWC4X | HOWW4X | 2026 | Addition | 0 | 220 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | 1320
Norfolk Boreas | NECT4 | Onshore 400kV-1 | 2026 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Hornsea 4A-1 Offshore Wind Farm | CREB41 | HOWD41 | 2028 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| CREB42 | HOWD41 | 2028 | Addition | 0 | 0.5 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| HOWD21 | HOWR2C | 2028 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWD21 | HOWR2C | 2028 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWD21 | HOWR2C | 2028 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWR2C | HOWW2F | 2028 | Addition | 0 | 24 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWR2C | HOWW2F | 2028 | Addition | 0 | 24 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWR2C | HOWW2F | 2028 | Addition | 0 | 24 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Hornsea 4A-2 Offshore Wind Farm | HOWD21 | HOWR2C | 2028 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWD21 | HOWR2C | 2028 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWR2C | HOWW2F | 2028 | Addition | 0 | 24 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| HOWR2C | HOWW2F | 2028 | Addition | 0 | 24 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Seagreen 1A offshore windfarm | COCK21 | Onshore 275kV-1 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Berwick 2 Offshore Wind Farm | BRNX4- | Onshore 400kV-1 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BRNX4- | Onshore 400kV-1 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BRNX4- | Onshore 400kV-1 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2028 | Addition | 0 | 72.3 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-1 | Offshore 275kV-2 | 2028 | Addition | 0 | 72.3 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-1 | Offshore 275kV-3 | 2028 | Addition | 0 | 72.3 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Offshore 66kV-1 | Offshore 66kV-2 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
| Offshore 66kV-2 | Offshore 66kV-3 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
Erebus Offshore Windfarm | PEMB11 | EOWF11 | 2028 | Addition | 0 | 2 | Cable | TBC | TBC | TBC | AC | N/A | 132 | TBC
| EOWF11 | EOWL11 | 2028 | Addition | 0 | 0 | Cable | TBC | TBC | TBC | AC | N/A | 132 | TBC
| EOWF61 | EOWF62 | 2028 | Addition | 0 | 50 | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
Vanguard East Offshore Wind Farm | NECT41 | VGEO41 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter LV | VGEWX1 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±365 | N/A | 1320
| Onshore AC Platform | Offshore AC Platform | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore AC Platform | Offshore AC Platform | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Awel Y Mor Extension Wind Farm | BODE41 | Onshore 400kV-1 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BODE41 | Onshore 400kV-2 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2028 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Sofia Offshore Wind Farm | SOFW4A | SOFWD | 2028 | Addition | 0 | 227 | Cable | 0.2757 | 0 | 0 | HVDC | ±320 | N/A | 660
Inch Cape Offshore Wind Farm | COCK21 | INCO21 | 2028 | Addition | 0 | 0.8 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Vanguard West Offshore Wind Farm | NECT41 | VGWO41 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Pentland Floating Offshore Windfarm | OWFD11 | Onshore 132 kV HV | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 132 | TBC
| Onshore 66 kV HV | Offshore 66 kV HV | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
Berwick 1 Offshore Wind Farm | BRNX4- | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BRNX4- | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BRNX4- | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2030 | Addition | 0 | 77.4 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-1 | Offshore 275kV-2 | 2030 | Addition | 0 | 77.4 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-1 | Offshore 275kV-3 | 2030 | Addition | 0 | 77.4 | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Offshore 66kV-1 | Offshore 66kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
| Offshore 66kV-2 | Offshore 66kV-3 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 66 | TBC
Berwick Bank Offshore Wind Farm C | BLYT41 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter station 400kV | Offshore Converter station | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 1800
Elizabeth Yellow One Offshore Windfarm | PEWO41 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-3 | Offshore 275kV-3 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Morecambe Offshore Wind Farm | PEWO41 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| PEWO42 | Onshore 400kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
OWPL Offshore Windfarm | SPIT41 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| SPIT42 | Onshore 400kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Project Elizabeth Offshore Windfarm | BODE41 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BODE42 | Onshore 400kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Rampion Extension Windfarm | BOLN41 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BOLN41 | Onshore 400kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Five Estuaries Wind Farm | EAAW4 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
North Falls Offshore Wind Farm | EAAW4 | Onshore 400kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Dogger Bank South West (was Irish Sea) | RWE 4 | BIRW42 | 2030 | Addition | TBC | TBC | TBC | TBC | TBC | TBC | TBC | ±320 | NA | TBC
Dogger Bank C East Offshore Wind Farm | DBCODC | DBCWDC | 2030 | Addition | 0 | 272 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | 1200
| DBCO41 | LACK41 | 2030 | Addition | 0 | 2 | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
East Anglia 2A Offshore Wind Farm | BRFO41 | EABO41 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2030 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
East Anglia 1 North Offshore Wind Farm | LEIS41 | EANO41 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| EANO21 | EANW21 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| EANO21 | EANW21 | 2030 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Cenos Central Offshore Wind Farm | PEHE41 | Onshore Converter HV | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter LV | Onshore DC Platform | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±300 | N/A | TBC
| Onshore AC Platform | Offshore AC Platform | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 300 | TBC
EQUINOR Offshore Windfarm | NORM41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| NORM42 | Onshore 400kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Green Volt Offshore Wind Farm | PEHE41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| PEHE41 | Onshore 400kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
EOLFI Offshore/Campion | SW_E2a | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | TBC | TBC
Stoura Offshore Wind Farm | SHET4 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | TBC | TBC
Caledonia Wind Farm | GRNS41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| GRNS41 | Onshore 400kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-3 | Offshore 275kV-3 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-4 | Offshore 275kV-4 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
East Anglia 2B Offshore Wind Farm | Onshore 220kV-2 | Offshore 220kV-2 | 2033 | Addition | 0 | 95 | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
GT R4 Wind Farm | WEMA41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-3 | Offshore 275kV-3 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Spiorad na Mara offshore windfarm | LEWI41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Ossian Offshore Wind farm | LINC41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| WEMA41 | Onshore 400kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter station 400kV-1 | Offshore Converter station -1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 2000
| Onshore Converter station 400kV-2 | Offshore Converter station -2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | ±525 | N/A | 2000
Ayre Offshore Wind Farm | BANN41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| BANN41 | Onshore 400kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
BELLROCK OFFSHORE WINDFARM | SW_E1A | Onshore 275kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Buchan 01 Offshore Wind Farm | NEDE41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| NEDE41 | Onshore 400kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 275kV-1 | Offshore 275kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
| Onshore 275kV-2 | Offshore 275kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 275 | TBC
Gatroben Offshore Wind Farm | CREB41 | Onshore Converter HV | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter LV | Onshore DC Platform | 2033 | Addition | 0 | 166 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | TBC
| Onshore AC Platform | Offshore AC Platform | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore AC Platform | Offshore AC Platform | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Morven Offshore Wind Farm | HAWP41 | Onshore Converter HV | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter LV | Onshore DC Platform | 2033 | Addition | 0 | 166 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | TBC
| Onshore AC Platform | Offshore AC Platform | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore AC Platform | Offshore AC Platform | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Morven Extension Offshore Wind Farm | HAWP41 | Onshore Converter HV | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter LV | Onshore DC Platform | 2033 | Addition | 0 | 166 | Cable | TBC | TBC | TBC | HVDC | ±320 | N/A | TBC
| Onshore AC Platform | Offshore AC Platform | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore AC Platform | Offshore AC Platform | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Stromar Offshore Wind Farm | GRNS41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| GRNS41 | Onshore 400kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore 220kV-1 | Offshore 220kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
| Onshore 220kV-2 | Offshore 220kV-2 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 220 | TBC
Merlin 2 Offshore Windfarm | ALVE41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
Marram Offshore Wind Farm | LOSD41 | Onshore 400kV-1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | AC | N/A | 400 | TBC
| Onshore Converter station 400kV-1 | Offshore Converter station -1 | 2033 | Addition | 0 | TBC | Cable | TBC | TBC | TBC | HVDC | TBC | N/A | 1500

## B-3-1a
B-3-1a - SHE Transmission Transformers for 2025/26
Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
ABNE1Q | ABNE3- | 0.2265 | 24.724 | -0.0048 | 120
ABNE1R | ABNE3- | 0.2283 | 24.6239 | -0.0018 | 120
AIGA1Q | AIGA5- | 1.7562 | 44.8545 | -0.0001 | 23
ALNE1Q | ALNE3J | 0.3715 | 26.189 | -0.0002 | 120
ALNE1R | ALNE3J | 0.3696 | 26.0307 | -0.0031 | 120
ANSU1- | ANSU3- | 0.8997 | 24.8949 | -0.0163 | 45
ARBR1Q | ARBR3- | 0.7044 | 28.2801 | -0.0117 | 45
ARBR1R | ARBR3- | 0.7038 | 28.2579 | -0.0117 | 45
ARDK1- | ARDK3- | 0.8056 | 24.8758 | -0.0163 | 45
ARMO1- | ARMO3- | 0.615 | 17.8227 | -0.0129 | 60
BEAU11 | BEAU1A | 0.1833 | 3.7288 | 0 | 150
BEAU11 | BEAU1B | 0.1833 | 3.7288 | 0 | 150
BEAU11 | BEAU3- | 1.0404 | 27.736 | -0.0117 | 45
BEAU11 | BEAU3- | 1.0404 | 27.736 | -0.0117 | 45
BEAU21 | BEAU11 | 0.6786 | 12.1644 | -0.0003 | 120
BEAU21 | BEAU11 | 0.6785 | 12.1895 | -0.0003 | 120
BEAU21 | BEAU11 | 0.6786 | 12.2312 | -0.0003 | 120
BEAU4- | BEAU21 | 0.0374 | 1.5937 | -0.0004 | 1200
BEAU4- | BEAU21 | 0.0376 | 1.5954 | -0.1302 | 1200
BEAU4- | BEAU21 | 0.0374 | 1.5937 | -0.1258 | 1200
BEIN1- | BEIN31 | 0.1925 | 10.3315 | -0.0031 | 120
BERB2Q | BERB3- | 0.292 | 19.8312 | -0.0092 | 120
BHLA1- | BHLA3- | 0.1987 | 17.5739 | -0.0199 | 120
BLHI21 | BLHI11 | 0.1506 | 5.3034 | -0.022 | 360
BLHI21 | BLHI11 | 0.1486 | 5.3035 | -0.0319 | 360
BLHI41 | BLHI21 | 0.0264 | 1.5331 | -0.0947 | 1200
BLHI41 | BLHI21 | 0.0262 | 1.5331 | -0.0911 | 1200
BOAG1Q | BOAG3- | 0.6105 | 24.9925 | -0.0002 | 60
BOAG1R | BOAG3- | 0.6051 | 24.826 | -0.0118 | 60
BRCW2J | BRCW3- | 0.2893 | 19.9146 | -0.0155 | 120
BRCW2K | BRCW3- | 0.2893 | 19.9146 | -0.0159 | 120
BRID1J | BRID3- | 0.6331 | 28.7597 | -0.1392 | 60
BRID1K | BRID3- | 0.6369 | 28.943 | -0.1392 | 60
BROA1Q | BROA3- | 2.4822 | 38.9209 | -0.076 | 30
BROR1- | BROR3- | 0.809 | 24.8757 | -0.0164 | 45
BUMU1Q | BUMU3- | 0.3661 | 25.3751 | -0.0694 | 90
BUMU1R | BUMU3- | 0.3758 | 25.4194 | -0.0694 | 90
CAAD1Q | CAAD31 | 0.2543 | 24.832 | -0.0049 | 120
CAAD1Q | CAAD32 | 0.2546 | 24.832 | -0.0049 | 120
CAAD1R | CAAD31 | 0.2558 | 24.832 | -0.007 | 120
CAAD1R | CAAD32 | 0.2558 | 24.832 | -0.007 | 120
CAIN2- | CAIN3J | 0.379 | 18.0794 | -0.0241 | 120
CASS1Q | CASS3- | 1.5181 | 39.6376 | -0.0263 | 30
CEAN1Q | CEAN5- | 0.9943 | 36.7199 | -0.012 | 30
CHAR11 | CHAR3- | 0.4409 | 26.9742 | -0.0494 | 90
CHAR11 | CHAR3- | 0.442 | 27.0408 | -0.0494 | 90
CLAC1Q | CLAC5- | 0.7672 | 25.5718 | -0.0851 | 60
CLAY1Q | CLAY3- | 0.8719 | 24.9014 | -0.2968 | 60
CLAY1T | CLAY3- | 0.8719 | 24.9014 | -0.2968 | 60
CLUN1Q | CLUN5J | 0.7305 | 19.5197 | -0.0851 | 60
CLUN1R | CLUN5K | 0.7051 | 19.5373 | -0.0788 | 60
COGA1- | COGA3- | 0.2691 | 17.8869 | -0.0097 | 90
CONN2Q | CONN1J | 0.143 | 5.3036 | -0.0252 | 360
CORI11 | CORI3- | 0.4571 | 19.8836 | -0.0158 | 90
CORI11 | CORI3B | 0.3843 | 17.7403 | -0.0056 | 90
COUA1N | COUA3- | 0.2143 | 25.0741 | -0.0002 | 120
COUA1S | COUA3- | 0.2152 | 25.1241 | -0.0002 | 120
CRAI11 | CRAI3- | 1.7798 | 29.847 | -0.0541 | 30
CRAI12 | CRAI3- | 1.7486 | 30.2161 | -0.0475 | 30
CRAR1R | CRAR3- | 0.4031 | 17.7732 | -0.0172 | 90
CREA1- | CREA3- | 0.329 | 9.9362 | -0.0533 | 120
CRSS11 | CRSS3- | 0.4099 | 17.9953 | -0.0168 | 90
CRSS1A | CRSS11 | 0.0582 | 2.145 | -0.0058 | 240
CRSS1B | CRSS11 | 0.0582 | 2.1492 | -0.0003 | 240
CRSS2A | CRSS11 | 0.2466 | 9.0008 | -0.0169 | 240
CRSS2B | CRSS11 | 0.2459 | 9.0175 | -0.0242 | 240
CULL1- | CULL5- | 1.5094 | 37.5697 | -0.2165 | 25
DAAS2- | DAAS3- | 0.292 | 19.8312 | -0.0092 | 120
DEAN1Q | DEAN5- | 1.0125 | 25.0796 | -0.1926 | 40
DORE1J | DORE3J | 0.2099 | 9.8894 | -0.0003 | 120
DORE1K | DORE3K | 0.2099 | 9.8894 | -0.0003 | 120
DOUN11 | DOUN3- | 0.4796 | 26.0734 | -0.0407 | 90
DOUN11 | DOUN3- | 0.4573 | 25.9515 | -0.0405 | 90
DOUN21 | DOUN11 | 0.2112 | 7.7054 | -0.0236 | 240
DOUN21 | DOUN11 | 0.2237 | 7.9135 | -0.0246 | 240
DUBE1- | DUBE3- | 1.5189 | 39.3707 | -0.0261 | 30
DUDH1Q | DUDH3- | 0.7798 | 24.9211 | -0.0118 | 60
DUDH1R | DUDH3- | 0.7797 | 23.9206 | -0.0118 | 60
DUGR1Q | DUGR3- | 0.6165 | 17.6559 | -0.0129 | 60
DUNM1- | DUNM3- | 0.1823 | 17.6657 | -0.0212 | 120
DUNO1Q | DUNO3- | 1.9925 | 24.4077 | -0.0163 | 45
DUNO1R | DUNO3- | 1.9932 | 24.4968 | -0.0163 | 45
DYCE1J | DYCE3- | 0.3975 | 24.7301 | -0.0165 | 90
DYCE1K | DYCE3- | 0.4015 | 24.819 | -0.0169 | 90
EDIN1- | EDIN3- | 0.5584 | 16.9908 | -0.0118 | 60
ELGI1Q | ELGI3- | 0.6255 | 27.9708 | -0.1022 | 90
ELGI1R | ELGI3- | 0.6289 | 27.7707 | -0.1949 | 90
ERRO11 | ERRO1C | 0.1833 | 3.7288 | 0 | 150
ERRO11 | ERRO1A | 0.04 | 1.9413 | 0 | 240
ERRO11 | ERRO1B | 0.04 | 1.9413 | 0 | 240
ERRO11 | ERRO5J | 0.7049 | 26.0405 | -0.0851 | 60
ERRO11 | ERRO5L | 0.7108 | 26.2571 | -0.0851 | 60
FAAR1Q | FAAR3J | 0.8997 | 28.3302 | -0.0492 | 90
FAAR1R | FAAR3K | 0.8968 | 28.2413 | -0.0492 | 90
FARI2J | FARI1J | 0.4989 | 8.2933 | -0.0546 | 120
FARI2K | FARI1K | 0.4955 | 8.3186 | -0.0546 | 120
FASN2Q | FASN31 | 0.2896 | 19.9146 | -0.0075 | 120
FASN2R | FASN31 | 0.2892 | 20.1646 | -0.0146 | 120
FAUG11 | FAUG3- | 0.5432 | 24.9941 | -0.0141 | 90
FAUG2Q | FAUG11 | 0.2606 | 7.7039 | -0.02 | 240
FAUG2R | FAUG11 | 0.2629 | 7.7038 | -0.0247 | 240
FAUG41 | FAUG12 | 0.106 | 4.0403 | -0.0815 | 480
FAUG41 | FAUG12 | 0.1047 | 4.0403 | -0.076 | 480
FAUG41 | FAUG11 | 0.2149 | 8.0138 | -0.0749 | 240
FAUG41 | FAUG11 | 0.3185 | 8.4523 | -0.1495 | 240
FERO1- | FERO3- | 0.3506 | 10.5053 | -0.0744 | 90
FETT1- | FETT3S | 0.38 | 25.0638 | -0.0263 | 120
FETT21 | FETT1- | 0.217 | 4.2737 | -0.0329 | 240
FIDD1Q | FIDD3- | 0.4568 | 26.2294 | -0.0404 | 90
FIDD1R | FIDD11 | 0.1042 | 3.8919 | 0 | 150
FIDD1R | FIDD3- | 0.4564 | 26.0849 | -0.0406 | 90
FINL1Q | FINL5- | 0.9554 | 27.0943 | -0.0051 | 45
FRAS1Q | FRAS3- | 0.7452 | 26.9008 | -0.0467 | 45
FRAS1R | FRAS3- | 0.7452 | 26.9008 | -0.0467 | 45
FWIL1Q | FWIL3- | 0.3663 | 26.2141 | -0.0266 | 120
FWIL1R | FWIL3- | 0.3693 | 26.3141 | -0.0264 | 120
FYRI2J | FYRI11 | 0.0971 | 3.8738 | -0.0474 | 480
FYRI2K | FYRI11 | 0.0967 | 3.8863 | -0.0589 | 480
GLEN1- | GLEN5- | 0.5499 | 21.936 | -0.3488 | 70
GLFA1- | GLFA3- | 0.5915 | 27.2269 | -0.0002 | 90
GORW2- | GORW3- | 0.2579 | 20.0567 | -0.0395 | 120
GREM1J | GREM3- | 0.5828 | 24.9932 | 0 | 90
GREM1K | GREM3- | 0.5828 | 24.9932 | 0 | 90
GRIF1S | GRIF3J | 0.2479 | 16.2981 | -0.0105 | 120
GRIF1T | GRIF3K | 0.2466 | 16.2481 | -0.0116 | 120
GRUB1Q | GRUB3- | 0.4445 | 24.8738 | -0.0505 | 90
GRUB1R | GRUB3- | 0.4364 | 24.9962 | -0.0505 | 90
INGA1Q | INGA5- | 1.1691 | 25.006 | -0.0053 | 30
INNE1J | INNE3- | 0.45 | 26.774 | -0.0494 | 90
INNE1K | INNE3- | 0.8987 | 27.9856 | -0.1392 | 60
INNE1L | INNE3- | 0.8959 | 27.8523 | -0.108 | 60
INVB2A | INVR11 | 0.2217 | 4.3026 | -0.0409 | 240
INVB2B | INVR11 | 0.2164 | 4.257 | -0.0381 | 240
KEIT11 | KEIT31 | 0.555 | 28.5502 | -0.0492 | 90
KEIT11 | KEIT32 | 0.3504 | 25.2753 | -0.0601 | 90
KEIT12 | KEIT31 | 0.5567 | 28.639 | -0.0492 | 90
KEIT12 | KEIT32 | 0.4521 | 25.8961 | -0.0492 | 90
KEIT2Q | KEIT11 | 0.2735 | 8.6123 | -0.029 | 240
KEIT2R | KEIT12 | 0.3328 | 8.9105 | -0.2242 | 240
KIIN11 | KIIN3- | 0.7745 | 24.8768 | -0.0079 | 45
KIIN12 | KIIN3- | 0.7689 | 24.5213 | -0.0079 | 45
KILO1- | KILO3- | 0.8801 | 27.7861 | -0.0117 | 45
KINT11 | KINT3- | 1.0391 | 27.6305 | -0.0002 | 60
KINT11 | KINT3- | 0.4561 | 26.1071 | -0.0405 | 90
KINT11 | KINT3- | 1.0391 | 27.6305 | -0.0002 | 60
KINT21 | KINT11 | 0.3751 | 10.2306 | -0.0845 | 240
KINT2A | KINT11 | 0.3771 | 10.193 | -0.1037 | 240
KINT2B | KINT11 | 0.6786 | 12.1477 | -0.0003 | 120
KINT4A | KINT21 | 0.0271 | 1.6306 | -0.126 | 1200
KINT4B | KINT21 | 0.0266 | 1.6248 | -0.1115 | 1200
KIOR1- | KIOR5- | 1.7809 | 45.4318 | -0.0001 | 22
KNOC21 | KNOC11 | 0.2216 | 4.311 | -0.0437 | 240
KNOC21 | KNOC11 | 0.2205 | 4.3319 | -0.0355 | 240
LAIR1Q | LAIR3- | 0.4521 | 24.6736 | -0.0491 | 90
LIMK1- | LIMK3- | 0.2426 | 17.9984 | 0 | 120
LOCB21 | LOCB11 | 0.22 | 8.197 | -0.0263 | 240
LOCB21 | LOCB11 | 0.2181 | 8.1262 | -0.025 | 240
LOCH1- | LOCH5J | 0.9531 | 38.8216 | -0.012 | 36
LOCH1- | LOCH5K | 0.9553 | 38.766 | -0.0122 | 36
LUIC1Q | LUIC5A | 0.7632 | 37.5478 | -0.0059 | 45
LUIC1R | LUIC5B | 0.7669 | 37.5477 | -0.0075 | 45
LUNA1Q | LUNA3- | 0.4555 | 25.0181 | -0.049 | 90
LUNA1R | LUNA3- | 0.2621 | 24.6736 | -0.0263 | 120
LYND1Q | LYND3- | 0.7797 | 24.2875 | -0.0118 | 60
LYND1R | LYND3- | 0.7796 | 24.721 | -0.0118 | 60
MACD1Q | MACD3- | 0.3691 | 25.264 | -0.0505 | 90
MACD1R | MACD3- | 0.3678 | 25.3418 | -0.0601 | 90
MELG41 | MELG11 | 0.108 | 3.9569 | -0.078 | 480
MELG41 | MELG11 | 0.1061 | 3.9569 | -0.0772 | 480
MILC1T | MILC3- | 0.7798 | 24.8211 | -0.0118 | 60
MILC1V | MILC3- | 0.8796 | 28.1196 | -0.1392 | 60
MILW1- | MILW3- | 0.4654 | 24.8957 | -0.0165 | 90
MOSS1Q | MOSS5A | 1.1913 | 36.8474 | -0.0049 | 30
MOSS1R | MOSS5B | 1.2135 | 36.9134 | -0.0056 | 30
MYBS1S | MYBS31 | 0.2645 | 24.6069 | -0.0264 | 120
MYBS1S | MYBS31 | 0.3837 | 24.9804 | -0.002 | 120
MYBS1S | MYBS31 | 0.3773 | 24.9805 | -0.0268 | 120
MYBS1T | MYBS31 | 0.2578 | 24.757 | -0.0412 | 120
MYBS1T | MYBS31 | 0.3773 | 24.9805 | -0.0268 | 120
MYBS1T | MYBS31 | 0.3837 | 24.9804 | -0.002 | 120
NAIR1Q | NAIR3- | 1.0542 | 28.5806 | -0.0135 | 60
NAIR1R | NAIR3- | 1.0488 | 28.5808 | -0.0148 | 60
NANT1- | NANT5- | 1.4756 | 56.6475 | -0.1494 | 30
ORRI1Q | ORRI5- | 2.1751 | 48.7015 | -0.0933 | 20
ORRI1R | ORRI3- | 0.5634 | 16.8239 | -0.0122 | 60
PEHE11 | PEHS5- | 2.5547 | 41.9222 | 0 | 15
PEHE21 | PEHE11 | 0.4842 | 9.9549 | -0.1024 | 240
PEHE21 | PEHE11 | 0.3422 | 8.8892 | -0.2099 | 240
PEHE21 | PEHE11 | 0.2649 | 9.2254 | -0.0285 | 240
PEHE2A | PEHE21 | 0.026 | 1.533 | -0.0005 | 1200
PEHE2B | PEHE21 | 0.026 | 1.533 | -0.0005 | 1200
PEHE41 | PEHE21 | 0.0263 | 1.6265 | -0.1101 | 1200
PEHE41 | PEHE21 | 0.0265 | 1.624 | -0.121 | 1200
PEHG1Q | PEHG3- | 1.05 | 28.4028 | -0.0117 | 45
PEHG1R | PEHG3- | 1.05 | 28.4028 | -0.0117 | 45
PERS11 | PERS3- | 0.4492 | 25.9961 | -0.0149 | 90
PERS11 | PERS3- | 0.4411 | 25.9296 | -0.0151 | 90
PERS2Q | PERS11 | 0.3363 | 8.9062 | -0.2373 | 240
PERS2R | PERS11 | 0.3341 | 8.8645 | -0.2414 | 240
PORA1Q | PORA3- | 1.8024 | 29.8122 | -0.0503 | 30
PORA1R | PORA3- | 1.8024 | 29.8122 | -0.0503 | 30
QUOI1- | QUOI5- | 1.3392 | 33.1063 | -0.012 | 30
RANN1Q | RANN3- | 0.4331 | 24.6629 | -0.0042 | 90
RANN1R | RANN3- | 0.4312 | 24.5518 | -0.0042 | 90
REDM1Q | REDM3- | 0.9095 | 26.9847 | -0.0157 | 60
REDM1R | REDM3- | 0.8997 | 27.8188 | -0.0157 | 60
ROTI41 | ROTI3J | 0.2061 | 24.5241 | -0.0378 | 120
ROTI41 | ROTI3K | 0.2106 | 24.5158 | -0.0382 | 120
SFEE1Q | SFEE5- | 1.3274 | 76.6552 | -0.0088 | 36
SFEE1R | SFEE5- | 1.3287 | 76.6552 | -0.0001 | 36
SFIL1Q | SFIL5- | 2.0136 | 39.9493 | -0.0199 | 25
SHIN11 | SHIN3- | 0.4495 | 26.0517 | -0.0002 | 90
SHIN11 | SHIN3- | 0.4614 | 26.2182 | -0.0183 | 90
SHIN11 | SHIN5- | 1.5767 | 75.5085 | -0.0038 | 40
SLOY1L | SLOY5L | 0.791 | 23.0664 | -0.0157 | 50
SLOY1M | SLOY5M | 0.79 | 22.8864 | -0.0157 | 50
SLOY1N | SLOY5N | 0.7941 | 22.9663 | -0.0144 | 50
SLOY1P | SLOY5P | 0.8001 | 23.1862 | -0.0149 | 50
SPIT21 | SPIT11 | 0.2184 | 8.2304 | -0.0228 | 240
SPIT21 | SPIT11 | 0.2184 | 8.1846 | -0.0213 | 240
SPIT21 | SPIT11 | 0.1287 | 4.99 | -0.0382 | 360
SPIT21 | SPIT11 | 0.1307 | 4.99 | -0.0407 | 360
STRB2- | STRB3- | 0.2098 | 19.8739 | -0.0215 | 120
STRI1Q | STRI3- | 0.5028 | 24.4393 | -0.0019 | 90
STRI1R | STRI3- | 0.497 | 24.3283 | -0.0002 | 90
STRL1- | STRL3A | 0.2008 | 17.6489 | -0.0003 | 120
STRL1- | STRL3B | 0.2009 | 17.7405 | -0.0003 | 120
STRL1- | STRL3C | 0.2021 | 17.6655 | -0.0003 | 120
STRW1- | STRW3- | 0.3634 | 17.5518 | -0.0002 | 90
TARL1J | TARL3- | 1.0755 | 40.9859 | -0.0216 | 30
TARL1K | TARL3- | 1.0396 | 39.6197 | -0.0261 | 30
TAYN1Q | TAYN3- | 0.3145 | 28.6983 | -0.0033 | 90
TAYN1R | TAYN3- | 0.3154 | 28.7872 | -0.0033 | 90
TEAL21 | TEAL11 | 0.3619 | 10.1602 | -0.0384 | 180
TEAL21 | TEAL11 | 0.2564 | 11.7305 | -0.0424 | 180
TEAL21 | TEAL11 | 0.5506 | 11.8761 | -0.0004 | 180
THUS11 | THUS3- | 0.2621 | 24.6736 | -0.0263 | 120
THUS11 | THUS3- | 0.2613 | 24.7403 | -0.0266 | 120
THUS21 | THUS11 | 0.0985 | 3.9363 | -0.0584 | 480
THUS21 | THUS11 | 0.1 | 3.9362 | -0.049 | 480
TOMT2J | TOMT11 | 0.098 | 3.905 | -0.0541 | 480
TOMT2K | TOMT11 | 0.0981 | 3.9384 | -0.0517 | 480
TUMB1Q | TUMB5- | 1.6295 | 77.7448 | -0.0986 | 21
TUMB1R | TUMB5- | 1.6066 | 76.6498 | -0.0986 | 21
TUMM2J | TUMM1J | 0.259 | 7.7457 | -0.0239 | 240
TUMM2K | TUMM1K | 0.2595 | 7.829 | -0.0229 | 240
VIKE1P | VIKE3P | 0.3704 | 11.1049 | -0.0003 | 135
VIKE1Q | VIKE3Q | 0.3704 | 11.1049 | -0.0003 | 135
VIKE1R | VIKE3R | 0.3704 | 11.1049 | -0.0003 | 135
VIKE1S | VIKE3S | 0.3704 | 11.1049 | -0.0003 | 135
WIOW1Q | WIOW3- | 0.8854 | 24.6508 | -0.0118 | 60
WIOW1R | WIOW3- | 0.8795 | 24.4842 | -0.0118 | 60
WOHI1Q | WOHI3- | 0.6199 | 27.2374 | -0.0494 | 90
WOHI1R | WOHI3- | 0.6099 | 27.3043 | -0.0494 | 90

## B-3-1b
B-3-1b - SPT Transformers for 2025/26
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
AREC1- | AREC3- | 0.4634 | 24.4456 | -0.0064 | 60
AREC1- | AREC3A | 0.3886 | 16.84 | -0.0241 | 90
AREC1- | AREC3B | 0.3915 | 16.7288 | -0.0227 | 90
AYR-2Q | AYR-3- | 0.4868 | 20.2441 | 0 | 120
AYR-2R | AYR-3- | 0.2752 | 25.1818 | -0.0142 | 120
BAGA1Q | BAGA3- | 0.741 | 27.0343 | 0 | 90
BAGA1R | BAGA3- | 0.741 | 27.2233 | 0 | 90
BAIN1Q | BAIN3- | 0.5545 | 26.2275 | -0.0056 | 60
BAIN1R | BAIN3- | 0.491 | 26.2454 | -0.0056 | 60
BENB1- | BENB3- | 0.2347 | 14.4814 | -0.011 | 120
BERW1Q | BERW3- | 0.9683 | 26.4656 | -0.0061 | 60
BERW1R | BERW3- | 0.7912 | 26.5549 | -0.0061 | 60
BLAH1- | BLAH3A | 0.3363 | 27.798 | -0.0152 | 90
BLAH1- | BLAH3A | 0.3386 | 27.9313 | -0.0106 | 90
BLAH1- | BLAH3B | 0.3394 | 27.9424 | -0.015 | 90
BLAH1- | BLAH3B | 0.342 | 28.0646 | -0.0103 | 90
BLCW1- | BLCW3- | 0.3083 | 16.9083 | -0.0283 | 90
BLKL1- | BLKL3A | 0.0943 | 18.6775 | 0 | 90
BLKL1- | BLKL3B | 0.0955 | 18.6553 | 0 | 90
BLLX1- | BLLX3- | 0.2833 | 16.8643 | -0.0133 | 90
BONN1- | BONN3- | 0.4288 | 27.1188 | -0.0146 | 90
BONN1- | BONN3- | 0.4334 | 27.5521 | -0.0092 | 90
BONN2A | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90
BROX1Q | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
BROX1R | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90
CAFA1Q | CAFA5R | 1.0894 | 32.6818 | 0 | 30
CATY1Q | CATY3- | 1.015 | 25.8801 | -0.1318 | 60
CATY1R | CATY3- | 0.4179 | 27.6524 | -0.0125 | 60
CCSS1- | CCSS3- | 0.273 | 13.8306 | -0.0276 | 120
CHAP1- | CHAP3- | 0.4338 | 27.5299 | -0.0175 | 90
CHAP1- | CHAP3- | 0.4294 | 27.5633 | -0.0188 | 90
CHAS2Q | CHAS3C | 0.4875 | 18.1601 | -0.1331 | 120
CHAS2R | CHAS3A | 0.5292 | 27.5616 | -0.1031 | 120
CLYM2- | CLYM3A | 0.4722 | 20.2028 | -0.1542 | 120
CLYM2- | CLYM3B | 0.4917 | 19.994 | -0.1425 | 120
CLYN2Q | CLYN3A | 0.3432 | 13.0038 | -0.0115 | 120
CLYN2Q | CLYN3B | 0.3423 | 12.9455 | -0.0108 | 120
CLYN2Q | CLYN3C | 0.3414 | 13.0205 | -0.0094 | 120
CLYN2Q | CLYN3D | 0.3472 | 12.9954 | -0.0133 | 120
CLYS2R | CLYS3A | 0.3406 | 12.9789 | -0.0112 | 120
CLYS2R | CLYS3B | 0.3475 | 13.0037 | -0.0112 | 120
COAL4- | COAL1A | 0.1055 | 6.777 | -0.0931 | 360
COAL4- | COAL1A | 0.1258 | 9.7909 | -0.0801 | 240
COAL4- | COAL1B | 0.1258 | 9.7909 | -0.0801 | 240
COAL4- | COAL1B | 0.0914 | 6.4382 | -0.0751 | 360
COAT2Q | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COAT2R | COAT3- | 0.2681 | 24.3152 | -0.021 | 120
COCK2- | COCK3- | 0.2841 | 27.8235 | -0.0171 | 120
COCK2- | COCK3- | 0.4792 | 18.7022 | -0.2214 | 120
COCK4Q | COCK2- | 0.0135 | 1.6479 | -0.3338 | 1000
COCK4R | COCK2- | 0.013 | 1.5999 | -0.2252 | 1000
COYL1- | COYL3- | 0.9944 | 20.8596 | -0.0881 | 60
COYL1- | COYL3- | 0.9217 | 21.6804 | 0 | 60
COYL2- | COYL1- | 0.1035 | 8.6744 | -0.051 | 240
COYL2- | COYL1- | 0.1036 | 8.7952 | -0.0513 | 240
CROO1Q | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1Q | CROO3K | 0.9748 | 26.6155 | -0.0058 | 60
CROO1R | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60
CROO1R | CROO3K | 0.9758 | 26.6321 | -0.0063 | 60
CRYR1- | CRYR31 | 0.2951 | 16.6641 | -0.2002 | 120
CRYR1- | CRYR32 | 0.2951 | 16.6641 | -0.2002 | 120
CRYR4- | CRYR1- | 0.1496 | 10.0489 | -0.0583 | 240
CRYR4- | CRYR1A | 0.1217 | 9.8451 | -0.067 | 240
CUMB1Q | CUMB3- | 0.7407 | 29.324 | -0.129 | 90
CUMB1R | CUMB3- | 0.741 | 27.111 | 0 | 90
CUMW1- | CUMW3- | 0.2341 | 14.4564 | -0.0113 | 120
CUPA1Q | CUPA3- | 0.4473 | 26.3962 | -0.0195 | 90
CUPA1R | CUPA3- | 0.4518 | 26.4517 | -0.0195 | 90
CURR1A | CURR5- | 3.225 | 79.0009 | 0 | 30
CURR1B | CURR5- | 3.23 | 79.0007 | 0 | 30
CURR2- | CURR1A | 0.1079 | 8.5702 | -0.0341 | 240
CURR2- | CURR1A | 0.1148 | 8.4492 | -0.073 | 240
CURR2- | CURR1B | 0.1205 | 8.4741 | -0.084 | 240
DALM1- | DALM3- | 0.447 | 27.333 | 0 | 90
DALM1- | DALM3- | 0.469 | 27.3326 | 0 | 90
DALM2Q | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DALM2R | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240
DENN2- | DENN1- | 0.1452 | 8.6093 | -0.1299 | 240
DENN4- | DENN2- | 0.0164 | 1.6449 | -0.1161 | 1000
DESA1Q | DESA3- | 0.2828 | 16.831 | -0.0195 | 90
DEVM1- | DEVM3- | 0.5537 | 26.9276 | -0.0087 | 60
DEVM4- | DEVM1- | 0.1335 | 8.3739 | -0.1562 | 240
DEVM4- | DEVM1- | 0.1338 | 8.3739 | -0.2103 | 240
DEVO1- | DEVO3- | 0.74 | 29.6674 | 0 | 90
DEVO1- | DEVO3- | 0.4705 | 26.4736 | -0.0191 | 90
DEWP2Q | DEWP3- | 0.2932 | 21.048 | -0.093 | 120
DEWP2R | DEWP3- | 0.2936 | 21.0667 | -0.079 | 120
DONO1- | DONO3A | 0.2348 | 14.4481 | -0.0068 | 120
DRCR1Q | DRCR3- | 0.5273 | 27.0838 | -0.0105 | 90
DRCR1R | DRCR3- | 0.5227 | 26.8727 | -0.0109 | 90
DRUM2Q | DRUM3- | 0.3963 | 23.9134 | -0.0247 | 120
DRUM2R | DRUM3- | 0.3917 | 24.4135 | -0.0224 | 120
DUMF1- | DUMF3A | 0.367 | 11.7276 | 0 | 90
DUMF1- | DUMF3B | 0.375 | 11.794 | 0 | 90
DUMF1- | DUMF3I | 0.766 | 20.5657 | 0 | 60
DUNB1Q | DUNB3A | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1R | DUNB3A | 0.8069 | 21.4849 | -0.3294 | 60
DUNB1S | DUNB3B | 0.4121 | 28.9304 | -0.0087 | 90
DUNB1T | DUNB3B | 0.3569 | 28.82 | -0.0089 | 90
DUNE1- | DUNE3- | 0.4271 | 19.5731 | -0.0091 | 90
DUNE1- | DUNE3- | 0.4249 | 19.3175 | -0.0084 | 90
DUNF1Q | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNF1R | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90
DUNH1S | DUNH3- | 0.3428 | 28.2868 | -0.0105 | 90
DUNH1T | DUNH3- | 0.3495 | 28.1867 | -0.0166 | 90
EAST1Q | EAST5- | 4.1511 | 74.885 | -0.1943 | 15
ECCL1- | ECCL3- | 1.054 | 26.8827 | 0 | 60
ECCL1- | ECCL3- | 1.04 | 26.7314 | 0 | 60
ECCL4A | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
ECCL4B | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240
EERH2- | EERH3- | 0.2569 | 25.607 | -0.0414 | 120
EERH2- | EERH3- | 0.306 | 18.0724 | -0.0486 | 120
EKIL2S | EKIL3A | 0.303 | 17.9224 | -0.0436 | 120
EKIL2T | EKIL3B | 0.303 | 17.8441 | -0.0485 | 120
EKIS2- | EKIS3A | 0.4948 | 24.3283 | -0.2487 | 120
EKIS2- | EKIS3B | 0.4773 | 24.2453 | -0.2651 | 120
ELDE1Q | ELDE3- | 0.9136 | 19.8123 | -0.3053 | 60
ELDE1R | ELDE3- | 0.9136 | 19.9791 | -0.3053 | 60
ELVA1- | ELVA3A | 0.5819 | 24.9432 | -0.0054 | 60
ELVA2R | ELVA1- | 0.0687 | 6.5302 | -0.7765 | 360
ELVA4- | ELVA2Q | 0.0309 | 3.2879 | -0.8983 | 500
ELVA4- | ELVA2R | 0.031 | 3.2859 | -0.8082 | 500
ENHI1- | ENHI3- | 0.3063 | 17.2084 | -0.0081 | 90
ERSK1Q | ERSK3- | 0.5259 | 26.8282 | -0.0075 | 60
ERSK1R | ERSK3- | 0.5296 | 27.1115 | -0.0073 | 60
EWEH1Q | EWEH3- | 0.2827 | 16.8532 | -0.0191 | 90
FALL4- | FALL3A | 0.2564 | 16.6647 | 0 | 120
FALL4- | FALL3B | 0.2564 | 16.6647 | 0 | 120
FINN1Q | FINN3- | 0.5198 | 26.0837 | -0.0091 | 90
FINN1R | FINN3- | 0.5221 | 25.9836 | -0.0092 | 90
GALA1- | GALA3- | 0.4311 | 25.9297 | -0.0244 | 90
GALA1- | GALA3- | 0.4452 | 26.6074 | -0.0132 | 90
GAWH1Q | GAWH3- | 0.2843 | 16.9754 | -0.0173 | 90
GIFF2Q | GIFF3A | 0.4557 | 30.1188 | -0.0331 | 90
GIFF2R | GIFF3B | 0.4868 | 18.3352 | -0.2147 | 120
GLGL1Q | GLGL3- | 0.3327 | 27.8536 | -0.0092 | 90
GLGL1R | GLGL3- | 0.3349 | 27.9091 | -0.0086 | 90
GLLE1- | GLLE5- | 2.3889 | 72.9609 | 0 | 30
GLLU1Q | GLLU3- | 0.961 | 24.5329 | 0 | 60
GLLU1R | GLLU3- | 1.069 | 25.0839 | 0 | 60
GLNI1- | GLNI3- | 0.6998 | 27.8134 | -0.1093 | 90
GLNI1- | GLNI3- | 0.6894 | 27.7692 | -0.1102 | 90
GLRO2- | GLRO3A | 0.479 | 24.4953 | 0 | 120
GLRO2- | GLRO3B | 0.4763 | 24.412 | 0 | 120
GORG1Q | GORG3- | 0.7875 | 26.555 | -0.0062 | 60
GORG1R | GORG3- | 0.8167 | 26.9876 | -0.0071 | 60
GOVA1Q | GOVA3- | 0.5223 | 26.1503 | -0.0083 | 90
GOVA1R | GOVA3- | 0.5155 | 26.1727 | -0.0108 | 90
GRMO2- | BPGR3J | 0.3876 | 19.4628 | -0.0275 | 120
GRMO2- | BPGR3K | 0.3093 | 18.8225 | -0.0373 | 120
GRMO2- | GRMO3C | 0.4781 | 25.1621 | -0.0871 | 120
GRMO2- | GRMO3C | 0.4985 | 25.2451 | -0.0869 | 120
GRNA4- | GRNA1- | 0.1472 | 10.0573 | -0.0558 | 240
GRNA4- | GRNA1- | 0.1252 | 9.7909 | -0.081 | 240
HADH1- | HADH3- | 0.438 | 13.3003 | 0 | 120
HAGR1Q | HAGR3- | 0.5381 | 25.2943 | -0.0108 | 60
HAGR1R | HAGR3- | 0.5478 | 25.8775 | -0.008 | 60
HARE1- | HARE3A | 0.2433 | 16.789 | -0.0205 | 90
HARE1- | HARE3B | 0.2411 | 16.8111 | -0.0205 | 90
HAWI1- | HAWI3- | 1.0278 | 25.6127 | -0.1152 | 60
HAWI1- | HAWI3- | 1.0136 | 25.8802 | -0.1316 | 60
HELE1Q | HELE3- | 0.9544 | 20.8615 | 0 | 60
HELE1R | HELE3- | 0.6843 | 28.6252 | -0.0082 | 60
HUER4- | HUER1- | 0.1122 | 9.3465 | -0.2007 | 360
HUER4- | HUER1- | 0.1134 | 9.4715 | -0.1992 | 360
HUNF1Q | HUNF3- | 0.8042 | 16.5638 | -0.06 | 60
HUNF1R | HUNF3- | 0.7893 | 16.4144 | -0.0596 | 60
HUNN4A | HUNN2A | 0.0538 | 2.9466 | -0.0947 | 240
HUNN4B | HUNN2B | 0.0537 | 2.9441 | -0.0946 | 240
INKE1Q | INKE3- | 0.6185 | 23.7697 | 0 | 90
INKE1R | INKE3- | 0.6222 | 23.7696 | 0 | 90
JOHN1Q | JOHN3- | 0.7058 | 27.8077 | -0.0092 | 60
JOHN1R | JOHN3- | 0.7078 | 27.9911 | -0.013 | 60
KAIM2- | KAIM3A | 0.4944 | 20.244 | -0.245 | 120
KAIM2- | KAIM3B | 0.4972 | 19.1602 | -0.2454 | 120
KEOO1- | KEOO5- | 2.9 | 71.608 | -0.028 | 30
KIER1Q | KIER3- | 0.4314 | 27.1188 | -0.0087 | 90
KIER1R | KIER3- | 0.7227 | 25.3341 | 0 | 90
KILB1Q | KILB3- | 0.9214 | 23.8656 | -0.6492 | 60
KILB1Q | KILB5- | 4.3575 | 97.6528 | -0.0539 | 20
KILB1R | KILB3- | 0.8919 | 23.8333 | -0.6287 | 60
KILB1R | KILB5- | 4.3825 | 97.2012 | -0.059 | 20
KILG2- | KILG3A | 0.1883 | 12.5319 | -0.0338 | 120
KILG2- | KILG3B | 0.1869 | 12.5153 | -0.028 | 120
KILG2- | KILG3C | 0.1866 | 12.4236 | -0.0359 | 120
KILS2- | KILS1- | 0.143 | 8.6447 | -0.1299 | 240
KILS2- | KILS3- | 0.4823 | 24.1619 | -0.2177 | 120
KILS2- | KILS3- | 0.5013 | 24.0114 | -0.1726 | 120
KILS4- | KILS2- | 0.018 | 1.6069 | -0.5085 | 1000
KILS4- | KILS2- | 0.0134 | 1.6649 | -0.5095 | 1000
KILS4T | KILS2- | 0.0148 | 1.6509 | -0.1193 | 1000
KILT2Q | KILT3A | 0.5309 | 28.5451 | -0.0524 | 120
KILT2R | KILT3A | 0.5379 | 28.745 | -0.0524 | 120
KILW1Q | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KILW1R | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90
KYPE1- | KYPE3- | 0.1922 | 14.207 | -0.0113 | 120
KYPE1- | KYPE3A | 0.3076 | 16.875 | -0.0289 | 90
LEVE1Q | LEVE3- | 0.979 | 20.6001 | 0 | 60
LEVE1R | LEVE3- | 0.944 | 20.7502 | 0 | 60
LING1Q | LING3- | 0.7346 | 29.6576 | -0.1478 | 90
LING1R | LING3- | 0.7309 | 28.7685 | -0.109 | 90
LINM1Q | LINM3- | 0.4309 | 27.7078 | -0.0186 | 90
LINM1R | LINM3- | 0.4283 | 27.73 | -0.0186 | 90
MAHI2- | MAHI1- | 0.1284 | 8.6824 | -0.2535 | 240
MAHI2- | MAHI3- | 0.2928 | 12.1973 | -0.0267 | 120
MAYB1- | MAYB3- | 1.84 | 33.2825 | 0 | 30
MAYB1- | MAYB3- | 1.84 | 34.3174 | 0 | 30
MIDM1- | KENE3- | 0.3875 | 17.9673 | -0.0311 | 70
MIDM1- | MIDM3- | 0.4664 | 13.6087 | -0.0075 | 60
MOFF1- | MOFF3A | 0.4635 | 24.1789 | -0.0101 | 60
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240
MOSH1Q | MOSH5J | 1.1896 | 19.9646 | 0 | 37
MOSH1R | MOSH5K | 1.1896 | 19.9646 | 0 | 37
MOSM1A | MOSM3Q | 1.4321 | 26.6282 | 0 | 45
MOSM1B | MOSM3R | 1.4321 | 26.6282 | 0 | 45
MOSM2- | MOSM1A | 0.151 | 8.332 | -0.1299 | 240
MOSM2- | MOSM1B | 0.157 | 8.7486 | -0.1299 | 240
NEAR2Q | NEAR3A | 0.4856 | 18.2435 | -0.1614 | 120
NEAR2R | NEAR3B | 0.4856 | 18.1602 | -0.1723 | 120
NECU2- | NECU1- | 0.1173 | 8.6992 | -0.0311 | 240
NECU2- | NECU1- | 0.1173 | 8.5659 | -0.0322 | 240
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0297 | 240
NECU2- | NECU1B | 0.1042 | 8.7827 | -0.0556 | 27
NECU2- | NECU1B | 0.1161 | 8.5534 | -0.0293 | 240
NECU2- | NECU1B | 0.1164 | 8.5534 | -0.0287 | 240
NECU2- | NECU1C | 0.0687 | 6.4941 | -0.0395 | 360
NECU2- | NECU1C | 0.0691 | 6.5052 | -0.0487 | 360
NEIL2- | NEIL1- | 0.1397 | 8.9572 | -0.0841 | 240
NEIL4Q | NEIL1C | 0.1122 | 9.3882 | -0.2007 | 360
NEIL4Q | NEIL2C | 0.0181 | 1.6169 | -0.4986 | 1000
NEIL4R | NEIL2D | 0.0133 | 1.6749 | -0.3581 | 1000
NETS1- | NETS3- | 0.8311 | 28.2878 | -0.0097 | 60
NOKY1- | NOKY3A | 0.2226 | 14.49 | -0.0076 | 120
NOKY1- | NOKY3B | 0.2344 | 14.3231 | -0.0107 | 120
PAIS1S | PAIS3- | 0.5609 | 26.1773 | -0.004 | 60
PAIS1T | PAIS3- | 0.7736 | 20.352 | -0.216 | 60
PART1Q | PART3- | 0.9103 | 21.2972 | 0 | 60
PART1R | PART3- | 0.93 | 21.5299 | 0 | 60
POOB2Q | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
POOB2R | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120
PORD2Q | PORD3- | 0.3702 | 18.3296 | -0.1621 | 120
PORD2R | PORD3- | 0.4559 | 30.0743 | -0.0337 | 90
REDH1- | REDH3- | 0.6267 | 27.5484 | 0 | 60
REDH1- | REDH3- | 0.94 | 20.7787 | 0 | 90
SACO1Q | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1Q | SACO3K | 0.9542 | 21.1451 | 0 | 60
SACO1R | SACO3J | 0.9444 | 24.4484 | 0 | 60
SACO1R | SACO3K | 0.9683 | 21.4114 | 0 | 60
SAKN1- | SAKN3- | 0.325 | 9.9364 | -0.0113 | 120
SANX1Q | SANX3- | 0.7366 | 27.1233 | -0.009 | 60
SANX1R | SANX3- | 0.7377 | 27.19 | -0.0098 | 60
SHRU2Q | SHRU3A | 0.535 | 28.5617 | -0.0629 | 120
SHRU2R | SHRU3B | 0.2914 | 23.7232 | -0.0252 | 120
SIGH2Q | SIGH3A | 0.4272 | 27.5522 | -0.032 | 180
SIGH2R | SIGH3A | 0.4296 | 27.53 | -0.0372 | 180
SMEA2- | SMEA1- | 0.1271 | 8.7241 | -0.043 | 240
SMEA4R | SMEA2- | 0.0134 | 1.6639 | -0.2312 | 1000
SPAV1Q | SPAV3- | 0.728 | 26.6656 | 0 | 90
SPAV1R | SPAV3- | 0.728 | 26.6656 | 0 | 90
STHA2A | STHA3- | 0.4557 | 30.1188 | -0.0331 | 90
STHA2B | STHA3- | 0.4917 | 19.994 | -0.1424 | 114
STHA4A | STHA2A | 0.018 | 1.7059 | -0.2252 | 1000
STHA4B | STHA2B | 0.0134 | 1.6949 | -2.0384 | 1000
STIR1S | STIR3- | 0.6 | 27.5446 | 0 | 90
STIR1T | STIR3- | 0.503 | 27.1331 | 0 | 90
STLE1Q | STLE3S | 0.4217 | 25.741 | -0.028 | 87
STLE1R | STLE3S | 0.4235 | 25.6743 | -0.0254 | 87
TELR1Q | TELR3- | 0.9688 | 26.4656 | -0.0572 | 60
TELR1R | TELR3- | 0.6325 | 28.5763 | -0.0081 | 60
TONG1- | TONG3- | 0.533 | 26.9114 | -0.0078 | 60
TONG1- | TONG3- | 0.5309 | 27.0615 | -0.008 | 60
TONG1- | TONG5- | 1.6834 | 33.9917 | -0.01 | 30
TONG1- | TONG5- | 1.6721 | 34.0924 | -0.0269 | 30
TONG1R | TONG1- | 0.0267 | 1.3331 | 0 | 90
TONG1R | TONG1Q | 0.0125 | 2.5 | 0 | 90
TORN4- | TORN1- | 0.1674 | 8.0399 | -0.0509 | 240
TORN4- | TORN1- | 0.1688 | 8.0816 | -0.0663 | 240
WESE1- | AIKE3A | 0.5667 | 13.2333 | 0 | 90
WESE1- | AIKE3B | 0.5667 | 13.2333 | 0 | 90
WFIE1A | WFIE3- | 0.6617 | 28.7591 | -0.0062 | 60
WFIE1B | WFIE3- | 0.6619 | 28.6257 | -0.0112 | 60
WFIE2- | WFIE1A | 0.1408 | 8.6113 | -0.1827 | 240
WFIE2- | WFIE1B | 0.1264 | 8.7366 | -0.1602 | 240
WGEO2Q | WGEO3- | 0.4889 | 18.2518 | -0.2083 | 120
WGEO2R | WGEO3- | 0.4557 | 30.1188 | -0.0331 | 120
WHHO2Q | WHHO3- | 0.4128 | 24.9549 | -0.0345 | 120
WHHO2R | WHHO3- | 0.5236 | 20.1599 | -0.1959 | 120
WHTL1S | WHTL3- | 2 | 27.1108 | 0 | 45
WHTL1T | WHTL3- | 2 | 27.1108 | 0 | 45
WISH2- | WISH1- | 0.1297 | 8.8874 | -0.2192 | 215
WISH2- | WISH3- | 0.4944 | 20.1606 | -0.2477 | 120
WISH2- | WISH3- | 0.4824 | 24.1285 | -0.2277 | 120
WISH2- | WISH3S | 0.4382 | 19.1617 | -0.195 | 120
WISH2- | WISH3T | 0.4889 | 18.3268 | -0.1166 | 120
WISH4- | WISH2- | 0.0163 | 1.6529 | -0.0792 | 1000
WISH4- | WISH2- | 0.0134 | 1.6849 | -0.0814 | 1000
WIYH2- | WIYH1- | 0.1568 | 8.4569 | -0.3494 | 240
WIYH2- | WIYH1- | 0.1524 | 8.457 | -0.3487 | 240
WIYH2- | WIYH1- | 0.0987 | 8.8078 | -0.0518 | 240
WIYH4Q | WIYH2- | 0.0133 | 1.6699 | -0.3581 | 1000
WLEE2- | WLEE3A | 0.2583 | 12.2648 | -0.0357 | 120
WLEE2- | WLEE3B | 0.2592 | 12.1922 | -0.0271 | 120
WLEE2- | WLEE3C | 0.26 | 12.3048 | -0.0301 | 120
WLEX2- | WLEX3A | 0.2306 | 12.2562 | -0.0292 | 120
WLEX2- | WLEX3B | 0.2306 | 12.2728 | -0.0271 | 120
WLEX2- | WLEX3C | 0.2306 | 12.2728 | -0.0275 | 120

## B-3-1c
B-3-1c - NGET Transformer for 2025/26
Node1 | Node2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
ABHA4A | ABHA11 | 0.1658 | 8.4025 | -1.5604 | 275
ABHA4B | ABHA12 | 0.1658 | 8.4025 | -1.5604 | 264
ABTH21 | ABTH11 | 0.1338 | 8.0531 | -0.1824 | 279
ABTH21 | ABTH12 | 0.1646 | 8.0383 | -0.1808 | 211
ABTH21 | ABTH13 | 0.0977 | 8.1994 | -1.7127 | 212
ALDW21 | ALDW31 | 0.4848 | 24.6692 | -0.018 | 135
ALDW21 | ALDW31 | 0.3543 | 25.4142 | -0.4983 | 135
ALDW21 | ALDW31 | 0.7076 | 26.5771 | -0.0784 | 83
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98
ALVE4A | ALVE11 | 0.1118 | 8.3874 | -0.0906 | 278
ALVE4B | ALVE11 | 0.1621 | 8.0984 | -0.0747 | 275
AMEM4A | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 270
AMEM4B | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 255
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 278
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 277
BARK21 | BARK11 | 0.1221 | 8.0449 | -0.2391 | 217
BARK21 | BARK11 | 0.093 | 8.3787 | -0.0308 | 240
BARK21 | BARW31 | 0.618 | 29.2635 | -0.2527 | 109
BARK21 | BARW32 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 278
BARK22 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 268
BARK22 | BARW31 | 0.618 | 29.2635 | -0.2527 | 110
BARK22 | BARW32 | 0.5135 | 18.2164 | -0.5477 | 100
BARK22 | BARW32 | 0.618 | 29.2635 | -0.2527 | 109
BARK41 | BARK21 | 0.0268 | 2.7989 | -0.3188 | 817
BARK41 | BARK22 | 0.0268 | 2.7989 | -0.3188 | 817
BEDD21 | BEDD11 | 0.1041 | 8.1035 | -0.0269 | 258
BEDD21 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 264
BEDD21 | BEDT1A | 0.1007 | 8.1333 | -0.2371 | 133
BEDD22 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 273
BEDD23 | BEDD11 | 0.1041 | 8.1035 | -0.0269 | 273
BEDD23 | BEDT1B | 0.2264 | 12.2479 | -0.6062 | 126
BEDD4A | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4A | BEDD23 | 0.0258 | 2.6799 | -1.2431 | 797
BEDD4B | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 800
BEDD4B | BEDD22 | 0.0211 | 2.6631 | -0.1477 | 950
BESW21 | BESW11 | 0.1004 | 8.1994 | -0.2371 | 240
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 273
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 267
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 267
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 278
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 274
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261
BISW21 | BISW11 | 0.1 | 8.0952 | -0.2374 | 278
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279
BISW21 | BISW11 | 0.0918 | 8.7537 | -0.0575 | 278
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 240
BLYT21 | BLYT1A | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT1B | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT61 | 0.2275 | 10.8456 | -0.0697 | 209
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138
BLYT41 | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1148
BLYT41 | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1148
BODE41 | SASA11 | 0.1311 | 7.9055 | -0.1016 | 240
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 310
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 309
BOLN41 | BOLN12 | 0.1557 | 8.3319 | -0.4146 | 276
BOLN41 | BOLN12 | 0.1264 | 8.4534 | -0.357 | 277
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 309
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278
BRAI4A | BRAI11 | 0.1057 | 8.1789 | -0.088 | 266
BRAI4B | BRAI11 | 0.1301 | 7.8864 | -0.4559 | 278
BRAW21 | BRAW11 | 0.1643 | 8.2692 | -0.5236 | 279
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 279
BRAW4A | BRAW21 | 0.0175 | 1.5879 | -4.0069 | 1094
BRED21 | BRED11 | 0.1057 | 7.8601 | -0.432 | 274
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278
BRFO41 | BRFO11 | 0.1123 | 8.3367 | -0.1053 | 272
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 271
BRFO41 | BRFO11 | 0.1307 | 7.9515 | -0.1098 | 240
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267
BRIM2A | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 263
BRIM2B | BRIM11 | 0.1266 | 8.6449 | -1.9406 | 274
BRIM2C | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIM2D | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 262
BRIN41 | BRIN21 | 0.0146 | 1.609 | -1.8746 | 1117
BRIN41 | BRIN22 | 0.0132 | 1.6756 | -0.4337 | 1117
BRLE41 | BRLE11 | 0.103 | 7.9231 | -0.0638 | 275
BRLE41 | BRLE12 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE13 | 0.1471 | 8.4008 | -0.1719 | 253
BRLE41 | BRLE14 | 0.103 | 7.9231 | -0.0638 | 270
BRLE41 | BRLE1A | 0.1303 | 7.8698 | -0.4285 | 263
BRLE41 | BRLE1B | 0.1303 | 7.8698 | -0.4285 | 263
BRWA41 | BRWA11 | 0.1123 | 8.3367 | -0.1053 | 240
BRWA42 | BRWA11 | 0.1123 | 8.3367 | -0.1053 | 240
BURW41 | BURW11 | 0.1059 | 8.3327 | -0.671 | 264
BURW41 | BURW11 | 0.1347 | 7.9905 | -0.1259 | 278
BURW41 | BURW11 | 0.1059 | 8.3327 | -0.671 | 264
BUSH21 | BUSH11 | 0.1221 | 8.0449 | -0.2391 | 279
BUSH21 | BUSH11 | 0.1221 | 8.0449 | -0.2391 | 279
BUSH21 | BUSH11 | 0.1048 | 8.8443 | -0.0335 | 278
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 279
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 279
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 278
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 279
BUST4A | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
BUST4B | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100
CANT41 | CANT13 | 0.1509 | 8.2849 | -0.3279 | 264
CANT41 | CANT14 | 0.1658 | 8.426 | -0.2939 | 264
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211
CAPE21 | CAPE11 | 0.196 | 8.3446 | -0.7059 | 198
CAPE21 | CAPE1A | 0.1221 | 8.0467 | -0.0391 | 279
CAPE21 | CAPE1B | 0.171 | 8.8392 | -0.0268 | 211
CAPE4A | CAPE21 | 0.0178 | 1.5995 | -1.2431 | 845
CAPE4B | CAPE21 | 0.0185 | 1.614 | -0.5638 | 886
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278
CARR21 | CARR11 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR11 | 0.1681 | 8.3396 | -1.4878 | 201
CARR21 | CARR12 | 0.1927 | 8.5256 | -0.5357 | 211
CARR21 | CARR12 | 0.2264 | 12.2479 | -0.6062 | 129
CARR21 | CARR12 | 0.2847 | 12.2467 | -1.4346 | 120
CARR41 | CARR11 | 0.1372 | 8.0197 | -0.1238 | 272
CARR4A | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CARR4B | CARR21 | 0.0185 | 1.614 | -0.5638 | 886
CELL41 | CELL11 | 0.1056 | 8.2208 | -0.6711 | 280
CELL41 | CELL11 | 0.1056 | 8.2208 | -0.6711 | 274
CELL41 | CELL11 | 0.1307 | 7.9515 | -0.1098 | 278
CELL41 | CELL12 | 0.1303 | 7.8698 | -0.4285 | 278
CELL41 | CELL12 | 0.1373 | 8.1976 | -0.1719 | 278
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 254
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 253
CHSI21 | CHSI11 | 0.0978 | 8.1332 | -0.0252 | 153
CHSI21 | CHSI11 | 0.0932 | 8.4078 | -0.0347 | 153
CHSI21 | CHSI1A | 0.167 | 7.9774 | -0.2092 | 255
CHSI21 | CHSI1B | 0.1411 | 8.6331 | -0.2264 | 249
CHTE21 | CHTE11 | 0.1 | 8.0952 | -0.2374 | 240
CHTE21 | CHTE11 | 0.1594 | 8.6081 | -0.2215 | 261
CHTE21 | CHTE12 | 0.0918 | 8.7537 | -0.0575 | 278
CHTE21 | CHTE12 | 0.1545 | 7.6337 | -0.562 | 251
CILF41 | CILF2A | 0.017 | 1.6132 | -5.1203 | 750
CILF41 | CILF2B | 0.017 | 1.6132 | -5.1203 | 750
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR11 | 0.1229 | 8.3873 | -0.1147 | 269
CITR41 | CITR12 | 0.1373 | 8.1976 | -0.1719 | 278
CITR41 | CITR12 | 0.0997 | 8.0088 | -0.093 | 266
CITR41 | CITR12 | 0.1264 | 7.974 | -0.1303 | 277
CONQ41 | CONQ11 | 0.1044 | 7.8701 | -0.103 | 261
CONQ41 | CONQ11 | 0.1036 | 7.8606 | -0.1003 | 259
CONQ41 | CONQ12 | 0.1045 | 7.8806 | -0.0998 | 263
CONQ41 | CONQ13 | 0.1264 | 8.4534 | -0.357 | 240
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 273
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 272
COVE21 | COVE12 | 0.1748 | 8.3565 | -0.2684 | 266
COVE21 | COVE12 | 0.1392 | 8.4361 | -0.781 | 279
COWL41 | COWL11 | 0.1307 | 7.9515 | -0.1098 | 278
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269
CREB41 | CREB12 | 0.1046 | 7.8493 | -0.0881 | 274
CREB41 | CREB21 | 0.0175 | 1.5799 | -0.1148 | 750
CREB41 | CREB21 | 0.0175 | 1.5799 | -0.1148 | 750
CREB41 | CREB22 | 0.0175 | 1.5799 | -0.1148 | 750
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253
CREB41 | CREB22 | 0.0176 | 1.5826 | -0.1148 | 750
CULJ4A | CULJ31 | 0.069 | 25 | 0 | 90
CULJ4A | CULJ32 | 0.069 | 25 | 0 | 90
CULJ4A | CULJ33 | 0.069 | 25 | 0 | 90
DIDC41 | DIDC31 | 0.2087 | 15.2319 | -0.0816 | 150
DIDC41 | DIDC31 | 0.2099 | 15.2986 | -0.0798 | 150
DRAK41 | DRAK11 | 0.1044 | 7.881 | -0.0832 | 272
DRAK41 | DRAK11 | 0.1303 | 7.8698 | -0.4285 | 278
DRAK41 | DRAK21 | 0.0178 | 1.5995 | -1.2431 | 849
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 277
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 274
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 206
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 206
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 440
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 440
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126
EASO41 | EASO12 | 0.103 | 7.9231 | -0.0638 | 263
EASO41 | EASO11 | 0.1018 | 7.841 | -0.432 | 274
EASO4A | EASO11 | 0.103 | 7.9231 | -0.0638 | 263
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 264
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 263
ECLA41 | ECLA12 | 0.1139 | 8.1036 | -2.059 | 278
ECLA41 | ECLA12 | 0.0997 | 8.0088 | -0.093 | 264
ELLA21 | ELLA11 | 0.1221 | 8.0449 | -0.2391 | 272
ELLA21 | ELLA11 | 0.1681 | 8.3396 | -1.4878 | 198
ELLA21 | ELLA12 | 0.1221 | 8.0467 | -0.0391 | 279
ELLA21 | ELLA12 | 0.1722 | 8.4551 | -0.2968 | 211
ELST21 | ELST12 | 0.1221 | 8.0467 | -0.0391 | 279
ELST21 | ELST13 | 0.1985 | 8.1167 | -0.4624 | 189
ELST21 | ELST13 | 0.1954 | 8.0796 | -0.2295 | 189
ELST21 | ELST14 | 0.1004 | 8.3615 | -0.2374 | 240
ELST22 | ELST11 | 0.1031 | 8.1045 | -0.0494 | 212
ELST41 | ELST12 | 0.1039 | 7.8456 | -0.9345 | 274
ELST41 | ELST22 | 0.0181 | 1.5835 | -3.6502 | 1201
ELST4B | ELST21 | 0.0176 | 1.5828 | -0.1018 | 1137
ENDE41 | ENDE11 | 0.1303 | 7.8698 | -0.4285 | 278
ENDE41 | ENDE11 | 0.1118 | 8.3874 | -0.0906 | 278
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 274
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 273
EXET41 | EXET11 | 0.1307 | 7.9515 | -0.1098 | 278
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 278
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 269
FAWL41 | FAWL11 | 0.105 | 8.1922 | -0.0663 | 269
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268
FECK21 | FECK61 | 0.3142 | 15.7855 | -1.1826 | 139
FECK41 | FECK21 | 0.0161 | 1.6372 | -0.1085 | 1189
FECK41 | FECK61 | 0.1832 | 14.0317 | -0.1803 | 199
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194
FERR21 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR21 | FERR61 | 0.237 | 10.8633 | -0.263 | 204
FERR23 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278
FERR23 | FERR61 | 0.237 | 10.8633 | -0.263 | 203
FERR2A | FERR11 | 0.0918 | 8.7537 | -0.0575 | 278
FERR4A | FERR22 | 0.0133 | 1.5936 | -1.2059 | 1100
FERR4A | FERR23 | 0.0186 | 1.5729 | -7.729 | 1113
FIDF21 | FIDF11 | 0.1392 | 8.4361 | -0.781 | 271
FIDF21 | FIDF12 | 0.1594 | 8.6081 | -0.2215 | 261
FLEE41 | FLEE11 | 0.1056 | 8.2208 | -0.6711 | 274
FLEE41 | FLEE11 | 0.1368 | 8.5406 | -0.262 | 232
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE11 | 0.1372 | 8.0197 | -0.1238 | 278
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279
FOUR21 | FOUR31 | 0.306 | 19.9977 | -0.5499 | 100
FOUR21 | FOUR71 | 1.255 | 65.8688 | -0.0404 | 45
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45
FROD21 | FROD11 | 0.1927 | 8.5256 | -0.5357 | 211
FROD22 | FROD11 | 0.1392 | 8.4361 | -0.781 | 269
FROD41 | FROD11 | 0.054 | 4.8906 | -0.1253 | 499
FROD41 | FROD21 | 0.0175 | 1.5799 | -0.1148 | 1000
FROD41 | FROD22 | 0.0132 | 1.6756 | -0.4337 | 1063
GRAI41 | GRAI11 | 0.1303 | 7.8698 | -0.4285 | 263
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 279
GREN41 | GREN11 | 0.1312 | 7.9156 | -0.537 | 278
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 278
GREN41 | GREN12 | 0.1035 | 7.8472 | -0.0758 | 274
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 279
GRIW41 | GRIW11 | 0.1658 | 8.4025 | -1.5604 | 273
GRIW41 | GRIW12 | 0.1658 | 8.4025 | -1.5604 | 268
HACK2A | HACK61 | 0.3231 | 13.4739 | -0.688 | 191
HACK2B | HACK61 | 0.2901 | 13.3302 | -0.6072 | 191
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278
HACK41 | HACK2A | 0.0182 | 1.5763 | -0.0904 | 1210
HACK41 | HACK2B | 0.0182 | 1.5763 | -0.0904 | 1210
HAMH41 | HAMH2A | 0.0175 | 1.5879 | -4.0069 | 1147
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 278
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 263
HARK21 | HARK11 | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK11 | 0.2264 | 12.2479 | -0.6062 | 137
HARK21 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK12 | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK13 | 0.1147 | 8.673 | -0.0358 | 222
HARK41 | HARK21 | 0.0192 | 2.6599 | -3.6035 | 751
HARK41 | HARK21 | 0.0292 | 2.402 | -0.2732 | 438
HARK41 | HARK21 | 0.0192 | 2.6599 | -3.6035 | 844
HARK41 | HARK21 | 0.0376 | 2.3797 | -3.9009 | 547
HARM21 | HARM61 | 0.3688 | 16.996 | -0.6416 | 127
HARM21 | HARM61 | 0.3688 | 16.996 | -0.6416 | 127
HAWP21 | HAWP61 | 0.3198 | 13.3295 | -0.6714 | 191
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 192
HAWP4A | HAWP21 | 0.0132 | 1.6756 | -0.4337 | 1063
HEYS41 | HEYS11 | 0.1372 | 8.0197 | -0.1238 | 278
HEYS41 | HEYS11 | 0.122 | 8.1963 | -0.2446 | 277
HEYS41 | HEYS11 | 0.1658 | 8.4025 | -1.5604 | 275
HIBU41 | ISLI11 | 0.1138 | 8.3534 | -0.0976 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240
HIGM41 | HIGM21 | 0.0186 | 1.5729 | -7.729 | 1044
HIGM41 | HIGM4A | 0.0002 | 0.2873 | 0 | 2750
HINP41 | HINP21 | 0.0376 | 2.3797 | -3.9009 | 539
HINP41 | HINP22 | 0.0376 | 2.3797 | -3.9009 | 539
HUMR41 | HUMR31 | 0.6667 | 22.467 | -0.1612 | 90
HUMR41 | HUMR31 | 0.6667 | 22.256 | -0.1612 | 90
HURS21 | HURS1B | 0.1221 | 8.0467 | -0.0391 | 279
HURS21 | HURS1C | 0.1441 | 8.6238 | -0.2707 | 279
HURS21 | HURS1D | 0.1392 | 8.4361 | -0.781 | 279
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 265
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 264
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 171
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 171
INDQ41 | INDQ11 | 0.1302 | 8.4532 | -10.3672 | 278
INDQ41 | INDQ11 | 0.1303 | 7.8698 | -0.4285 | 278
INDQ41 | INDQ11 | 0.1278 | 8.0061 | -0.2276 | 256
INDQ41 | INDQ11 | 0.1471 | 8.4008 | -0.1719 | 254
INDQ41 | INDQ31 | 0.2141 | 15.3985 | -0.0916 | 150
IROA21 | IROA11 | 0.1221 | 8.0449 | -0.2391 | 279
IROA21 | IROA11 | 0.1366 | 8.0648 | -0.0471 | 279
IROA21 | IROA12 | 0.1053 | 8.0652 | -0.0304 | 217
IROA21 | IROA12 | 0.1685 | 7.8148 | -1.385 | 210
IROA21 | IROA13 | 0.1266 | 8.6449 | -1.9406 | 250
IROA21 | IROA13 | 0.1685 | 7.8148 | -1.385 | 210
IRON41 | IRON11 | 0.1557 | 8.3736 | -0.4146 | 278
IRON41 | IRON12 | 0.1557 | 8.3736 | -0.4146 | 277
IRON41 | IRON13 | 0.158 | 8.362 | -2.2121 | 278
IVER21 | IVER11 | 0.136 | 8.0364 | -0.2504 | 279
IVER21 | IVER11 | 0.1145 | 8.0992 | -0.2495 | 279
IVER21 | IVER11 | 0.136 | 8.0364 | -0.2504 | 265
IVER21 | IVER61 | 0.2156 | 10.909 | -0.0589 | 153
IVER21 | IVER61 | 0.6246 | 18.124 | -9.5679 | 125
IVER21 | IVER61 | 0.4958 | 18.1599 | -9.5679 | 125
IVER22 | IVER11 | 0.136 | 8.0364 | -0.2504 | 279
IVER22 | IVER61 | 0.2124 | 10.9368 | -0.1254 | 153
IVER4A | IVER21 | 0.0176 | 1.5828 | -0.1018 | 1135
IVER4A | IVER22 | 0.0133 | 1.5936 | -1.2059 | 1100
IVER4B | IVER21 | 0.0326 | 2.3798 | -3.9003 | 572
IVER4B | IVER2A | 0.0132 | 1.4627 | -2.0624 | 841
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110
KEAD41 | KEAD11 | 0.1621 | 8.2484 | -0.0747 | 256
KEAD41 | KEAD11 | 0.1056 | 8.2208 | -0.6711 | 274
KEAD42 | KEAD11 | 0.1118 | 8.3874 | -0.0906 | 278
KEAD4C | KEAD41 | 0.0002 | 0.4178 | 0 | 2750
KEAD4D | KEAD41 | 0.0002 | 0.2873 | 0 | 2750
KEAR21 | KEAR11 | 0.1041 | 8.1035 | -0.0269 | 280
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96
KEAR41 | KEAR21 | 0.0117 | 1.591 | -4.4806 | 1098
KEAR41 | KEAR21 | 0.0175 | 1.5879 | -4.0069 | 1000
KEMS41 | KEMS11 | 0.1658 | 8.426 | -0.2939 | 268
KEMS41 | KEMS11 | 0.1139 | 8.1036 | -2.059 | 264
KEMS41 | KEMS4A | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | KEMS4B | 0.0071 | 0.2875 | 0 | 2750
KEMS41 | SHEE11 | 0.1621 | 8.0984 | -0.0747 | 236
KIBY21 | KIBY11 | 0.1221 | 8.0449 | -0.2391 | 279
KIBY21 | KIBY11 | 0.1221 | 8.0449 | -0.2391 | 279
KIBY21 | KIBY11 | 0.1392 | 8.4361 | -0.781 | 279
KIBY21 | KIBY11 | 0.1594 | 8.6081 | -0.2215 | 261
KIBY21 | KIBY11 | 0.1681 | 8.3396 | -1.4878 | 211
KINO41 | KINO11 | 0.1303 | 7.8698 | -0.4285 | 278
KINO41 | KINO11 | 0.1056 | 8.2208 | -0.6711 | 274
KIRK21 | KIRK11 | 0.1221 | 8.0467 | -0.0391 | 279
KIRK21 | KIRK11 | 0.1147 | 8.673 | -0.0358 | 264
KIRK21 | KIRK11 | 0.097 | 8.0997 | -0.027 | 266
KIRK21 | KIRK2A | 0.002 | 0.9802 | 0 | 760
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279
KNAR21 | KNAR11 | 0.0981 | 8.0536 | -0.0541 | 280
KNAR21 | KNAR11 | 0.0993 | 8.0911 | -0.031 | 280
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 128
LACK21 | LACK61 | 0.4736 | 16.5344 | -0.54 | 126
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 126
LACK41 | LACK21 | 0.0175 | 1.5879 | -4.0069 | 1100
LACK41 | LACK21 | 0.0174 | 1.598 | -0.1503 | 1154
LACK41 | LACK2A | 0.0152 | 1.6463 | -0.1118 | 1185
LACK41 | LACK2B | 0.0182 | 1.5763 | -0.0904 | 1210
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278
LALE21 | LALE11 | 0.1954 | 8.0796 | -0.2295 | 201
LALE21 | LALE11 | 0.196 | 8.3446 | -0.7059 | 200
LAND41 | LAND11 | 0.1372 | 8.0197 | -0.1238 | 278
LAND41 | LAND11 | 0.148 | 7.4973 | -0.3849 | 278
LAND42 | LAND11 | 0.1057 | 7.9352 | -0.339 | 263
LEGA41 | LEGA11 | 0.1303 | 7.8698 | -0.4285 | 278
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278
LEGA41 | LEGA11 | 0.1175 | 8.6648 | -0.4173 | 263
LEGA4A | LEGA41 | 0.001 | 0.35 | 0 | 2002
LEGA4B | LEGA41 | 0.001 | 0.35 | 0 | 2002
LEIS4A | LEIS11 | 0.1057 | 7.8601 | -0.432 | 272
LISD21 | LISD11 | 0.1221 | 8.0467 | -0.0391 | 279
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266
LISD21 | LISD11 | 0.1266 | 8.6449 | -1.9406 | 262
LITT41 | LITT11 | 0.1621 | 8.0984 | -0.0747 | 240
LITT41 | LITT11 | 0.0997 | 8.0088 | -0.093 | 240
LITT41 | LITT11 | 0.103 | 7.9231 | -0.0638 | 278
LITT41 | LITT2A | 0.014 | 2.6567 | -0.1528 | 1028
LITT41 | LITT2B | 0.014 | 2.6567 | -0.1528 | 1028
LOVE41 | LOVE11 | 0.1303 | 7.8698 | -0.4285 | 278
LOVE41 | LOVE11 | 0.1042 | 7.831 | 0 | 274
LOVE41 | LOVE12 | 0.1046 | 7.8493 | -0.0881 | 274
LOVE41 | LOVE12 | 0.1847 | 8.1296 | -0.2979 | 269
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113
MACC41 | MACC21 | 0.018 | 1.6146 | -1.5533 | 884
MAGA21 | GRAN61 | 0.1642 | 10.921 | -0.0326 | 207
MAGA21 | GRAN61 | 0.1757 | 10.5541 | -0.0326 | 205
MANN41 | MANN11 | 0.1459 | 8.045 | -0.2605 | 279
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272
MANN41 | MANN11 | 0.1326 | 8.774 | -0.7141 | 259
MANN41 | MANN11 | 0.1303 | 7.8698 | -0.4285 | 278
MELK41 | MELK11 | 0.119 | 8.3617 | -1.9877 | 278
MELK41 | MELK11 | 0.1041 | 7.8535 | -0.0851 | 265
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278
MELK41 | MELK2A | 0.017 | 1.6132 | -5.1203 | 750
MELK41 | MELK2B | 0.021 | 1.6919 | -12.3815 | 886
MILH2A | MILH11 | 0.179 | 8.3648 | -4.7616 | 211
MILH2A | MILH11 | 0.1266 | 8.6449 | -1.9406 | 264
MILH2B | MILH12 | 0.1004 | 8.1994 | -0.2371 | 240
MILH2B | MILH12 | 0.1266 | 8.6449 | -1.9406 | 264
MITY41 | MITY11 | 0.1375 | 7.9905 | -0.1246 | 278
MITY41 | MITY11 | 0.122 | 8.1963 | -0.2446 | 274
MITY41 | MITY12 | 0.1044 | 7.8701 | -0.103 | 274
MITY41 | MITY12 | 0.1812 | 9.1787 | -0.1253 | 278
MITY41 | MITY31 | 0.2087 | 15.2319 | -0.2971 | 150
MITY41 | MITY31 | 0.2087 | 15.2319 | -0.2971 | 150
MITY41 | MITY31 | 0.2087 | 15.2319 | -0.2971 | 150
MONF41 | MONF21 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF41 | MONF22 | 0.0181 | 1.6409 | -0.1418 | 1100
MONF4A | MONF21 | 0.0176 | 1.5828 | -0.1018 | 1138
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 270
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 269
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 270
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 267
NEEP21 | NEEP31 | 0.4243 | 23.4128 | -0.2038 | 120
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120
NEEP4A | NEEP21 | 0.0133 | 1.5936 | -1.2059 | 1100
NEWX21 | NEWX11 | 0.1053 | 8.0451 | -0.0277 | 280
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 279
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 279
NEWX21 | NEWX61 | 0.2188 | 10.8367 | -0.1908 | 180
NEWX21 | NEWX61 | 0.3204 | 14.3298 | -0.2424 | 180
NEWX21 | NEWX62 | 0.1868 | 10.9484 | -0.0207 | 207
NEWX21 | NEWX62 | 0.2972 | 12.4333 | -0.1533 | 209
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 268
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 261
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 269
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 260
NHYD2A | NHYD61 | 0.3061 | 13.2187 | -0.4552 | 187
NHYD2B | NHYD61 | 0.3061 | 13.2187 | -0.4552 | 187
NHYD2B | NHYD61 | 0.2364 | 13.3312 | -0.1929 | 180
NINF41 | NINF11 | 0.1303 | 7.8698 | -0.4285 | 278
NINF41 | NINF11 | 0.1658 | 8.4025 | -1.5604 | 273
NINF41 | NINF12 | 0.1054 | 7.888 | -0.0861 | 259
NINF41 | NINF12 | 0.1658 | 8.4025 | -1.5604 | 273
NORL2A | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORL2B | NORL31 | 0.545 | 19.7925 | -0.1407 | 114
NORM41 | NORM11 | 0.1303 | 7.8698 | -0.4285 | 240
NORM41 | NORM11 | 0.1264 | 8.4534 | -0.357 | 277
NORM41 | NORM12 | 0.1118 | 8.3874 | -0.0906 | 278
NORM41 | NORM1A | 0.1509 | 7.9378 | -0.9251 | 253
NORM41 | NORM1B | 0.1509 | 7.9378 | -0.9251 | 267
NORM41 | NORM31 | 0.2331 | 15.3182 | -0.0967 | 150
NORT21 | NORT11 | 0.1041 | 8.1035 | -0.0269 | 240
NORT21 | NORT11 | 0.0964 | 8.0828 | -0.0344 | 280
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262
NORT41 | NORT21 | 0.0186 | 1.5729 | -7.729 | 1136
NORT41 | NORT21 | 0.0117 | 1.591 | -4.4806 | 1133
NURS41 | NURS11 | 0.1307 | 8.3156 | -0.7141 | 252
NURS41 | NURS11 | 0.1307 | 8.3156 | -0.7141 | 253
NURS4A | NURS11 | 0.1003 | 7.916 | -0.065 | 262
OCKH21 | OCKH11 | 0.1221 | 8.0449 | -0.2391 | 279
OCKH21 | OCKH11 | 0.1221 | 8.0449 | -0.2391 | 279
OCKH21 | OCKH11 | 0.179 | 8.3648 | -4.7616 | 202
OCKH21 | OCKH2A | 0.0104 | 0.867 | -4.0354 | 760
OFFE21 | OFFE31 | 0.5135 | 18.2228 | -0.5477 | 115
OFFE21 | OFFE32 | 0.593 | 20.7915 | -0.122 | 113
OLDB21 | OLDB11 | 0.0985 | 8.1944 | -0.0158 | 240
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261
OLDB2A | OLDB11 | 0.1004 | 8.3615 | -0.2374 | 261
OLDB4A | OLDB21 | 0.0107 | 1.5596 | -0.0734 | 1172
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269
OSBA42 | OSBA11 | 0.1372 | 8.0197 | -0.1238 | 278
PADI41 | PADI11 | 0.1064 | 8.1768 | -0.0914 | 274
PADI41 | PADI11 | 0.1051 | 7.8585 | -0.0834 | 262
PELH41 | PELH11 | 0.1175 | 8.6648 | -0.4173 | 264
PELH41 | PELH12 | 0.1175 | 8.6648 | -0.4173 | 264
PEMB41 | PEMB11 | 0.1658 | 8.4025 | -1.5604 | 276
PEMB41 | PEMB11 | 0.1471 | 8.4008 | -0.1719 | 275
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1441 | 8.6238 | -0.2707 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266
PENN4A | PENN21 | 0.0176 | 1.5828 | -0.1018 | 1138
PENN4B | PENN21 | 0.0132 | 1.6756 | -0.4337 | 1063
PENT41 | PENT11 | 0.1307 | 8.3156 | -0.7141 | 257
PENT41 | PENT11 | 0.1621 | 8.0984 | -0.0747 | 255
PEWO2A | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO2B | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265
PEWO41 | PENW11 | 0.1311 | 7.9055 | -0.1016 | 278
PEWO41 | PEWO2A | 0.0182 | 1.5763 | -0.0904 | 1129
PEWO41 | PEWO2A | 0.0178 | 1.5995 | -1.2431 | 845
PEWO41 | PEWO2B | 0.0175 | 1.5879 | -4.0069 | 1139
PEWO41 | PEWO2B | 0.021 | 1.669 | -12.6082 | 876
PEWO41 | PEWO4A | 0.0046 | 0.2858 | -16.2245 | 2750
PEWO41 | PEWO4B | 0.0071 | 0.2875 | -16.2245 | 2750
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120
POPP21 | POPP31 | 0.335 | 30.5815 | -0.0453 | 110
POPP21 | POPP31 | 0.2731 | 30.5821 | -0.0312 | 110
PYLE21 | PYLE11 | 0.1221 | 8.0467 | -0.0391 | 279
PYLE21 | PYLE11 | 0.2009 | 8.1596 | -0.5003 | 211
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 270
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 273
RATS41 | RATS11 | 0.1042 | 7.841 | -0.0895 | 274
RATS41 | RATS11 | 0.1047 | 8.2285 | -0.0886 | 262
RATS41 | RATS12 | 0.1373 | 8.1976 | -0.1719 | 278
RATS41 | RATS12 | 0.1278 | 8.0061 | -0.2276 | 277
RATS41 | RATS2A | 0.0146 | 1.609 | -1.8746 | 1125
RAYL41 | RAYM11 | 0.1045 | 7.8618 | -0.0882 | 271
RAYL41 | RAYM11 | 0.1303 | 7.8698 | -0.4285 | 262
RAYL41 | RAYM11 | 0.1035 | 7.8568 | -0.0758 | 271
RAYL41 | RAYM11 | 0.1309 | 7.8656 | -0.4549 | 262
REBR21 | REBR32 | 0.665 | 28.1922 | -0.151 | 111
REBR22 | REBR31 | 0.3375 | 30.6481 | -0.1769 | 132
REBR22 | REBR31 | 0.665 | 28.1922 | -0.151 | 112
RICH41 | RICH11 | 0.1186 | 7.8741 | -0.456 | 240
RICH41 | RICH11 | 0.1181 | 7.9033 | -0.4117 | 240
ROCH21 | ROCH11 | 0.1183 | 8.3928 | -0.0783 | 278
ROCH21 | ROCH11 | 0.1183 | 8.3928 | -0.0783 | 278
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278
ROCH21 | ROCH12 | 0.0926 | 8.387 | -0.0404 | 240
ROCH4A | ROCH21 | 0.0098 | 1.5863 | -0.0631 | 1100
ROCK41 | ROCK1A | 0.054 | 4.8906 | -0.1253 | 460
RUGE41 | RUGE11 | 0.1147 | 8.1595 | -1.9621 | 267
RUGE41 | RUGE11 | 0.1147 | 8.1595 | -1.9621 | 267
RYEH41 | RYEH13 | 0.1372 | 8.0197 | -0.1238 | 253
RYEH42 | RYEH12 | 0.1055 | 8.2414 | -0.0848 | 267
RYEH43 | RYEH11 | 0.1326 | 8.774 | -0.7141 | 260
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211
SAFO41 | SAFO11 | 0.1054 | 8.1656 | -0.1095 | 240
SAFO41 | SAFO11 | 0.1054 | 8.1606 | -0.1098 | 240
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256
SELL4A | SELL11 | 0.0996 | 8.0568 | -1.1981 | 275
SELL4A | SELL11 | 0.0996 | 8.0568 | -1.1981 | 273
SELL4A | SELL12 | 0.103 | 7.9231 | -0.0638 | 270
SELL4A | SELL13 | 0.1621 | 8.0984 | -0.0747 | 256
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 115
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 114
SHRE4B | SHRE11 | 0.1068 | 7.9576 | -0.1072 | 240
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 267
SIZE41 | SIZE12 | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE1A | 0.103 | 7.9231 | -0.0638 | 268
SIZE41 | SIZE1B | 0.103 | 7.9231 | -0.0638 | 269
SJOW21 | LODR61 | 0.3062 | 11.0235 | -0.4552 | 198
SJOW21 | SJOW13 | 0.1845 | 7.8956 | -0.1938 | 249
SJOW41 | LODR61 | 0.1529 | 12.1324 | -0.0623 | 273
SJOW41 | LODR61 | 0.1403 | 12.3367 | -0.6356 | 240
SJOW41 | LODR62 | 0.1455 | 13.3242 | -0.0759 | 265
SJOW41 | LODR62 | 0.1307 | 7.9515 | -0.1098 | 240
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 271
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 272
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 270
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 271
SJOW41 | SJOW13 | 0.1055 | 8.1881 | -0.0865 | 274
SJOW41 | SJOW21 | 0.0224 | 2.5703 | -0.5831 | 804
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 278
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 270
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 240
SMAN21 | SMAN11 | 0.1221 | 8.0449 | -0.2391 | 279
SMAN21 | SMAN11 | 0.1441 | 8.6238 | -0.2707 | 266
SMAN21 | SMAN12 | 0.1441 | 8.6238 | -0.2707 | 266
SMAN21 | SMAN12 | 0.1221 | 8.0467 | -0.0391 | 279
SPEN41 | SPEN11 | 0.1293 | 7.8614 | -0.537 | 278
SPEN41 | SPEN11 | 0.1305 | 7.8823 | -0.5369 | 278
SPEN42 | SPEN11 | 0.1315 | 7.8822 | -0.5369 | 278
SSHI22 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
SSHI22 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110
STAH4A | STAH11 | 0.1056 | 8.2208 | -0.6711 | 274
STAH4B | STAH11 | 0.1046 | 7.8493 | -0.0881 | 271
STAL21 | STAL11 | 0.0964 | 8.0828 | -0.0344 | 280
STAL21 | STAL11 | 0.1221 | 8.0449 | -0.2391 | 279
STAL21 | STAL11 | 0.1681 | 8.3396 | -1.4878 | 198
STAL21 | STAL11 | 0.1954 | 8.0796 | -0.2295 | 189
STAL4A | STAL21 | 0.0146 | 1.609 | -1.8746 | 1117
STAY41 | STAY4A | 0.0002 | 0.4178 | -13.831 | 2695
STAY41 | STYC11 | 0.103 | 7.9231 | -0.0638 | 266
STAY41 | STYC12 | 0.1046 | 7.8493 | -0.0881 | 271
STEW21 | STEN11 | 0.0933 | 8.4245 | -0.0402 | 179
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 138
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.1221 | 8.0467 | -0.0391 | 274
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137
STEW41 | STEW21 | 0.0107 | 1.5596 | -0.0734 | 1172
STEW41 | STEW21 | 0.0107 | 1.5596 | -0.0734 | 1165
STOB41 | STOB11 | 0.1057 | 7.8601 | -0.432 | 274
STOB41 | STOB11 | 0.1057 | 7.8601 | -0.432 | 271
STSB4B | STSB4A | 0.0003 | 0.1825 | 0 | 1999
SUND41 | SUND11 | 0.13 | 7.8739 | -0.4746 | 278
SUND41 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 252
SUND41 | SUND31 | 0.2106 | 15.2133 | -0.0768 | 150
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 254
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 250
SWAN22 | SWAN11 | 0.179 | 6.6532 | -4.7616 | 211
SWAN22 | SWAN11 | 0.1923 | 8.2361 | -0.4425 | 211
SWAN41 | SWAN11 | 0.1303 | 7.8698 | -0.4285 | 256
SWAN41 | SWAN12 | 0.1303 | 7.8698 | -0.4285 | 256
SWAN41 | SWAN21 | 0.0182 | 1.5763 | -0.0904 | 1210
SWAN4A | SWAN22 | 0.0178 | 1.5995 | -1.2431 | 851
SWAN4B | SWAN12 | 0.1307 | 7.9515 | -0.1098 | 263
TAUN41 | TAUN11 | 0.1049 | 8.1792 | -0.1104 | 274
TAUN42 | TAUN11 | 0.1459 | 8.045 | -0.2605 | 279
TEMP21 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
TEMP22 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76
THOM21 | THOM61 | 0.3985 | 16.203 | -0.4431 | 122
THOM41 | THOM21 | 0.0186 | 1.5729 | -7.729 | 879
THOM41 | THOM21 | 0.0185 | 1.614 | -0.5638 | 879
THOM42 | THOM2A | 0.0133 | 1.5936 | -1.2059 | 1100
THOM42 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209
THUR21 | THUR61 | 0.1699 | 10.8431 | -0.0403 | 200
TILB21 | TILB11 | 0.1381 | 7.9571 | -0.0844 | 240
TILB21 | TILB12 | 0.1 | 8.0952 | -0.2374 | 240
TILB41 | TILB13 | 0.1004 | 8.1994 | -0.2371 | 240
TILB41 | TILB14 | 0.1303 | 7.8698 | -0.4285 | 278
TILB4A | TILB21 | 0.0376 | 2.1949 | -10.6848 | 829
TILB4B | TILB21 | 0.0117 | 1.591 | -4.4806 | 1102
TINP21 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111
TINP21 | TINP32 | 0.3028 | 23.5814 | -0.4756 | 135
TINP22 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111
TINP22 | TINP32 | 0.3028 | 23.5814 | -0.4756 | 120
TODP21 | TODP61 | 0.3931 | 16.5106 | -2.1281 | 139
TODP21 | TODP61 | 0.3931 | 16.6317 | -0.6202 | 101
TOTT21 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TOTT22 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265
TOTT23 | TOTT12 | 0.1688 | 8.3316 | -1.1711 | 265
TOTT24 | TOTT12 | 0.179 | 8.3648 | -4.7616 | 198
TRAW21 | TRAW11 | 0.0998 | 8.1961 | -0.0206 | 176
TRAW21 | TRAW11 | 0.0937 | 8.437 | -0.1095 | 150
TRAW41 | TRAW21 | 0.0132 | 1.6756 | -0.4337 | 966
TRAW41 | TRAW21 | 0.021 | 1.669 | -12.6082 | 888
TREM21 | TREM31 | 0.4636 | 17.894 | -0.1238 | 116
TREM21 | TREM31 | 0.593 | 20.7915 | -0.122 | 115
TYNE21 | TYNE11 | 0.1221 | 8.0449 | -0.2391 | 279
TYNE21 | TYNE11 | 0.1411 | 8.6331 | -0.2264 | 267
TYNE21 | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
TYNE2A | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44
UPPB21 | UPPB31 | 0.4636 | 17.894 | -0.1238 | 113
UPPB21 | UPPB31 | 0.5107 | 17.9527 | -0.2251 | 113
UPPB22 | UPPB11 | 0.0979 | 8.4411 | -0.0271 | 262
UPPB22 | UPPB11 | 0.097 | 8.457 | -0.0263 | 222
USKM21 | ALST31 | 0.5135 | 18.2228 | -0.5477 | 116
USKM21 | ALST32 | 0.5107 | 17.9527 | -0.2251 | 116
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 263
USKM21 | USKM11 | 0.1145 | 8.1367 | -0.2304 | 279
USKM21 | USKM12 | 0.1145 | 8.1367 | -0.2304 | 263
WALH41 | PORH11 | 0.1307 | 8.3156 | -0.7141 | 253
WALH41 | PORH11 | 0.103 | 7.9231 | -0.0638 | 275
WALH41 | PORH11 | 0.1372 | 8.0197 | -0.1238 | 278
WALH41 | PORH11 | 0.1036 | 7.8597 | -0.0784 | 274
WALP41 | WALP11 | 0.1057 | 7.8601 | -0.432 | 274
WALP41 | WALP11 | 0.1304 | 7.9364 | -0.479 | 278
WALP41 | WALP11 | 0.1509 | 8.2849 | -0.3279 | 275
WALP41 | WALP11 | 0.1621 | 8.0984 | -0.0747 | 275
WALP41 | WALP11 | 0.1759 | 7.9134 | -0.4285 | 274
WALX4A | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4A | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1136
WALX4B | WALX21 | 0.0176 | 1.5828 | -0.1018 | 1137
WALX4B | WALX22 | 0.0176 | 1.5828 | -0.1018 | 1137
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 264
WASF2A | WASF1A | 0.197 | 7.9698 | -0.2553 | 207
WASF2B | WASF1B | 0.197 | 7.9698 | -0.2553 | 207
WATS21 | WATS11 | 0.1441 | 8.6238 | -0.2707 | 279
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 127
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 126
WATS22 | WATS11 | 0.1392 | 8.4361 | -0.781 | 266
WATS22 | WATS11 | 0.1923 | 8.081 | -1.4418 | 189
WBOL21 | WBOL61 | 0.1868 | 10.9484 | -0.0207 | 180
WBOL21 | WBOL61 | 0.4736 | 16.5344 | -0.54 | 134
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 127
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 127
WBUR41 | WBUR11 | 0.1056 | 8.2208 | -0.6711 | 274
WBUR42 | WBUR11 | 0.1175 | 8.6648 | -0.4173 | 263
WBUR42 | WBUR12 | 0.1175 | 8.6648 | -0.4173 | 265
WHAM41 | WHAM11 | 0.1068 | 7.9576 | -0.1072 | 263
WHAM41 | WHAM11 | 0.1057 | 7.9352 | -0.339 | 264
WHAM41 | WHAM12 | 0.0997 | 8.0088 | -0.093 | 271
WHAM41 | WHAM12 | 0.1057 | 7.9352 | -0.339 | 263
WHAM41 | WHAM4A | 0.001 | 0.35 | 0 | 2000
WHAM41 | WHAM4B | 0.001 | 0.35 | 0 | 2000
WHGA21 | WHGA11 | 0.1 | 8.0952 | -0.2374 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279
WHSO21 | WHSO2A | 0.005 | 0.463 | 0 | 750
WHSO21 | WHSO31 | 0.4435 | 14.3532 | -0.577 | 100
WHSO21 | WHSO31 | 0.4435 | 14.3532 | -0.577 | 100
WHSO21 | WHSO32 | 0.4435 | 14.3131 | -0.577 | 100
WHSO22 | WHSO2B | 0.005 | 0.463 | 0 | 750
WHSO22 | WHSO32 | 0.4435 | 14.3532 | -0.577 | 100
WHSO41 | WHSO22 | 0.0185 | 1.614 | -0.5638 | 886
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114
WIEN2A | WIEN11 | 0.1 | 8.1202 | -0.2373 | 240
WIEN2B | WIEN11 | 0.1366 | 8.0648 | -0.0471 | 279
WILE41 | WILL11 | 0.1056 | 8.2208 | -0.6711 | 253
WILE41 | WILL11 | 0.1046 | 7.8493 | -0.0881 | 271
WILE41 | WILL11 | 0.1303 | 7.8698 | -0.4285 | 269
WILE41 | WILL12 | 0.1035 | 8.3458 | -0.0962 | 278
WILT2A | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2B | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207
WILT2C | GRST61 | 0.2275 | 10.8456 | -0.0697 | 198
WILT2D | GRST61 | 0.2972 | 12.4333 | -0.1533 | 206
WIMB41 | WIMB11 | 0.1354 | 7.753 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1366 | 7.753 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240
WIMB41 | WIMB21 | 0.0187 | 2.6578 | -0.1527 | 950
WIMB41 | WIMB21 | 0.0187 | 2.6578 | -0.1527 | 950
WISD21 | WISD11 | 0.1 | 8.0952 | -0.2374 | 240
WISD21 | WISD11 | 0.0932 | 8.3661 | -0.0408 | 240
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 240
WISD21 | WISD2A | 0.002 | 0.6673 | 0 | 750
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 201
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200
WISD41 | WISD21 | 0.0188 | 2.6115 | -1.4373 | 949
WISD42 | WISD21 | 0.019 | 2.602 | -1.3261 | 949
WMEL21 | WMEL11 | 0.2889 | 13.4969 | -0.3904 | 130
WMEL21 | WMEL11 | 0.2925 | 13.4802 | -0.528 | 130
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199
WMEL21 | WMEL12 | 0.1923 | 8.2361 | -0.4425 | 197
WTHU4A | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WTHU4B | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100
WWEY21 | WWEY11 | 0.1067 | 8.0868 | -0.034 | 280
WWEY21 | WWEY12 | 0.1382 | 8.4614 | -0.1786 | 250
WWEY22 | WWEY11 | 0.1007 | 8.1333 | -0.2371 | 240
WWEY22 | WWEY12 | 0.1382 | 8.4489 | -0.1786 | 240
WWEY4A | WWEY21 | 0.017 | 1.6132 | -5.1203 | 750
WWEY4A | WWEY22 | 0.0185 | 1.614 | -0.5638 | 1100
WWEY4B | WWEY21 | 0.0178 | 1.5995 | -1.2431 | 845
WWEY4B | WWEY2A | 0.0178 | 1.5995 | -1.2431 | 845
WYLF41 | WYLF11 | 0.1509 | 8.2849 | -0.3279 | 276
WYLF41 | WYLF11 | 0.1229 | 8.3873 | -0.1147 | 269
WYMO41 | WYMO11 | 0.1509 | 8.2849 | -0.3279 | 273
WYMO41 | WYMO11 | 0.1303 | 7.8698 | -0.4285 | 273

## B-3-1d
B.3.1d- OFTO Transformers for 2025/26
OFTO | Wind Farm | Node 1 | Node 2 | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA) | Voltage Ratio (kV)
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSW11 | BOSW31 | 0.316 | 15.0833 | 0 | 120 | 132/33
TC Beatrice OFTO Limited | Beatrice Offshore Wind Farm | BEAT41 | BEAT21 | 0.054 | 5.009 | 0 | 320 | 400/220
|  | BEAT41 | BEAT22 | 0.054 | 5.009 | 0 | 320 | 400/220
|  | BEIW21 | BEIW31 | 0.076 | 5.65 | 0 | 310 | 220/33
|  | BEIW22 | BEIW32 | 0.076 | 5.65 | 0 | 310 | 220/33
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BBWO41 | BBWO21 | 0.0141 | 11.9334 | -0.3558 | 200 | 400/220
|  | BBWO41 | BBWO21 | 0.0141 | 11.9334 | -0.3558 | 200 | 400/220
|  | BBWW21 | BBWW31 | 0.11508 | 6.0889 | -0.8147 | 200 | 220/34
|  | BBWW21 | BBWW32 | 0.11573 | 6.0739 | -0.8147 | 200 | 220/34
DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank A Offshore Wind Farm | DBAWD | DBAW61 | 0.001 | 5.72 | 0 | 664 | 392/66
|  | DBAO41 | DBAOD | 0.001 | 3.52 | 0 | 426 | 400/379
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDW11 | DUDW31 | 0.13 | 6 | 0 | 200 | 132/33
|  | DUDW12 | DUDW32 | 0.13 | 6 | 0 | 200 | 132/33
|  | NECT41 | DUDO11 | 0.09 | 6 | -0.2956 | 200 | 400/132
|  | NECT41 | DUDO12 | 0.09 | 6 | -0.2956 | 200 | 400/132
East Anglia One Limited | East Anglia Offshore Wind Farm | BRST41 | BRST21 | 0.0296 | 3.44 | 0 | 400 | 400/220
|  | BRST42 | BRST22 | 0.0296 | 3.44 | 0 | 400 | 400/220
|  | EAAW21 | EAAW61 | 0.1037 | 7.035 | 0 | 200 | 220/66
|  | EAAW21 | EAAW63 | 0.1037 | 7.035 | 0 | 200 | 220/66
|  | EAAW22 | EAAW62 | 0.1037 | 7.035 | 0 | 200 | 220/66
|  | EAAW22 | EAAW64 | 0.1037 | 7.035 | 0 | 200 | 220/66
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GANW11 | GANW31 | 0.378 | 12.122 | 0 | 90 | 132/33
|  | GANW11 | GANW33 | 0.378 | 12.122 | 0 | 90 | 132/33
|  | GANW12 | GANW32 | 0.378 | 12.222 | 0 | 90 | 132/33
|  | GANW12 | GANW34 | 0.378 | 12.222 | 0 | 90 | 132/33
Greater Gabbard OFTO Plc | Greater Gabbard Offshore Wind Farm | GREG14 | GREG3A | 0.411 | 23.33 | 0 | 90 | 132/33
|  | GREG14 | GREG3B | 0.411 | 23.33 | 0 | 90 | 132/33
|  | GREG11 | GREG31 | 0.4 | 23.44 | 0 | 90 | 132/33
|  | GREG11 | GREG32 | 0.4 | 23.44 | 0 | 90 | 132/33
|  | GREG12 | GREG33 | 0.4 | 23.44 | 0 | 90 | 132/33
|  | GREG12 | GREG34 | 0.4 | 23.44 | 0 | 90 | 132/33
|  | GREG13 | GREG35 | 0.4 | 23.44 | 0 | 90 | 132/33
|  | GREG13 | GREG36 | 0.4 | 23.44 | 0 | 90 | 132/33
TC Gunfleet Sands OFTO Limited | Gunfleet Sands Offshore Wind Farm | GUNS11 | GUNS31 | 0.2372 | 8.5717 | 0 | 120 | 132/33
|  | GUNS11 | GUNS32 | 0.2372 | 8.5717 | 0 | 120 | 132/33
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | BODE41 | GWYO11 | 0.054688 | 3.5313 | 0 | 320 | 400/132
|  | BODE41 | GWYO12 | 0.054688 | 3.5313 | 0 | 320 | 400/132
|  | GWAW11 | GWAW31 | 0.15625 | 11.3313 | 0 | 160 | 132/33
|  | GWAW12 | GWAW32 | 0.15625 | 11.3625 | 0 | 160 | 132/33
|  | GWBW11 | GWBW31 | 0.15625 | 11.3438 | 0 | 160 | 132/33
|  | GWBW12 | GWBW32 | 0.15625 | 11.375 | 0 | 160 | 132/33
Diamond Transmission Partners Hornsea One Limited | Hornsea One Offshore Wind Farm | HOWA41 | HOWA21 | 0.016279 | 2.6767 | 0 | 430 | 400/220
|  | HOWA41 | HOWA21 | 0.016279 | 2.6744 | 0 | 430 | 400/220
|  | HOWA41 | HOWA21 | 0.016279 | 2.6744 | 0 | 430 | 400/220
|  | HOWW2A | HOWW3A | 0.0875 | 5.9042 | 0 | 240 | 220/34
|  | HOWW2A | HOWW3A | 0.0875 | 5.9042 | 0 | 240 | 220/34
|  | HOWW2B | HOWW3B | 0.0875 | 5.925 | 0 | 240 | 220/34
|  | HOWW2B | HOWW3B | 0.0875 | 5.925 | 0 | 240 | 220/34
|  | HOWW2C | HOWW3C | 0.0875 | 5.9208 | 0 | 240 | 220/34
|  | HOWW2C | HOWW3C | 0.0875 | 5.9042 | 0 | 240 | 220/34
Breesea Limited | Hornsea Two Offshore Wind Farm | HOWB41 | HOWB21 | 0.029474 | 2.4968 | 0 | 475 | 400/220
|  | HOWB41 | HOWB21 | 0.0295 | 2.4968 | 0 | 475 | 400/220
|  | HOWB41 | HOWB21 | 0.029474 | 2.4968 | 0 | 475 | 400/220
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
|  | HOWW2D | HOWW6D | 0.081481 | 4.9296 | 0 | 270 | 220/66
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HUMO21 | HUMO11 | 0.1875 | 11.4375 | 0 | 160 | 275/132
|  | HUMO22 | HUMO12 | 0.1875 | 11.4375 | 0 | 160 | 275/132
|  | HUMW11 | HUMW31 | 0.23192 | 8.5714 | 0 | 140 | 132/33
|  | HUMW12 | HUMW32 | 0.23192 | 8.5714 | 0 | 140 | 132/33
TC Lincs OFTO Limited | Lincs Offshore Wind Farm | LINO41 | LINO11 | 0.0417 | 4.6665 | 0 | 300 | 400/132
|  | LINO41 | LINO12 | 0.0417 | 4.6665 | 0 | 300 | 400/132
|  | LINS11 | LINS31 | 0.05 | 5.83 | 0 | 240 | 132/33
|  | LINS12 | LINS32 | 0.05 | 5.83 | 0 | 240 | 132/33
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO4A | LONO11 | 0.33 | 6.4556 | 0 | 180 | 400/150
|  | LONO4B | LONO12 | 0.33 | 6.4111 | 0 | 180 | 400/150
|  | LONO4A | LONO13 | 0.33 | 6.4611 | 0 | 180 | 400/150
|  | LONO4B | LONO14 | 0.33 | 6.4389 | 0 | 180 | 400/150
|  | LOAW11 | LOAW31 | 0.402 | 6.56 | 0 | 180 | 150/33
|  | LOAW12 | LOAW32 | 0.4045 | 6.57 | 0 | 180 | 150/33
|  | LOYW11 | LOYW31 | 0.407 | 6.58 | 0 | 180 | 150/33
|  | LOYW12 | LOAW34 | 0.4045 | 6.57 | 0 | 180 | 150/33
Moray East Offshore Wind Limited | Moray East Offshore Wind Farm | MOWE21 | MOWE61 | 0.08 | 4.53 | 0 | 315 | 220/66
|  | MOWE22 | MOWE62 | 0.08 | 4.53 | 0 | 315 | 220/66
|  | MOWE23 | MOWE63 | 0.08 | 4.53 | 0 | 315 | 220/66
|  | MORF41 | MORO21 | 0.079 | 5.21 | 0 | 340 | 400/220
|  | MORF42 | MORO22 | 0.079 | 5.21 | 0 | 340 | 400/220
|  | MORF43 | MORO23 | 0.079 | 5.21 | 0 | 340 | 400/220
Ocean Winds Limited | Moray West Offshore Wind Farm | MOWO41 | MOWO21 | 0.16 | 11.63 | 0 | 470 | 400/220
|  | MOWO42 | MOWO22 | 0.16 | 11.63 | 0 | 470 | 400/220
|  | MOWW21 | MOWW61 | 0.25 | 11.99 | 0 | 440 | 220/66
|  | MOWW22 | MOWW62 | 0.25 | 11.99 | 0 | 440 | 220/66
NEART NA GAOITHE OFFSHORE WIND LIMITED | Neart na Gaoithe Offshore Wind Farm | NNGO41 | NNGO21 | 0.11154 | 4.4462 | 0 | 260 | 400/220
|  | NNGO42 | NNGO22 | 0.11154 | 4.4462 | 0 | 260 | 400/220
|  | NNGW21 | NNGW61 | 0.13478 | 5.4217 | 0 | 230 | 220/66
|  | NNGW22 | NNGW62 | 0.13478 | 5.4217 | 0 | 230 | 220/66
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMW11 | ORMW31 | 0.464 | 14.421 | 0 | 85 | 132/33
|  | ORMW11 | ORMW32 | 0.465 | 14.479 | 0 | 85 | 132/33
|  | ORMO11 | ORMO31 | 0.348 | 13.465 | 0 | 110 | 132/33
Diamond Transmission Partners RB Limited | Race Bank Offshore Wind Farm | RACO41 | RACO21 | 0.03165 | 3.1526 | 0 | 360 | 400/220
|  | RACO42 | RACO22 | 0.031779 | 3.1582 | 0 | 360 | 400/220
|  | RACW21 | RACW31 | 0.11449 | 6.0389 | 0 | 200 | 220/34
|  | RACW21 | RACW32 | 0.11465 | 6.0789 | 0 | 200 | 220/34
|  | RACW22 | RACW33 | 0.11476 | 6.0989 | 0 | 200 | 220/34
|  | RACW22 | RACW34 | 0.11435 | 6.0689 | 0 | 200 | 220/34
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | RAMW11 | RAMW3A | 0.14 | 5.31 | 0 | 240 | 150/33
|  | RAMW12 | RAMW3B | 0.14 | 5.32 | 0 | 240 | 150/33
|  | TWNE41 | TWNE11 | 0.073 | 5.1 | 0 | 240 | 400/150
|  | TWNE42 | TWNE12 | 0.073 | 5.1 | 0 | 240 | 400/150
TC Robin Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | RORE31 | 0.87 | 41.4 | 0 | 20 | 132/33
| Robin Rigg West Offshore Wind Farm | RORW11 | RORW31 | 0.87 | 41.4 | 0 | 20 | 132/33
Seagreen Wind Energy Limited | Seagreen One Wind Farm | SGRX21 | SGRO21 | 0.03 | 2.97 | 0 | 410 | 275/220
|  | SGRX22 | SGRO22 | 0.03 | 2.94 | 0 | 410 | 275/220
|  | SGRX23 | SGRO23 | 0.03 | 2.94 | 0 | 410 | 275/220
|  | SGRW21 | SGRW61 | 0.052 | 3.71 | 0 | 390 | 220/66
|  | SGRW22 | SGRW62 | 0.052 | 3.71 | 0 | 390 | 220/66
|  | SGRW22 | SGRW62 | 0.052 | 3.71 | 0 | 390 | 220/66
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SSAW11 | SSAW31 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSAW11 | SSAW32 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSBW11 | SSBW31 | 0.23 | 12.07 | 0 | 90 | 132/33
|  | SSBW11 | SSBW32 | 0.23 | 12.07 | 0 | 90 | 132/33
Thanet OFTO Limited | Thanet Offshore Wind Farm | THOW11 | THOW31 | 0.0093 | 1.1111 | -0.0063 | 90 | 132/33
|  | THOW11 | THOW33 | 0.0093 | 1.1111 | -0.0063 | 90 | 132/33
|  | THOW12 | THOW32 | 0.0093 | 1.1111 | -0.0063 | 90 | 132/33
|  | THOW12 | THOW34 | 0.0093 | 1.1111 | -0.0063 | 90 | 132/33
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNW21 | TKNW61 | 0.07 | 3.33 | 0 | 420 | 220/66
|  | TKNE21 | TKNE61 | 0.07 | 3.33 | 0 | 420 | 220/66
|  | TKNO41 | TKNO21 | 0.036 | 3.78 | 0 | 450 | 400/220
|  | TKNO42 | TKNO22 | 0.036 | 3.78 | 0 | 450 | 400/220
Diamond Transmission Partners Walney Extension Limited | Walney Extension Offshore Wind Farm | WACW21 | WACW31 | 0.115 | 6.02 | -0.9268 | 200 | 220/34
|  | WACW21 | WACW32 | 0.115 | 6.02 | -0.9268 | 200 | 220/34
|  | WADW21 | WADW31 | 0.115 | 6.02 | 0 | 200 | 220/34
|  | WADW21 | WADW32 | 0.115 | 6.02 | 0 | 200 | 220/34
|  | WOWE41 | WOWE21 | 0.0255 | 2.617 | 0 | 470 | 400/220
|  | WOWE42 | WOWE22 | 0.0255 | 2.617 | 0 | 470 | 400/220
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAW11 | WAAW31 | 0.42 | 8.75 | 0 | 120 | 132/33
|  | WAAW11 | WAAW32 | 0.42 | 8.75 | 0 | 120 | 132/33
Blue Transmission Walney 2 OFTO Limited | Walney 2 Offshore Wind Farm | WABW11 | WABW31 | 0.2395 | 8.2882 | 0 | 120 | 132/33
|  | WABW11 | WABW32 | 0.2432 | 8.3214 | 0 | 120 | 132/33
WoDS Transmission plc | West of Duddon Sands Offshore Wind Farm | WDSO41 | WDSO11 | 0.20833 | 5 | 0 | 240 | 400/155
|  | WDSO42 | WDSO12 | 0.20833 | 5 | 0 | 240 | 400/155
|  | WDSW11 | WDSW31 | 0.20833 | 5 | 0 | 240 | 155/34
|  | WDSW12 | WDSW32 | 0.20833 | 5 | 0 | 240 | 155/34
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERO21 | WERO11 | 0.09 | 6.62 | 0 | 180 | 275/150
|  | WERO22 | WERO11 | 0.09 | 6.58 | 0 | 180 | 275/150
|  | WERW11 | WERW31 | 0.12 | 7.14 | 0 | 140 | 150/34
|  | WERW11 | WERW32 | 0.12 | 7.14 | 0 | 140 | 150/34

## B-3-2a
B-3-2a - SHE TransmissionTransformer Changes 2026/27 to 2033/34
Node1 | Node2 | Year | Status | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating (MVA)
AIGA1Q | AIGA5- | 2026 | Change | 1.7562 | 44.8545 | -0.0041 | 22
ERRO1A | ERRO3- | 2026 | Addition | 0.5828 | 24.9932 | -0.0002 | 90
ERRO1A | ERRO3- | 2026 | Addition | 0.5828 | 24.9932 | -0.0002 | 90
GREM1J | GREM31 | 2026 | Addition | 0.5828 | 24.9932 | -0.0002 | 90
GREM1K | GREM31 | 2026 | Addition | 0.5828 | 24.9932 | -0.0002 | 90
TEAL2A | TEAL21 | 2026 | Addition | 0.0143 | 1.1276 | -0.001 | 675
TEAL2A | TEAL21 | 2026 | Addition | 0.0143 | 1.1276 | -0.001 | 675
TUMB1Q | TUMB5- | 2026 | Removed | 1.6295 | 77.7448 | -0.0986 | 21
TUMB1R | TUMB5- | 2026 | Removed | 1.6066 | 76.6498 | -0.0986 | 21
ABED11 | ABED31 | 2028 | Addition | 0.9139 | 24.9833 | 0 | 60
AIGA1Q | AIGA5- | 2028 | Removed | 1.7562 | 44.8545 | -0.0041 | 22
AIGN11 | AIGN51 | 2028 | Addition | 1.7577 | 44.8906 | -0.0002 | 36
ALYT41 | ALYT21 | 2028 | Addition | 0.0377 | 1.5996 | -0.1302 | 1200
ALYT41 | ALYT21 | 2028 | Addition | 0.0377 | 1.5996 | -0.1302 | 1200
ANSN2- | ANSN3- | 2028 | Addition | 0.3937 | 17.9957 | 0 | 120
ANSU1- | ANSU3- | 2028 | Removed | 0.8997 | 24.8949 | -0.0163 | 45
ARBR1Q | ARBR3- | 2028 | Change | 0.4181 | 24.9965 | 0 | 120
ARBR1R | ARBR3- | 2028 | Change | 0.4181 | 24.9965 | 0 | 120
BEAU21 | BEAU11 | 2028 | Change | 0.1494 | 5.3312 | -0.0319 | 360
BEAU21 | BEAU11 | 2028 | Change | 0.1494 | 5.3312 | -0.0319 | 360
BEAU21 | BEAU11 | 2028 | Change | 0.1494 | 5.3312 | -0.0319 | 360
BEIB11 | BEIB31 | 2028 | Addition | 0.3405 | 17.9968 | 0 | 90
BLHI21 | BLHI11 | 2028 | Addition | 0.1494 | 5.3312 | -0.0319 | 360
CHLS11 | CHLS31 | 2028 | Addition | 0.2426 | 17.9984 | 0 | 120
CLOI11 | CLOI31 | 2028 | Addition | 0.1333 | 7.9989 | -0.0173 | 150
CONN2Q | CONN11 | 2028 | Addition | 0.1001 | 3.9987 | -0.0584 | 480
CRAR1R | CRAR3- | 2028 | Removed | 0.4031 | 17.7732 | -0.0172 | 90
CRAS2- | CRAS3- | 2028 | Addition | 0.3937 | 17.9957 | 0 | 120
CRDH21 | CRDH11 | 2028 | Addition | 0.1001 | 3.9987 | -0.0584 | 480
CRDH21 | CRDH11 | 2028 | Addition | 0.1001 | 3.9987 | -0.0584 | 480
CRMU21 | CRMU31 | 2028 | Addition | 0.3937 | 17.9957 | 0 | 120
CRMU21 | CRMU31 | 2028 | Addition | 0.3937 | 17.9957 | 0 | 120
CRSN21 | CRSN11 | 2028 | Addition | 0.1001 | 3.9987 | -0.0584 | 480
CRSN21 | CRSN11 | 2028 | Addition | 0.1001 | 3.9987 | -0.0584 | 480
DONW21 | DONW2A | 2028 | Addition | 0.1494 | 5.3312 | -0.0276 | 360
FARI2J | FARI1J | 2028 | Change | 0.2704 | 7.9954 | -0.02 | 240
FARI2K | FARI1K | 2028 | Change | 0.2704 | 7.9954 | -0.02 | 240
FETT41 | FETT1- | 2028 | Change | 0.108 | 3.9569 | -0.078 | 480
FINS11 | FINS31 | 2028 | Addition | 0.4181 | 24.9965 | 0 | 120
FINS11 | FINS31 | 2028 | Addition | 0.4181 | 24.9965 | 0 | 120
FINS21 | FINS11 | 2028 | Addition | 0.044 | 5.833 | -0.0276 | 360
FRAS1Q | FRAS3- | 2028 | Change | 0.9139 | 24.9833 | 0 | 60
FRAS1R | FRAS3- | 2028 | Change | 0.9139 | 24.9833 | 0 | 60
HICL11 | HICL31 | 2028 | Addition | 0.9139 | 24.9833 | 0 | 60
KINT11 | KINT3- | 2028 | Removed | 1.0391 | 27.6305 | -0.0002 | 60
KINT11 | KINT3- | 2028 | Change | 0.4181 | 24.9965 | 0 | 120
KINT21 | KINT11 | 2028 | Change | 0.2704 | 7.9954 | -0.02 | 240
KINT21 | KINT11 | 2028 | Change | 0.2704 | 7.9954 | -0.02 | 240
KINT21 | KINT11 | 2028 | Change | 0.2704 | 7.9954 | -0.02 | 240
LAIS11 | LAIS31 | 2028 | Addition | 0.9139 | 24.9833 | 0 | 60
LOYE1- | LOYE5J | 2028 | Addition | 0.9531 | 38.8216 | -0.012 | 36
LOYE1- | LOYE5K | 2028 | Addition | 0.9553 | 38.766 | -0.0122 | 36
PORA1Q | PORA3- | 2028 | Removed | 1.8024 | 29.8122 | -0.0503 | 30
PORA1R | PORA3- | 2028 | Removed | 1.8024 | 29.8122 | -0.0503 | 30
SFIL1Q | SFIL5- | 2028 | Change | 0.948 | 38.5161 | 0 | 36
STWO11 | STWO31 | 2028 | Addition | 0.3405 | 17.9968 | 0 | 90
TEAS1- | TEAS31 | 2028 | Addition | 0.4181 | 24.9965 | 0 | 120
ACHE11 | ACHE31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
ALYT41 | ALYT21 | 2030 | Removed | 0.0377 | 1.5996 | -0.1302 | 1200
ALYT41 | ALYT21 | 2030 | Removed | 0.0377 | 1.5996 | -0.1302 | 1200
BANN41 | BANN21 | 2030 | Addition | 0.0377 | 1.5996 | -0.1302 | 1200
BANN41 | BANN21 | 2030 | Addition | 0.0377 | 1.5996 | -0.1302 | 1200
BERB2R | BERB3A | 2030 | Addition | 0.3937 | 17.9957 | 0 | 120
BING41 | BING11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
BING41 | BING11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
BLEX1- | BLEX3- | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
BLGH11 | BLGH31 | 2030 | Addition | 0.5828 | 24.9932 | -0.0002 | 90
BLHI2A | BLHI21 | 2030 | Addition | 0.0059 | 0.4624 | 0 | 865
BLHI2A | BLHI21 | 2030 | Addition | 0.0059 | 0.4624 | 0 | 865
BOAG1Q | BOAG3- | 2030 | Change | 0.2265 | 24.724 | -0.0048 | 120
BOAG1R | BOAG3- | 2030 | Change | 0.2265 | 24.724 | -0.0048 | 120
BRCW11 | BRCW3- | 2030 | Addition | 0.4181 | 24.9965 | 0 | 120
BRCW11 | BRCW3- | 2030 | Addition | 0.4181 | 24.9965 | 0 | 120
BRCW2J | BRCW3- | 2030 | Removed | 0.2893 | 19.9146 | -0.0155 | 120
BRCW2K | BRCW3- | 2030 | Removed | 0.2893 | 19.9146 | -0.0159 | 120
BROA11 | BROA3A | 2030 | Addition | 1.1951 | 25.0827 | 0 | 45
CAAI41 | CAAI11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
CAAI41 | CAAI11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
CASS1Q | CASS3- | 2030 | Change | 0.4181 | 24.9965 | 0 | 120
CLAT1- | CLAT3- | 2030 | Addition | 0.4181 | 24.9965 | 0 | 120
CLGO11 | CLGO3A | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
CLGO11 | CLGO3B | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
CLGO11 | CLGO3C | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
CLGO2J | CLGO11 | 2030 | Addition | 0.1494 | 5.3312 | -0.0319 | 360
CLGO2K | CLGO11 | 2030 | Addition | 0.1494 | 5.3312 | -0.0319 | 360
CMBS41 | CMBS11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
CMBS41 | CMBS11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
CULL1- | CULL5- | 2030 | Change | 1.5105 | 37.5974 | -0.3144 | 36
DEAN1Q | DEAN5- | 2030 | Removed | 1.0125 | 25.0796 | -0.1926 | 40
DEAW1- | DEAW5- | 2030 | Addition | 1.0133 | 25.0996 | -0.2185 | 45
DELL11 | DELL31 | 2030 | Addition | 0.9139 | 24.9833 | 0 | 60
DUDH1Q | DUDH3- | 2030 | Removed | 0.7798 | 24.9211 | -0.0118 | 60
DUDH1R | DUDH3- | 2030 | Removed | 0.7797 | 23.9206 | -0.0118 | 60
EDIN11 | EDIN3A | 2030 | Addition | 0.7697 | 17.9835 | 0 | 60
EDIN11 | EDIN3B | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
ELCH11 | ELCH31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
ELCH11 | ELCH31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
EMMO41 | EMMO21 | 2030 | Addition | 0.0377 | 1.5996 | -0.1302 | 1200
EMMO41 | EMMO21 | 2030 | Addition | 0.0377 | 1.5996 | -0.1302 | 1200
EMMO41 | EMMO21 | 2030 | Addition | 0.0377 | 1.5996 | -0.1302 | 1200
FASN1A | FASN31 | 2030 | Addition | 0.4181 | 24.9965 | 0 | 120
FASN1B | FASN31 | 2030 | Addition | 0.4181 | 24.9965 | 0 | 120
FASN2Q | FASN31 | 2030 | Removed | 0.2896 | 19.9146 | -0.0075 | 120
FASN2R | FASN31 | 2030 | Removed | 0.2892 | 20.1646 | -0.0146 | 120
FAUG41 | FAUG11 | 2030 | Change | 0.2145 | 7.9971 | -0.0749 | 240
FAUG41 | FAUG11 | 2030 | Change | 0.2145 | 7.9971 | -0.0749 | 240
FETT41 | FETT11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
GARV11 | GARV31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
GARV11 | GARV31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
GLDY11 | GLDY31 | 2030 | Addition | 0.7222 | 7.2222 | 0 | 180
GLUE1- | GLUE3- | 2030 | Addition | 0.5828 | 24.9932 | -0.0002 | 90
GLUE1- | GLUE3- | 2030 | Addition | 0.5828 | 24.9932 | -0.0002 | 90
GLUE1- | GLUE3- | 2030 | Addition | 0.5828 | 24.9932 | -0.0002 | 90
HARI1- | HARI3- | 2030 | Addition | 0.6806 | 17.9871 | -0.0128 | 60
HEBW11 | HEBW31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
HEBW11 | HEBW31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
HEST11 | HEST31 | 2030 | Addition | 1.1951 | 25.0827 | 0 | 45
HOME11 | HOME31 | 2030 | Addition | 0.7697 | 17.9835 | 0 | 60
KINA41 | KINA1A | 2030 | Addition | 0.1248 | 8.0824 | -0.0644 | 240
KINA41 | KINA1B | 2030 | Addition | 0.1248 | 8.0824 | -0.0644 | 240
KION11 | KION51 | 2030 | Addition | 1.7805 | 45.4207 | -0.0002 | 36
KIOR1- | KIOR5- | 2030 | Removed | 1.7809 | 45.4318 | -0.0001 | 22
KRKN11 | KRKN31 | 2030 | Addition | 0.3405 | 17.9968 | 0 | 90
LAFD11 | LAFD31 | 2030 | Addition | 0.5828 | 24.9932 | -0.0002 | 90
LEWI41 | LEWI11 | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
LEWI41 | LEWI11 | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
LEWI41 | LEWI11 | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
LOCA21 | LOCA5D | 2030 | Addition | 0.1395 | 6.8837 | 0 | 215
LOCA21 | LOCA5E | 2030 | Addition | 0.1395 | 6.8837 | 0 | 215
LOCA21 | LOCA5F | 2030 | Addition | 0.1395 | 6.8837 | 0 | 215
LOCL41 | LOCL11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
LOCL41 | LOCL11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
LOSD41 | LOSD11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
LOSD41 | LOSD11 | 2030 | Addition | 0.108 | 3.9569 | -0.078 | 480
LUNA1Q | LUNA3- | 2030 | Change | 0.4181 | 24.9965 | 0 | 120
LUNA1R | LUNA3- | 2030 | Change | 0.4181 | 24.9965 | 0 | 120
MEYG11 | MEYG31 | 2030 | Addition | 0.7311 | 19.9866 | 0 | 60
MEYG11 | MEYG31 | 2030 | Addition | 0.097 | 5.7408 | 0 | 209
MEYG11 | MEYG31 | 2030 | Addition | 0.9518 | 19.9773 | 0 | 60
MSHL11 | MSHL31 | 2030 | Addition | 0.4736 | 17.9938 | 0 | 90
MUAI11 | MUAI31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
MUAI11 | MUAI31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
OURA1- | OURA3- | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
STOR1Q | STOR31 | 2030 | Addition | 0.4181 | 24.9965 | 0 | 120
STOR1R | STOR31 | 2030 | Addition | 0.4181 | 24.9965 | 0 | 120
STSO11 | STSO31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
STSO11 | STSO31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
TNGF11 | TNGF31 | 2030 | Addition | 0.2426 | 17.9984 | 0 | 120
TOSY11 | TOSY31 | 2030 | Addition | 0.3405 | 17.9968 | 0 | 90
TUMM2J | TUMM1J | 2030 | Removed | 0.259 | 7.7457 | -0.0239 | 240
TUMM2K | TUMM1K | 2030 | Removed | 0.2595 | 7.829 | -0.0229 | 240
WIOW11 | WIOW3- | 2030 | Change | 0.4181 | 24.9965 | 0 | 120
WIOW11 | WIOW3- | 2030 | Change | 0.4181 | 24.9965 | 0 | 120
BEWF1- | BEWF3- | 2033 | Addition | 0.128 | 9.4991 | 0 | 120
BRID1J | BRID3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
BRID1K | BRID3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
CAIN2- | CAIN3J | 2033 | Removed | 0.379 | 18.0794 | -0.0241 | 120
CENS21 | CENS11 | 2033 | Addition | 0.044 | 5.833 | 0 | 360
CENS21 | CENS11 | 2033 | Addition | 0.044 | 5.833 | 0 | 360
CENS21 | CENS11 | 2033 | Addition | 0.044 | 5.833 | 0 | 360
CNBH11 | CNBH31 | 2033 | Addition | 0.2426 | 17.9984 | 0 | 120
CNBH11 | CNBH31 | 2033 | Addition | 0.2426 | 17.9984 | 0 | 120
COUA1Q | COUA3- | 2033 | Addition | 0.4181 | 24.9965 | 0 | 120
COUA1R | COUA3- | 2033 | Addition | 0.4181 | 24.9965 | 0 | 120
DUNO1Q | DUNO3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
DUNO1R | DUNO3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
EDAY11 | EDAY31 | 2033 | Addition | 0.4181 | 24.9965 | 0 | 120
ELGI11 | ELGI3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
ELGI11 | ELGI3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
FIDD1Q | FIDD3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
FIDD1R | FIDD3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
INVR1A | INVR11 | 2033 | Addition | 0.0565 | 2.0826 | -0.0058 | 240
INVR1A | INVR11 | 2033 | Addition | 0.0565 | 2.0826 | -0.0058 | 240
KINM4A | KINM31 | 2033 | Addition | 0.2916 | 14.5804 | 0 | 120
KIWF21 | KIWF31 | 2033 | Addition | 0.3937 | 17.9957 | 0 | 120
LOFA41 | LOFA51 | 2033 | Addition | 0.0873 | 3.8504 | 0 | 350
LUNH21 | LUNH31 | 2033 | Addition | 0.3937 | 17.9957 | 0 | 120
LUNH21 | LUNH31 | 2033 | Addition | 0.3937 | 17.9957 | 0 | 120
NAIR1Q | NAIR3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
NAIR1R | NAIR3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
NCCS21 | NCCS11 | 2033 | Addition | 0.1001 | 3.9987 | -0.0584 | 480
NCCS21 | NCCS11 | 2033 | Addition | 0.1001 | 3.9987 | -0.0584 | 480
NCCS21 | NCCS3- | 2033 | Addition | 0.379 | 18.0794 | -0.0241 | 120
NEMA41 | NEMA1Q | 2033 | Addition | 0.108 | 3.9569 | -0.078 | 480
NEMA41 | NEMA1R | 2033 | Addition | 0.108 | 3.9569 | -0.078 | 480
NEMA41 | NEMA4A | 2033 | Addition | 0.001 | 0.21 | 0 | 2780
NEMA41 | NEMA4A | 2033 | Addition | 0.001 | 0.21 | 0 | 2780
ORRI1Q | ORRI5- | 2033 | Change | 0.948 | 38.5161 | 0 | 36
PEHE21 | PHCC7B | 2033 | Addition | 0.1278 | 5.4234 | -0.1122 | 1070
PEHE41 | PEHE21 | 2033 | Addition | 0.0263 | 1.6265 | -0.1101 | 1200
PEHG1Q | PEHG3- | 2033 | Change | 0.5828 | 24.9932 | -0.0002 | 90
PEHG1R | PEHG3- | 2033 | Change | 0.5828 | 24.9932 | -0.0002 | 90
SHIN11 | SHIN3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
SHIN11 | SHIN3- | 2033 | Change | 0.4181 | 24.9965 | 0 | 120
SLOY1L | SLOY51 | 2033 | Change | 0.8557 | 25 | 0 | 60
SLOY1M | SLOY51 | 2033 | Change | 0.8557 | 25 | 0 | 60
SLOY1N | SLOY51 | 2033 | Change | 0.8557 | 25 | 0 | 60
SLOY1P | SLOY51 | 2033 | Change | 0.8557 | 25 | 0 | 60
SOYK11 | SOYK31 | 2033 | Addition | 0.4181 | 24.9965 | 0 | 120
YELL21 | YELL11 | 2033 | Addition | 0.108 | 3.9569 | 0 | 480

## B-3-2b
B-3-2b - SPT Transformer Changes 2026/27 to 2033/34
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
GALA1- | GALA7J | 2026 | Addition | 0.917 | 55.0024 | 0 | 10
GALA1- | GALA7K | 2026 | Addition | 0.917 | 55.0024 | 0 | 10
GIFF2R | GIFF3B | 2026 | Change | 0.4557 | 30.1188 | -0.0331 | 120
MAHI2- | MAHI1B | 2026 | Addition | 0.1284 | 8.6824 | -0.2535 | 240
AREX1- | AREX3- | 2028 | Addition | 0.306 | 17.3751 | -0.0002 | 90
COBA4- | COBA3- | 2028 | Addition | 0.2383 | 11.6642 | -0.0232 | 120
COCK4Q | MEAC1- | 2028 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
COYL1- | COYL3- | 2028 | Change | 0.4096 | 14.4609 | 0 | 60
CROO1Q | CROO3J | 2028 | Change | 0.3635 | 25.4418 | 0 | 60
CROO1R | CROO3J | 2028 | Change | 0.3635 | 25.4418 | 0 | 60
DAER1- | DAER3- | 2028 | Addition | 0.1922 | 14.207 | -0.0113 | 120
DEBS2- | DEBS3A | 2028 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
DEBS2- | DEBS3B | 2028 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
DEBS2- | DEBS3C | 2028 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
DEBS2- | DEBS3D | 2028 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
DEBS2- | DEBS3E | 2028 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
DEVM1- | DEVM3- | 2028 | Change | 0.2481 | 17.4427 | -0.0228 | 60
ECCL4A | ECCL0B | 2028 | Addition | 0.0846 | 6.5568 | -0.8231 | 300
ECCL4B | ECCL0D | 2028 | Addition | 0.0846 | 6.5568 | -0.8231 | 300
HLND1- | HLND3- | 2028 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
HORI1- | HORI3A | 2028 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
HORI1- | HORI3B | 2028 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
HUNE4- | HUER1- | 2028 | Removed | 0.1122 | 9.3465 | -0.2007 | 360
HUNE4- | HUER1- | 2028 | Removed | 0.1134 | 9.4715 | -0.1992 | 360
HUNE4- | HUNE1- | 2028 | Addition | 0.1122 | 9.3465 | -0.2007 | 360
HUNE4- | HUNE1- | 2028 | Addition | 0.1134 | 9.4715 | -0.1992 | 360
KINN4- | KINN2A | 2028 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
KINN4- | KINN2B | 2028 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
LORG1- | LORG3- | 2028 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
MAHI2- | MAHI1C | 2028 | Addition | 0.1284 | 8.6824 | -0.2535 | 240
MOFF1- | MOFF3- | 2028 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
MOFF4- | MOFF1A | 2028 | Addition | 0.0914 | 6.4382 | -0.0751 | 360
NETS1- | NETS3- | 2028 | Addition | 0.8311 | 28.2878 | -0.0097 | 60
REDS1A | REDS3A | 2028 | Addition | 0.1922 | 14.207 | -0.0113 | 120
REDS1Q | REDS3- | 2028 | Addition | 0.3635 | 25.4418 | 0 | 90
REDS1R | REDS3- | 2028 | Addition | 0.3635 | 25.4418 | 0 | 90
REDS4- | REDS1A | 2028 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
REDS4- | REDS1A | 2028 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
STOC1- | STOC3- | 2028 | Addition | 0.1922 | 14.207 | -0.0113 | 120
BANR1- | BANR3- | 2030 | Addition | 0.1922 | 14.207 | -0.0113 | 120
BONN2A | BONN1- | 2030 | Removed | 0.1559 | 8.9445 | -0.1694 | 240
BONN2B | BONN1- | 2030 | Removed | 0.1559 | 8.9445 | -0.1694 | 240
BONN4- | BONN1- | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
BONN4- | BONN1- | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
CLFO1- | CLFO3- | 2030 | Addition | 0.1922 | 14.207 | -0.0113 | 120
CLYM4- | CLYM2- | 2030 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
CLYM4- | CLYM2- | 2030 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
CONL4- | CONL2Q | 2030 | Addition | 0.06 | 3.2995 | 0 | 500
CONL4- | CONL2R | 2030 | Addition | 0.06 | 3.2995 | 0 | 500
CRCK2- | CRCK3- | 2030 | Addition | 0.2857 | 19.998 | 0 | 90
CRCK2- | CRCK3A | 2030 | Addition | 0.2857 | 19.998 | 0 | 90
CUMB1Q | CUMB3- | 2030 | Removed | 0.7407 | 29.324 | -0.129 | 90
CUMB1R | CUMB3- | 2030 | Removed | 0.741 | 27.111 | 0 | 90
CUMB2- | CUMB3- | 2030 | Addition | 0.2857 | 19.998 | 0 | 90
CUMB2- | CUMB3- | 2030 | Addition | 0.2857 | 19.998 | 0 | 90
CURR1A | CURR3- | 2030 | Addition | 0.3635 | 25.4418 | 0 | 90
CURR1A | CURR5- | 2030 | Removed | 3.225 | 79.0009 | 0 | 30
CURR1B | CURR3- | 2030 | Addition | 0.3635 | 25.4418 | 0 | 90
CURR1B | CURR5- | 2030 | Removed | 3.23 | 79.0007 | 0 | 30
DUMF1- | DUMF3C | 2030 | Addition | 0.3635 | 25.4418 | 0 | 90
EUCH1- | EUCH3- | 2030 | Addition | 0.1922 | 14.207 | -0.0113 | 120
FALL4- | FALL1Q | 2030 | Addition | 0.172 | 13.3322 | -0.1127 | 240
FALL4- | FALL3C | 2030 | Addition | 0.2564 | 16.6647 | 0 | 120
GALN4- | GALN1Q | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
GALN4- | GALN1R | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
GHPS4- | GHPS1A | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
GHPS4- | GHPS1A | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
GHPS4- | GHPS1B | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
GHPS4- | GHPS1B | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
GNSH1- | MARG3A | 2030 | Addition | 0.1922 | 14.207 | -0.0113 | 120
GNSH1- | MARG3B | 2030 | Addition | 0.1922 | 14.207 | -0.0113 | 120
KNOK1- | KNOK3- | 2030 | Addition | 0.1922 | 14.207 | -0.0113 | 120
LAMB4T | LAMB2- | 2030 | Addition | 0.015 | 1.6499 | -0.2252 | 1000
MOSM2- | MOSM1A | 2030 | Removed | 0.151 | 8.332 | -0.1299 | 240
MOSM2- | MOSM1B | 2030 | Removed | 0.157 | 8.7486 | -0.1299 | 240
MOSM4- | MOSM1A | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
MOSM4- | MOSM1B | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
NEWL1- | NEWL3A | 2030 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
NEWL1- | NEWL3B | 2030 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
NLEI1- | NLEI3A | 2030 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
NLEI1- | NLEI3B | 2030 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
OFOA1- | OFOA3- | 2030 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
OLDH4- | OLDH1- | 2030 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
OLDH4- | OLDH1- | 2030 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
QUAN1- | QUAN3- | 2030 | Addition | 0.1922 | 14.207 | -0.0113 | 120
QUAN1- | QUAN3A | 2030 | Addition | 0.4635 | 24.1789 | -0.0101 | 60
REDS4- | REDS1C | 2030 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
REDS4- | REDS1D | 2030 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
SHRG1- | SHRG3- | 2030 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
STHA2B | STHA3B | 2030 | Addition | 0.4557 | 30.1188 | -0.0331 | 27
TONG1- | TONG1R | 2030 | Removed | 0.0267 | 1.3331 | 0 | 90
TONG1Q | TONG1R | 2030 | Removed | 0.0125 | 2.5 | 0 | 90
WFIE2- | WFIE1A | 2030 | Removed | 0.1408 | 8.6113 | -0.1827 | 240
WFIE2- | WFIE1B | 2030 | Removed | 0.1264 | 8.7366 | -0.1602 | 240
WFIE4- | WFIE1A | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
WFIE4- | WFIE1B | 2030 | Addition | 0.1055 | 6.777 | -0.0931 | 360
WIYH4Q | WIYH2- | 2030 | Addition | 0.0133 | 1.6699 | -0.3581 | 1000
BONN4- | BONN1- | 2033 | Change | 0.1119 | 9.3882 | -0.1905 | 360
BONN4- | BONN1- | 2033 | Change | 0.1119 | 9.3882 | -0.1905 | 360
BTCK1- | BTCK3- | 2033 | Addition | 0.3635 | 25.4418 | 0 | 90
BTCK1- | BTCK3- | 2033 | Addition | 0.3635 | 25.4418 | 0 | 90
BTCK4- | BTCK1- | 2033 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
BTCK4- | BTCK1- | 2033 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
CHAP1- | CHAP3B | 2033 | Addition | 0.4338 | 27.5299 | -0.0175 | 90
CHAP1- | CHAP3B | 2033 | Addition | 0.4294 | 27.5633 | -0.0188 | 90
COAN4- | COAN1- | 2033 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
DENN2- | DENN1A | 2033 | Addition | 0.1452 | 8.6093 | -0.1299 | 240
HARB1- | HARB3- | 2033 | Addition | 0.2843 | 16.9754 | -0.0173 | 90
HARB4Q | HARB1- | 2033 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
HARB4R | HARB1- | 2033 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
MOIL2- | MOIL1- | 2033 | Addition | 0.1476 | 8.7488 | -0.1299 | 240
MOSM4- | MOSM1Q | 2033 | Addition | 0.1119 | 9.3882 | -0.1905 | 360
SMEA4R | SMEA2- | 2033 | Change | 0.0115 | 1.2692 | -0.312 | 1000
WESS4- | WESS1- | 2033 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
WESS4- | WESS1- | 2033 | Addition | 0.1128 | 8.7493 | -0.1127 | 240
WMHL2- | WMHL3A | 2033 | Addition | 0.1883 | 12.5319 | -0.0338 | 120
WMHL2- | WMHL3B | 2033 | Addition | 0.1883 | 12.5319 | -0.0338 | 120

## B-3-2c
B-3-2c - NGET Transformer Changes 2026/27 to 2033/34
Node1 | Node2 | Year | Status | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Rating (MVA)
AMEM41 | AMEM11 | 2026 | Addition | 0.1057 | 8.2064 | -0.078 | 240
BENR41 | BENR11 | 2026 | Addition | 0.114 | 8.3284 | -0.1022 | 240
BENR41 | BENR12 | 2026 | Addition | 0.1143 | 8.3534 | -0.103 | 240
BIGG41 | BIGG11 | 2026 | Addition | 0.148 | 8.1678 | -0.3849 | 240
BIGG41 | BIGG11 | 2026 | Addition | 0.148 | 8.1678 | -0.3849 | 240
BRAW21 | BRAW31 | 2026 | Addition | 0.2894 | 11.6521 | 0 | 120
BRIN41 | BRIN22 | 2026 | Change | 0.0133 | 1.5936 | -1.2059 | 1100
CITR41 | CITR11 | 2026 | Change | 0.1132 | 8.2492 | -0.1115 | 278
CITR41 | CITR12 | 2026 | Change | 0.1132 | 8.2492 | -0.1115 | 278
CITR41 | CITR12 | 2026 | Removed | 0.0997 | 8.0088 | -0.093 | 266
CITR41 | CITR12 | 2026 | Addition | 0.1132 | 8.2492 | -0.1115 | 278
COTS41 | COTS11 | 2026 | Addition | 0.1233 | 5 | -0.8284 | 300
COTS41 | COTS12 | 2026 | Addition | 0.1233 | 5 | -0.8284 | 300
COTS41 | COTS13 | 2026 | Addition | 0.1233 | 5 | -0.8284 | 300
COTS41 | COTS14 | 2026 | Addition | 0.1233 | 5 | -0.8284 | 300
ELST41 | ELST11 | 2026 | Addition | 0.1373 | 8.1976 | -0.9295 | 274
FLEE41 | FLEE31 | 2026 | Addition | 0.2141 | 15.3985 | -0.0916 | 150
HYLC21 | HYCL61 | 2026 | Addition | 0.2275 | 10.8456 | -0.0697 | 180
HYLC21 | HYCL61 | 2026 | Addition | 0.2275 | 10.8456 | -0.0697 | 180
HYLC21 | HYCL61 | 2026 | Addition | 0.2275 | 10.8456 | -0.0697 | 180
IVER21 | IVER11 | 2026 | Change | 0.0744 | 8.3386 | -0.0377 | 360
IVER21 | IVER11 | 2026 | Change | 0.0744 | 8.3386 | -0.0377 | 360
IVER22 | IVER11 | 2026 | Change | 0.0744 | 8.3386 | -0.0377 | 360
LHOR4A | LHOR11 | 2026 | Addition | 0.1373 | 8.1976 | -0.1719 | 240
LHOR4A | LHOR12 | 2026 | Addition | 0.1307 | 7.9515 | -0.1098 | 240
LLFG41 | BUTE11 | 2026 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
LLFG41 | BUTE11 | 2026 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
LLFG41 | BUTE11 | 2026 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
LLFG41 | BUTE11 | 2026 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
LLFG41 | LLFG11 | 2026 | Addition | 0.1057 | 8.2064 | -0.078 | 460
LLFG41 | LLFG11 | 2026 | Addition | 0.1057 | 8.2064 | -0.078 | 460
LLFG41 | LLFG11 | 2026 | Addition | 0.1057 | 8.2064 | -0.078 | 460
MANN41 | MANN31 | 2026 | Addition | 0.2262 | 15.019 | -0.0538 | 150
MELK41 | MELK11 | 2026 | Addition | 0.119 | 8.3617 | -1.9877 | 278
MELK41 | MELK11 | 2026 | Removed | 0.119 | 8.3617 | -1.9877 | 278
MELK41 | MELK31 | 2026 | Addition | 0.2106 | 15.2133 | -0.0768 | 150
MILH2B | MILH12 | 2026 | Change | 0.1004 | 8.1994 | -0.2371 | 240
MILH2B | MILH12 | 2026 | Removed | 0.1004 | 8.1994 | -0.2371 | 240
MILH2B | MILH12 | 2026 | Addition | 0.179 | 8.3648 | -4.7616 | 199
NEWX41 | NEWX21 | 2026 | Addition | 0.0098 | 1.5863 | -0.0631 | 1100
NEWX41 | NEWX21 | 2026 | Addition | 0.0098 | 1.5863 | -0.0631 | 1100
PEMB41 | PEMB11 | 2026 | Addition | 0.1539 | 7.9777 | -0.6329 | 240
WYMO4B | WYMO41 | 2026 | Addition | 0.2141 | 15.3985 | -0.0916 | 150
BLYT41 | BLYT11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
BLYT41 | BLYT11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
BOLN41 | BOLN31 | 2028 | Addition | 0.2262 | 15.019 | -0.0538 | 150
BRIM2C | BRIM11 | 2028 | Removed | 0.1688 | 8.3316 | -1.1711 | 262
BRIM2D | BRIM11 | 2028 | Addition | 0.1264 | 7.974 | -0.1303 | 262
BRIM4C | BRIM11 | 2028 | Removed | 0.1688 | 8.3316 | -1.1711 | 262
BRIM4D | BRIM11 | 2028 | Addition | 0.1264 | 7.974 | -0.1303 | 262
COVE21 | COVE12 | 2028 | Change | 0.1004 | 8.1994 | -0.2371 | 279
DIDC41 | DIDC11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
DIDC41 | DIDC11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
DIDC42 | DIDC11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
DRAK41 | DRAK11 | 2028 | Addition | 0.1123 | 8.3367 | -0.1053 | 240
FERR21 | FERR11 | 2028 | Addition | 0.0985 | 8.1944 | -0.0158 | 240
HACK41 | HACK21 | 2028 | Removed | 0.0182 | 1.5763 | -0.0904 | 1210
HACK21 | HACK61 | 2028 | Removed | 0.3231 | 13.4739 | -0.688 | 191
HACK41 | HACK22 | 2028 | Removed | 0.0182 | 1.5763 | -0.0904 | 1210
HACK22 | HACK61 | 2028 | Removed | 0.2901 | 13.3302 | -0.6072 | 191
HACK41 | HACK61 | 2028 | Addition | 0.2039 | 16.1765 | -0.9837 | 191
HACK41 | HACK61 | 2028 | Addition | 0.2039 | 16.1765 | -0.9837 | 191
HARG41 | HARG11 | 2028 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARG41 | HARG11 | 2028 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARK21 | HARK11 | 2028 | Removed | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK11 | 2028 | Removed | 0.2264 | 12.2479 | -0.6062 | 137
HARK21 | HARK12 | 2028 | Removed | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK12 | 2028 | Removed | 0.3328 | 11.6619 | -0.9523 | 137
HARK21 | HARK13 | 2028 | Removed | 0.1147 | 8.673 | -0.0358 | 222
HARK41 | HARK21 | 2028 | Removed | 0.0192 | 2.6599 | -3.6035 | 751
HARK41 | HARK12 | 2028 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARK41 | HARK12 | 2028 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARK41 | HARK13 | 2028 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARK41 | HARK13 | 2028 | Addition | 0.148 | 7.4973 | -0.3849 | 240
HARK41 | HARK21 | 2028 | Removed | 0.0376 | 2.3797 | -3.9009 | 547
HARK41 | HARK21 | 2028 | Removed | 0.0292 | 2.402 | -0.2732 | 438
HARK41 | HARK21 | 2028 | Removed | 0.0192 | 2.6599 | -3.6035 | 844
HARK41 | HARK21 | 2028 | Addition | 0.0192 | 2.6599 | -3.6035 | 844
HARK41 | HARK22 | 2028 | Addition | 0.0192 | 2.6599 | -3.6035 | 751
IMPP41 | IMPP11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
IMPP41 | IMPP11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
IMPP41 | IMPP31 | 2028 | Removed | 0.2262 | 15.019 | -0.0538 | 171
IMPP41 | IMPP31 | 2028 | Removed | 0.2262 | 15.019 | -0.0538 | 171
IROA21 | IROA11 | 2028 | Change | 0.1053 | 8.0652 | -0.0304 | 240
IROA21 | IROA12 | 2028 | Change | 0.1053 | 8.0652 | -0.0304 | 240
KENG41 | KENG61 | 2028 | Addition | 0.1844 | 13.1765 | -0.0474 | 180
MONF42 | MONF23 | 2028 | Addition | 0.013 | 1.6263 | -0.0877 | 1100
MONF42 | MONF23 | 2028 | Addition | 0.013 | 1.6263 | -0.0877 | 1100
MONF41 | MONF24 | 2028 | Addition | 0.013 | 1.6263 | -0.0877 | 1100
MONF41 | MONF24 | 2028 | Addition | 0.013 | 1.6263 | -0.0877 | 1100
OVTO41 | OVTO21 | 2028 | Addition | 0.013 | 1.6263 | -0.0877 | 1100
OVTO41 | OVTO21 | 2028 | Addition | 0.013 | 1.6263 | -0.0877 | 1100
OVTO42 | OVTO21 | 2028 | Addition | 0.013 | 1.6263 | -0.0877 | 1100
OVTO42 | OVTO21 | 2028 | Addition | 0.013 | 1.6263 | -0.0877 | 1100
PITS21 | PITS31 | 2028 | Change | 0.3486 | 24.9976 | -0.3225 | 110
PORT21 | PORT31 | 2028 | Addition | 0.3541 | 13.8844 | -2.5672 | 180
PORT21 | PORT31 | 2028 | Addition | 0.3541 | 13.8844 | -2.5672 | 180
PORT21 | PORT31 | 2028 | Addition | 0.3541 | 13.8844 | -2.5672 | 180
PORT21 | PORT31 | 2028 | Addition | 0.3541 | 13.8844 | -2.5672 | 180
RAYL41 | RAYL31 | 2028 | Addition | 0.2106 | 15.2133 | -0.0768 | 150
USKM21 | USKM11 | 2028 | Addition | 0.1221 | 8.0449 | -0.2391 | 263
UXBM41 | UXBM11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
UXBM41 | UXBM11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
UXBM41 | UXBM11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
UXBM41 | UXBM11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
UXBM41 | UXBM11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
UXBM41 | UXBM11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
WALX41 | WALX21 | 2028 | Addition | 0.0176 | 1.5828 | -0.1018 | 1136
WALX41 | WALX21 | 2028 | Removed | 0.0176 | 1.5828 | -0.1018 | 1136
WALX41 | WALX22 | 2028 | Addition | 0.0176 | 1.5828 | -0.1018 | 1136
WALX41 | WALX22 | 2028 | Removed | 0.0176 | 1.5828 | -0.1018 | 1136
WALX42 | WALX21 | 2028 | Removed | 0.0176 | 1.5828 | -0.1018 | 1137
WALX42 | WALX22 | 2028 | Removed | 0.0176 | 1.5828 | -0.1018 | 1137
WANB41 | WANB31 | 2028 | Addition | 0.2087 | 15.3319 | -0.2971 | 150
WHAM41 | WHAM12 | 2028 | Change | 0.1138 | 8.3534 | -0.0976 | 263
WISD21 | WISD61 | 2028 | Addition | 0.1401 | 8.2113 | -0.0548 | 240
WISD21 | WISD61 | 2028 | Change | 0.1401 | 8.2113 | -0.0548 | 240
WISD21 | WISD61 | 2028 | Change | 0.1401 | 8.2113 | -0.0548 | 240
WISD41 | WISD62 | 2028 | Addition | 0.1844 | 13.1765 | -0.0474 | 180
WOOL41 | WOOL11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
WOOL41 | WOOL11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
WOOL41 | WOOL11 | 2028 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
ABTB21 | ABEB11 | 2030 | Addition | 0.0744 | 8.3386 | -0.0377 | 360
ABTB21 | ABEB11 | 2030 | Addition | 0.0744 | 8.3386 | -0.0377 | 360
ABTB21 | ABTB11 | 2030 | Addition | 0.0744 | 8.3386 | -0.0377 | 360
ABTB21 | ABTB11 | 2030 | Addition | 0.0744 | 8.3386 | -0.0377 | 360
ABTB21 | ABTB11 | 2030 | Addition | 0.0744 | 8.3386 | -0.0377 | 360
ABTB21 | ABTB11 | 2030 | Addition | 0.0744 | 8.3386 | -0.0377 | 360
ABTH21 | ABTH11 | 2030 | Removed | 0.0977 | 8.1994 | -1.7127 | 212
ABTH21 | ABTH11 | 2030 | Removed | 0.1338 | 8.0531 | -0.1824 | 279
ABTH21 | ABTH12 | 2030 | Removed | 0.1646 | 8.0383 | -0.1808 | 211
ALVE41 | ALVE11 | 2030 | Addition | 0.1118 | 8.3874 | -0.0906 | 278
ALVE41 | ALVE11 | 2030 | Addition | 0.1621 | 8.0984 | -0.0747 | 275
ALVE41 | ALVE11 | 2030 | Removed | 0.1118 | 8.3874 | -0.0906 | 278
ALVE42 | ALVE11 | 2030 | Removed | 0.1621 | 8.0984 | -0.0747 | 275
BARK21 | BARW31 | 2028 | Addition | 0.3028 | 23.5814 | -0.4756 | 100
BENR41 | BENR11 | 2030 | Addition | 0.1143 | 8.3534 | -0.103 | 240
BLYT41 | BLYT21 | 2030 | Addition | 0.0152 | 1.6463 | -0.1118 | 1148
BLYT41 | BLYT21 | 2030 | Addition | 0.0152 | 1.6463 | -0.1118 | 1148
BRYN4A | BRYN11 | 2030 | Addition | 0.148 | 7.4973 | -0.3849 | 240
CHTE41 | CHTE21 | 2030 | Addition | 0.0129 | 1.619 | -0.0742 | 1100
CHTE41 | CHTE21 | 2030 | Addition | 0.0129 | 1.619 | -0.0742 | 1100
CHTE41 | CHTE21 | 2030 | Addition | 0.0129 | 1.619 | -0.0742 | 1100
COVE21 | COVE11 | 2030 | Addition | 0.0998 | 8.1961 | -0.0206 | 360
DRAX42 | DRAX12 | 2030 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
HARK21 | HARK21 | 2030 | Removed | 0.2802 | 9.9227 | -0.0925 | 150
HARK21 | HARK21 | 2030 | Removed | 0.2802 | 9.9227 | -0.0925 | 150
HARK41 | HARK31 | 2030 | Addition | 0.3995 | 7.99 | -0.1682 | 150
HARK41 | HARK33 | 2030 | Addition | 0.3995 | 7.99 | -0.1682 | 150
HAWP41 | HAWP21 | 2030 | Addition | 0.013 | 1.6263 | -0.0877 | 1000
HIGB42 | HIGB31 | 2030 | Addition | 0.2087 | 15.3319 | -0.2971 | 150
HIGB41 | HIGB21 | 2030 | Addition | 0.0186 | 1.5729 | -7.729 | 1044
HIGM41 | HIGM21 | 2030 | Removed | 0.0186 | 1.5729 | -7.729 | 1044
HIGM4A | HIGM41 | 2030 | Removed | 0.0002 | 0.2873 | 0 | 2750
LALE21 | LALE11 | 2030 | Change | 0.0744 | 8.3386 | -0.0377 | 360
LALE21 | LALE11 | 2030 | Change | 0.0744 | 8.3386 | -0.0377 | 360
LECH41 | LETH11 | 2030 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
LECH42 | LETH11 | 2030 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
LECH43 | LETH11 | 2030 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
LECH44 | LETH11 | 2030 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
MELK41 | MELK11 | 2030 | Addition | 0.1138 | 8.3534 | -0.0976 | 240
MIDL41 | MIDL11 | 2030 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
MIDL41 | MIDL11 | 2030 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
SJOW21 | SJOW13 | 2030 | Removed | 0.1845 | 7.8956 | -0.1938 | 249
SJOW41 | SJOW13 | 2030 | Addition | 0.1373 | 8.1976 | -0.9295 | 249
SJOW21 | LODR61 | 2030 | Removed | 0.3062 | 11.0235 | -0.4552 | 198
SJOW41 | LODR61 | 2030 | Addition | 0.3062 | 11.0235 | -0.4552 | 198
SJOW41 | SJOW21 | 2030 | Removed | 0.0224 | 2.5703 | -0.5831 | 804
SUND42 | SUND12 | 2030 | Change | 0.1064 | 8.1768 | -0.0914 | 254
TWIN41 | TWIN11 | 2030 | Addition | 0.1373 | 8.1976 | -0.1719 | 278
TWIN42 | TWIN12 | 2030 | Addition | 0.1373 | 8.1976 | -0.1719 | 278
USKM21 | USKM11 | 2030 | Addition | 0.1221 | 8.0449 | -0.2391 | 263
WALP42 | WALP12 | 2030 | Addition | 0.1042 | 7.891 | -0.4318 | 240
WARL21 | WARL12 | 2030 | Addition | 0.0998 | 8.1961 | -0.0206 | 240
WISD21 | WISD61 | 2030 | Change | 0.1401 | 8.2113 | -0.0548 | 240
BLNE41 | BLNE21 | 2033 | Addition | 0.0152 | 1.6463 | -0.1118 | 1148
BLNE41 | BLNE21 | 2033 | Addition | 0.0152 | 1.6463 | -0.1118 | 1148
BLNE41 | BLNE21 | 2033 | Addition | 0.0152 | 1.6463 | -0.1118 | 1148
BLNE41 | BLNE21 | 2033 | Addition | 0.0152 | 1.6463 | -0.1118 | 1148
BLNE41 | BLYT11 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
BLNE41 | BLYT12 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
BLNE41 | BLYT1A | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
BLNE41 | BLYT1B | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
BLNE41 | BLYT61 | 2033 | Addition | 0.1806 | 13.2154 | -0.049 | 180
BLNE41 | BLYT61 | 2033 | Addition | 0.1806 | 13.2154 | -0.049 | 180
BLNE41 | BLYT61 | 2033 | Addition | 0.1806 | 13.2154 | -0.049 | 180
BLNE41 | BLYT61 | 2033 | Addition | 0.1806 | 13.2154 | -0.049 | 180
BLYT41 | BLYT11 | 2033 | Removed | 0.0675 | 4.3908 | -0.2942 | 460
BLYT41 | BLYT12 | 2033 | Removed | 0.0675 | 4.3908 | -0.2942 | 460
BLYT21 | BLYT1A | 2033 | Removed | 0.1666 | 8.378 | -0.1047 | 278
BLYT21 | BLYT1B | 2033 | Removed | 0.1666 | 8.378 | -0.1047 | 278
BLYT41 | BLYT21 | 2033 | Removed | 0.0152 | 1.6463 | -0.1118 | 1148
BLYT41 | BLYT21 | 2033 | Removed | 0.0152 | 1.6463 | -0.1118 | 1148
BLYT41 | BLYT21 | 2033 | Removed | 0.0152 | 1.6463 | -0.1118 | 1148
BLYT41 | BLYT21 | 2033 | Removed | 0.0152 | 1.6463 | -0.1118 | 1148
BLYT21 | BLYT61 | 2033 | Removed | 0.2275 | 10.8456 | -0.0697 | 209
BLYT21 | BLYT61 | 2033 | Removed | 0.45 | 16.8273 | -1.3475 | 138
BLYT21 | BLYT61 | 2033 | Removed | 0.45 | 16.8273 | -1.3475 | 138
CARL41 | CARL41 | 2033 | Addition | 0.0002 | 0.4178 | -13.7492 | 2750
CARL41 | CARL41 | 2033 | Addition | 0.0002 | 0.4178 | -13.7492 | 2750
ECLA41 | ECLA11 | 2033 | Removed | 0.1139 | 8.1036 | -2.059 | 278
ECLA41 | ECLA11 | 2033 | Removed | 0.0997 | 8.0088 | -0.093 | 264
ECLA41 | ECLA12 | 2033 | Removed | 0.1175 | 8.6648 | -0.4173 | 263
ECLA41 | ECLA12 | 2033 | Removed | 0.1175 | 8.6648 | -0.4173 | 264
KIBY41 | KIBY21 | 2033 | Addition | 0.0124 | 1.619 | -5.4994 | 1100
KIBY41 | KIBY21 | 2033 | Addition | 0.0124 | 1.619 | -5.4994 | 1100
KIBY41 | KIBY21 | 2033 | Addition | 0.0124 | 1.619 | -5.4994 | 1100
LALE21 | LALE11 | 2033 | Change | 0.0744 | 8.3386 | -0.0377 | 360
LALE21 | LALE11 | 2033 | Change | 0.0744 | 8.3386 | -0.0377 | 360
LOWF41 | LOWF11 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
LOWF41 | LOWF11 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
LOWF41 | LOWF11 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
NECL41 | NECL11 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
NECL41 | NECL11 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
NECL42 | NECL12 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
NECL42 | NECL12 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
WARL41 | NWAR11 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
WARL41 | NWAR11 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
WARL41 | NWAR12 | 2033 | Addition | 0.0675 | 4.3908 | -0.2942 | 460
STWT41 | STEW21 | 2033 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
STWT42 | STEW21 | 2033 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
THOM21 | THOM61 | 2033 | Removed | 0.3985 | 16.2118 | -0.4431 | 122
THOM41 | THOM21 | 2033 | Addition | 0.0124 | 1.619 | -1.098 | 1100
THOM42 | THOM21 | 2033 | Removed | 0.0185 | 1.614 | -0.5638 | 879
TIBB41 | TIBB21 | 2033 | Addition | 0.0117 | 1.591 | -4.4806 | 1000
TIBB41 | TILB12 | 2033 | Addition | 0.1381 | 7.9571 | -0.0844 | 240
TIBB42 | TILB11 | 2033 | Addition | 0.1381 | 7.9571 | -0.0844 | 240
TILB21 | TILB11 | 2033 | Removed | 0.1 | 8.0952 | -0.2374 | 240
TILB21 | TILB12 | 2033 | Removed | 0.1004 | 8.1994 | -0.2371 | 240
TILB4A | TILB21 | 2033 | Removed | 0.0376 | 2.1949 | -10.6848 | 829
TILB4B | TILB21 | 2033 | Removed | 0.0117 | 1.591 | -4.4806 | 1102
WARL41 | WARL21 | 2033 | Addition | 0.0152 | 1.6463 | -0.1118 | 1100
TILN41 | TILN41 | 2030 | Addition | 0.0002 | 0.2873 | 0 | 2750
TILN41 | TILN41 | 2030 | Addition | 0.0002 | 0.2873 | 0 | 2750
NERY41 | NERY41 | 2033 | Addition | 0.0002 | 0.2873 | 0 | 2750
NERY42 | NERY42 | 2033 | Addition | 0.0002 | 0.4178 | 0 | 2750
WALB41 | WALB41 | 2033 | Addition | 0.0002 | 0.4207 | -16.2245 | 2750
WALB42 | WALB42 | 2033 | Addition | 0.0002 | 0.4207 | -16.2245 | 2750

## B-3-2d
B.3.2d - OFTO Transformer Changes 2026/27 to 2033/34
Wind Farm | Node 1 | Node 2 | Year | Status | R (% on 100 MVA) | X (% on 100 MVA) | B (% on 100 MVA) | Rating(MVA) | Voltage(kV)
Dogger Bank B Offshore Wind Farm | DBBO41 | DBBODC | 2026 | Addition | 0.07 | 3.52 | 0 | 426 | 400/379
| DBBWDC | DBBW61 | 2026 | Addition | 0.001 | 5.72 | 0 | 664 | 392/66
East Anglia 3A Offshore Wind Farm | BRFO41 | Onshore Converter station | 2026 | Addition | 0.031 | 2.75 | 0 | 1390 | 400/360
| EACO41 | Offshore Converter station | 2026 | Addition | 0.0104 | 1.274 | 0 | 682 | 330/66
| EACO41 | Ofshore Converter station | 2026 | Addition | 0.0104 | 1.274 | 0 | 682 | 330/66
Hornsea 3A-1 Offshore Wind Farm | HOWC41 | HOWC4X | 2026 | Addition | TBC | TBC | TBC | 469 | 400/390
Hornsea 3A-2 Offshore Wind Farm | HOWC42 | HOWC4X | 2026 | Addition | TBC | TBC | TBC | 469 | 400/390
Hornsea 4A-1 Offshore Wind Farm | HOWW2F | HOWW6F | 2028 | Addition | TBC | TBC | TBC | 338 | 275/66
Hornsea 4A-2 Offshore Wind Farm | HOWD41 | HOWD21 | 2028 | Addition | TBC | TBC | TBC | 594 | 400/275
Seagreen 1A offshore windfarm | Onshore 275kV-1 | Onshore 220kV-1 | 2028 | Addition | TBC | TBC | TBC | TBC | 275/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2028 | Addition | TBC | TBC | TBC | TBC | 220/66
Berwick 2 Offshore Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2028 | Addition | TBC | TBC | TBC | 660 | 400/275
| Onshore 400kV-1 | Onshore 275kV-1 | 2028 | Addition | TBC | TBC | TBC | 660 | 400/275
| Onshore 400kV-1 | Onshore 275kV-1 | 2028 | Addition | TBC | TBC | TBC | 660 | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2028 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2028 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 275kV-3 | Offshore 66kV-3 | 2028 | Addition | TBC | TBC | TBC | 430 | 275/66
Erebus Offshore windfarm | EOWL11 | EOWF61 | 2028 | Addition | TBC | TBC | TBC | 120 | 132/66
| EOWL11 | EOWF61 | 2028 | Addition | TBC | TBC | TBC | 120 | 132/66
Vanguard East Offshore Wind Farm | VGEO41 | Onshore Converter LV | 2028 | Addition | TBC | TBC | TBC | TBC | 400/365
| VGEWX1 | Onshore AC platform | 2028 | Addition | TBC | TBC | TBC | TBC | 365/220
| Offshore AC Platform HV | VGEWX2 | 2028 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore AC Platform HV | VGEWX3 | 2028 | Addition | TBC | TBC | TBC | TBC | 220/66
Awel Y Mor Extension Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2028 | Addition | TBC | TBC | TBC | TBC | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2028 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2028 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2028 | Addition | TBC | TBC | TBC | TBC | 220/66
Sofia Offshore Wind Farm | SOFWD | SOFW61 | 2028 | Addition | 0.0117 | 2.91 | 0 | 940 | 360/66
| SOFWD | SOFW61 | 2028 | Addition | 0.0117 | 2.91 | 0 | 940 | 360/66
Inch Cape Offshore Wind Farm | INCO2A | INCO21 | 2028 | Addition | 0.064 | 8.35 | 0 | 610 | 275/220
| INCO2A | INCO22 | 2028 | Addition | 0.064 | 8.35 | 0 | 610 | 275/220
| INCW21 | INCW61 | 2028 | Addition | 0.093 | 5.45 | 0 | 545 | 220/66
| INCW22 | INCW62 | 2028 | Addition | 0.093 | 5.45 | 0 | 545 | 220/66
Pentland Floating Offshore Windfarm | Onshore 132 kV HV | Onshore 66 kV HV | 2030 | Addition | TBC | TBC | TBC | 120 | 132/66
| Onshore 132 kV HV | Onshore 66 kV HV | 2030 | Addition | TBC | TBC | TBC | 120 | 132/66
Berwick 1 Offshore Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | 660 | 400/275
| Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | 660 | 400/275
| Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | 660 | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | 430 | 275/66
| Offshore 275kV-3 | Offshore 66kV-3 | 2030 | Addition | TBC | TBC | TBC | 430 | 275/66
Berwick Bank Offshore Wind Farm C | Onshore 400kV-1 | Onshore Converter station 400kV | 2030 | Addition | TBC | TBC | TBC | TBC | 400/525
| Offshore Converter station 400kV | Offshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 525/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-3 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
Elizabeth Yellow One | Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-1 | Onshore 275kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-3 | Offshore 66kV-3 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
Vanguard West Offshore Wind Farm | VGWWX1 | VGWWX2 | 2030 | Addition | TBC | TBC | TBC | TBC | TBC
| VGWWX1 | VGWWX3 | 2030 | Addition | TBC | TBC | TBC | TBC | TBC
Morecambe Offshore Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | 450 | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2030 | Addition | TBC | TBC | TBC | 450 | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 275kV-2 | Offshore 66kV-4 | 2030 | Addition | TBC | TBC | TBC | TBC | 220/66
OWPL Offshore Windfarm | Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-3 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-4 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
Project Elizabeth Offshore Windfarm | Onshore 400kV-1 | Onshore 275kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-3 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-4 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
Rampion Extension Windfarm | Onshore 400kV-1 | Onshore 220kV-1 | 2030 | Addition | TBC | TBC | TBC | 450 | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2030 | Addition | TBC | TBC | TBC | 450 | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | 400 | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | 400 | 220/66
Five Estuaries Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 220/66
North Falls Offshore Wind Farm | Onshore 400kV-1 | Onshore 275V-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2030 | Addition | TBC | TBC | TBC | TBC | 275/66
Dogger Bank C East Offshore Wind Farm | DBCO41 | DBCODC | 2030 | Addition | TBC | TBC | TBC | 426 | 400/379
| DBCWDC | DBCW61 | 2030 | Addition | TBC | TBC | TBC | 664 | 392/66
| DBCW21 | DBCW63 | 2030 | Addition | TBC | TBC | TBC | TBC | 220/66
| DBCW21 | DBCW64 | 2030 | Addition | TBC | TBC | TBC | TBC | 220/66
East Anglia 2A Offshore Wind Farm | EABO41 | Onshore 220kV-1 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2030 | Addition | TBC | TBC | TBC | 525 | 220/66
East Anglia 1 North Offshore Wind Farm | EANO41 | EANO21 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| EANO41 | EANO21 | 2030 | Addition | TBC | TBC | TBC | TBC | 400/275
| EANW21 | EANW61 | 2030 | Addition | TBC | TBC | TBC | 525 | 275/66
| EANW21 | EANW61 | 2030 | Addition | TBC | TBC | TBC | 525 | 275/66
Cenos Central Offshore Wind Farm | Onshore Converter HV | Onshore Converter LV | 2033 | Addition | TBC | TBC | TBC | 800 | 400/300
| Onshore Converter HV | Onshore Converter LV | 2033 | Addition | TBC | TBC | TBC | 800 | 400/300
| Onshore DC Platform |  | 2033 | Addition | TBC | TBC | TBC | 400 | 300/66
| Offshore AC Platform HV | Ofshore AC platform LV | 2033 | Addition | TBC | TBC | TBC | 400 | 300/66
| Offshore AC Platform HV | Ofshore AC platform LV | 2033 | Addition | TBC | TBC | TBC | 400 | 300/66
| Offshore AC Platform HV | Ofshore AC platform LV | 2033 | Addition | TBC | TBC | TBC | 400 | 300/66
EQUINOR Offshore Windfarm | Onshore 400kV-1 | Onshore 275kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
Green Volt Offshore Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2033 | Addition | TBC | TBC | TBC | 450 | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2033 | Addition | TBC | TBC | TBC | 450 | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2033 | Addition | TBC | TBC | TBC | 400 | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | 400 | 220/66
Caledonia Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-1 | Onshore 275kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-3 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-4 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-3 | Offshore 66kV-3 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-4 | Offshore 66kV-4 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
East Anglia 2B Offshore Wind Farm | EABO41 | Onshore 220kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-2 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | 525 | 220/66
GT R4 Wind Farm (Outer Dowsing) | Onshore 400kV-1 | Onshore 275kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-1 | Onshore 275kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-3 | Offshore 66kV-3 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
Spiorad na Mara | Onshore 400kV-1 | Onshore 275kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-1 | Onshore 275kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
Ayre Offshore Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
BELLROCK OFFSHORE WINDFARM | Onshore 275kV-1 | Onshore 220kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-1 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
Buchan 01 Offshore Wind Farm | Onshore 400kV-1 | Onshore 275kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Onshore 400kV-2 | Onshore 275kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/275
| Offshore 275kV-1 | Offshore 66kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-2 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
Gatroben Offshore Wind Farm | Onshore Converter HV | Onshore Converter LV | 2033 | Addition | TBC | TBC | TBC | TBC | 400/320
| Onshore DC Platform | Onshore AC platform | 2033 | Addition | TBC | TBC | TBC | TBC | 320/220
| Offshore AC Platform HV | Offshore AC Platform LV | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore AC Platform HV | Offshore AC Platform LV | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
Morven Offshore Wind Farm | Onshore Converter HV | Onshore Converter LV | 2033 | Addition | TBC | TBC | TBC | TBC | 400/320
| Onshore DC Platform | Onshore AC platform | 2033 | Addition | TBC | TBC | TBC | TBC | 320/220
| Offshore AC Platform HV | Offshore AC Platform LV | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore AC Platform HV | Offshore AC Platform LV | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
Morven Extension Offshore Wind Farm | Onshore Converter HV | Onshore Converter LV | 2033 | Addition | TBC | TBC | TBC | TBC | 400/320
| Onshore DC Platform | Onshore AC platform | 2033 | Addition | TBC | TBC | TBC | TBC | 320/220
| Offshore AC Platform HV | Offshore AC Platform LV | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore AC Platform HV | Offshore AC Platform LV | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
Stromar Offshore Wind Farm | Onshore 400kV-1 | Onshore 220kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/220
| Onshore 400kV-2 | Onshore 220kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-1 | Offshore 66kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
| Offshore 220kV-2 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 220/66
East Anglia 2B Offshore Wind Farm | EABO41 | Onshore 220kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 400/220
| Offshore 220kV-2 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | 525 | 220/66
Marram | Onshore 400kV-1 | Onshore Converter station 400kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | TBC
| Offshore Converter station 400kV-1 | Offshore 275kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | TBC
| Offshore 275kV-1 | Offshore 66kV-1 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-2 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66
| Offshore 275kV-1 | Offshore 66kV-3 | 2033 | Addition | TBC | TBC | TBC | TBC | 275/66

## B-4-1a
B-4-1a - SHE Transmission Reactive Compensation Equipment 2025/26
Site Name | Node | Unit Number | MVar Generation | MVar Absorption | Compensation Type | Connection Voltage (kV)
ALYTH | ALYT21 | 1 | 225 | 225 | SVC | 275
ALYTH | ALYT21 | 1 | 100 | 0 | Mechanically Switched Capacitor | 275
BEAULY | BEAU11 | 2 | 46 | 0 | Mechanically Switched Capacitor | 132
BEAULY | BEAU11 | 1 | 46 | 0 | Mechanically Switched Capacitor | 132
BEAULY | BEAU21 | 1 | 150 | 150 | SVC | 275
BEAULY | BEAU3U | 1 | 0 | 88 | Reactor | 33
BEAULY | BEAU3V | 2 | 0 | 88 | Reactor | 33
CROSSAIG | CRSS3W | 1 | 0 | 60 | Reactor | 33
CROSSAIG | CRSS3X | 2 | 0 | 60 | Reactor | 33
DOUNREAY | DOUN3W | 1 | 0 | 59 | Reactor | 33
DOUNREAY | DOUN3X | 2 | 0 | 62 | Reactor | 33
FORT AUGUSTUS | FAUG3W | 3 | 0 | 60 | Reactor | 33
FORT AUGUSTUS | FAUG3X | 1 | 0 | 60 | Reactor | 33
FORT AUGUSTUS | FAUG3Y | 2 | 0 | 59 | Reactor | 33
FORT AUGUSTUS | FAUG3Z | 4 | 0 | 60 | Reactor | 33
KINARDOCHY | KINA21 | 1 | 100 | 0 | Mechanically Switched Capacitor | 275
KINARDOCHY | KINA2J | 1 | 225 | 225 | SVC | 275
KINTORE | KINT11 | 4 | 0 | 97 | Reactor | 132
KINTORE | KINT11 | 2 | 0 | 97 | Reactor | 132
KINTORE | KINT3W | 1 | 0 | 62 | Reactor | 33
KINTORE | KINT3Y | 3 | 0 | 62 | Reactor | 33
MELGARVE | MELG4J | 1 | 100 | 100 | Statcom | 400
MELGARVE | MELG4K | 2 | 100 | 100 | Statcom | 400
TEALING | TEAL11 | 1 | 0 | 97 | Reactor | 132
TEALING | TEAL11 | 1 | 46 | 0 | Mechanically Switched Capacitor | 132
TEALING | TEAL21 | 1 | 225 | 75 | SVC | 275
TEALING | TEAL3W | 2 | 0 | 32 | Reactor | 33
TEALING | TEAL3Y | 3 | 0 | 62 | Reactor | 33

## B-4-1b
B-4-1b - SPT Reactive Compensation Equipment 2025/26
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Bonnybridge | BONN3U | 1 | 0 | 60 | Reactor | 33
Bonnybridge | BONN3V | 2 | 0 | 60 | Reactor | 33
Coalburn | COAL3U | 1 | 0 | 60 | Reactor | 33
Coalburn | COAL3V | 2 | 0 | 60 | Reactor | 33
Cockenzie | COCK2- | 1 | 231 | 0 | Mechanically Switched Capacitor | 275
Crystal Rig | CRYR3V | 1 | 0 | 60 | Reactor | 33
Currie | CURR3W | 1 | 0 | 60 | Reactor | 33
Dewar Place | DEWP3- | 1 | 0 | 60 | Reactor | 33
Dewar Place | DEWP3- | 2 | 0 | 60 | Reactor | 33
Eccles | ECCL3V | 1 | 0 | 60 | Reactor | 33
Elvanfoot | ELVA3V | 1 | 0 | 60 | Reactor | 33
Elvanfoot | ELVA4- | 1 | 226 | 0 | Mechanically Switched Capacitor | 400
Hunterston Converter Station | HUCS4- | 1 | 248 | 382 | Statcom | 400
Hunterston East | HUNE4- | 1 | 0 | 200 | Reactor | 400
Hunterston North | HUNN3W | 1 | 0 | 60 | Reactor | 33
Hunterston North | HUNN3X | 2 | 0 | 60 | Reactor | 33
Kilgallioch | KILG2- | 1 | 0 | 60 | Reactor | 275
Kilmarnock South | KILS3U | 1 | 0 | 60 | Reactor | 33
Kilmarnock South | KILS3X | 2 | 0 | 60 | Reactor | 33
Longannet | LOAN2- | 1 | 225 | 0 | Mechanically Switched Capacitor | 275
Longannet | LOAN2- | 2 | 225 | 0 | Mechanically Switched Capacitor | 275
Mark Hill | MAHI3U | 1 | 0 | 60 | Reactor | 33
Moffat | MOFF3U | 1 | 0 | 60 | Reactor | 33
Moffat | MOFF4- | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 70 | Statcom | 275
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 33 | Sync comp | 275
Neilston | NEIL3U | 1 | 0 | 60 | Reactor | 33
Neilston | NEIL3V | 2 | 0 | 60 | Reactor | 33
Smeaton | SMEA3U | 1 | 0 | 60 | Reactor | 33
Smeaton | SMEA3V | 2 | 0 | 60 | Reactor | 33
Strathaven | STHA3V | 1 | 0 | 60 | Reactor | 33
Torness | TORN4- | 1 | 0 | 150 | Reactor | 400
Torness | TORN4- | 2 | 0 | 150 | Reactor | 400
Wishaw (Gowkthrapple) | WISH3W | 1 | 0 | 60 | Reactor | 33
Windyhill | WIYH2- | 1 | 150 | 0 | Mechanically Switched Capacitor | 275
Windyhill | WIYH3W | 1 | 0 | 60 | Reactor | 33

## B-4-1c
B-4-1c - NGET Reactive Compensation Equipment for 2025/26
Site Name | Node | Unit Number | Mvar Generation | Mvar Absorption | Compensation Type | Connection Voltage (kV)
Aberthaw | ABHA11 | 3 | 45 | 0 | Mechanically Switched Capacitor | 132
Aberthaw | ABHA12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
Aberthaw | ABTH11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Aberthaw | ABTH11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Alverdiscott | ALVE11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Barking | BARK22 | 1 | 0 | 30 | Reactor | 13
Barking | BARK22 | 2 | 0 | 30 | Reactor | 13
Barking | BARK22 | 3 | 0 | 30 | Reactor | 13
Barking | BARK22 | 4 | 0 | 30 | Reactor | 13
Beddington | BEDD21 | 1 | 0 | 60 | Reactor | 13
Beddington | BEDD21 | 2 | 0 | 60 | Reactor | 13
Beddington | BEDD21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Beddington | BEDD21 | 3 | 0 | 100 | Reactor | 275
Beddington | BEDD22 | 4 | 0 | 60 | Reactor | 13
Beddington | BEDD22 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275
Beddington | BEDD23 | 5 | 0 | 60 | Reactor | 13
Beddington | BEDD23 | 6 | 0 | 100 | Reactor | 275
Berkswell | BESW11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Berkswell | BESW12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Berkswell | BESW12 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Birkenhead | BIRK21 | 1 | 0 | 30 | Reactor | 13
Birkenhead | BIRK21 | 2 | 0 | 30 | Reactor | 13
Bishops Wood | BISW11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Bishops Wood | BISW11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Blyth | BLYT21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275
Blyth | BLYT21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Bolney | BOLN11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Bolney | BOLN11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Bolney | BOLN12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Bolney | BOLN12 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Bolney | BOLN41 | 2 | 0 | 60 | Reactor | 13
Bolney | BOLN41 | 1 | 225 | 100 | SVC | 32
Bolney | BOLN41 | 1 | 0 | 60 | Reactor | 13
Bolney | BOLN41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Bolney | BOLN41 | 2 | 228 | 0 | Mechanically Switched Capacitor | 400
Bradford West | BRAW11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Bradford West | BRAW21 | 1 | 0 | 30 | Reactor | 13
Bradford West | BRAW21 | 2 | 0 | 30 | Reactor | 13
Bradford West | BRAW21 | 3 | 0 | 60 | Reactor | 13
Bradford West | BRAW21 | 4 | 0 | 100 | Reactor | 275
Bredbury | BRED21 | 1 | 0 | 30 | Reactor | 13
Bredbury | BRED21 | 2 | 0 | 30 | Reactor | 13
Bredbury | BRED21 | 3 | 0 | 30 | Reactor | 13
Bredbury | BRED21 | 4 | 0 | 30 | Reactor | 13
Bramford | BRFO11 | 1 | 59 | 0 | Mechanically Switched Capacitor | 132
Bramford | BRFO11 | 2 | 59 | 0 | Mechanically Switched Capacitor | 132
Bramford | BRFO11 | 3 | 59 | 0 | Mechanically Switched Capacitor | 132
Bramford | BRFO41 | 1 | 0 | 200 | Reactor | 400
Bridgwater | BRWA11 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
Bridgwater | BRWA11 | 2 | 45 | 0 | Mechanically Switched Capacitor | 132
Burwell | BURW41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Burwell | BURW41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400
Bushbury | BUSH11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Bushbury | BUSH11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Bushbury | BUSH11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Bushbury | BUSH21 | 1 | 0 | 60 | Reactor | 13
Bushbury | BUSH21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275
Bustleholme | BUST21 | 1 | 0 | 30 | Reactor | 13
Bustleholme | BUST21 | 2 | 0 | 30 | Reactor | 13
Bustleholme | BUST21 | 3 | 0 | 60 | Reactor | 13
Canterbury North | CANT41 | 1 | 0 | 200 | Reactor | 400
Capenhurst | CAPE21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Cellarhead | CELL11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Cellarhead | CELL11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Cellarhead | CELL12 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Cellarhead | CELL12 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Cellarhead | CELL41 | 1 | 0 | 30 | Reactor | 13
Cellarhead | CELL41 | 2 | 0 | 30 | Reactor | 13
Cellarhead | CELL41 | 3 | 0 | 30 | Reactor | 13
Cellarhead | CELL41 | 1 | 150 | 95 | SVC | 8
Cellarhead | CELL41 | 4 | 0 | 30 | Reactor | 13
Cellarhead | CELL41 | 1 | 150 | 95 | SVC | 8
Cellarhead | CELL41 | 5 | 230 | 0 | Mechanically Switched Capacitor | 400
Cellarhead | CELL41 | 6 | 230 | 0 | Mechanically Switched Capacitor | 400
Chickerell | CHIC41 | 2 | 0 | 60 | Reactor | 13
Chickerell | CHIC41 | 1 | 0 | 200 | Reactor | 400
Chickerell | CHIC42 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Chickerell | CHIC42 | 3 | 0 | 200 | Reactor | 400
Chesterfield | CHTE21 | 1 | 0 | 60 | Reactor | 13
Cilfynydd | CILF41 | 1 | 0 | 60 | Reactor | 13
Cilfynydd | CILF41 | 2 | 0 | 60 | Reactor | 13
Cilfynydd | CILF41 | 3 | 0 | 200 | Reactor | 400
Cilfynydd | CILF41 | 4 | 0 | 200 | Reactor | 400
City Road | CITR41 | 1 | 56 | 0 | Mechanically Switched Capacitor | 13
City Road | CITR41 | 2 | 56 | 0 | Mechanically Switched Capacitor | 13
City Road | CITR41 | 1 | 0 | 200 | Reactor | 400
Cottam | COTT41 | 1 | 0 | 200 | Reactor | 400
Coventry | COVE11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Coventry | COVE11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Coventry | COVE12 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Coventry | COVE21 | 1 | 0 | 60 | Reactor | 13
Cowley | COWL11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Cowley | COWL11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Cowley | COWL11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Cowley | COWL41 | 1 | 0 | 200 | Reactor | 400
Cowley | COWL41 | 2 | 0 | 200 | Reactor | 400
Drakelow | DRAK41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Drakelow | DRAK41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Drakelow | DRAK41 | 1 | 0 | 200 | Reactor | 400
Drakelow | DRAK41 | 2 | 0 | 200 | Reactor | 400
Drax | DRAX41 | 1 | 0 | 60 | Reactor | 13
Drax | DRAX41 | 2 | 0 | 60 | Reactor | 13
East Claydon | ECLA12 | 1 | 61 | 0 | Mechanically Switched Capacitor | 132
East Claydon | ECLA41 | 1 | 0 | 30 | Reactor | 13
East Claydon | ECLA41 | 2 | 0 | 30 | Reactor | 13
East Claydon | ECLA41 | 3 | 0 | 30 | Reactor | 13
East Claydon | ECLA41 | 4 | 0 | 30 | Reactor | 13
East Claydon | ECLA41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
East Claydon | ECLA41 | 5 | 0 | 200 | Reactor | 400
East Claydon | ECLA41 | 3 | 230 | 0 | Mechanically Switched Capacitor | 400
Elland | ELLA21 | 1 | 0 | 60 | Reactor | 13
Exeter | ELLA21 | 1 | 150 | 95 | SVC | 8
Exeter | ELLA21 | 2 | 150 | 95 | SVC | 8
Elstree | ELST41 | 1 | 0 | 200 | Reactor | 400
Enderby | ENDE41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Enderby | ENDE41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Exeter | EXET11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Exeter | EXET41 | 1 | 28 | 0 | Mechanically Switched Capacitor | 13
Exeter | EXET41 | 3 | 28 | 0 | Mechanically Switched Capacitor | 13
FECKENHAM | FECK21 | 1 | 150 | 75 | SVC | 275
Feckenham | FECK41 | 1 | 0 | 30 | Reactor | 13
Feckenham | FECK41 | 2 | 0 | 30 | Reactor | 13
Fleet | FLEE11 | 1 | 53 | 0 | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 2 | 53 | 0 | Mechanically Switched Capacitor | 132
Fleet | FLEE11 | 3 | 53 | 0 | Mechanically Switched Capacitor | 132
Fleet | FLEE41 | 1 | 0 | 30 | Reactor | 13
Fleet | FLEE41 | 2 | 0 | 30 | Reactor | 13
Fleet | FLEE41 | 3 | 0 | 30 | Reactor | 13
Fleet | FLEE41 | 4 | 0 | 30 | Reactor | 13
Fleet | FLEE41 | 4 | 230 | 0 | Mechanically Switched Capacitor | 400
Flintshire Bridge | FLIB41 | 1 | 0 | 235 | Reactor | 400
Flintshire Bridge | FLIB41 | 2 | 0 | 235 | Reactor | 400
Flintshire Bridge | FLIB41 | 3 | 0 | 235 | Reactor | 400
Frodsham | FROD41 | 1 | 0 | 200 | Reactor | 400
Grain | GRAI41 | 1 | 0 | 200 | Reactor | 400
Grendon | GREN11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Grendon | GREN11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Grendon | GREN11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Grendon | GREN41 | 1 | 0 | 60 | Reactor | 13
Grendon | GREN41 | 4 | 225 | 0 | Mechanically Switched Capacitor | 400
Grendon | GREN41 | 5 | 230 | 0 | Mechanically Switched Capacitor | 400
Grendon | GREN41 | 6 | 230 | 0 | Mechanically Switched Capacitor | 400
Grendon | GREN41 | 7 | 225 | 0 | Mechanically Switched Capacitor | 400
Greystones A | GRST2A | 1 | 0 | 100 | Reactor | 275
Greystones B | GRST2B | 2 | 0 | 100 | Reactor | 275
Hams Hall | HAMH41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Hams Hall | HAMH41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Hams Hall | HAMH41 | 1 | 0 | 200 | Reactor | 400
Harker | HARK21 | 1 | 146 | 124 | SVC | 14
Harker | HARK21 | 2 | 146 | 124 | SVC | 14
Harker | HARK21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Harker | HARK41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400
Harker | HARK41 | 3 | 225 | 0 | Mechanically Switched Capacitor | 400
Harker | HARK41 | 4 | 225 | 0 | Mechanically Switched Capacitor | 400
Hurst | HURS21 | 1 | 0 | 60 | Reactor | 13
Hurst | HURS21 | 2 | 0 | 60 | Reactor | 13
Hurst | HURS21 | 3 | 0 | 100 | Reactor | 275
Hurst | HURS21 | 4 | 0 | 100 | Reactor | 275
Hurst | HURS21 | 5 | 0 | 100 | Reactor | 275
Hurst | HURS21 | 6 | 0 | 100 | Reactor | 275
Hurst | HURS21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Hutton | HUTT41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400
Indian Queens | INDQ11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Indian Queens | INDQ11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Indian Queens | INDQ11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Indian Queens | INDQ41 | 1 | 0 | 60 | Reactor | 13
Indian Queens | INDQ41 | 4 | 230 | 0 | Mechanically Switched Capacitor | 400
Indian Queens | INDQ41 | 2 | 0 | 200 | Reactor | 400
Iron Acton | IROA11 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
Ironbridge | IRON11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Ironbridge | IRON12 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Ironbridge | IRON12 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Ironbridge | IRON41 | 4 | 231 | 0 | Mechanically Switched Capacitor | 400
Ironbridge | IRON41 | 1 | 0 | 200 | Reactor | 400
Iver | IVER21 | 1 | 0 | 60 | Reactor | 13
Iver | IVER21 | 2 | 0 | 60 | Reactor | 13
IVER | IVER4A | 1 | 0 | 55 | Reactor | 400
IVER | IVER4B | 2 | 0 | 55 | Reactor | 400
Jordanthorpe | JORD31 | 1 | 0 | 60 | Reactor | 33
Kearsley | KEAR11 | 1 | 53 | 0 | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | 2 | 53 | 0 | Mechanically Switched Capacitor | 132
Kearsley | KEAR11 | 3 | 53 | 0 | Mechanically Switched Capacitor | 132
Kearsley | KEAR21 | 1 | 0 | 60 | Reactor | 13
Kirkby | KIBY11 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
Kirkby | KIBY11 | 2 | 45 | 0 | Mechanically Switched Capacitor | 132
Kirkby | KIBY11 | 3 | 45 | 0 | Mechanically Switched Capacitor | 132
Kirkby | KIBY11 | 4 | 45 | 0 | Mechanically Switched Capacitor | 132
Kingsnorth | KINO41 | 1 | 0 | 30 | Reactor | 13
Kingsnorth | KINO41 | 2 | 0 | 30 | Reactor | 13
Kingsnorth | KINO41 | 3 | 0 | 30 | Reactor | 13
Kingsnorth | KINO41 | 4 | 0 | 30 | Reactor | 13
Kingsnorth | KINO41 | 5 | 0 | 200 | Reactor | 400
Kingsnorth | KINO41 | 6 | 0 | 200 | Reactor | 400
Kirkstall | KIRK21 | 1 | 0 | 60 | Reactor | 13
Kirkstall | KIRK21 | 2 | 0 | 60 | Reactor | 13
Kirkstall | KIRK21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Lackenby | LACK21 | 1 | 20 | 0 | Mechanically Switched Capacitor | 13
Lackenby | LACK21 | 2 | 20 | 0 | Mechanically Switched Capacitor | 13
Lackenby | LACK21 | 3 | 20 | 0 | Mechanically Switched Capacitor | 13
Laleham | LALE21 | 1 | 0 | 100 | Reactor | 275
Laleham | LALE21 | 2 | 0 | 100 | Reactor | 275
Laleham | LALE21 | 3 | 0 | 100 | Reactor | 275
Landulph | LAND11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Landulph | LAND41 | 1 | 0 | 30 | Reactor | 13
Landulph | LAND41 | 2 | 0 | 30 | Reactor | 13
Landulph | LAND42 | 1 | 60 | 60 | SVC | 13
Landulph | LAND42 | 3 | 0 | 200 | Reactor | 400
Legacy | LEGA41 | 1 | 0 | 60 | Reactor | 13
Legacy | LEGA41 | 2 | 0 | 60 | Reactor | 13
Legacy | LEGA41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Lister Drive | LISD21 | 1 | 0 | 100 | Reactor | 275
Lovedean | LOVE41 | 1 | 0 | 60 | Reactor | 13
Lovedean | LOVE41 | 1 | 150 | 95 | SVC | 8
Lovedean | LOVE41 | 2 | 0 | 60 | Reactor | 13
Lovedean | LOVE41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Lovedean | LOVE41 | 1 | 0 | 200 | Reactor | 400
Lovedean | LOVE41 | 2 | 0 | 200 | Reactor | 400
Mannington | MANN11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Mannington | MANN11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Mannington | MANN11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Mannington | MANN11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Mannington | MANN11 | 5 | 60 | 0 | Mechanically Switched Capacitor | 132
Mannington | MANN11 | 6 | 60 | 0 | Mechanically Switched Capacitor | 132
Melksham | MELK11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132
Melksham | MELK11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Melksham | MELK11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Melksham | MELK41 | 1 | 0 | 60 | Reactor | 13
Melksham | MELK41 | 2 | 0 | 60 | Reactor | 13
Melksham | MELK41 | 3 | 0 | 200 | Reactor | 400
Mill Hill | MILH2A | 1 | 0 | 30 | Reactor | 13
Mill Hill | MILH2A | 2 | 0 | 30 | Reactor | 13
Mill Hill | MILH2A | 3 | 0 | 30 | Reactor | 13
Mill Hill | MILH2B | 4 | 0 | 30 | Reactor | 13
Monk Fryston | MONF21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Nechells | NECH21 | 1 | 0 | 30 | Reactor | 13
Nechells | NECH21 | 2 | 0 | 60 | Reactor | 13
Nechells | NECH21 | 3 | 0 | 30 | Reactor | 13
New Cross | NEWX21 | 1 | 0 | 100 | Reactor | 275
New Cross | NEWX21 | 2 | 0 | 100 | Reactor | 275
Ninfield | NINF41 | 1 | 225 | 100 | SVC | 57
Ninfield | NINF41 | 1 | 0 | 200 | Reactor | 400
Ninfield | NINF41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
NINFIELD | NINF41 | 1 | 150 | 150 | SVC | 57
Nursling | NURS41 | 1 | 0 | 60 | Reactor | 13
Ocker Hill | OCKH21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Oldbury | OLDB21 | 1 | 0 | 30 | Reactor | 13
Oldbury | OLDB21 | 2 | 0 | 30 | Reactor | 13
Pelham | PELH41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Pelham | PELH41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400
Pelham | PELH41 | 1 | 0 | 200 | Reactor | 400
Pembroke | PEMB41 | 1 | 0 | 60 | Reactor | 13
Pembroke | PEMB41 | 3 | 0 | 60 | Reactor | 13
Pentir | PENT41 | 1 | 0 | 200 | Reactor | 400
Pentir | PENT41 | 2 | 0 | 200 | Reactor | 400
Penwortham | PEWO41 | 1 | 0 | 60 | Reactor | 13
Pitsmoor | PITS31 | 1 | 0 | 60 | Reactor | 33
Pitsmoor | PITS31 | 2 | 0 | 60 | Reactor | 33
Port Ham | PORH11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Port Ham | PORH11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Rainhill | RAIN11 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
Rainhill | RAIN11 | 2 | 45 | 0 | Mechanically Switched Capacitor | 132
Rainhill | RAIN12 | 3 | 45 | 0 | Mechanically Switched Capacitor | 132
Rainhill | RAIN12 | 4 | 45 | 0 | Mechanically Switched Capacitor | 132
Ratcliffe-On-Soar | RATS41 | 1 | 0 | 200 | Reactor | 400
Rayleigh | RAYL41 | 1 | 0 | 60 | Reactor | 13
Richborough | RICH41 | 1 | 225 | 100 | SVC | 32
Richborough | RICH41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Rochdale | ROCH11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Rochdale | ROCH11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Rochdale | ROCH11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Rowdown | ROWD41 | 1 | 0 | 200 | Reactor | 400
Rye House | RYEH41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Rye House | RYEH41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400
Sandford | SAFO41 | 1 | 0 | 200 | Reactor | 400
Sandford | SAFO41 | 2 | 0 | 200 | Reactor | 400
Sellindge Compound A | SELL4A | 2 | 150 | 150 | SVC | 57
Sellindge Compound A | SELL4A | 1 | 150 | 150 | SVC | 57
Sellindge Compound A | SELL4A | 1 | 0 | 200 | Reactor | 400
St. Johns Wood | SJOW12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
St. Johns Wood | SJOW12 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
St. Johns Wood | SJOW12 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
St. Johns Wood | SJOW21 | 1 | 0 | 60 | Reactor | 13
ST.JOHNS WOOD | SJOW21 | 1 | 150 | 144 | SVC | 275
ST.JOHNS WOOD | SJOW21 | 2 | 150 | 106 | SVC | 275
St. Johns Wood | SJOW41 | 1 | 0 | 200 | Reactor | 400
St. Johns Wood | SJOW41 | 2 | 0 | 200 | Reactor | 400
St. Johns Wood | SJOW41 | 3 | 0 | 200 | Reactor | 400
Skelton Grange | SKLG11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Skelton Grange | SKLG21 | 1 | 0 | 100 | Reactor | 275
Skelton Grange | SKLG21 | 4 | 154 | 0 | Mechanically Switched Capacitor | 275
Spennymoor | SPEN41 | 1 | 0 | 60 | Reactor | 13
Stalybridge | STAL41 | 1 | 0 | 200 | Reactor | 400
Stella West | STEW21 | 1 | 0 | 100 | Reactor | 275
Stella West | STEW41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Stella West | STEW41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Stocksbridge | STSB41 | 1 | 0 | 200 | Reactor | 400
Sundon | SUND41 | 1 | 0 | 30 | Reactor | 13
Sundon | SUND41 | 2 | 0 | 30 | Reactor | 13
Sundon | SUND41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
Sundon | SUND42 | 3 | 0 | 30 | Reactor | 13
Sundon | SUND42 | 4 | 0 | 30 | Reactor | 13
Sundon | SUND42 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400
Thorpe Marsh | THOM41 | 1 | 0 | 200 | Reactor | 400
Thorpe Marsh | THOM42 | 2 | 0 | 200 | Reactor | 400
Tottenham | TOTT21 | 1 | 0 | 100 | Reactor | 275
Tottenham | TOTT21 | 2 | 0 | 100 | Reactor | 275
Tottenham | TOTT22 | 3 | 0 | 100 | Reactor | 275
Tynemouth | TYNE2A | 4 | 0 | 60 | Reactor | 13
Uskmouth | USKM12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
Walham | WALH41 | 1 | 0 | 60 | Reactor | 13
Walham | WALH41 | 2 | 0 | 60 | Reactor | 13
Walham | WALH41 | 1 | 57 | 0 | Mechanically Switched Capacitor | 13
Walham | WALH41 | 3 | 0 | 200 | Reactor | 400
Walpole | WALP11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132
Walpole | WALP11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132
Walpole | WALP11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132
Walpole | WALP41 | 1 | 0 | 60 | Reactor | 13
Walpole | WALP41 | 2 | 0 | 60 | Reactor | 13
Warley | WARL11 | 1 | 52 | 0 | Mechanically Switched Capacitor | 132
Warley | WARL11 | 2 | 52 | 0 | Mechanically Switched Capacitor | 132
Warley | WARL11 | 3 | 52 | 0 | Mechanically Switched Capacitor | 132
West Ham | WHAM41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400
West Ham | WHAM41 | 1 | 0 | 200 | Reactor | 400
Whitegate | WHGA21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275
Whitegate | WHGA21 | 1 | 0 | 60 | Reactor | 13
Whitegate | WHGA21 | 2 | 0 | 60 | Reactor | 13
Willington East | WILE41 | 1 | 150 | 95 | SVC | 7.9
Willington East | WILE41 | 1 | 0 | 200 | Reactor | 400
Wimbledon | WIMB41 | 1 | 0 | 225 | Reactor | 400
Willesden | WISD21 | 1 | 0 | 60 | Reactor | 13
Willesden | WISD21 | 2 | 0 | 30 | Reactor | 13
Willesden | WISD21 | 3 | 0 | 30 | Reactor | 13
West Melton | WMEL12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132
West Melton | WMEL12 | 2 | 45 | 0 | Mechanically Switched Capacitor | 132
West Melton | WMEL12 | 3 | 45 | 0 | Mechanically Switched Capacitor | 132
West Weybridge | WWEY21 | 1 | 0 | 100 | Reactor | 275
Wylfa | WYLF41 | 1 | 0 | 200 | Reactor | 400
Wymondley | WYMO41 | 1 | 0 | 200 | Reactor | 400
Wymondley | WYMO41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400
Wymondley | WYMO41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400

## B-4-1d
B.4.1d - OFTO Reactive Compensation Equipment 2025/26
OFTO | Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
TC Barrow OFTO Limited | Barrow Offshore Wind Farm | BOSO11 | 1 | 0 | 24 | Reactor | 132
TC Beatrice OFTO Limited | Beatrice Offshore Windfarm | BEAT21 | SHR1 | 0 | 115 | Reactor | 220
|  | BEAT22 | SHR2 | 0 | 115 | Reactor | 220
|  | BEAT21 | SHR3 | 0 | 115 | Reactor | 220
|  | BEAT22 | SHR4 | 0 | 115 | Reactor | 220
|  | BEAT41 | SVC1 | 144 | 155 | SVC | 400
|  | BEAT41 | SVC2 | 144 | 155 | SVC | 400
Diamond Transmission Partners BBE Limited | Burbo Bank Extension Wind Farm | BBWO41 | 1 | 0 | 60 | Reactor | 400
|  | BBWO21 | 1 | 0 | 125 | Reactor | 220
|  | BBWO41 | SVC1 | 82.17 | 82.17 | SVC | 400
TC Dudgeon OFTO plc | Dudgeon Offshore Wind Farm | DUDO11 | SHR1 | 0 | 85 | Reactor | 132
|  | DUDO12 | SHR2 | 0 | 85 | Reactor | 132
|  | NECT41 | SVC1 | 125 | 125 | SVC | 400
|  | NECT41 | SVC2 | 125 | 125 | SVC | 400
East Anglia One Limited | East Anglia Offshore Wind Farm | EAAW21 | SH1 | 0 | 174 | Reactor | 220
|  | EAAW22 | SH2 | 0 | 174 | Reactor | 220
|  | BRST21 | VSR-1 | 0 | 228 | Reactor | 220
|  | BRST22 | VSR-2 | 0 | 228 | Reactor | 220
|  | BRST41 | SVC1 | 215 | 215 | SVC | 400
|  | BRST42 | SVC2 | 215 | 215 | SVC | 400
Diamond Transmission Partners Galloper Limited | Galloper Offshore Wind Farm | GALO11 | SVC3 | 70 | 70 | SVC | 132
|  | GALO12 | SVC4 | 70 | 70 | SVC | 132
|  | GALO11 | MSR 05 | 0 | 85 | Reactor | 132
|  | GALO12 | MSR 06 | 0 | 85 | Reactor | 132
Greater Gabbard OFTO plc | Greater Gabbard Offshore Wind Farm | GGON11 | 1 | 55 | 0 | Mechanically Switched Capacitor | 132
|  | GGON12 | 2 | 55 | 0 | Mechanically Switched Capacitor | 132
|  | GGON13 | 3 | 55 | 0 | Mechanically Switched Capacitor | 132
|  | GGON11 | 1 | 0 | 43 | Reactor | 132
|  | GGON12 | 2 | 0 | 43 | Reactor | 132
|  | GGON13 | 3 | 0 | 43 | Reactor | 132
|  | GANW3A | 1 | 0 | 30 | Reactor | 33
|  | GANW3B | 1 | 0 | 30 | Reactor | 33
|  | GGON11 | 1 | 50 | 50 | SVC | 132
|  | GGON12 | 2 | 50 | 50 | SVC | 132
|  | GGON13 | 3 | 50 | 50 | SVC | 132
TC Gunfleet Sands OFTO Limited | Gunfleet Sands Offshore Wind Farm | CLTO11 | 1 | 0 | 64 | Reactor | 132
Gwynt y Môr OFTO plc | Gwynt Y Mor Offshore Wind Farm | BODE41 | 1 | 50 | 50 | SVC | 400
|  | BODE41 | 2 | 50 | 50 | SVC | 400
|  | BODE41 | 1A | 0 | 55 | Reactor | 400
|  | BODE41 | 1B | 0 | 55 | Reactor | 400
|  | BODE41 | 2A | 0 | 55 | Reactor | 400
|  | BODE41 | 2B | 0 | 55 | Reactor | 400
|  | BODE41 | 1A | 30 | 0 | Mechanically Switched Capacitor | 400
|  | BODE41 | 1B | 30 | 0 | Mechanically Switched Capacitor | 400
|  | BODE41 | 2A | 30 | 0 | Mechanically Switched Capacitor | 400
|  | BODE41 | 2B | 30 | 0 | Mechanically Switched Capacitor | 400
Diamond Transmission Partners Hornsea One Limited | Hornsea One Offshore Wind Farm | HOWA41 | 3 | 0 | 75 | Reactor | 400
|  | HOWA41 | 4 | 0 | 75 | Reactor | 400
|  | HOWA21 | 1 | 0 | 300 | Variable Shunt Reactor | 220
|  | HOWA21 | 2 | 0 | 300 | Variable Shunt Reactor | 220
|  | HOWA21 | 3 | 0 | 300 | Variable Shunt Reactor | 220
|  | HOWR2A | 1 | 0 | 220 | Reactor | 220
|  | HOWR2A | 2 | 0 | 220 | Reactor | 220
|  | HOWR2A | 3 | 0 | 220 | Reactor | 220
|  | HOWW2A | 1 | 0 | 85 | Reactor | 220
|  | HOWW2B | 1 | 0 | 105 | Reactor | 220
|  | HOWW2C | 1 | 0 | 135 | Reactor | 220
|  | HOWA21 | 1 | 160 | 200 | SVC | 220
|  | HOWA21 | 2 | 160 | 200 | SVC | 220
|  | HOWA21 | 3 | 160 | 200 | SVC | 220
Breesea Limited | Hornsea Two Offshore Wind Farm | HOWB41 | 3 | 0 | 85 | Reactor | 400
|  | HOWB41 | 4 | 0 | 85 | Reactor | 400
|  | HOWB21 | VSR1 | 0 | 300 | Reactor | 220
|  | HOWB21 | VSR2 | 0 | 300 | Reactor | 220
|  | HOWB21 | VSR3 | 0 | 300 | Reactor | 220
|  | HOWB21 | SVC1 | 240 | 240 | SVC | 220
|  | HOWB21 | SVC2 | 240 | 240 | SVC | 220
|  | HOWB21 | SVC3 | 240 | 240 | SVC | 220
|  | HOWW2D | 1 | 0 | 90 | Reactor | 220
|  | HOWW2D | 2 | 0 | 90 | Reactor | 220
|  | HOWW2D | 3 | 0 | 90 | Reactor | 220
|  | HOWR2B | 1 | 0 | 170 | Reactor | 220
|  | HOWR2B | 2 | 0 | 170 | Reactor | 220
|  | HOWR2B | 3 | 0 | 170 | Reactor | 220
Humber Gateway OFTO Limited | Humber Gateway Offshore Wind Farm | HUMO11 | 1 | 0 | 28.2 | Reactor | 132
|  | HUMO12 | 2 | 0 | 28.2 | Reactor | 132
|  | HUMO31 | 1A | 0 | 28 | Reactor | 33
|  | HUMO31 | 1B | 0 | 28 | Reactor | 33
|  | HUMO32 | 2A | 0 | 28 | Reactor | 33
|  | HUMO32 | 2B | 0 | 28 | Reactor | 33
|  | HUMO31 | 1 | 24 | 24 | SVC | 33
|  | HUMO32 | 2 | 24 | 24 | SVC | 33
TC Lincs OFTO Limited | Lincs Offshore Wind Farm | LINO41 | SVC1 | 94 | 139 | SVC | 400
|  | LINO13 | SR1 | 0 | 46 | Reactor | 132
|  | LINO14 | SR2 | 0 | 46 | Reactor | 132
|  | LINS31 | SR1 | 0 | 40 | Reactor | 33
|  | LINS32 | SR2 | 0 | 40 | Reactor | 33
Blue Transmission London Array Limited | London Array Offshore Wind Farm | LONO41 | 1A | 52 | 52 | SVC | 400
|  | LONO42 | 2A | 52 | 52 | SVC | 400
|  | LONO43 | 1B | 52 | 52 | SVC | 400
|  | LONO44 | 2B | 52 | 52 | SVC | 400
Moray East Offshore Wind Limited | Moray East Offshore Wind Farm | MOWE21 | SHR1 | 0 | 75 | Reactor | 220
|  | MOWE22 | SHR1 | 0 | 75 | Reactor | 220
|  | MOWE23 | SHR1 | 0 | 75 | Reactor | 220
|  | MORO21 | SHR1A | 0 | 110 | Reactor | 220
|  | MORO21 | SHR1B | 0 | 110 | Reactor | 220
|  | MORO22 | SHR2A | 0 | 110 | Reactor | 220
|  | MORO22 | SHR2B | 0 | 110 | Reactor | 220
|  | MORO23 | SHR3A | 0 | 110 | Reactor | 220
|  | MORO23 | SHR3B | 0 | 110 | Reactor | 220
|  | MORF21 | MSR1 | 0 | 133 | Reactor | 275
|  | MORF21 | SVC1 | 174 | 197 | SVC | 275
|  | MORF22 | MSR2 | 0 | 133 | Reactor | 275
|  | MORF22 | SVC2 | 174 | 197 | SVC | 275
|  | MORF23 | MSR3 | 0 | 133 | Reactor | 275
|  | MORF23 | SVC3 | 174 | 197 | SVC | 275
NEART NA GAOITHE OFFSHORE WIND LIMITED | Neart na Gaoithe Offshore Wind Farm | NNGW21 | 1 | 0 | 125 | Reactor | 220
|  | NNGW22 | 1 | 0 | 125 | Reactor | 220
|  | NNGO21 | SVC1 | 79 | 74 | SVC | 220
|  | NNGO22 | SVC2 | 79 | 74 | SVC | 220
TC Ormonde OFTO Limited | Ormonde Offshore Wind Farm | ORMO31 | SR1 | 0 | 35 | Reactor | 33
|  | ORMO31 | SR2 | 0 | 35 | Reactor | 33
|  | ORMO31 | MSC1 | 15 | 0 | Mechanically Switched Capacitor | 33
|  | ORMO31 | SVC 1 | 28 | 28 | SVC | 33
Diamond Transmission Partners RB Limited | Race Bank Offshore windfarm | RACO21 | VSR1 | 0 | 200 | Variable Shunt Reactor | 220
|  | RACO22 | VSR2 | 0 | 200 | Variable Shunt Reactor | 220
|  | RACW21 | SR1 | 0 | 90 | Reactor | 220
|  | RACW22 | SR2 | 0 | 90 | Reactor | 220
|  | RACO21 | 1 | 120 | 120 | SVC | 220
|  | RACO22 | 2 | 120 | 120 | SVC | 220
TC Rampion OFTO Limited | Rampion Offshore Wind Farm | TWNE41 | SVC1 | 75 | 121 | SVC | 400
|  | TWNE42 | SVC2 | 75 | 121 | SVC | 400
|  | TWNE11 | SHR1 | 0 | 64 | Reactor | 150
|  | TWNE12 | SHR2 | 0 | 64 | Reactor | 150
Seagreen Wind Energy Limited | Seagreen One Wind Farm | SGRO21 | 1 | 0 | 177 | Reactor | 220
|  | SGRO22 | 2 | 0 | 177 | Reactor | 220
|  | SGRO23 | 3 | 0 | 177 | Reactor | 220
|  | SGRX21 | SVC1 | 118 | 118 | SVC | 275
|  | SGRX22 | SVC2 | 118 | 118 | SVC | 275
|  | SGRX23 | SVC3 | 118 | 118 | SVC | 275
TC Robin Rigg OFTO Limited | Robin Rigg East Offshore Wind Farm | RORE11 | 1 | 0 | 18 | Reactor | 33
|  | RORE11 | 1 | 12 | 0 | Mechanically Switched Capacitor | 33
| Robin Rigg West Offshore Wind Farm | RORW11 | 1 | 0 | 18 | Shunt Reactor | 33
|  | RORW11 | 1 | 12 | 0 | Mechanically Switched Capacitor | 33
Blue Transmission Sheringham Shoal Limited | Sheringham Shoal Offshore Wind Farm | SALL11 | 1 | 0 | 60 | Reactor | 132
|  | SALL12 | 2 | 0 | 60 | Reactor | 132
Thanet OFTO Limited | Thanet Offshore Wind Farm | THAW11 | SVC 1 | 49.3 | 49.3 | SVC | 132
|  | THAW12 | SVC 2 | 49.3 | 49.3 | SVC | 132
Triton Knoll Wind Farm Limited | Triton Knoll Offshore Wind Farm | TKNO21 | SHR1 | 0 | 172 | Reactor | 220
|  | TKNO22 | SHR2 | 0 | 172 | Reactor | 220
|  | TKNW21 | SHR4 | 0 | 43 | Reactor | 220
|  | TKNE21 | SHR3 | 0 | 43 | Reactor | 220
|  | TKNO42 | MSR2B | 0 | 163 | Reactor | 400
|  | TKNO42 | MSR2C | 0 | 163 | Reactor | 400
|  | TKNO42 | SVC2A | 143 | 143 | SVC | 400
|  | TKNO41 | MSR1B | 0 | 163 | Reactor | 400
|  | TKNO41 | MSR1C | 0 | 163 | Reactor | 400
|  | TKNO41 | SVC1A | 143 | 143 | SVC | 400
Diamond Transmission Partners Walney Extension Limited | Walney Extension Offshore Wind Farm | WOWE41 | SHR1 | 0 | 62 | Reactor | 400
|  | WOWE21 | VSR-1 | 0 | 250 | Reactor | 220
|  | WACW21 | SHR1 | 0 | 90 | Reactor | 220
|  | WOWE21 | SVC1 | 140 | 140 | SVC | 220
|  | WOWE42 | SHR2 | 0 | 62 | Reactor | 400
|  | WOWE22 | VSR-2 | 0 | 250 | Reactor | 220
|  | WADW21 | SHR2 | 0 | 90 | Reactor | 220
|  | WOWE22 | SVC2 | 140 | 140 | SVC | 220
Blue Transmission Walney 1 OFTO Limited | Walney 1 Offshore Wind Farm | WAAO1A | RCT1 | 0 | 64 | Reactor | 132
Blue Transmission Walney 2 OFTO Limited | Walney 2 Offshore Wind Farm | WABO1A | RCT1 | 0 | 80 | Reactor | 132
WoDS Transmission plc | West of Duddon Sands Offshore Wind Farm | WDSO41 | 1A | 0 | 30 | Reactor | 400
|  | WDSO42 | 2A | 0 | 30 | Reactor | 400
|  | WDSO11 | SR3 | 0 | 60 | Reactor | 155
|  | WDSO12 | SR4 | 0 | 60 | Reactor | 155
|  | WDSO41 | SVC1 | 50 | 50 | SVC | 400
|  | WDSO42 | SVC2 | 50 | 50 | SVC | 400
TC Westermost Rough OFTO Limited | Westermost Rough Offshore Wind Farm | WERO21 | 1 | 25 | 25 | SVC | 275
|  | WERO21 | 2 | 25 | 25 | SVC | 275
|  | WERO21 | 1 | 0 | 50 | Reactor | 275

## B-4-2a
B-4-2a - SHE Transmission Reactive Compensation Equipment Changes 2026/27 to 2033/34
Site Name | Node | Unit Number | Year | Status | MVar Generation | MVar Absorption | Compensation Type | Connection Voltage (kV)
ALYTH | ALYT41 | 1 | 2028 | Change | 101 | 0 | Mechanically Switched Capacitor | 400
ALYTH | ALYT41 | 1 | 2028 | Change | 225 | 225 | SVC | 400
Dounreay West | DONW31 | 1 | 2028 | Addition | 0 | 45 | Reactor | 33
Dounreay West | DONW31 | 2 | 2028 | Addition | 0 | 45 | Reactor | 33
ORKNEY FINSTOWN | FINS31 | 2 | 2028 | Addition | 0 | 45 | Reactor | 33
ORKNEY FINSTOWN | FINS31 | 1 | 2028 | Addition | 0 | 45 | Reactor | 33
BROADFORD | BROA11 | 1 | 2030 | Addition | 0 | 60 | Reactor | 132
BROADFORD | BROA11 | 2 | 2030 | Addition | 0 | 60 | Reactor | 132
EDINBANE | EDIN11 | 1 | 2030 | Addition | 0 | 60 | Reactor | 132
EDINBANE | EDIN11 | 2 | 2030 | Addition | 0 | 60 | Reactor | 132
FORT AUGUSTUS | FAUG41 | 1 | 2030 | Addition | 0 | 100 | Reactor | 400
KINARDOCHY | KINA41 | 1 | 2030 | Change | 101 | 0 | Mechanically Switched Capacitor | 400
ALYTH | ALYT41 | 1 | 2033 | Addition | 225 | 225 | SVC | 400
ALYTH | ALYT41 | 2 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
Eday | EDAY11 | 1 | 2033 | Addition | 0 | 60 | Reactor | 132
EMMOCK | EMMO41 | 1 | 2033 | Addition | 225 | 225 | SVC | 400
EMMOCK | EMMO41 | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
HURLIE | HURL41 | 1 | 2033 | Addition | 225 | 0 | Mechanically Switched Capacitor | 400
KNOCKNAGAEL | KNOC11 | 1 | 2033 | Addition | 0 | 200 | Reactor | 132
KNOCKNAGAEL | KNOC21 | 1 | 2033 | Addition | 250 | 250 | SVC | 275
KNOCKNAGAEL | KNOC3W | 2 | 2033 | Addition | 0 | 60 | Reactor | 33

## B-4-2b
B-4-2b - SPT Reactive Compensation Equipment Changes 2026/27 to 2033/34
Site Name | Node | Unit Number | Year | Status | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Gretna | GRNA3U | 1 | 2026 | Addition | 0 | 60 | Reactor | 33
Kincardine | KINC2- | 1 | 2030 | Addition | 232 | 0 | Mechanically Switched Capacitor | 275
Kincardine | KINC2- | 2 | 2030 | Addition | 232 | 0 | Mechanically Switched Capacitor | 275
Longannet | LOAN2- | 1 | 2030 | Removed | 232 | 0 | Mechanically Switched Capacitor | 275
Longannet | LOAN2- | 2 | 2030 | Removed | 232 | 0 | Mechanically Switched Capacitor | 275
Kincardine North | KINN4- | 1 | 2033 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Whiteminhill Energy Park | WMHL2- | 1 | 2033 | Addition | 0 | 60 | Reactor | 275

## B-4-2c
B-4-2c - NGET Reactive Compensation Equipment Changes 2026/27 to 2033/34
Site Name | Node | Unit Number | Year | Status | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV)
Burwell Main | BURW41 | 1 | 2026 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Jordanthorpe | JORD21 | 1 | 2026 | Addition | 0 | 100 | Reactor | 275
Taunton | TAUN42 | 1 | 2026 | Addition | 0 | 200 | Reactor | 400
Wimbledon | WIMB41 | 1 | 2026 | Addition | 0 | 200 | Reactor | 400
Harker GIS | HARG41 | 1 | 2028 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Harker | HARK41 | 1 | 2028 | Removed | 230 | 0 | Mechanically Switched Capacitor | 400
Harker | HARK41 | 2 | 2028 | Removed | 230 | 0 | Mechanically Switched Capacitor | 400
Harker | HARK41 | 3 | 2028 | Removed | 230 | 0 | Mechanically Switched Capacitor | 400
Harker GIS | HARG41 | 1 | 2028 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Harker GIS | HARG41 | 2 | 2028 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Iron Acton | IROA21 | 1 | 2028 | Removed | 60 | 60 | SVC | 13
Iron Acton | IROA21 | 2 | 2028 | Removed | 60 | 60 | SVC | 13
Margam | MAGA21 | 1 | 2028 | Addition | 154 | 0 | Mechanically Switched Capacitor | 275
Melksham | MELK41 | 1 | 2028 | Addition | 0 | 200 | Reactor | 400
Rye House | RYEH41 | 1 | 2028 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Rye House | RYEH41 | 2 | 2028 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Trawsfynydd | TRAW41 | 1 | 2028 | Addition | 0 | 200 | Reactor | 400
Aberthaw B | ABTB11 | 1 | 2030 | Addition | 60 | 0 | Mechanically Switched Capacitor | 132
Aberthaw B | ABTB11 | 2 | 2030 | Addition | 60 | 0 | Mechanically Switched Capacitor | 132
Aberthaw | ABTH11 | 1 | 2030 | Removed | 60 | 0 | Mechanically Switched Capacitor | 132
Aberthaw | ABTH11 | 2 | 2030 | Removed | 60 | 0 | Mechanically Switched Capacitor | 132
Bramford | BRFO41 | 1 | 2030 | Addition | 0 | 200 | Reactor | 400
Bramford | BRFO42 | 2 | 2030 | Addition | 0 | 200 | Reactor | 400
Bramford | BRFO43 | 3 | 2030 | Addition | 0 | 200 | Reactor | 400
Bramford | BRFO44 | 4 | 2030 | Addition | 0 | 200 | Reactor | 400
East Anglia Coastal | EACS41 | 1 | 2030 | Addition | 0 | 200 | Reactor | 400
East Anglia Coastal | EACS41 | 2 | 2030 | Addition | 0 | 200 | Reactor | 400
East Anglia Coastal | EACS41 | 3 | 2030 | Addition | 0 | 200 | Reactor | 400
East Anglia Coastal | EACS41 | 4 | 2030 | Addition | 0 | 200 | Reactor | 400
Elstree | ELST41 | 2 | 2030 | Addition | 0 | 200 | Reactor | 400
Harker GIS | HARG41 | 1 | 2030 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Harker GIS | HARG41 | 2 | 2030 | Addition | 150 | 150 | SVC | 32
Harker GIS | HARG41 | 3 | 2030 | Addition | 150 | 150 | SVC | 32
Harker | HARK21 | 1 | 2030 | Removed | 154 | 0 | Mechanically Switched Capacitor | 275
Harker | HARK21 | 2 | 2030 | Removed | 85 | 75 | SVC | 14
Harker | HARK21 | 3 | 2030 | Removed | 85 | 75 | SVC | 14
Lackenby | LACK41 | 1 | 2030 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Norton | NORT41 | 1 | 2030 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Pelham | PELH41 | 1 | 2030 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Pelham | PELH42 | 2 | 2030 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Penwortham | PEWO41 | 1 | 2030 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Penwortham | PEWO41 | 2 | 2030 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Rayleigh | RAYL41 | 1 | 2030 | Addition | 0 | 200 | Reactor | 400
Rayleigh | RAYL41 | 2 | 2030 | Addition | 0 | 200 | Reactor | 400
St. Johns Wood | SJOW21 | 1 | 2030 | Removed | 150 | 144 | SVC | 16
St. Johns Wood | SJOW21 | 2 | 2030 | Removed | 150 | 106 | SVC | 16
St. Johns Wood | SJOW21 | 3 | 2030 | Removed | 0 | 60 | Reactor | 13
St. Johns Wood | SJOW41 | 4 | 2030 | Addition | 0 | 60 | Reactor | 13
Spennymoor | SPEN41 | 1 | 2030 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
Tilbury North | TILN41 | 1 | 2030 | Addition | 0 | 200 | Reactor | 400
Tilbury North | TILN41 | 2 | 2030 | Addition | 0 | 200 | Reactor | 400
Blyth | BLYT21 | 2 | 2033 | Removed | 154 | 0 | Mechanically Switched Capacitor | 275
Blyth | BLYT21 | 1 | 2033 | Removed | 154 | 0 | Mechanically Switched Capacitor | 275
East Claydon | ECLA11 | 1 | 2033 | Removed | 61 | 0 | Mechanically Switched Capacitor | 132
East Claydon | ECLA41 | 1 | 2033 | Removed | 0 | 30 | Reactor | 13
East Claydon | ECLA41 | 2 | 2033 | Removed | 0 | 30 | Reactor | 13
East Claydon | ECLA41 | 3 | 2033 | Removed | 0 | 30 | Reactor | 13
East Claydon | ECLA41 | 4 | 2033 | Removed | 0 | 30 | Reactor | 13
East Claydon | ECLA41 | 2 | 2033 | Removed | 230 | 0 | Mechanically Switched Capacitor | 400
East Claydon | ECLA41 | 5 | 2033 | Removed | 0 | 200 | Reactor | 400
East Claydon | ECLA41 | 3 | 2033 | Removed | 230 | 0 | Mechanically Switched Capacitor | 400
Lackenby | LACK21 | 1 | 2033 | Removed | 20 | 0 | Mechanically Switched Capacitor | 13
Lackenby | LACK21 | 2 | 2033 | Removed | 20 | 0 | Mechanically Switched Capacitor | 13
Lackenby | LACK21 | 3 | 2033 | Removed | 20 | 0 | Mechanically Switched Capacitor | 13
East Claydon (New) | NECL11 | 1 | 2033 | Addition | 0 | 60 | Reactor | 132
East Claydon (New) | NECL11 | 1 | 2033 | Addition | 61 | 0 | Mechanically Switched Capacitor | 132
East Claydon (New) | NECL12 | 2 | 2033 | Addition | 0 | 60 | Reactor | 132
East Claydon (New) | NECL41 | 2 | 2033 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
East Claydon (New) | NECL41 | 3 | 2033 | Addition | 0 | 200 | Reactor | 400
East Claydon (New) | NECL42 | 3 | 2033 | Addition | 230 | 0 | Mechanically Switched Capacitor | 400
New Warley | NWAR11 | 1 | 2033 | Addition | 52 | 0 | Mechanically Switched Capacitor | 132
New Warley | NWAR11 | 2 | 2033 | Addition | 52 | 0 | Mechanically Switched Capacitor | 132
New Warley | NWAR11 | 3 | 2033 | Addition | 52 | 0 | Mechanically Switched Capacitor | 132
New Warley | NWAR12 | 4 | 2033 | Addition | 52 | 0 | Mechanically Switched Capacitor | 132
New Warley | NWAR12 | 5 | 2033 | Addition | 52 | 0 | Mechanically Switched Capacitor | 132
New Warley | NWAR12 | 6 | 2033 | Addition | 52 | 0 | Mechanically Switched Capacitor | 132
South Shields | SSHI21 | 1 | 2033 | Addition | 154 | 0 | Mechanically Switched Capacitor | 275
Tynemouth | TYNE21 | 1 | 2033 | Addition | 154 | 0 | Mechanically Switched Capacitor | 275

## B-4-2d
B.4.2d - OFTO Reactive Compensation Equipment Changes 2026/27 to 2033/34
Wind Farm | Node 1 | Unit Number | Year | Status | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage(kV)
Hornsea 4A-1 Offshore Wind Farm | HOWD21 | 1 | 2028 | Addition | 0 | 100 | Reactor | 275
| HOWD21 | 2 | 2028 | Addition | 0 | 100 | Reactor | 275
| HOWD21 | 3 | 2028 | Addition | 0 | 100 | Reactor | 275
| HOWR2C | 1 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWR2C | 2 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWR2C | 3 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWD21 | 1 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWD21 | 2 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWD21 | 3 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWR2C | 1 | 2028 | Addition | 0 | 300 | Reactor | 275
| HOWR2C | 2 | 2028 | Addition | 0 | 300 | Reactor | 275
| HOWR2C | 3 | 2028 | Addition | 0 | 300 | Reactor | 275
| HOWD41 | 1 | 2028 | Addition | 0 | 75 | Reactor | 400
| HOWD41 | 1 | 2028 | Addition | TBC | TBC | SVC | 400
| HOWD41 | 2 | 2028 | Addition | TBC | TBC | SVC | 400
| HOWD41 | 3 | 2028 | Addition | TBC | TBC | SVC | 400
Seagreen 1A offshore windfarm | Offshore 275kV-1 | 1 | 2028 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-1 | 2 | 2028 | Addition | 0 | TBC | Reactor | 275
| Offshore 220kV-1 | 3 | 2028 | Addition | 0 | TBC | Reactor | 220
| Offshore 220kV-2 | 4 | 2028 | Addition | 0 | TBC | Reactor | 220
Berwick 2 Offshore Wind Farm | Onshore 400kV-1 | 1 | 2028 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 2 | 2028 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 3 | 2028 | Addition | 0 | TBC | Reactor | 275
| Onshore 275kV-1 | 1 | 2028 | Addition | 0 | TBC | Reactor | 275
| Onshore 275kV-1 | 2 | 2028 | Addition | 0 | TBC | Reactor | 275
| Onshore 275kV-1 | 3 | 2028 | Addition | 0 | TBC | Reactor | 275
| Onshore 275kV-1 | 1 | 2028 | Addition | 100 | 100 | SVC | 275
| Onshore 275kV-1 | 2 | 2028 | Addition | 100 | 100 | SVC | 275
| Onshore 275kV-1 | 3 | 2028 | Addition | 100 | 100 | SVC | 275
| Offshore 275kV-1 | 1 | 2028 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2028 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-3 | 3 | 2028 | Addition | 0 | TBC | Reactor | 275
Erebus Offshore Windfarm | EOWL11 | 1 | 2028 | Addition | 40 | 40 | SVC | 132
| EOWL11 | 1 | 2028 | Addition | 0 | TBC | Reactor | 132
Hornsea 4A-2 Offshore Wind Farm | HOWD21 | 1 | 2028 | Addition | 0 | 100 | Reactor | 275
| HOWD21 | 2 | 2028 | Addition | 0 | 100 | Reactor | 275
| HOWR2C | 1 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWR2C | 2 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWD21 | 3 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWD21 | 4 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWR2C | 3 | 2028 | Addition | 0 | 300 | Reactor | 275
| HOWR2C | 4 | 2028 | Addition | 0 | 300 | Reactor | 275
| HOWD41 | 1 | 2028 | Addition | 0 | 75 | Reactor | 400
| HOWD41 | 2 | 2028 | Addition | TBC | TBC | SVC | 400
| HOWD41 | 3 | 2028 | Addition | TBC | TBC | SVC | 400
Hornsea 4A-1 Offshore Wind Farm | HOWD21 | 1 | 2028 | Addition | 0 | 100 | Reactor | 275
| HOWD21 | 2 | 2028 | Addition | 0 | 100 | Reactor | 275
| HOWD21 | 3 | 2028 | Addition | 0 | 100 | Reactor | 275
| HOWR2C | 1 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWR2C | 2 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWR2C | 3 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWD21 | 1 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWD21 | 2 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWD21 | 3 | 2028 | Addition | 0 | 150 | Reactor | 275
| HOWR2C | 1 | 2028 | Addition | 0 | 300 | Reactor | 275
| HOWR2C | 2 | 2028 | Addition | 0 | 300 | Reactor | 275
| HOWR2C | 3 | 2028 | Addition | 0 | 300 | Reactor | 275
| HOWD41 | 1 | 2028 | Addition | 0 | 75 | Reactor | 400
| HOWD41 | 1 | 2028 | Addition | TBC | TBC | SVC | 400
| HOWD41 | 2 | 2028 | Addition | TBC | TBC | SVC | 400
| HOWD41 | 3 | 2028 | Addition | TBC | TBC | SVC | 400
Awel Y Mor Extension Wind Farm | Offshore 220kV-1 | 1 | 2028 | Addition | 0 | TBC | Reactor | 220
| Offshore 220kV-2 | 2 | 2028 | Addition | 0 | TBC | Reactor | 220
| Onshore 400kV-1 | 1 | 2028 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 1 | 2028 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 2 | 2028 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 2 | 2028 | Addition | TBC | TBC | SVC | 400
Inch Cape Offshore Wind Farm | INCO2A | 1 | 2028 | Addition | 0 | 215 | Reactor | 220
| INCO2A | 2 | 2028 | Addition | 0 | 87 | Reactor | 220
| INCW21 | 1 | 2028 | Addition | 0 | 215 | Reactor | 220
| INCW22 | 2 | 2028 | Addition | 0 | 87 | Reactor | 220
| INCO31 | 1 | 2028 | Addition | 177 | 177 | SVC | 275
| INCO31 | 2 | 2028 | Addition | 177 | 177 | SVC | 275
Pentland Floating Offshore Windfarm | Onshore 132 kV | 1 | 2030 | Addition | 40 | 40 | SVC | 132
| Onshore 132 kV | 1 | 2030 | Addition | 0 | TBC | Reactor | 132
Berwick 1 Offshore Wind Farm | Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 2 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 3 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 275kV-1 | 2 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 275kV-1 | 3 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 275kV-1 | 1 | 2030 | Addition | 100 | 100 | SVC | 275
| Onshore 275kV-1 | 2 | 2030 | Addition | 100 | 100 | SVC | 275
| Onshore 275kV-1 | 3 | 2030 | Addition | 100 | 100 | SVC | 275
| Offshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2030 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-3 | 3 | 2030 | Addition | 0 | TBC | Reactor | 275
Berwick Bank Offshore Wind Farm C | Offshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 2 | 2030 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 3 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 4 | 2030 | Addition | TBC | TBC | SVC | 400
Elizabeth Yellow One Offshore Windfarm | Offshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 2 | 2030 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-1 | 3 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 4 | 2030 | Addition | TBC | TBC | SVC | 400
Morecambe Offshore Wind Farm | Offshore 220kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 275
| Offshore 220kV-2 | 2 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 2 | 2030 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 3 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 4 | 2030 | Addition | TBC | TBC | SVC | 400
OWPL Offshore Windfarm | Offshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 2 | 2030 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 3 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 4 | 2030 | Addition | TBC | TBC | SVC | 400
Project Elizabeth Offshore Windfarm | Offshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2030 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 1 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 2 | 2030 | Addition | TBC | TBC | SVC | 400
Rampion Extension Windfarm | Offshore 220kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 220
| Offshore 220kV-2 | 2 | 2030 | Addition | 0 | TBC | Reactor | 220
| Onshore 400kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 1 | 2030 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 2 | 2030 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 3 | 2030 | Addition | TBC | TBC | SVC | 400
North Falls Offshore Wind Farm | Offshore 275kV-1 | 1 | 2030 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2030 | Addition | 0 | TBC | Reactor | 275
Cenos Central Offshore Wind Farm | Onshore 400kV-1 | 1 | 2033 | Addition | TBC | TBC | SVC | 300
| Onshore 400kV-1 | 2 | 2033 | Addition | TBC | TBC | SVC | 300
| Onshore 400kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 300
| Onshore 400kV-1 | 2 | 2033 | Addition | 0 | TBC | Reactor | 300
| Onshore 400kV-1 | 3 | 2033 | Addition | 0 | TBC | Reactor | 300
| Onshore 400kV-1 | 4 | 2033 | Addition | 0 | TBC | Reactor | 300
EQUINOR Offshore Windfarm | Onshore 275kV-1 | 1 | 2033 | Addition | TBC | TBC | SVC | 275
| Onshore 275kV-1 | 2 | 2033 | Addition | TBC | TBC | SVC | 275
| Onshore 275kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 275
| Onshore 275kV-1 | 2 | 2033 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-1 | 3 | 2033 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-1 | 4 | 2033 | Addition | 0 | TBC | Reactor | 275
Green Volt Offshore Wind Farm | Offshore 220kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 220
| Offshore 220kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 220
| Onshore 400kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 2 | 2033 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 3 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 4 | 2033 | Addition | TBC | TBC | SVC | 400
Caledonia Offshore Wind Farm | Offshore 275kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 1 | 2033 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 2 | 2033 | Addition | TBC | TBC | SVC | 400
GT R4 Wind Farm | Offshore 275kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 1 | 2033 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-1 | 2 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 2 | 2033 | Addition | TBC | TBC | SVC | 400
Spiorad na Mara | Offshore 275kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 1 | 2033 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-1 | 2 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 2 | 2033 | Addition | TBC | TBC | SVC | 400
Ossian 1 Offshore Wind farm | Offshore 275kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 2 | 2033 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 3 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 3 | 2033 | Addition | TBC | TBC | SVC | 400
Ossian 2 Offshore Wind farm | Offshore 220kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 220
| Offshore 220kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 220
| Onshore 400kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 2 | 2033 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 3 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 3 | 2033 | Addition | TBC | TBC | SVC | 400
Ayre Offshore Wind Farm | Offshore 220kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 220
| Offshore 220kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 220
| Onshore 400kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 1 | 2033 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 2 | 2033 | Addition | TBC | TBC | SVC | 400
BELLROCK OFFSHORE WINDFARM | Offshore 220kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 220
| Offshore 220kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 220
Buchan 01 Offshore Wind Farm | Offshore 275kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 275
| Offshore 275kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 275
| Onshore 400kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 1 | 2033 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 2 | 2033 | Addition | TBC | TBC | SVC | 400
Stromar Offshore Wind Farm | Offshore 220kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 220
| Offshore 220kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 220
| Onshore 400kV-1 | 1 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-1 | 1 | 2033 | Addition | TBC | TBC | SVC | 400
| Onshore 400kV-2 | 2 | 2033 | Addition | 0 | TBC | Reactor | 400
| Onshore 400kV-2 | 2 | 2033 | Addition | TBC | TBC | SVC | 400

## B-5-1
B.5.1 - Intra GB HVDC 2025/26 to 2033/34
Interconnector Name | Existing | Planned from year | Node 1 | Node 2 | Type | Rated Voltage (kV) | Length(km) | Metallic Return | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Node 1 MVAr Gen | Node 1 MVAr Abs | Node 2 MVAr Gen | Node 2 MVAr Abs
Caithness Moray Shetland Multi-Terminal Link - Terminal 1 | Yes | Existing | SPIT21 | Central DC Substation | VSC | ±320 | 31 | No | 800 | 800 | 800 | 800 | 263 | 263 | N/A | N/A
Caithness Moray Shetland Multi-Terminal Link - Terminal 2 | Yes | Existing | BLHI41 | Central DC Substation | VSC | ±320 | 136 | No | 1200 | 1200 | 1200 | 1200 | 394 | 394 | N/A | N/A
Caithness Moray Shetland Multi-Terminal Link - Terminal 3 | Yes | Existing | KERG11 | Central DC Substation | VSC | ±320 | 269 | No | 600 | 600 | 600 | 600 | 197 | 197 | N/A | N/A
Western HVDC Link | Yes | Existing | FLIB41 | HUCS4- | LCC | ±600 | 422 | No | 2250 | 2250 | 2250 | 2250 | 1712 | 705 | 688 | 1946
Eastern Green Link 2 | No | 2030 | DRAX41 | PEHE41 | VSC | ±525 | 505 | No | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657
Eastern Green Link 1 | No | 2030 | BRNX4- | HAWP41 | VSC | ±525 | 193 | No | 2000 | 2000 | 2000 | 2000 | 660 | 660 | 657 | 657
PSDC HVDC Link | No | 2030 | BANN41 | LOSD41 | VSC | ±525 | 145 | Yes | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657
Western Isles HVDC Link | No | 2030 | LEWI41 | FNLN41 | VSC | ±525 | 170 | No | 1800 | 1800 | 1800 | 1800 | 592 | 592 | 592 | 592
Eastern HVDC Link 4 | No | 2033 | WALP41 | WFIE4A | VSC | ±525 | 525 | No | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657
Eastern Green Link 3 | No | 2033 | WALP41 | LOSD41 | VSC | ±525 | 650 | Yes | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657
Offshore HVDC - SCD1 (Sealink) | No | 2033 | MINC41 | SAXM41 | VSC | ±525 | 138 | No | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657