National Electricity Transmission System

Security and Quality of Supply Standard

Version 2.12

Contents

Page

|  | Introduction | 4 |
| --- | --- | --- |
|  | Generation Connection Criteria Applicable to the Onshore Transmission System | 12 |
|  | Demand Connection Criteria Applicable to Onshore Transmission System | 18 |
|  | Design of the Main Interconnected Transmission System | 24 |
|  | Operation of the Onshore Transmission System | 27 |
|  | Voltage Limits in Planning and Operating the Onshore Transmission System | 32 |
|  | Generation Connection Criteria Applicable to an Offshore Transmission System | 40 |
|  | Demand Connection Criteria Applicable to an Offshore Transmission System | 49 |
|  | Operation of an Offshore Transmission System | 53 |
|  | Voltage Limits in Planning and Operating an Offshore Transmission System | 55 |
|  | Terms and Definitions | 56 |
| Appendix A | Recommended Substation Configuration and Switching Arrangements | 77 |
| Appendix B | Circuit Complexity on the Onshore Transmission System | 82 |
| Appendix C | Modelling of Security Planned Transfer | 85 |
| Appendix D | Application of the Interconnection Allowance | 87 |
| Appendix E | Modelling of Economy Planned Transfer | 90 |
| Appendix F | Application of the Boundary Allowance | 92 |
| Appendix G | Guidance on Economic Justification | 94 |
| Appendix H | Frequency Risk and Control Report Methodology and Application | 96 |
| Appendix I | System Restoration Requirements | 101 |
| Appendix J | Governance Framework | 103 |

- Introduction

Role and Scope

1.1		Pursuant to conditions, D3 and E16 of the Transmission Licences and condition E7 of the ESO licence, this Security and Quality of Supply Standard (the “Standard”) sets out a coordinated set of criteria and methodologies (for example cost-benefit techniques and weather related operation) that Licensees shall use in the planning and operation of the national electricity transmission system of Great Britain. This Standard is administered by the NETS SQSS panel who will consider, develop, and submit to the authority, proposals to modify the contents of the documents as required to ensure its objectives, as defined in licence condition E7 of the ESO licence, are met at all times. In developing such proposals, the NETS SQSS panel will ensure industry participation. The constitution of the NETS SQSS panel and its procedures are set out in Appendix J of this Standard. For the avoidance of doubt the national electricity transmission system is made up of both the onshore transmission system and the offshore transmission systems.

1.2		Both planning and operational criteria are set out in this Standard and these will determine the need for services provided to the relevant Licensees, e.g. reactive power as well as transmission equipment. The planning criteria set out the requirements for the transmission capacity (either investment or purchase of services) for the national electricity transmission system. The planning criteria set out the requirements for the transmission capacity (either investment or purchase of services) for the national electricity transmission system. The planning criteria also require consideration to be given to the operation and maintenance of the national electricity transmission system and so refer to the associated operational criteria where appropriate. The operational criteria are used in real time and in the development of plans for using the national electricity transmission system to permit satisfactory operation.

1.3		Additional criteria, for example covering more detailed and other aspects of quality of supply, are contained in the Grid Code and the SO-TO Code, which should be read in conjunction with this document.

1.4 		External interconnections between the onshore transmission system and external systems (e.g. in Ireland & France) are covered by separate agreements, which will normally be consistent with this Standard. This Standard may be specifically referenced in the relevant agreements and shall apply to the extent of that reference.

1.5	The consideration of secured events as defined in this Standard may lead to the identification of inadequate capability of equipment or systems not owned or operated by the Licensees (for example, the overloading of lower voltage connections between grid supply points). In such cases the Licensees will notify the network operators affected. Reinforcement or alternative operation of the national electricity transmission system to alleviate inadequacies of equipment or systems not owned or operated by the Licensees would be undertaken where it is agreed by the network operators affected and the relevant Licensees.

1.6	The criteria presented in this Standard represent the minimum requirements for the planning and operation of the national electricity transmission system. While it is a requirement for transmission capacity to meet the planning criteria, it does not follow that the transmission capacity should be reduced so that it only meets the minimum requirement of those criteria. For example, it may not be beneficial to reduce the ratings of lines to reflect lower loading levels which have arisen due to changes in the generation or demand patterns.

Document Structure

1.7	This Standard contains technical terms and phrases specific to transmission systems and the Electricity Supply Industry. The meanings of some terms or phrases in this Standard may also differ from those commonly used. For this reason a ‘Terms and Definitions’ has been included as Section 11 to this document. All defined terms have been identified in the text by the use of italics.

1.8		The criteria and methodologies applicable to the onshore transmission system differ in certain respects from those applicable to the offshore transmission systems. In view of this, the two sets of criteria and methodologies are presented separately for clarity. The criteria and methodologies applicable to the onshore transmission system are presented in Sections 2 to 6 and the criteria and methodologies applicable to offshore transmission systems are presented in Sections 7 to 10.

Onshore Criteria and Methodologies

1.9	For ease of use, the criteria and methodologies relating to the planning of the onshore transmission system have been presented according to the functional parts of the onshore transmission system to which they primarily apply. These parts are the generation points of connection at which power stations feed into the Main Interconnected Transmission System (MITS) through the remainder of the MITS to the Grid Supply Points (GSP) where demand is connected. These parts are illustrated schematically in Figure 1.1.

Section of the

Onshore Transmission System

Demand point of connection

Generation point of connection

Generation circuit

Grid Supply Point

Generation connection criteria

Demand connection criteria

overlap

overlap

Main Interconnected Transmission System

(MITS) criteria

Section of the

Onshore Transmission System

Demand point of connection

Generation point of connection

Generation circuit

Grid Supply Point

Generation connection criteria

Demand connection criteria

overlap

overlap

Main Interconnected Transmission System

(MITS) criteria

Figure 1.1 The onshore transmission system with a directly connected power station

1.10 	The generation connection criteria applicable to the onshore transmission system are set out in Section 2 and cover the connections which extend from the grid entry points (GEPs) and reach into the MITS. The criteria also cover the risks affecting the national electricity transmission system arising from the generation circuits.

1.11 	The demand connection criteria applicable to the onshore transmission system are given in Section 3 and cover the connections which extend from the lower voltage side of the GSP transformers and again reach into the MITS.

1.12 	Section 4 sets out the criteria for minimum transmission capacity on the MITS, which extends from the generation points of connection through to the demand points of connection on the high voltage side of the GSP transformers.

1.13 The criteria relating to the operation of the onshore transmission system are presented in Section 5.

Offshore Criteria and Methodologies

1.14	For ease of use, the criteria and methodologies relating to the planning of the offshore transmission systems have also been presented according to the functional parts of an offshore transmission system to which they primarily apply. An offshore transmission system extends from the offshore grid entry point/s (GEP) at which offshore power stations feed into the offshore transmission system through the remainder of the offshore transmission system to the point of connection of the offshore transmission system at the first onshore substation. This point of connection at the first onshore substation is the interface point (IP) in the case of a direct connection to the onshore transmission system or the user system interface point (USIP) in the case of a connection to an onshore user system.

1.15 	The first onshore substation may be owned by the offshore Licensee, the onshore Licensee or onshore user system owner. Ownership boundaries are determined by the relevant Licensees and/or distribution licensees (as the case may be). Normally, and unless otherwise agreed, in the case of there being AC transformation or DC conversion facilities at the first onshore substation if the offshore transmission owner owns the first onshore substation, the interface point or user system interface point (as the case may be) would be on the HV busbars. If the first onshore substation is owned by the onshore transmission owner or onshore user system owner, the interface point or user system interface point (as the case may be) would be on the LV busbars. In the case of the former, the first onshore substation must meet the criteria relating to offshore transmission systems and, in the case of the latter, the first onshore substation must meet the appropriate onshore criteria.

1.16 	The functional parts of an offshore transmission system include: the offshore connection facilities on the offshore platform/s, which may include:

1.16.1 	the offshore grid entry point/s (GEP) at which offshore power stations feed into an offshore transmission system,

1.16.2	any offshore supply point/s (OSP) where offshore power station demand is supplied from an offshore transmission system

1.16.3 	AC or DC offshore transmission circuits

the cable circuit/s which may include:

    - AC or DC cable offshore transmission circuits connecting an offshore platform either directly to an onshore overhead line forming part of the offshore transmission system or to onshore connection facilities forming part of the offshore transmission system

an overhead line section, which may include:

1.16.5 	AC or DC overhead line offshore transmission circuits connecting the cable offshore transmission circuits either directly to the first onshore substation or to onshore AC transformation or AC/DC conversion facilities not forming part of the first onshore substation.

onshore connection facilities, which may include:

1.16.6 	AC/DC conversion facilities connecting DC overhead line or DC cable offshore transmission circuits to the interface point or user system interface point (as the case may be). Such facilities may constitute the first onshore substation

1.16.7 	AC transformation facilities connecting AC overhead line or AC cable offshore transmission circuits to the interface point or user system interface point (as the case may be). Such facilities may constitute the first onshore substation.

1.17 The above functional parts of an offshore transmission system are illustrated schematically in Figure 1.2. There are many variations to the form of an offshore transmission system. Figure 1.2, and Figure 1.3, illustrate just two such examples. The offshore generator has the option to connect to an offshore transmission system at a voltage level (in that system) of their choosing. Accordingly, the offshore GEP can be at a voltage level of the generator’s choosing and the extent of the offshore generation connection criteria would vary accordingly. However, under the default arrangements, the offshore generator’s circuits cannot be wholly or mainly at a voltage level of 132kV or above since such a combination of circuits would then constitute part of an offshore transmission system. Please note that, while Figure 1.2, and subsequent Figure 1.3, have been drawn such that they represent the functional parts of an AC offshore transmission system, they are equally representative of the functional parts of a DC offshore transmission system.

Circuits Owned by the Offshore Generator

GEP and OSP

Offshore Platform

Offshore Transmission Circuit

Offshore

Shoreline

Onshore

Interface Point (IP) or User System Interface Point (USIP)

First Onshore Substation

Owned by Offshore Transmission Owner

Offshore Generation Connection Criteria

Section of Offshore Transmission System

Offshore Power Station Demand Connection Criteria

Overlap of Criteria

Figure 1.2 An offshore transmission system with a directly connected power station and first onshore substation owned by the offshore transmission owner

Circuits Owned by the Offshore Generator

GEP and OSP

Offshore Platform

Offshore Transmission Circuit

Offshore

Shoreline

Onshore

Interface Point (IP) or User System Interface Point (USIP)

First Onshore Substation

Owned by Offshore Transmission Owner

Offshore Generation Connection Criteria

Section of Offshore Transmission System

Offshore Power Station Demand Connection Criteria

Overlap of Criteria

Figure 1.2 An offshore transmission system with a directly connected power station and first onshore substation owned by the offshore transmission owner

1.18	The boundaries between functional parts of an offshore transmission system will vary according to circumstances. In the example illustrated in Figure 1.3, the first onshore substation is owned by the onshore transmission system owner or user system owner. Accordingly, the interface point or user system interface point, as the case may be, would be at the lower voltage side rather than the higher voltage side of the transformers at the first onshore substation. Similarly, the extent of the offshore generation and demand connection criteria also move with the interface point or user system interface point. The first onshore substation forms part of the onshore transmission system or onshore user system as the case may be.

GEP and OSP

Offshore Platform

Offshore Transmission Circuit

Offshore

Shoreline

Onshore

IP or USIP

First Onshore Substation

Owned by onshore TO or  onshore DO

Offshore Generation Connection Criteria

Section of Offshore Transmission System

Offshore Demand Connection Criteria

Overlap

Figure 1.3 The offshore transmission system with a directly connected power station and first onshore substation owned by the onshore TO or onshore DO

Circuits Owned by the Offshore Generator

Cable Sealing End

Overhead Line Section

GEP and OSP

Offshore Platform

Offshore Transmission Circuit

Offshore

Shoreline

Onshore

IP or USIP

First Onshore Substation

Owned by onshore TO or  onshore DO

Offshore Generation Connection Criteria

Section of Offshore Transmission System

Offshore Demand Connection Criteria

Overlap

Figure 1.3 The offshore transmission system with a directly connected power station and first onshore substation owned by the onshore TO or onshore DO

Circuits Owned by the Offshore Generator

Cable Sealing End

Overhead Line Section

1.19	The generation connection criteria applicable to an offshore transmission system are set out in Section 7 and cover the connections which extend from the offshore grid entry points (GEP), through the offshore transmission system, to the interface point (IP) or onshore user system interface point (USIP), as the case may be.

1.20 	The demand connection criteria applicable to an offshore transmission system are given in Section 8 and cover the connection of station demand at the offshore platform. These criteria extend from the offshore supply point (OSP) on the offshore platform through the offshore transmission system to the onshore interface point (IP) or onshore user system interface point (USIP), as the case may be.

1.21 	The criteria relating to the operation of an offshore transmission system are presented in Section 9.

1.22 	Voltage limits for use in planning Overlap of Criteria operating an offshore transmission and system are presented in Section 10.

Overlap of Criteria

1.23 	As described above, and illustrated in Figures 1.1, 1.2 and 1.3, there will be parts of the national electricity transmission system where more than one set of criteria apply. In such places the requirements of all relevant criteria must be met. Particular examples are:

1.23.1	should an offshore transmission system be connected to the onshore MITS by two or more AC offshore transmission circuits routed to different onshore substations or to separate busbar sections at the same onshore substation, those AC offshore transmission circuits would parallel the MITS. In such cases the onshore criteria would also apply to the relevant sections of the offshore transmission system;

1.23.2	where sites are composite and have a mixture of demand connections and generation connections, the security afforded to the block of demand customers shall be not less than that provided for a standard demand connection of an identical size. The applicable security standard should therefore be the more secure of the corresponding criteria of Section 2 or Section 3. Specifically excluded from this category is a generation site with on-site station demand. Such sites shall be treated as a generation site connected to the onshore transmission system with appropriate security levels.

1.23.3	Where some sections of a transmission licensee’s transmission system extends between NGET’s transmission system and/or or SPT’s transmission system and/or SHET’s transmission system, where different criteria apply, that section would have to meet the criteria applicable to the transmission systems it extends between; NGET’s transmission system and/or or SPT’s transmission system and/or SHET’s transmission system.

1.24	Directions related to National Security

1.24.1 	The Secretary of State may issue a direction to the ISOP as referred to in condition B4 of the ESO Licence where in the opinion of the Secretary of State there is a risk relating to national security that may detrimentally impact the resilience, safety or security of the energy system, or the continuity of essential services, and it is in the interest of national security that a direction should be issued to the ISOP.

1.24.2 	The ISOP must comply with any such direction that has been issued by the Secretary of State. Licensees should note that the ISOP is not required to comply with any other obligation in the ESO Licence where and to the extent that compliance with that obligation would be inconsistent with the requirement to comply with such a direction, for the period set out in the direction. This includes the requirement set out in condition E3 of the ESO Licence to comply with this Standard.

1.24.3 	The ISOP is required under condition B4 of its ESO Licence to inform the Secretary of State of any conflict with the obligations as identified in 1.24.2 as soon as reasonably practicable after the conflict is identified. The ISOP will include in such a notice, details of any identified impact or non-compliance that will be caused or will be likely to be caused to Licensees, and in such a case will also seek clarification of whether this can be shared with the affected Licensee.

1.24.4  	Where reasonably practicable and subject to the agreement of the Secretary of State to share any such specific details, the ISOP will inform affected Licensees as identified in 1.24.3 of what actions the ISOP will or has taken, or not taken, to comply with a direction or amended direction (including when such a direction is revoked) and what identified impact or non-compliance this will or is likely to cause to the Licensee.

1.24.5 	The ISOP's obligations under this Standard shall be suspended without liability where and to the extent that compliance with any such obligation would be inconsistent with the requirement upon the ISOP to comply with a direction.

1.24.6 	A Licensee's obligations under this Standard shall be suspended without liability where and to the extent that the Licensee is unable to comply with any such obligation as a result of any action taken, or not taken, by the ISOP to comply with a direction.

1.24.7 	The Secretary of State may at any time amend or revoke any direction issued to the ISOP as referred to in condition B4 of the ESO Licence).

1.24.8	For the purposes of this paragraph 1.24: “User” means a Transmission Licensee other than the ISOP.

1.25	Advisory and Information Requests

1.25.1	The ISOP is required to provide advice, analysis or information to the Authority or to a Minister of the Crown when requested in accordance with section 171 of the Energy Act 2023 and condition D1 of the ESO licence and gas system planner licence.

1.25.2	The ISOP may by notice request from Users such information as it reasonably requires in connection with the exercise of any of its functions, in accordance with section 172 of the Energy Act 2023. It will do so by the issue of an information request notice. The purposes of this may include to assist in the fulfilment of a request for advice, analysis or information as set out in 1.25.1.

1.25.3	The ISOP is required by condition D2 of the ESO licence and GSP licence to prepare, submit for approval by the Authority and publish on its website once approved an information request statement that sets out further detail on the process the ISOP expects to follow when requesting information from other parties.

The Information request statement must include, but need not be limited to, the following matters as set out in condition D2(5) of the ESO Licence and GSP licence:

(a)	the process the ISOP expects to follow when issuing an information request notice, including any further detail around the expected engagement between the ISOP and recipient of an Information Request Notice; and

(b)	the details to be included in an Information Request Notice issued by the ISOP.

1.25.4 	A User to whom a request is made under 1.25.2 must, so far as reasonably practicable, provide the requested information within such reasonable period, and in such reasonable form and manner, as may be specified in the Information Request Notice.

1.25.5		The ISOP must, unless the Authority otherwise consents, maintain for a period of 6 years and provide to the Authority where required a record of information requests as detailed in condition D2.12 of the ESO licence and GSP licence including:

- a copy of the Information Request Notice;

- any subsequent variations to the original information requested;

- the recipient’s response to the notice, including any refusal or challenges to the notice or requested information;

- the time taken for the recipient to provide the requested information;

- the manner and form the information was provided in; and

- the information provided in response to the notice, and whether such information complied, in the ISOP’s view, with the Information Request Notice.

1.25.6 	For the purpose of paragraph 1.25, "User" means a Licensee other than the ISOP.

- Generation connection Criteria Applicable to the Onshore Transmission System

2.1		This section presents the planning criteria applicable to the connection of one or more power stations to the onshore transmission system. The criteria in this section will also apply to the connections from a GSP to the onshore transmission system by which power stations embedded within a customer’s network (e.g. distribution network) are connected to the onshore transmission system.

2.2		In those parts of the onshore transmission system where the criteria of Section 3 and/or Section 4 also apply, those criteria must also be met.

2.3		In planning generation connections, this Standard is met if the connection design either:

2.3.1		satisfies the deterministic criteria detailed in paragraphs 2.5 to 2.13; or

2.3.2	varies from the design necessary to meet paragraph 2.3.1 above in a manner which satisfies the conditions detailed in paragraphs 2.15 to 2.18.

2.4		It is permissible to design to standards higher than those set out in paragraphs 2.5 to 2.13 provided the higher standards can be economically justified.  Guidance on economic justification is given in Appendix G.

Limits to Loss of Power Infeed Risks

2.5		For the purpose of applying the criteria of paragraph 2.6, the loss of power

infeed resulting from a secured event on the onshore transmission system shall be calculated as follows:

2.5.1 	the sum of the registered capacities of the generating units

disconnected from the system by a secured event, plus

2.5.2 	the planned import from any external systems disconnected from the system by the same event, less

2.5.3 	the forecast minimum demand disconnected from the system by the same event but excluding (from the deduction) any demand forming part of the forecast minimum demand which may be automatically tripped for system frequency control purposes and excluding (from the deduction) the demand of the largest single end customer.

2.6		Generation connections shall be planned such that, starting with an intact

system, the consequences of secured events on the onshore transmission system shall be as follows:

2.6.1	following a fault outage of any single transmission circuit, no loss of power infeed shall occur;

2.6.2 	following the planned outage of any single section of busbar or mesh corner, no loss of power infeed shall occur;

2.6.3 	following a fault outage of any single generation circuit or single section of busbar or mesh corner, the loss of power infeed shall not exceed the infrequent infeed loss risk;

2.6.4 	following the concurrent fault outage of any two transmission circuits, or any two generation circuits on the same double circuit overhead line, or the fault outage of any single busbar coupler circuit breaker or busbar section circuit breaker or mesh circuit breaker, the loss of power infeed shall not exceed the infrequent infeed loss risk;

2.6.5 	following the fault outage of any single transmission circuit, single section of busbar or mesh corner, during the planned outage of any other single transmission circuit or single section of busbar or mesh corner, the loss of power infeed shall not exceed the infrequent infeed loss risk;

2.6.6 	following the fault outage of any single busbar coupler circuit breaker or busbar section circuit breaker or mesh circuit breaker, during the planned outage of any single section of busbar or mesh corner, the loss of power infeed shall not exceed the infrequent infeed loss risk.

2.7	The maximum length of overhead line connections in a generation circuit for

generating units which are directly connected to the onshore transmission system shall not exceed:

2.7.1 5km for generating units of expected annual energy output greater than or equal to 2000GWh, otherwise:

2.7.2 20km.

Generation Connection Capacity Requirements

Background conditions

2.8	The connection of a particular power station shall meet the criteria set out in

paragraphs 2.9 to 2.13 under the following background conditions:

2.8.1	the active power output of the power station shall be set equal to its

registered capacity or, for the purpose of Sub-Synchronous Oscillations studies, that which provides the lowest level of damping for the sub-synchronous mode under consideration;

2.8.2 the reactive power output of the power station shall be set to the full leading or lagging output that corresponds to an active power output equal to registered capacity, or for the purpose of assessment of system stability and voltage control issues, that which may reasonably be expected under the conditions described in paragraph 2.8.4;

2.8.3 for connections to an offshore transmission system, the reactive power output of the offshore power station/s shall normally, and unless otherwise agreed, be set to deliver zero reactive power at the offshore grid entry point with active power output equal to registered capacity; and the reactive power delivered at the interface point shall be set in accordance with the reactive requirements placed on the offshore Licensee set out in Section K of the STC (System Operator – Transmission Owner Code); and

2.8.4 conditions on the onshore transmission system shall be set to those which ought reasonably to be expected to arise in the course of a year of operation. Such conditions shall include forecast demand cycles, typical power station operating regimes and typical planned outage patterns modified where appropriate by the provisions of paragraph 2.11.

Pre-fault criteria

2.9 The transmission capacity for the connection of a power station shall be planned such that, for the background conditions described in paragraph 2.8, prior to any fault there shall not be any of the following:

2.9.1	equipment loadings exceeding the pre-fault rating;

2.9.2 	voltages outside the pre-fault planning voltage limits or insufficient voltage performance margins;

2.9.3 system instability; or

2.9.4 Unacceptable Sub-Synchronous Oscillations.

Post-fault criteria – background condition of no local system outage

2.10 The transmission capacity for the connection of a power station shall also be planned such that for the background conditions described in paragraph 2.8 with no local system outage and for the secured event of a fault outage on the onshore transmission system of any of the following:

2.10.1 a single transmission circuit, a single generation circuit, a single generating unit (or several generating units sharing a common circuit breaker), a single Power Park Module, or a single DC converter, a reactive compensator or other reactive power provider;

2.10.2 a double circuit overhead line on the supergrid;

2.10.3 a double circuit overhead line where any part of either circuit is in NGET’s transmission system or SHET’s transmission system;

2.10.4 a single transmission circuit with the prior outage of another transmission circuit;

2.10.5 a section of busbar or mesh corner; or

2.10.6 a single transmission circuit with the prior outage of a generation circuit, generating unit (or several generating units, sharing a common circuit breaker, that cannot be separately isolated), a Power Park Module, a DC converter, a reactive compensator or other reactive power provider, or;

2.10.7 a single generation circuit, a single generating unit (or several generating units, sharing a common circuit breaker), a single Power Park Module, a single DC converter, a reactive compensator or other reactive power provider with the prior outage of a single transmission circuit

there shall not be any of the following:

2.10.8 a loss of supply capacity except as permitted by the demand connection criteria detailed in Section 3;

2.10.9 unacceptable overloading of any primary transmission equipment;

2.10.10 unacceptable voltage conditions or insufficient voltage performance margins;

2.10.11 system instability; or

2.10.12 Unacceptable Sub-Synchronous Oscillations.

2.11 Under planned outage conditions it shall be assumed that the prior circuit outage specified in paragraphs 2.10.3, 2.10.5 and 2.10.6 reasonably forms part of the typical outage pattern referred to in paragraph 2.8.4 rather than in addition to that typical outage pattern.

Post-fault criteria – background condition with a local system outage

2.12 The transmission capacity for the connection of a power station shall also be planned such that for the background conditions described in paragraph 2.8 with a local system outage on the onshore transmission system, the operational security criteria set out in Section 5 and Section 9 can be met.

2.13 Where necessary to satisfy the criteria set out in paragraph 2.12, investment should be made in transmission capacity except where operational measures suffice to meet the criteria in paragraph 2.12 provided that maintenance access for each transmission circuit can be achieved and provided that such measures are economically justified. The operational measures to be considered include rearrangement of transmission outages and appropriate reselection of generating units from those expected to be available, for example through balancing services. Guidance on economic justification is given in Appendix G.

Switching Arrangements

2.14 Guidance on substation configurations and switching arrangements are described in Appendix A. These guidelines provide an acceptable way towards meeting the criteria of paragraph 2.6. However, other configurations and switching arrangements which meet those criteria are also acceptable.

Variations to Connection Designs

2.15 Variations, arising from a generation customer’s request, to the generation connection design necessary to meet the requirements of paragraphs 2.5 to 2.14 shall also satisfy the requirements of this Standard provided that the varied design satisfies the conditions set out in paragraphs 2.16.1 to2.16.3. For example, such a generation connection design variation may be used to take account of the particular characteristics of a power station.

2.16 Any generation connection design variation must not, other than in respect of the generation customer requesting the variation, either immediately or in the foreseeable future:

2.16.1 reduce the security of the MITS to below the minimum planning criteria specified in Section 4; or

2.16.2 result in additional investment or operational costs to any particular customer or overall, or a reduction in the security and quality of supply of the affected customers’ connections to below the planning criteria in this section or Section 3, unless specific agreements are reached with affected customers; or

2.16.3 compromise any licensee’s ability to meet other statutory obligations or licence obligations.

2.17 Should system conditions subsequently change, for example due to the proposed connection of a new customer, such that either immediately or in the foreseeable future, the conditions set out in paragraphs 2.16.1 to 2.16.3 are no longer satisfied, then alternative arrangements and/or agreements must be put in place such that this Standard continues to be satisfied.

2.18 The additional operational costs referred to in paragraph 2.16.2 and/or any potential reliability implications shall be calculated by simulating the expected operation of the national electricity transmission system in accordance with the operational criteria set out in Section 5 and Section 9. Guidance on economic justification is given in Appendix G.

3. Demand Connection Criteria Applicable to the Onshore Transmission System

3.1	This section presents the planning criteria for the connection of demand groups

to the remainder of the onshore transmission system.

3.2	In those parts of the onshore transmission system where the criteria of Section

2 and/or Section 4 also apply, those criteria must also be met.

3.3	In planning demand connections, this standard is met if the connection design

either:

3.3.1	satisfies the deterministic criteria detailed in paragraphs 3.5 to 3.12; or

3.3.2 	varies from the design necessary to meet paragraph 3.3.1 above in a manner which satisfies the conditions detailed in paragraphs 3.17 to 3.20.

3.4	It is permissible to design to standards higher than those set out in paragraphs

3.5 to 3.12 provided the higher standards can be economically justified. Guidance on economic justification is given in Appendix G.

Demand Connection Capacity Requirements

3.5	The group demand which is applicable for the assessment of connection

capacity requirements is dependent on the nature of the associated connections, i.e.:

3.5.1 where the network associated with a transmission connection comprises demand connections and connections to small or medium power stations (including those in composite-user sites), group demand for future years is equal to the Network Operator’s estimated maximum demand for the group which they believe could reasonably be imposed on the onshore transmission system, after taking due cognisance of demand diversity and the expected operation of any embedded small or medium power stations.

3.5.2 where the network associated with a transmission connection hosts the connection of one or more large power stations, irrespective of whether the large power station is connected at the transmission interface point or embedded within the Network Operator’s system, the group demand at the date and time of the system/site maximum demand or other relevant assessment period is equal to:

3.5.2.1 the Network Operator’s group demand in accordance with paragraph 3.5.1, plus:

3.5.2.2 the output of large power station(s).

3.6	Where considered appropriate, diversity may be applied to the summation of

the power flows arising from consideration of paragraphs 3.5.2.1 and 3.5.2.2

3.7	The transmission capacity for the connection of a particular demand group shall

meet the criteria set out in paragraphs 3.7 to 3.11 under the following background conditions:

3.7.1 when there are no planned outages, the demand of the demand group shall be set equal to group demand;

3.7.2 when there is a planned outage local to the demand group, the demand of the demand group shall be set equal to maintenance period demand;

3.7.3 the security contribution of small and medium power stations embedded is implicitly accounted for in the group demand established by the Network Operator as in paragraph 3.5.1 and need not be considered separately;

3.7.4 the security contribution of a large power station embedded within a customer’s network (e.g. distribution network) or connected at the transmission interface point shall be as specified in paragraphs 3.13 to 3.15 and Table 3.2;

3.7.5 any transfer capacity (i.e. the ability to transfer demand from one demand group to another) declared by Network Operators shall be represented taking account of any restrictions on the timescales in which the transfer capacity applies. Any transfer capacity declared by the Network Operators for use in planning timescales must be reflective of that which could practically be used in operational timescales; and

3.7.6 demand and generation outside the demand group shall be set in accordance with the planned transfer conditions using the appropriate method described in Appendix C.

3.8 The transmission capacity for the connection of a demand group shall be planned such that, for the background conditions described in paragraph 3.7, under intact system conditions there shall not be any of the following:

3.8.1	equipment loadings exceeding the pre-fault rating;

3.8.2 	voltages outside the pre-fault planning voltage limits or insufficient voltage performance margins; or

3.8.3	system instability.

3.9	The transmission capacity for the connection of a demand group shall also be

planned such that for the background conditions described in paragraph 3.7 and for the planned outage of a single transmission circuit or a single section of busbar or mesh corner, there shall not be any of the following:

3.9.1 a loss of supply capacity for a group demand of greater than 1MW;

3.9.2 unacceptable overloading of any primary transmission equipment;

3.9.3	voltages outside the pre-fault planning voltage limits or insufficient

voltage performance margins; or

3.9.4 system instability.

3.10 The transmission capacity for the connection of a demand group shall also be planned such that for the background conditions described in paragraph 3.7 and the initial conditions of:

3.10.1 an intact system condition; or

3.10.2 the single planned outage of another transmission circuit, a generation circuit, a generating unit (or several generating units, sharing a common circuit breaker, that cannot be separately isolated), a power park module, a DC converter, a reactive compensator or other reactive power provider,

for the secured event of a fault outage of: 3.10.3 a single transmission circuit,

3.10.4 a single generation circuit, a single generating unit (or several generating units sharing a common circuit breaker), power park module or a DC converter,

there shall not be any of the following:

3.10.5 a loss of supply capacity such that the provisions set out in Table 3.1 are not met;

3.10.6 unacceptable overloading of any primary transmission equipment;

3.10.7 unacceptable voltage conditions or insufficient voltage performance margins; or

3.10.8 system instability.

3.11 In addition to the requirements of paragraphs 3.7 to 3.9 for the background conditions described in paragraph 3.7, the system shall also be planned such that:

3.11.1 operational switching or infrequent operational switching shall not cause unacceptable voltage conditions.

3.12 For a secured event on connections to more than one demand group, the permitted loss of supply capacity for that secured event is the maximum of the permitted loss of supply capacities set out in Table 3.1 for each of these demand groups.

Table 3.1 Minimum Planning Supply Capacity Following Secured Events

| Class | Group Demand | Initial System Conditions |
| --- | --- | --- |

|  | Minimum | Maximum | Intact System | With Single Planned Outage Note 1 |
| --- | --- | --- | --- | --- |
| A | 0 | £1 MW | In repair time Group Demand | Nil |
| B | >1 MW | £12 MW | Within 3 hours Group Demand minus 1MW In repair time Group Demand | Nil |
| C | >12 MW | £60 MW | Within 15 minutes Smaller of (Group Demand minus 12MW) and two-thirds of Group Demand Within 3 hours Group Demand | Nil |
| D | >60 MW | £300 MW | Immediately Group Demand minus 20MWNote 2 Within 3 hours Group Demand | Within 3 hours Smaller of (Group Demand minus 100MW) and one-third of Group Demand Within time to restore planned outage Group Demand |
| E | >300 MW | £1500 MW | Immediately Group Demand Note 3 | Immediately Maintenance Period Demand Within time to restore planned outage Group Demand |
| F | >1500 MW | ¥ | Immediately Group Demand | Immediately Group Demand |

Assessment of Contribution to Security from Generation

Note 1 The planned outage may be of a transmission circuit, generation circuit, generating unit, reactive compensator or other reactive power provider.

Note 2 The group demand may be lost for up to 60 seconds if this leads to significant economies. Note 3 Up to 60MW may be lost for up to 60 seconds if this leads to significant economies.

3.13 Where network assets are insufficient to meet the security requirements, it is necessary to assess the contribution to security from large power stations connected at either the transmission connection interface or embedded within the Networks Operator’s system. This will identify whether the aggregate generation capacity of the large power station connected to the network has the potential to meet any deficit in system security from network assets.

3.14 The combined contribution by large power stations shall never have a greater impact on system security than the loss of the largest circuit infeed to the group. The contributions from embedded small and medium power stations provide additional capacity to enable the supply of demand which may not otherwise be met following a secured event, but shall not replace the requirement for system connection. The assessment of contribution of generation to group security will therefore consider;

3.14.1 the generation annual load factor;

3.14.2 the availability of generation under outage conditions;

3.14.3 the fuel source availability, i.e. whether energy is continuous, stored, storable or predictable;

3.14.4 common-mode failure mechanisms such as common fuel source, connections or plant stability / ride-through capability;

3.14.5 capping of generation contribution in the event that the generation contribution is dominant with respect to circuit infeed capability.

3.15 The effective contribution of large power stations to demand group importing capacity, shall not exceed the levels indicated in Table 3.2 while taking due account of the considerations detailed in paragraph 3.13.

Table 3.2 Effective contribution of embedded large power stations to demand group importing capacity in NGET’s transmission system

| Expected annual load factor of generation | Initial system conditions |  |
| --- | --- | --- |
|  | Intact system | with single Planned Outage |
| Over 30% | 67% of Registered Capacity | For demand groups greater than 60MW only 67% of Registered Capacity |
| Over 10% to 30% | Smaller of 67% of Registered Capacity and 20% of Group Demand | For demand groups greater than 300MW only Smaller of 67% of Registered Capacity and 13% of Group Demand |
| up to 10% | Smaller of 67% of Registered Capacity and 10% of Group Demand | For demand groups greater than 300MW only Smaller of 67% of Registered Capacity and 7% of Group Demand |

Switching Arrangements

3.16 Guidance on substation configurations and switching arrangements are described in Appendix A. These guidelines provide an acceptable way towards meeting the criteria of this chapter. However, other configurations and switching arrangements which meet the criteria are also acceptable.

Variations to Connection Designs

3.17 Variations, arising from a demand customers request, to the demand connection design necessary to meet the requirements of paragraphs 3.5 to 3.12 shall also satisfy the requirements of this standard provided that the varied design satisfies the conditions set out in paragraphs 3.18.1 to 3.18.3. For example, such a demand connection design variation may be used to reflect the nature of connection of embedded generation or particular load cycles.

3.18 Any demand connections design variation must not, other than in respect of the demand customer requesting the variation, either immediately or in the foreseeable future:

3.18.1 reduce the security of the MITS to below the minimum planning criteria specified in Section 4; or

3.18.2 result in additional investment or operational costs to any particular customer or overall, or a reduction in the security and quality of supply of the affected customers’ connections to below the planning criteria in the section or Section 2, unless specific agreements are reached with affected customers; or

3.18.3 compromise any licensee’s ability to meet other statutory obligations or licence obligations.

3.19 Should system conditions change, for example due to the proposed connection of a new customer, such that either immediately or in the foreseeable future, the conditions set out in paragraphs 3.18.1 to 3.18.3 are no longer satisfied, then alternative arrangements and/or agreements must be put in place such that this standard continues to be satisfied.

3.20 The additional operational costs referred to in paragraph 3.18.2 and/or any potential reliability implications shall be calculated by simulating the expected operation of the onshore transmission system in accordance with the operational criteria set out in Section 5 and Section 9. Guidance on economic justification is given in Appendix G.

4.	Design of the Main Interconnected Transmission System

4.1	This section presents the planning criteria for the Main Interconnected

Transmission System (MITS).

4.2	In those parts of the onshore transmission system where the criteria of Section

2 and/or Section 3 also apply, those criteria must also be met. In those parts of the offshore transmission system where the criteria of Section 7 and/or Section 8 also apply, those criteria must also be met.

4.3	In planning the MITS, this Standard is met if the design satisfies the minimum

deterministic criteria detailed in paragraphs 4.4 to 4.12. It is permissible to design to standards higher than those set out in paragraphs 4.4 to 4.12 provided the higher standards can be economically justified. Guidance on economic justification is given in Appendix G.

Minimum Transmission Capacity Requirements At ACS peak demand with an intact system

4.4	The MITS shall meet the criteria set out in paragraphs 4.5 to 4.6 under both the

Security and Economy background conditions below:

Security Background

4.4.1	generating units’ outputs shall be set to those arising from the security

planned transfer condition described in Appendix C;

4.4.2 power flows shall be set to those arising from the security planned transfer condition (using the appropriate method described in Appendix C) prior to any fault, and such power flows modified by an appropriate application of the interconnection allowance (using the methods described in Appendix D) under secured events;

Economy Background

4.4.3 generating units’ outputs shall be set to those arising from the economy planned transfer condition described in Appendix E;

4.4.4 power flows shall be set to those arising from the economy planned transfer condition (using the appropriate method described in Appendix E) prior to any fault, and such power flows modified by an appropriate application of the boundary allowance (using the methods described in Appendix F) under secured events;

Security and Economy Backgrounds

4.4.5 sensitivity cases on the conditions described in 4.4.2 and 4.4.4 shall comprise generating units with output equal to their registered capacities such that the required power transfers described in 4.4.2 and 4.4.4 above are approximated by selection of individual units; and

4.4.6 the expected availability of generation reactive capability shall be set to that which ought reasonably to be expected to arise. This shall take into account the variation of reactive capability with the active power output (for example, as defined in the machine performance chart). In the absence of better data the expected available capability shall not exceed 90% of the Grid Code specified capability, (unless modified by a direction of the Authority) or 90% of the contracted capability for the active power output level, whichever is relevant.

4.5	The minimum transmission capacity of the MITS shall be planned such that, for

the background conditions described in paragraph 4.4, prior to any fault there shall not be:

4.5.1	equipment loadings exceeding the pre-fault rating;

4.5.2 voltages outside the pre-fault planning voltage limits or insufficient voltage performance margins;

4.5.3 system instability; or

4.5.4 Unacceptable Sub-Synchronous Oscillations.

4.6	The minimum transmission capacity of the MITS shall also be planned such

that for the conditions described in paragraph 4.4 and for the secured event of a fault outage of any of the following:

4.6.1	a single transmission circuit, a reactive compensator or other reactive

power provider;

4.6.2 a single generation circuit, a single generating unit (or several generating units sharing a common circuit breaker), a single power park module, or a single DC converter;

4.6.3 a double circuit overhead line on the supergrid;

4.6.4 a double circuit overhead line where any part of either circuit is in NGET’s transmission system or SHET’S transmission system;

4.6.5 a section of busbar or mesh corner; or

4.6.6 provided both the fault outage and prior outage involve plant that is wholly in NGET’s transmission area, any single transmission circuit with the prior outage of another transmission circuit containing either a transformer in series or a cable section located wholly or mainly outside a substation, or a generating unit (or several generating units, sharing a common circuit breaker, that cannot be separately isolated), reactive compensator or other reactive power provider,

4.6.7 there shall not be any of the following:

loss of supply capacity (except as permitted by the demand connection criteria detailed in Section 3 and Section 8);

4.6.8 unacceptable overloading of any primary transmission equipment;

4.6.9 unacceptable voltage conditions or insufficient voltage performance margins;

4.6.10 system instability; or

4.6.11 Unacceptable Sub-Synchronous Oscillations, Under conditions in the course of a year of operation

4.7	The MITS shall meet the criteria set out in paragraphs 4.8 to 4.10 under the

following background conditions:

4.7.1	conditions on the national electricity transmission system shall be set

to those which ought reasonably to be foreseen to arise in the course of a year of operation. Such conditions shall include forecast demand cycles, typical power station operating regimes and typical planned outage patterns; and

4.7.2 the expected availability of generation reactive capability shall be set to that which ought reasonably to be expected to arise. This shall take into account the variation of reactive capability with the active power output (for example, as defined in the machine performance chart). In the absence of better data the expected available capability shall not exceed 90% of the Grid Code specified capability, (unless modified by a direction of the Authority) or 90% of the contracted capability for the active power output level, whichever is relevant.

4.8	The minimum transmission capacity of the MITS shall be planned such that, for

the background conditions described in paragraph 4.7, prior to any fault there shall not be:

4.8.1	equipment loadings exceeding the pre-fault rating;

4.8.2 voltages outside the pre-fault planning voltage limits or insufficient voltage performance margins;

4.8.3 system instability; or

4.8.4 Unacceptable Sub-Synchronous Oscillations.

4.9	The minimum transmission capacity of the MITS shall also be planned such

that, for the background conditions described in paragraph 4.7, the operational security criteria set out in Section 5 can be met.

4.10 Where necessary to satisfy the criteria set out in paragraphs 4.8 and 4.9, investment should be made in transmission capacity except where operational measures suffice to meet the criteria in paragraphs 4.8 and 4.9 provided that maintenance access for each transmission circuit can be achieved and provided that such measures are economically justified. The operational measures to be considered include rearrangement of transmission outages and appropriate reselection of generating units from those expected to be available, for example through balancing services. Guidance on economic justification is given in Appendix G.

General Criteria

4.11 In addition to the requirements set out in paragraphs 4.4 to 4.10, the system shall also be planned such that:

4.11.1 operational switching or infrequent operational switching shall not cause unacceptable voltage conditions,

4.12 Transmission circuits comprising the supergrid part of the MITS shall not exceed the circuit complexity limit defined in paragraphs B.3 to B.7 of Appendix B.

4.13 Guidance on complexity of transmission circuits on the MITS operated at a nominal voltage of 132kV is given in paragraphs B.8 to B.13 of Appendix B. Relaxation of the restrictions cited in paragraphs B.8 to B.13 may be justified in certain circumstances following appropriate liaison between the relevant Licensees responsible for the design of the circuits and their operation.

Switching Arrangements

4.14 Guidance on substation configurations and switching arrangements are described in Appendix A. These guidelines provide an acceptable way towards meeting the criteria of this section. However, other configurations and switching arrangements which meet the criteria are also acceptable.

5. Operation of the Onshore Transmission System

Normal Operational Criteria

5.1	The onshore transmission system shall be operated under prevailing system

conditions so that for the secured event of a fault outage on the onshore transmission system of any of the following:

5.1.1	a single transmission circuit, a reactive compensator or other reactive

power provider; or

5.1.2 a single generation circuit, a single generating unit (or several generating units sharing a common circuit breaker), a single power park module, or a single DC converter; or

5.1.3 the most onerous loss of power infeed; or

5.1.4 the most onerous loss of power outfeed; or

5.1.5 where the system is designed to be secure against a fault outage of a

section of busbar or mesh corner under planned outage conditions, a section of busbar or mesh corner,

there shall not be any of the following:

5.1.6 a loss of supply capacity except as specified in Table 5.1

5.1.7 unacceptable frequency conditions;

5.1.8 unacceptable overloading of any primary transmission equipment;

5.1.9 unacceptable voltage conditions;

5.1.10 system instability; or

5.1.11 Unacceptable Sub-Synchronous Oscillations.

5.2	For a secured event on the onshore transmission system on connections to

more than one demand group the permitted loss of supply capacity for that secured event is the maximum of the permitted loss of supply capacities set out

in Table 5.1 for each of these demand groups.

5.3	The onshore transmission system shall be operated under prevailing system

conditions so that for the secured event on the onshore transmission system of a fault outage of:

5.3.1 a double circuit overhead line; or

5.3.2 a section of busbar or mesh corner,

there shall not be any of the following:

5.3.3 a loss of supply capacity greater than 1500 MW; 5.3.4 unacceptable frequency conditions;

5.3.5 unacceptable voltage conditions affecting one or more Grid Supply Points for which the total group demand is greater than 1500 MW;

5.3.6 system instability of one or more generating units connected to the supergrid; or

5.3.7 Unacceptable Sub-Synchronous Oscillations.

5.4	The onshore transmission system shall be operated under prevailing system

conditions so that for the secured event on the supergrid of a fault outage of:

5.4.1	a double circuit overhead line where any part of either circuit is in

NGET’s transmission system; or

5.4.2 a section of busbar or mesh corner in NGET’s transmission system, there shall not be:

5.4.3 unacceptable overloading of primary transmission equipment in NGET’s transmission system;

5.4.4 unacceptable voltage conditions in NGET’s transmission system. Table 5.1 Maximum permitted loss of supply capacity following secured events

| Group Demand | Initial system conditions |  |
| --- | --- | --- |
|  | Prevailing system conditions with no local system outage Note 1,2 | Prevailing system conditions with a local system outage Note 1 |
| over 1500 MW | None | None Note 3 |
| over 300 MW to 1500 MW | None Note 4 | None Note 3 |
| over 60 MW to 300 MW | None except that where such facilities and suitable measures for restoration are available, up to 20 MW by automatic disconnection Note 5 | Whole group up to Group Demand for up to the operational specified time to restore supply capacity |
| over 12 MW to 60 MW | None except that where such facilities and suitable measures for restoration are available, up to 12 MW by automatic disconnection for up to 15 minutes. | Whole group up to Group Demand |
| over 1 MW to 12 MW | Whole group up to Group Demand for up to the operational specified time to restore supply capacity | Whole group up to Group Demand |
| up to 1 MW | Whole group up to Group Demand for up to the operational specified time to restore supply capacity | Whole group up to Group Demand |

Notes

- The time to restore any lost supply capacity shall be as short as practicable. If any part of any lost supply capacity can be restored in less than the specified maximum time to restore all of it, it shall be restored.

- Where the supply capacity was designed in such a way, there should be no loss of supply capacity.

- Where the supply capacity to the Grid Supply Point was designed in accordance with the demand connection criteria in Section 3 in such a way as to permit it, a loss of supply capacity equal to any amount by which the prevailing demand exceeds the maintenance period demand may be permitted up to a maximum of 1500 MW for no longer than the operational specified time to restore supply capacity.

- Where the supply capacity to the Grid Supply Point was designed in accordance with the demand connection criteria in Section 3 in such a way as to permit it, up to 60 MW may be lost for up to 60 seconds.

- Where the supply capacity to the Grid Supply Point was designed in accordance with the demand connection criteria in Section 3 in such a way as to permit it, up to the group demand may be lost for up to 60 seconds.

Conditional Further Operational Criteria

5.5	If:

5.5.1	there are adverse conditions such that the likelihood of a double circuit

overhead line fault is significantly higher than normal; or

5.5.2	there is no significant economic justification for failing to secure the

onshore transmission system to this criterion and the probability of loss of supply capacity is not increased by following this criterion,

the onshore transmission system shall be operated under prevailing system conditions so that for the secured event of

5.5.3 a fault outage on the supergrid of a double circuit overhead line there shall not be:

5.5.4 where possible and there is no significant economic penalty, any loss of supply capacity greater than 300 MW;

5.5.5 unacceptable overloading of any primary transmission equipment; 5.5.6 unacceptable voltage conditions;

5.5.7 system instability; or

5.5.8 Unacceptable Sub-Synchronous Oscillations.

5.6	During periods of major system risk, the ISOP may implement measures to mitigate the consequences of this risk. Such measures may include: providing additional reserve; reducing system-to-generator intertrip risks, securing as far as possible appropriate two-circuit combinations, or reducing system transfers, for example through balancing services.

5.7	In the case that neither of the conditions in paragraphs 5.5.1 and 5.5.2 is met, it is acceptable to utilise short term post fault actions to avoid unacceptable overloading of primary transmission equipment which may include a requirement for demand reduction; however, this will not be used as a method of increasing reserve to cover abnormal post fault generation reduction. Where possible these post fault actions shall be notified to the appropriate Network Operator or Generator. Normally the provisions of the Grid Code, in respect of Emergency Manual Demand Disconnection and/or, for example through balancing services, will be applied. Additional post fault actions beyond the Grid Code provisions may be applied, but only where they have been agreed in advance with the appropriate Network Operator or Generator.

5.8	The ISOP shall use the latest version of the Frequency Risk and Control Report as consulted on and approved by the Authority to determine the events for which unacceptable frequency conditions shall not occur. The Frequency Risk and Control Report assessment includes consideration of any consequential loss of distributed energy resources associated with any such event.

Post-fault Restoration of System Security

5.9	Following the occurrence of a secured event on the onshore transmission system, measures shall be taken to re-secure the system to the above operational criteria as soon as reasonably practicable. To this end, it is permissible to put operational measures in place pre-fault to facilitate the speedy restoration of system security.

Authorised Variations from the Operational Criteria

5.10 Provided it is in accordance with the appropriate requirements of the demand connection criteria in Section 3, there may be associated loss of supply capacity due to a secured event, for example by virtue of the design of the generation connections and/or the designed switching arrangements at the substations concerned.

5.11 Exceptions to the criteria in paragraphs 5.1 to 5.7 and 5.9 may be required:

5.11.1 where variations to the connection designs as per paragraphs 3.12 to 3.15 have been agreed; or

5.11.2 in relation to 5.1.7 and 5.3.4 only, based on the outcome of an assessment conducted in accordance with the Frequency Risk and Control Report.

5.12 The principles of these operational criteria shall be applied at all times except in special circumstances where the ISOP, following consultation with the appropriate Network Operator, Generator or Non-Embedded Customer, may need to give instructions to the contrary to preserve overall system integrity.

6.	Voltage Limits in Planning and Operating the Onshore

6.	Voltage Limits in Planning and Operating the Onshore

Transmission System

Voltage and Voltage Performance Margins in Planning Timescales 6.1. A voltage condition is unacceptable in planning timescales if:

6.1.1. There is any inability to achieve pre-fault steady-state voltages as specified in Table 6.1 at onshore transmission system substations or GSPs,

or

6.1.2.	if, after either:

6.1.2.1. a secured event,

or

6.1.2.2. operational switching,

and the affected site remains directly connected to the onshore transmission system in the steady state after the relevant event above, any of the following conditions applies:

6.1.2.3. the voltage step change at an interface between the onshore transmission system and a User System exceeds that specified in Table 6.5

or

6.1.2.4. there is any inability following such an event to achieve a steady state voltage as specified in Table 6.2 at onshore transmission system substations or GSPs using manual and/or automatic facilities available, including the switching in or out of relevant equipment,

or

6.1.3.	if, pre-fault, or after either:

6.1.3.1. a secured event,

or

6.1.3.2. operational switching

there are insufficient voltage performance margins, as evidenced by:

- voltage collapse;

- over-sensitivity of system voltage; or

- unavoidably exceeding the continuous reactive capability expected to be available from generating units or other reactive sources, so that accessible reactive reserves are exhausted;

under any of the following conditions:

i)	credible demand sensitivities;

- the unavailability of any single reactive compensator or other reactive power provider; or

- the loss of any one automatic switching system or any automatic voltage control system for on-load tap changing.

6.2. The steady state voltages are to be achieved without widespread post-fault re-despatch of generating unit reactive output or changes to set-points of SVCs or automatic reactive switching schemes and without exceeding the available reactive capability of generation or SVCs. In particular, following a secured event, the target voltages at Grid Supply Points should be achieved after the operation of local reactive switching and auto-switching schemes, and after the operation of Grid Supply Transformer tap-changers.

6.3. The pre-fault planning voltage limits and targets on the onshore transmission system are as shown in Table 6.1.

Table 6.1: Pre-Fault Steady State Voltage Limits and Requirements in Planning Timescales

| - Voltage Limits on Transmission Networks |  |  |  |
| --- | --- | --- | --- |
| Nominal Voltage | PU Value (1pu relates to the Nominal Voltage) | Minimum (percentage of Nominal Voltage) (Note 1) | Maximum (percentage of Nominal Voltage) |
| Greater than 300kV | 0.975pu-1.025pu | -2.5% | +2.5% Note 2 |
| 200kV up to and including 300kV | 0.95pu-1.05pu | -5% | +5% |
| 132kV up to and including 200kV | 0.95pu-1.05pu | -5% | +5% |
| - Voltages to be Achievable at Interfaces to Distribution Networks and Non-Embedded Customers |  |  |  |
| Any Nominal Voltage | 1.05pu at forecast Group Demand 1.00pu at forecast Minimum Demand or as otherwise agreed with the relevant Network Operator or Non-Embedded Customer |  |  |

Notes

1.	It is permissible to relax these to the limits specified in Table 6.2 if:

- following a secured event, the voltage limits specified in Table 6.2 can be achieved, and

- there is judged to be sufficient certainty of meeting Security and Quality of Supply Standards in operational timescales.

2.	It is permissible to relax this to 105% of the nominal voltage if there is judged to be sufficient
certainty that the limit of 105% of the nominal voltage can be met in operational timescales.

6.4. The voltage limits in Table 6.2 are to be observed following any secured event.

Table 6.2 Steady State Voltage Limits and Requirements in Planning Timescales

| - Voltage Limits on Transmission Networks |  |  |  |
| --- | --- | --- | --- |
| Nominal Voltage | PU Value (1pu relates to the Nominal Voltage) | Minimum (percentage of Nominal Voltage) | Maximum (percentage of Nominal Voltage) |
| Greater than 300kV | 0.95pu-1.025pu | -5% Note 3 | +2.5% Note 4 |
| 200kV up to and including 300kV | 0.90pu-1.05pu | -10% | +5% |
| 132kV up to and including 200kV | 0.90pu-1.05pu | -10% | +5% |
| - Voltage Limits at Interfaces to Distribution Networks and Non-Embedded Customers |  |  |  |
| Any Nominal Voltage | See below for the minimum voltage that must be achievable. Must always exceed lower limits of Table 6.4(b) |  | +5% |
| - Voltages to be Achievable at Interfaces to Distribution Networks and Non-Embedded Customers |  |  |  |
| Any Nominal Voltage | 1.00pu at any demand level Note 5 or as otherwise agreed with the relevant Network Operator or Non-Embedded Customer. |  |  |

Notes

3.	It is permissible to relax this to 90% of the nominal voltage if the affected substations are on the
same radially fed spur post-fault, and:

- there is no lower voltage interconnection from these substations to other supergrid substations; and

- no auxiliaries of large power stations are derived from them.

4.	It is permissible to relax this to 105% of the nominal voltage if there is judged to be sufficient
certainty of meeting Security and Quality of Supply Standards in operational timescales, and operational measures to achieve these are identified at the planning stage.

5. May be relaxed downwards following a secured event involving the outage of a Grid Supply Transformer, provided that there is judged to be sufficient certainty that the limits of Table 6.4(b) can be met in operational timescales.

6.5. For a site or a group of sites with a combined group demand of less than 1500MW, operational measures shall be identified at the planning stage to ensure that the requirements of Table 6.3 and 6.4 can be met in operational

timescales for all sites remaining connected following any secured event for which it is not required to secure the full group demand.

Voltage Limits in Operational Timescales

6.6. A voltage condition is unacceptable in operational timescales if:

6.6.1. there is any inability to achieve pre-fault steady-state voltages as specified in Table 6.3 at onshore transmission system substations or GSPs

or

6.6.2.	if, after either

6.6.2.1. a secured event,

or

6.6.2.2. operational switching

and the affected site remains directly connected to the onshore transmission system in the steady state after the relevant event above, either of the following conditions applies:

6.6.2.3. the voltage step change at an interface between the onshore transmission system and a User System exceeds that specified in Table 6.5,

or

6.6.2.4. there is any inability following such an event to achieve a steady state voltage as specified in Table 6.4 at onshore transmission system substations or GSPs using manual and/or automatic facilities available, including the switching in or out of relevant equipment.

Table 6.3 Pre-Fault Steady State Voltage Limits and Targets in Operational Timescales

| - Voltage Limits on Transmission Networks |  |  |  |
| --- | --- | --- | --- |
| Nominal Voltage | PU Value (1pu relates to the Nominal Voltage) | Minimum (percentage of Nominal Voltage) | Maximum (percentage of Nominal Voltage) |
| Greater than 300kV | 0.95pu-1.05pu | -5% Note 6 | +5% Note 7 |
| 200kV up to 300kV | 0.95pu-1.10pu | -5% Note 6 | +10% Note 7 |
| 132kV up to and including 200kV | 0.95pu-1.10pu | -5% Note 6 | +10% Note 7 |
| - Voltages to be Achievable at Interfaces to Distribution Networks and Non-Embedded Customers |  |  |  |
| Any Nominal Voltage | Target voltages and voltage ranges as agreed with the relevant Distribution Network Operators or Non-Embedded Customers, within the limits of Table 6.4 |  |  |

Notes

6.	It is permissible to relax this to 90% at substations if no auxiliaries of large power stations are
derived from them.

7.	Operation at a higher limit than that specified above is permitted only subject to the written agreement of the relevant Onshore Transmission Licensee in relation to one or more locations on the Onshore Transmission Licensee's transmission system. Any such agreement shall specify the affected locations, the applicable higher limit, the duration for which it applies, and any restrictions or conditions under which operation at the higher limit is permitted.

Table 6.4 Steady State Voltage Limits and Targets in Operational Timescales

| - Voltage Limits on Transmission Networks |  |  |  |
| --- | --- | --- | --- |
| Nominal Voltage | PU Value (1pu relates to the Nominal Voltage) | Minimum (percentage of Nominal Voltage) | Maximum (percentage of Nominal Voltage) |
| Greater than 300kV | 0.90pu-1.05pu | -10% | +5% Note 8 |
| 200kV up to and including 300kV | 0.90pu-1.10pu | -10% | +10% Note 9 |
| 132kV up to and including 200kV | 0.90pu-1.10pu | -10% | +10% Note 9 |
| - Voltage Limits at Interfaces to Distribution Networks and Non-Embedded Customers |  |  |  |
| Nominal Voltage |  |  |  |
| 132kV | 0.90pu-1.10pu | -10% | +10% Note 10 |
| At less than 132kV | 0.94pu-1.06pu | -6% | +6% Note 10 |

Notes

8.	May be relaxed to 110% for no longer than 15 minutes following a secured event.

9.	Operation at a higher limit than that specified above is permitted only subject to the prior written agreement of the relevant Onshore Transmission Licensee, in respect of one or more specified locations on the onshore licensee’s transmission system. Any such agreement shall specify the affected locations, the applicable higher limit, the duration for which it applies, and any restrictions or conditions under which operation at the higher limit is permitted.

10.	Relaxation is permitted as per Note 9 provided that this has been agreed with the relevant Network Operator and/or Non-Embedded Customer(s) in accordance with the Grid Code.

Voltage Step Change Limits in All Timescales

6.7. Voltage step change limits must be observed at every interface point between the national electricity transmission system and Users’ plant. The voltage step change limits do not apply where no User is connected.

6.8. The voltage step change limits must be applied with load response taken into account.

Table 6.5 Voltage Step Change Limits in Planning and Operational Timescales

| Type of Event | Voltage Fall | Voltage Rise |
| --- | --- | --- |
| (a) At substations supplying User Systems at any voltage |  |  |
| 1. Following operational switching at intervals of less than 8 minutes | In accordance with Figure 6.1 |  |
| - Following operational switching at intervals of more than 8 minutes, - except for infrequent operational switching events as described below | -3% | +3% |
| - Following infrequent operational switching (Notes 8, 9) | -6% | +6% |
| - In planning timescales, following a fault outage of a double circuit supergrid overhead line (Note 10) | -6% | +6% |

| 6. Following any other secured event, (Note 11) except as detailed below: |  | -6% | +6% |
| --- | --- | --- | --- |
| (b) At substations supplying User Systems at voltages above 132kV |  |  |  |
| 7. Following a secured event involving a fault outage of a section of busbar or a mesh corner |  | -12% | +6% |
| 8. In operational timescales, following a secured event involving a fault outage of a double circuit overhead line |  | -12% | +6% |
| (c) At substations supplying User Systems at 132kV As (a) and (b) plus: |  |  |  |
| 9. Following a secured event involving loss of a double circuit transmission overhead line, and one or more supergrid transformers stepping down to 132 kV |  | -12% | +6% |
| 10. Following a secured event involving loss of a single transmission circuit and one or more |  | -12% | +6% |
| supergrid transformers stepping down to 132kV, with a prior outage of another circuit connected to the substation or of another mesh corner at the substation |  |  |  |
| 11. Following a secured event involving loss of a double circuit transmission overhead line operating at 132kV (Note 12) |  | -12% | +6% |
| (d) At substations supplying User Systems at voltages below 132kV As (a), (b) and (c) plus: |  |  |  |
| 12. Following a secured event involving the loss of one or more Grid Supply Transformers |  | -12% | +6% |

Notes

11.	An individual User must not experience voltage steps exceeding ±3% due to infrequent operational
switching:

- on a regular basis, and / or

- at intervals of less than two hours,

- unless abnormal conditions prevail

Infrequent operational switching would typically include disconnection of circuits for routine maintenance. It would not include switching out of circuits for voltage control, or switching out of circuits to allow safe access to other plant, where it is foreseen that such switching may be a regular practice; such events would be classed as operational switching.

12.	Voltage steps exceeding ±3% due to infrequent operational switching may be accepted only on
busbars or circuits fed directly by the transmission circuits involved in the infrequent operational switching.

13.	It is permissible to relax this to -12%, +6% in Scotland if the aggregate demand of sites experiencing voltage falls between 6% and 12% and does not exceed 1500MW.

14.	Operationally, the -6% requirement may be relaxed to -12% at a site or sites with a combined group demand of less than 1500MW, provided all other NETS SQSS requirements are met, if the -6% requirement may only be met by shedding load.

15.	In planning timescales, for demand groups with aggregate demand less than 1500MW, this criterion applies to any demand left connected post-fault. Operationally, this criterion only applies for demand groups with aggregate demand greater than 1500MW.

Figure

6.1 Maximum Voltage Step Changes Permitted for Operational Switching derived from ER P28 B.1.2

7.	Generation Connection Criteria Applicable to an Offshore

Transmission System

7.1	This section presents the planning criteria applicable to the connection of one

or more offshore power stations to an offshore transmission system. The criteria in this section apply from the offshore grid entry point/s (GEP) at which each offshore power station connects to an offshore transmission system, through the remainder of the offshore transmission system to the point of connection at the first onshore substation, which is the interface point (IP) in the case of a direct connection to the onshore transmission system or the user system interface point (USIP) in the case of a connection to an onshore user system.

7.2	Planning criteria are defined for all elements of an offshore transmission system

including: the offshore transmission circuits and equipment on the offshore platform (whether AC or DC); the offshore transmission circuits from the offshore platform to the interface point or user system interface point (as the case may be) including undersea cables and any overhead lines (whether AC or DC); and any onshore AC voltage transformation facilities or DC converter facilities.

7.3	In those parts of the national electricity transmission system where the criteria

of Section 8 and/or Section 4 also apply, those criteria must also be met.

7.4 In planning offshore generation connections, this Standard is met if the connection design either:

7.4.1	satisfies the deterministic criteria detailed in paragraphs 7.6 to 7.18; or

7.4.2 varies from the design necessary to meet paragraph 7.4.1 above in a manner which satisfies the conditions detailed in paragraphs 7.20 to 7.23.

7.5	It is permissible to design to standards higher than those set out in paragraphs

7.6 to 7.18 provided the higher standards can be economically justified. Guidance on economic justification is given in Appendix G.

Limits to Loss of Power Infeed Risks

7.6	For the purpose of applying the criteria of paragraphs 7.7 to 7.12, the loss of

power infeed resulting from a secured event shall be calculated as follows:

7.6.1 the sum of the registered capacities of the offshore power park modules or offshore gas turbines disconnected from the system by a secured event, less

7.6.2 the forecast minimum demand disconnected from the system by the same event but excluding (from the deduction) any demand forming part of the forecast minimum demand which may be automatically tripped for system frequency control purposes and excluding (from the deduction) the demand of the largest single end customer.

Offshore Platforms (AC and DC)

7.7	Offshore generation connections on offshore platforms shall be planned such

that, starting with an intact system, the consequences of secured events on the offshore transmission system shall be as follows;

7.7.1 AC Circuits on an offshore platform

7.7.1.1 in the case of offshore power park module only connections, and where the offshore grid entry point capacity is 90MW or more, following a planned outage or a fault outage of a single AC offshore transformer circuit on the offshore platform, the loss of power infeed shall not exceed the smaller of either:

50% of the offshore grid entry point capacity; or the full normal infeed loss risk.

7.7.1.2 in the case of gas turbine only connections, and where the offshore grid entry point capacity is 90MW or more, following a planned outage or a fault outage of a single AC offshore transmission circuit on the offshore platform, there shall be no loss of power infeed;

7.7.1.3 following a fault outage of a single AC offshore transmission circuit on the offshore platform, during a planned outage of

another AC offshore transmission circuit on the offshore platform, the further loss of power infeed shall not exceed the infrequent infeed loss risk.

7.7.2 DC Circuits on an offshore platform

7.7.2.1 following a planned outage or a fault outage of a single DC converter on the offshore platform, the loss of power infeed shall not exceed the infrequent infeed loss risk;

7.7.2.2 following a fault outage of a single DC converter on the offshore platform, during a planned outage of another DC converter on the offshore platform, the further loss of power infeed shall not exceed the infrequent infeed loss risk.

7.7.3 Busbars and Switchgear on an offshore platform

7.7.3.1 following a planned outage of any single section of busbar or mesh corner, the loss of power infeed shall not exceed the normal infeed loss risk;

7.7.3.2 following a fault outage of any single section of busbar or mesh corner, the loss of power infeed shall not exceed the infrequent infeed loss risk;

7.7.3.3 following a fault outage of any single busbar coupler circuit breaker or busbar section circuit breaker or mesh circuit breaker, the loss of power infeed shall not exceed the infrequent infeed loss risk;

7.7.3.4 following a fault outage of any single section of busbar or mesh corner, during a planned outage of any other single section of busbar or mesh corner, the loss of power infeed shall not exceed the infrequent infeed loss risk;

7.7.3.5 following a fault outage of any single busbar coupler circuit breaker or busbar section circuit breaker or mesh circuit breaker, during a planned outage of any single section of busbar or mesh corner, the loss of power infeed shall not exceed the infrequent infeed loss risk.

Cable Circuits (AC and DC)

7.8 The transmission connections between one offshore platform and another offshore platform or from an offshore platform to the interface point or user system interface point at the first onshore substation shall be planned such that, starting with an intact system and for the full offshore grid entry point capacity at the offshore grid entry point, the consequences of secured events shall be as follows:

7.8.1 following a planned outage or a fault outage of a single cable offshore transmission circuit, the loss of power infeed shall not exceed the infrequent infeed loss risk; and

7.8.2 following a fault outage of a  single cable offshore transmission circuit during a planned outage of another cable offshore transmission circuit the further loss of power infeed shall not exceed the infrequent infeed loss risk single cable offshore transmission circuit during a planned outage of another cable offshore transmission circuit the further loss of power infeed shall not exceed the infrequent infeed loss risk.

Overhead Line Sections (AC and DC)

7.9	In the case AC overhead line connections of 132kV, between the incoming AC

cable offshore transmission circuits and the first onshore substation or the onshore AC transformation facilities (as the case may be), the justification for a minimum of one circuit or two circuits is illustrated in Figure 7.1. In Figure 7.1 the justification is presented as a function of route length and offshore grid entry point capacity. The area above the line represents justification for a minimum of two circuits and the area below the line represents justification for a minimum of one circuit.

Two Circuits

Two Circuits

One Circuit

One Circuit

Figure 7.1 Justification for a Minimum of One Circuit or a Minimum of Two Circuits
for 132kV AC Overhead Lines

7.10 In the case of AC overhead line connections of 220kV or above, between the incoming AC cable offshore transmission circuits and the first onshore substation or the onshore AC transformation facilities (as the case may be), a single circuit is justified as a minimum for offshore grid entry point capacities of 1250MW or less and two circuits are justified as a minimum for offshore grid entry point capacities greater than 1250MW.

7.11 Overhead line (AC or DC) connections between the cable (AC or DC) offshore transmission circuits and the first onshore substation or the onshore AC transformation facilities or DC conversion facilities, as the case may be, shall be planned such that, starting with an intact system and for the full offshore grid

entry point capacity at the offshore grid entry point, the consequences of a

secured event on the offshore transmission system shall be as follows:

7.11.1 following a planned outage or a fault outage of a single overhead line circuit, the loss of power infeed shall not exceed the infrequent infeed loss risk;

7.11.2 following a fault outage of a single overhead line circuit during a planned outage of another overhead line circuit, the further loss of power infeed shall not exceed the infrequent infeed loss risk.

Onshore Connection Facilities (AC and DC)

7.12 The transmission connections at the onshore AC transformation or DC conversion facilities shall be planned such that, starting with an intact system, the consequences of secured events on the offshore transmission system shall be as follows;

7.12.1 AC Circuits

7.12.1.1 in the case of offshore power park module only connections, and where the offshore grid entry point capacity is 120MW or more, following a planned outage or a fault outage of a single AC offshore transformer circuit at the onshore AC transformation facilities, the loss of power infeed shall not exceed the smaller of either:

50% of the offshore grid entry point capacity; or the full normal infeed loss risk.

7.12.1.2 in the case of gas turbine only connections, following a planned outage or a fault outage of a single AC offshore transmission circuit at the onshore AC transformation facilities, the loss of power infeed shall not exceed the normal infeed loss risk;

7.12.1.3 following a fault outage of a single AC offshore transmission circuit at the onshore AC transformation facilities, during a planned outage of another AC offshore transmission circuit at the onshore AC transformation facilities, the further loss of power infeed shall not exceed the infrequent infeed loss risk.

7.12.2 DC Circuits

7.12.2.1 following a planned outage or a fault outage of a single DC converter at the onshore DC conversion facilities, the loss of power infeed shall not exceed the infrequent infeed loss risk;

7.12.2.2 following a fault outage of a single DC converter at the onshore DC conversion facilities, during a planned outage of

another DC converter at the onshore DC conversion facilities, the further loss of power infeed shall not exceed the infrequent infeed loss risk.

7.12.3 Busbars and Switchgear

7.12.3.1 in the case of offshore power park module connections or multiple gas turbine connections, following a planned outage of any single section of busbar or mesh corner, no loss of power infeed shall occur;

7.12.3.2 in the case of a single gas turbine connection, following a planned outage of any single section of busbar or mesh corner, the loss of power infeed shall not exceed the infrequent infeed loss risk;

7.12.3.3 following a fault outage of any single section of busbar or mesh corner, the loss of power infeed shall not exceed the infrequent infeed loss risk;

7.12.3.4 following a fault outage of any single busbar coupler circuit breaker or busbar section circuit breaker or mesh circuit breaker, the loss of power infeed shall not exceed the infrequent infeed loss risk;

7.12.3.5 following a fault outage of any single section of busbar or mesh corner, during a planned outage of any other single section of busbar or mesh corner, the loss of power infeed shall not exceed the infrequent infeed loss risk;

7.12.3.6 following a fault outage of any single busbar coupler circuit breaker or busbar section circuit breaker or mesh circuit breaker, during a planned outage of any single section of busbar or mesh corner, the loss of power infeed shall not exceed the infrequent infeed loss risk.

Generation Connection Capacity Requirements Background conditions

7.13 The connection of a particular offshore power station shall meet the criteria set out in paragraphs 7.14 to 7.23 under the following background conditions:

7.13.1 the active power output of the offshore power station shall be set to deliver active power at the offshore grid entry point equal to its registered capacity or, for the purpose of Sub-Synchronous Oscillations studies, that which provides the lowest level of damping for the sub-synchronous mode under consideration;

7.13.2 the reactive power output of the offshore power station shall normally, and unless otherwise agreed, be set to deliver zero reactive power at the offshore grid entry point with active power output equal to registered

capacity; and the reactive power delivered at the interface point shall be set in accordance with the reactive requirements placed on the offshore Licensee set out in Section K of the STC (System Operator – Transmission Owner Code); and

7.13.3 conditions on the national electricity transmission system shall be set to those which ought reasonably to be expected to arise in the course of a year of operation. Such conditions shall include forecast demand cycles, typical power station operating regimes and typical planned outage patterns modified where appropriate by the provisions of paragraph 7.16.

Pre-Fault Criteria – background conditions of no local system outage

7.14 The transmission capacity of the offshore transmission circuits for the connection of one or more offshore power stations shall be planned such that, for the background conditions described in paragraph 7.13, with no local system outage and prior to any fault, there shall not be any of the following:

7.14.1 equipment loadings exceeding the pre-fault rating;

7.14.2 voltages outside the pre-fault planning voltage limits or insufficient voltage performance margins;

7.14.3 system instability; or

7.14.4 Unacceptable Sub-Synchronous Oscillations.

Post-Fault Criteria – background conditions of no local system outage

7.15 The transmission capacity of the offshore transmission circuits for the connection of one or more offshore power stations shall also be planned such that for the background conditions described in paragraph 7.13 with no local system outage and for the secured event on the offshore transmission system of any of the following:

7.15.1 in the case of an offshore power park module connection with an OffGEP capacity of 90MW or more, with the OffGEP capacity reduced by 50%, a fault outage or planned outage of a single AC offshore transmission circuit on the offshore platform;

7.15.2 in the case of an offshore power park module connection with an OffGEP capacity of 120MW or more, with the OffGEP capacity reduced to 50%, a fault outage or a planned outage of a single AC offshore transmission circuit at the onshore transformation facilities

And in all cases other than specified in 7.15.1 and 7.15.2 above:

7.15.3 a fault outage or a planned outage of a single offshore transmission circuit;

And in all cases:

7.15.4 	a fault outage or a planned outage of a generation circuit, a generating unit (or several generating units sharing a common circuit breaker), a power park module, a DC converter, single reactive compensator or other reactive provider;

7.15.5	a fault outage of a single offshore transmission circuit during a planned outage of another offshore transmission circuit; generation circuit, a generating unit (or several generating units sharing a common circuit breaker), a power park module, a DC converter, a reactive compensator or other reactive power provider;

7.15.6 	a fault outage or a planned outage of a single section of busbar or mesh corner;

7.15.7 	There shall not be any of the following:

a loss of supply capacity except as permitted by the demand connection criteria detailed in Section 8;

7.15.8  unacceptable overloading of any primary transmission equipment;

7.15.9  unacceptable voltage conditions or insufficient voltage performance margins;

7.15.10 system instability; or

7.15.11 Unacceptable Sub-Synchronous Oscillations.

7.16 	Under planned outage conditions it shall be assumed that the planned outage specified in paragraphs 7.15.5 reasonably forms part of the typical outage pattern referred to in paragraph 7.13.3 rather than in addition to the typical outage pattern.

Post-fault criteria – background conditions with a local system outage

7.17 	The transmission capacity of the offshore transmission circuits for the connection of one or more offshore power stations to an offshore transmission system shall also be planned such that, for the background conditions described in paragraph 7.13 with a local system outage, the operational security criteria set out in Section 9 can be met.

7.18 	Where necessary to satisfy the criteria set out in paragraph 7.17, investment should be made in transmission capacity except where operational measures suffice to meet the criteria in paragraph 7.17 provided that maintenance access for each offshore transmission circuit can be achieved and provided that such measures are economically justified. The operational measures to be considered include rearrangement of transmission outages and appropriate reselection of generating units from those expected to be available, for example through balancing services. Guidance on economic justification is given in Appendix G.

Switching Arrangements

7.19 	Guidance on offshore substation configurations and switching arrangements are described in Appendix A. These guidelines provide an acceptable way towards meeting the criteria of paragraphs 7.7 to 7.12. However, other configurations and switching arrangements which meet those criteria are also acceptable.

Variations to Connection Designs

7.20 	Variations, arising from a generation customer’s request, to the generation connection design necessary to meet the requirements of paragraphs 7.6 to 7.18 shall also satisfy the requirements of this Standard provided that the varied design satisfies the conditions set out in paragraphs 7.21.1 to 7.21.3. For example, such a generation connection design variation may be used to take account of the particular characteristics of an offshore power station.

7.21 	Any generation connection design variation must not, other than in respect of the generation customer requesting the variation, either immediately or in the foreseeable future:

7.21.1 	reduce the security of the MITS to below the minimum planning criteria specified in Section 4; or

7.21.2 	result in additional investment or operational costs to any particular customer or overall, or a reduction in the security and quality of supply of the affected customers’ connections to below the planning criteria in this section or Section 8, unless specific agreements are reached with affected customers; or

7.21.3 	compromise any Licensee’s ability to meet other statutory obligations or licence obligations.

7.22 system conditions subsequently change, for example due to the proposed connection of a new customer, such that either immediately or in the foreseeable future, the conditions set out in paragraphs 7.21.1 to 7.21.3 are no longer satisfied, then alternative arrangements and/or agreements must be put in place such that this Standard continues to be satisfied.

7.23 The additional operational costs referred to in paragraph 7.21.2 and/or any potential reliability implications shall be calculated by simulating the expected operation of the national electricity transmission system in accordance with the operational criteria set out in Section 5 and Section 9. Guidance on economic justification is given in Appendix G

.

8	Demand Connection Criteria Applicable to an Offshore Transmission System

8.1	This section presents the planning criteria applicable to the connection of offshore power station demand groups to the remainder of the national electricity transmission system.

8.2	In those parts of an offshore transmission system where the criteria of Section 7 also apply, those criteria must also be met.

8.3	In planning demand connections, this Standard is met if the connection design either:

8.3.1	satisfies the deterministic criteria detailed in paragraphs 8.5 to 8.10; or

8.3.2	varies from the design necessary to meet paragraph 8.3.1 above in a manner which satisfies the conditions detailed in paragraphs 8.12 to 8.15.

8.4	It is permissible to design to standards higher than those set out in paragraphs 8.5 to 8.10 provided the higher standards can be economically justified. Guidance on economic justification is given in Appendix G.

Offshore Power Station Demand Connection Capacity Requirements

8.5	The connection of a particular offshore power station demand group shall meet the criteria set out in paragraphs 8.6 to 8.10 under the following background conditions:

8.5.1	when the power output of the offshore power station is set to zero and there are no planned outages, the demand of the offshore power station demand group shall be set equal to group demand; and

8.5.2	demand and generation outside the offshore power station demand group shall be set in accordance with the planned transfer conditions using the appropriate method described in Appendix C.

8.6	The transmission capacity for the connection of an offshore power station demand group shall be planned such that, for the background conditions described in paragraph 8.5, under intact system conditions there shall not be any of the following:

8.6.1	equipment loadings exceeding the pre-fault rating;

8.6.2	voltages outside the pre-fault planning voltage limits or insufficient voltage performance margins; or

8.6.3 system instability.

8.7	The transmission capacity for the connection of an offshore power station demand group shall also be planned such that for the background conditions described in paragraph 8.5 and for the planned outage of a single transmission  circuit or a single section of busbar or mesh corner, there shall not be any of the following:

8.7.1	a loss of supply capacity for a group demand of greater than 1 MW;

8.7.2	unacceptable overloading of any primary transmission equipment;

8.7.3	voltages outside the pre-fault planning voltage limits or insufficient voltage performance margins; or

8.7.4	system instability.

8.8	The transmission capacity for the connection of an offshore power station demand group shall also be planned such that for the background conditions described in paragraph 8.5 and the initial conditions of

8.8.1	an intact system condition; or

8.8.2	the single planned outage of another transmission circuit or a generating unit (or several generating units, sharing a common circuit breaker, that cannot be separately isolated), a power park module, or a DC converter, a reactive compensator or other reactive power provider,

for the secured event of a fault outage of 8.8.3	a single transmission circuit, or

8.8.4	a single generating unit (or several generating units sharing a common circuit breaker), a single power park module, or a single DC converter

there shall not be any of the following:

8.8.5 	a loss of supply capacity such that the provisions set out in Table 8.1 are not met;

8.8.6	unacceptable overloading of any primary transmission equipment;

8.8.7 	unacceptable voltage conditions or insufficient voltage performance margins; or

8.8.8 system instability.

8.9	In addition to the requirements of paragraphs 8.6 to 8.8, for the background conditions described in paragraph 8.5, the system shall also be planned such that operational switching does not cause unacceptable voltage conditions.

8.10 For a secured event on connections to more than one offshore power station demand group , the permitted loss of supply capacity for that secured event is the maximum of the permitted loss of supply capacities set out in Table 8.1 for each of these offshore power station demand groups.

Table 8.1 Minimum planning supply capacity following secured events

| Group Demand | Initial system conditions |  |
| --- | --- | --- |
|  | Intact system | With single planned outage Note 1 |
| over 1 MW to 12 MW | Within 3 hours Group Demand minus 1 MW In repair time Group Demand | Nil |
| up to 1 MW | In repair time Group Demand | Nil |

Notes

1.		The planned outage may be of a transmission circuit, generating unit, reactive compensator or other reactive power provider.

Switching Arrangements

8.11 Guidance on substation configurations and switching arrangements are described in Appendix A. These guidelines provide an acceptable way towards meeting the criteria of this chapter. However, other configurations and switching arrangements which meet the criteria are also acceptable.

Variations to Connection Designs

8.12 Variations, arising from a generator’s request, to the demand connection design necessary to meet the requirements of paragraphs 8.5 to 8.10 shall also satisfy the requirements of this Standard provided that the varied design satisfies the conditions set out in paragraphs 8.13.1 to 8.13.3. For example, such a demand connection design variation may be used to limit overall costs.

8.13 Any demand connection design variation must not, other than in respect of the generator requesting the variation, either immediately or in the foreseeable future:

8.13.1 reduce the security of the MITS to below the minimum planning criteria specified in Section 4; or

8.13.2 result in additional investment or operational costs to any particular customer or overall, or a reduction in the security and quality of supply of the affected customers’ connections to below the planning criteria in this section or Section 7, unless specific agreements are reached with affected customers; or

8.13.3 compromise any Licensee’s ability to meet other statutory obligations or licence obligations.

8.14	Should system conditions change, for example due to the proposed connection of a new customer, such that either immediately or in the foreseeable future, the conditions set out in paragraphs 8.13.1 to 8.13.3 are no longer satisfied, then alternative arrangements and/or agreements must be put in place such that this Standard continues to be satisfied.

8.15	The additional operational costs referred to in paragraph 8.13.2 and/or any potential reliability implications shall be calculated by simulating the expected operation of the national electricity transmission system in accordance with the operational criteria set out in Section 5 and Section 9. Guidance on economic justification is given in Appendix G.

9. Operation of an Offshore Transmission System

Normal Operational Criteria

9.1	An offshore transmission system shall be operated under prevailing system

conditions so that for the secured event on the offshore transmission system of a fault outage of any of the following:

9.1.1 a single transmission circuit, a reactive compensator or other reactive

power provider; or

9.1.2 a single generation circuit, a single generating unit (or several

generating units sharing a common circuit breaker), a single power park module, or a single DC converter, or

9.1.3 the most onerous loss of power infeed; or 9.1.4 the most onerous loss of power outfeed; or 9.1.5 a section of busbar or mesh corner, or

9.1.6 a double circuit overhead line

9.1.7	there shall not be any of the following:

a loss of supply capacity except as specified in Table 9.1;

9.1.8 unacceptable frequency conditions;

9.1.9 unacceptable overloading of any primary transmission equipment;

9.1.10 unacceptable voltage conditions;

9.1.11 system instability; or

9.1.12 Unacceptable Sub-Synchronous Oscillations.

Table 9.1 Maximum permitted loss of supply capacity following secured events

| Group Demand | Initial system conditions |  |
| --- | --- | --- |
|  | Prevailing system conditions with no local system outage | Prevailing system conditions with a local system outage |
| over 1 MW to 12 MW | Whole group up to Group Demand for up to the operational specified time to restore supply capacity | Whole group up to Group Demand |
| up to 1 MW | Whole group up to Group Demand for up to the operational specified time to restore supply capacity | Whole group up to Group Demand |

Notes

1.	The time to restore any lost supply capacity shall be as short as practicable. If any part of any lost
supply capacity can be restored in less than the specified maximum time to restore all of it, it shall be restored.

Conditional Further Operational Criteria

9.2	The ISOP shall use the latest version of the Frequency Risk and Control Report as consulted on and approved by the Authority to determine the events for which unacceptable frequency conditions shall not occur. The Frequency Risk and Control Report assessment includes consideration of any consequential loss of distributed energy resources associated with any such event.

Post-fault Restoration of System Security

9.3	Following the occurrence of a secured event, measures shall be taken to re-

secure an offshore transmission system to the above operational criteria as soon as reasonably practicable. To this end, it is permissible to put operational measures in place pre-fault to facilitate the speedy restoration of system security.

Authorised Variations from the Operational Criteria

9.4	Exceptions to the criteria in paragraphs 9.1 and 9.3 may be required:

9.4.1	where variations to the connection designs as per paragraphs 7.21 to

7.24 and paragraphs 8.12 to 8.15 have been agreed; or

9.4.2	in relation to 9.1.8 only, based on the outcome of an assessment

conducted in accordance with the Frequency Risk and Control Report.

9.5	The principles of these operational criteria shall be applied at all times except

in special circumstances where ISOP, following consultation with the appropriate Generator, may need to give instructions to the contrary to preserve overall system integrity.

10

10.	Voltage Limits in Planning and Operating an Offshore

10.	Voltage Limits in Planning and Operating an Offshore

Transmission System

Voltage Limits

10.1 The pre-fault planning voltage limits and steady state voltage limits on an offshore transmission system are as shown in Table 10.1.

Table 10.1 Pre-fault planning voltage limits and steady state voltage limits in both
planning and operational timescales

| Nominal voltage | Minimum | Maximum |
| --- | --- | --- |
| 400kV Note 1 | - 10% | + 5% |
| Less than 400kV down to 132kV inclusive | - 10% | + 10% |
| Less than 132kV | - 6% | + 6% |

Notes

1.	For 400kV, the maximum limit is aligned with the equivalent onshore limit pending review in the

light of technological developments.

10.2 A voltage condition on an offshore transmission system is unacceptable in both planning and operational timescales if, after either

10.2.1 a secured event, or 10.2.2 operational switching,

and the affected site remains directly connected to the national electricity transmission system in the steady state after the relevant event above, the following condition applies:

10.2.3 there is any inability following such an event to achieve a steady state voltage as specified in Table 10.1 at offshore transmission system substations or OSPs using manual and/or automatic facilities available, including the switching in or out of relevant equipment.

10.3 In planning timescales, the steady state voltages are to be achieved without widespread post-fault generation transformer re-tapping or post-fault adjustment of SVC set points to increase the reactive power output or to avoid exceeding the available reactive capability of generation or SVCs.

11.	Terms and Definitions

ACS Peak Demand	The estimated unrestricted winter peak demand (MW

and MVar) on the total system for the average cold spell (ACS) condition. This represents the demand to be met by large power stations (directly connected or embedded), medium power stations (directly connected or embedded) and small power stations (directly connected or embedded) and by electricity imported into the onshore transmission system from external systems across external interconnections (and which is not adjusted to take into account demand management or other techniques that could modify demand).

Adverse Conditions	For the purpose of this Standard, those conditions that

significantly increase the likelihood of an overhead line fault, e.g. high winds, lightning, very high or very low ambient temperatures, high precipitation levels, high insulator or atmospheric pollution, flooding.

Ancillary Services	This means:

- such services as any authorised electricity operator may be required to have available as Ancillary Services pursuant to the Grid Code; and

- such services as any authorised electricity operator or person making transfers on external interconnections may have agreed to have available as being ancillary services pursuant to agreement made with the ISOP and which may be offered for purchase by the ISOP.

Annual Load Factor	The ratio of the actual energy output of a generating

unit, CCGT module or power station (as the case may be) to the maximum possible energy output of that generating unit, CCGT module or power station (as the case may be) over a year. It is often expressed in percentage terms.

| Assimilated Law | Has the same meaning as that given by section 6(7) of the European Union (Withdrawal) Act 2018. |
| --- | --- |

Authority	This means the Gas and Electricity Markets Authority

established by section 1(1) of the Utilities Act 2000.

Authority Guidance on

Code Modification Prioritisation	means the guidance published by the Authority from 	time to time on code modification prioritisation.

Average Cold Spell (ACS)	A particular combination of weather elements which

give rise to a level of peak demand within a financial year (1 April to 31 March) which has a 50% chance of being exceeded as a result of weather variation alone.

Balancing Mechanism	This is the mechanism for the making and acceptance

of offers and bids pursuant to the arrangements contained in the Balancing and Settlement Code (BSC)

Balancing Services	This means:

- Ancillary Services;

- Offers and bids in the Balancing Mechanism; and

- Other services available to the ISOP, which serve to assist the ISOP in operating the national electricity transmission system in accordance with the Electricity Act 1989 (Act) and the Conditions of the ESO Licence or in doing so efficiently and economically.

Boundary Allowance	An allowance in MW to be added in whole or in part to

transfers arising out of the Economy planned transfer condition to take some account of year round variations in levels of generation and demand. This allowance is calculated by an empirical method described in Appendix F of this Standard.

Busbar	The common connection point of two or more

transmission circuits.

| Business Day | Any weekday (other than a Saturday) on which banks are open for domestic business in the City of London. |
| --- | --- |
| Chairperson | The Chairperson of the Panel appointed in accordance with Paragraph J.4.3. |
| Competitively Appointed Transmission Owner (CATO) | A person who is a holder of a transmission licence (as defined in Section 6(1)(b) of the Electricity Act 1989) to own and operate an onshore transmission system that has been granted on the basis of competitive tendering undertaken pursuant to Section 6C of the Electricity Act 1989. |
| Core Industry Documents | Shall have the same definition as in Standard Condition A1 of the transmission licence and licence condition A1.4 of the ESO licence. |

Corrective Action	Manual and automatic action taken after an outage or

switching action to assist recovery of satisfactory system conditions; for example, tap changing or switching of plant.

Credible Demand Sensitivities	Such variations in demands above those forecast as

are appropriate to the locations and the forecast error for the number of years ahead for which the forecast has been produced, e.g. that which corresponds to an 80% demand forecast confidence level.

DC Converter	Any apparatus used as part of the national electricity

transmission system to convert alternating current electricity to direct current electricity, or vice-versa. A DC Converter is a standalone operative configuration at a single site comprising one or more converter bridges, together with one or more converter transformers, converter control equipment, essential protective and switching devices and auxiliaries, if any, used for conversion. In a bipolar arrangement, a DC Converter represents the bipolar configuration.

Demand Group	A site or group of sites which collectively take power

from the remainder of the onshore transmission system.

Demand Point of Connection	For the purpose of defining the boundaries between the

MITS and Grid Supply Point transformer circuits, the Demand Point of Connection is taken to be the Busbar clamp in the case of an air insulated substation, gas zone separator in the case of a gas insulated substation, or other equivalent point as may be determined by the relevant Licensees for new types of substation.

Distribution Licensee	Means the holder of a Distribution Licence in respect of

an onshore distribution system granted under Section 6 (1) (c) of the Electricity Act 1989 (as amended under the Utilities Act 2000 and the Energy Act 2004).

Double Circuit Overhead Line	In the case of the onshore transmission system, this is

a transmission line which consists of two circuits sharing the same towers for at least one span in SHET’s transmission system or NGET’s transmission system or for at least 2 miles in SPT’s transmission system.

In the case of an offshore transmission system, this is a transmission line which consists of two circuits sharing the same towers for at least one span.

| Economy Planned Transfer Conditions | The condition arising from scaling the registered capacity of each power station according to the type of generation such that the total of the scaled capacities is equal to the ACS peak demand. This scaling shall follow the techniques described in Appendix E. |
| --- | --- |

| Electricity System Operator (ESO Licence) | A licence granted or treated as granted under section 6(1)(da) of the Electricity Act 1989. |
| --- | --- |

External Interconnection	Apparatus for the transmission of electricity to or from

the onshore transmission system into or out of an external system.

External System	A transmission or distribution system located outside

the national electricity transmission system operator area, which is electrically connected to the onshore transmission system by an external interconnection

Fault Outage	An outage of one or more items of primary transmission

equipment and/or user equipment, which may or may not result in a loss of power infeed or loss of power outfeed, initiated by automatic action unplanned at that time, and which may or may not involve the passage of fault current.

First Onshore Substation	The first onshore substation defines the onshore limit

of an offshore transmission system. An offshore transmission system cannot extend beyond the first onshore substation.

Accordingly, the security criteria relating to an offshore transmission system extend from the offshore GEP up to the interface point or user system interface point (as the case may be), which is located at the first onshore substation.

The security criteria relating to the onshore transmission system extend from the interface point located at the first onshore substation and extend across the remainder of the onshore transmission system.

The security criteria relating to an onshore user system extend from the user system interface point located at the first onshore substation and extend across the remainder of the relevant user system.

The first onshore substation will comprise, inter alia, facilities for the connection between, or isolation of, transmission circuits and/or distribution circuits. These facilities will include at least one busbar to which the offshore transmission system connects and one or more circuit breakers and disconnectors. For the avoidance of doubt, if the substation does not include these elements, then it does not constitute the first onshore substation.

The first onshore substation may be owned by the offshore transmission owner, the onshore transmission owner or onshore user system owner as determined by the relevant Licensee and/or distribution licensee as the case may be.

Normally, in the case of there being transformation facilities at the first onshore substation and unless otherwise agreed, if the offshore transmission owner owns the first onshore substation, the interface point would be on the HV busbars and, if the first onshore substation is owned by the onshore transmission owner or onshore user system owner, the interface point or user system interface point (as the case may be) would be on the LV busbars.

Forecast Minimum Demand	This is the minimum demand level expected at a GSP

or OSP or a group of GSPs or group of OSPs. Unless more specific data are available, this is the expected demand at the time of the annual minimum demand on the national electricity transmission system as provided under the Grid Code. In the case of a group of GSPs or group of OSPs, the demand diversity within the group should be taken into account.

Frequency Risk and Control Report

Frequency Risk and Control Report

The periodic report setting out the results of an assessment of the operational frequency risks on the system produced by the ISOP and approved by the Authority and as set out in the SQSS Appendix H, and prepared in accordance with the Frequency Risk and Control Report Methodology as also prepared and approved as set out in the SQSS Appendix H. The report shall include an assessment of the magnitude, duration and likelihood of transient frequency deviations, forecast impact and the cost of securing the system and confirm which risks will or will not be secured operationally by the ISOP in accordance with paragraphs 5.8, 5.11.2, 9.2 and 9.4.2.

Frequency Risk and

Control Report Methodology

Frequency Risk and

Control Report Methodology

The methodology by which a Frequency Risk Control Report will be developed, consulted on and approved by the Authority, and as set out in the SQSS Appendix H.

Gas System Planner  Licence		A licence granted or treated as granted under section 7AA(1) of the Gas Act 1986.

Generating Plant Type	A type of generating unit classified by the type of prime

move, e.g. thermal hydro.

Generating Units	An onshore generating unit or an offshore generating

unit.

Generation Circuit	The sole electrical connection between one or more

generating units and the Main Interconnected Transmission System i.e. a radial circuit which if removed would disconnect the generating units.

Generation Point of Connection	For the purpose of defining the boundaries between the

MITS and generation circuits, the generation point of connection is taken to be the busbar clamp in the case of an air insulated substation, gas zone separator in the case of a gas insulated substation, or other equivalent point as may be determined by the relevant licensees for new types of substation

Generator	A person who generates electricity under licence or

exemption under the Electricity Act 1989 as amended by the Utilities Act 2000 and the Energy Act 2004 as a generator in Great Britain or Offshore.

| Governance Framework | Means the SQSS Governance Framework as contained in Appendix J. |
| --- | --- |

Great Britain (GB)	The landmass of England and Wales and Scotland,

including internal waters.

Grid Entry Point (GEP)	A point at which a generating unit or a CCGT module

or an offshore power park module, as the case may be, which is directly connected to the national electricity transmission system, connects to the national electricity transmission system. The default point of connection is taken to be the busbar clamp in the case of an air insulated substation, gas zone separator in the case of a gas insulated substation, or equivalent point as may be determined by the relevant licensees for new types of substation.

Grid Supply Point (GSP)	A point of supply from the onshore transmission system

to network operators or non-embedded customers.

Group Demand	For a single GSP or OSP: The forecast maximum

demand for the GSP or OSP provided in accordance with the requirements of the Grid Code by the network operators or non-embedded customers taking demand from the national electricity transmission system. For multiple GSPs or OSPs: The sum of the forecast maximum demands for the GSPs or OSPs as provided by the network operators or non-embedded customers taking demand from the national electricity transmission system.

Information Request Notice	 A notice that will be issued by the ISOP to a relevant party setting out the ISOP’s reasonable requirements for relevant information in accordance with section 172 of the Energy Act 2023. This will be prepared in accordance with the ISOP’s published information request statement.

Information Request Statement    	A statement prepared and published by the ISOP, in accordance with section 172 of the Energy Act 2023 and condition D2.5 of its ESO Licence and Gas System Planner Licence, setting out the process that the ISOP will follow when requesting information from relevant parties by the issue of an information request notice.

Infrequent Infeed Loss Risk	Until 31st March 2014, this is a loss of power infeed risk

of 1320MW. From April 1st 2014, this is a loss of power infeed risk of 1800MW.

| Infrequent Operational Switching | Operational switching associated with rare or infrequent events rather than routine management of the system. Infrequent operational switching includes, for example, isolation of circuits for maintenance and subsequent re-energisation, and operation of intertrip schemes consequent upon secured events. It would not include switching out of circuits for voltage control, or switching out of circuits to allow safe access to other plant, where it is foreseen that such switching may be a regular practice; such events would be classed as operational switching. |
| --- | --- |

Insufficient Voltage Performance	In all timescales and in particular the post-fault periods

Margins	(i.e. before, during and after the automatic controls take

place), there are insufficient voltage performance margins when the following occurs:

Insufficient Voltage Performance	In all timescales and in particular the post-fault periods

Margins	(i.e. before, during and after the automatic controls take

place), there are insufficient voltage performance margins when the following occurs:

voltage collapse;

- over-sensitivity of system voltage; or

- unavoidably exceeds the reactive capability of generating units such that accessible reactive reserves are exhausted;

A.1	under any of the following conditions:

- credible demand sensitivities;

- the unavailability of any single reactive compensator or other reactive power provider; or

- the loss of any one automatic switching system or any automatic voltage control system for on-load tap changing.

Intact System	This is the national electricity transmission system with

no system outages i.e. with no planned outages (e.g. for maintenance) and no unplanned outages (e.g. subsequent to a fault).

Interconnection Allowance	An allowance in MW to be added in whole or in part to

transfers arising out of the Security planned transfer condition to take some account of non-average conditions (e.g. power station availability, weather and demand). This allowance is calculated by an empirical method described in Appendix D of this Standard.

Interface Point (IP)	A point at which an offshore transmission system,

which is directly connected to an onshore transmission system, connects to the onshore transmission system. The Interface Point is located at the first onshore substation which the offshore transmission circuits reach onshore. The default point of connection, within the first onshore substation, is taken to be the busbar clamp in the case of an air insulated substation, gas zone separator in the case of a gas insulated substation, on either the lower voltage (LV) busbars or the higher voltage (HV) busbars as may be determined by the relevant licensees. Normally, and unless otherwise agreed, if the offshore transmission owner owns the first onshore substation, the interface point would be on the HV busbars and, if the first onshore substation is owned by the onshore transmission owner, the interface point would be on the LV busbars.

Independent System Operator

and Planner (ISOP)                        Means a person designated by the Secretary of State under section 162 of the Energy Act 2023 as the holder of the ESO licence, and the Gas System Planner licence, for the time being that person is the NESO.

Large Power Station	A power station which is:

1. directly connected to

- NGET’s transmission system where such power station has a registered capacity of 100MW or more;

- SPT’s transmission system where such power station has a registered capacity of 30MW or more; or

- SHET’s transmission system where such power station has a registered capacity of 10MW or more;

Or

2.	Embedded within a user system (or part thereof)

where such user system (or part thereof) is connected under normal operating conditions to:

- NGET’s transmission system where such power station has a registered capacity of 100MW or more; or

- SPT’s transmission system where such power station has a registered capacity of 30MW or more; or

C.	SHET’s transmission system where such power

station has a registered capacity of 10MW or more.

Or

3. In offshore waters, a power station connected to an offshore transmission system with a registered capacity of 10MW or more.

| Licensee | Means the holder, for the time being, of a Transmission Licence or the ISOP as the holder of the ESO Licence, and in each case being a party that is required by their licence to comply with the Security and Quality of Supply Standard as approved by the Authority, and shall be construed accordingly. |
| --- | --- |

Local System Outage	In the context of a demand group or offshore power

station demand group, a planned outage or unplanned outage local to a demand group or offshore power station demand group, as the case may be, such that it has a direct effect on the supply capacity to that demand group or offshore power station demand group. In the context of planning generation connections, a planned outage local to a power station such that it has a direct effect on the generation connection capacity requirements for that power station

Loss of Power Infeed	The output of a generating unit or a group of generating

units or the import from external systems disconnected from the national electricity transmission system by a secured event, less the demand disconnected from the national electricity transmission system by the same secured event.

For the avoidance of doubt if, following such a secured event, demand associated with the normal operation of the affected generating unit or generating units is automatically transferred to a supply point which is not disconnected from the system, e.g. the station board, then this shall not be deducted from the total loss of power infeed to the system.

For the purpose of the operational criteria:

- the loss of power infeed includes the output of a single generating unit, CCGT Module, boiler, nuclear reactor or import from an external system via a HVDC Link.

- In the case of an offshore generating unit or group of offshore generating units, the loss of power infeed is measured at the interface point, or user system interface point, as appropriate.

- In the case of an offshore generating unit or group of offshore generating units for which infeed will be automatically re-distributed to one or more interface points or user system interface points through one or more interlinks, the re-distribution should be taken into account in determining the total generation capacity that is disconnected. However, in assessing this re-distribution, consequential losses of infeed that might occur in the re-distribution timescales due to wider generation instability or tripping, including losses at distribution voltage levels, should be taken into account.

Loss of Power Outfeed	The load taken by storage units, non-embedded

customers, grid supply points, or the export to external systems disconnected from the national electricity transmission system by a secured event, less the generation disconnected from the national electricity transmission system by the same secured event.

For the avoidance of doubt if, following such a secured event, demand associated with the normal operation of the affected outfeed is automatically transferred to a grid supply point which is not disconnected from the national electricity transmission system, then this shall not be added to the total loss of power outfeed to the system.

For the purpose of the operational criteria:

- the loss of power outfeed includes demand from pump storage, battery storage and other storage, non-embedded customers, and export to external systems via a HVDC Link.

- In the case of an offshore transmission system, the loss of power outfeed is measured at the interface point, or user system interface point, as appropriate.

Loss of Supply Capacity	This is the reduction in the supply capacity at a Grid

Supply Point or offshore supply point as a result of the Licensees’ failure to maintain the potential to provide the supply capacity in full. For the avoidance of doubt, where the Licensees do maintain the potential to provide a supply but, following an outage, demand is lost because of circuit configurations not under the control of the Licensees, that lost supply does not constitute loss of supply capacity.

| Main Interconnected Transmission System (MITS) | This comprises all the 400kV and 275kV elements of the onshore transmission system and, in Scotland, the 132kV elements of the onshore transmission system operated in parallel with the supergrid, and any elements of an offshore transmission system operated in parallel with the supergrid, but excludes generation circuits, transformer connections to lower voltage systems, external interconnections between the onshore transmission system and external systems, and any offshore transmission systems radially connected to the onshore transmission system via single interface points. |
| --- | --- |

Maintenance Period Demand	This is the demand level experienced at a GSP and is

the maximum demand level expected during the normal maintenance period. This level is such that the period in which maintenance could be undertaken is not unduly limited. Unless better data are available this should be 67% of the group demand.

Major System Fault	An event or sequence of events so fast that it is not

practically possible to re-secure the system between each one, more onerous than those included in the normal set of secured events.

Major System Risk	A period of major system risk is one in which secured

events are judged to be significantly more likely than under the circumstances addressed by the normal criteria of this Standard, or they are judged to have a significantly greater impact than normal, or events not normally secured against are judged to be significantly more likely than normal such that measures should be taken to mitigate their impact.

Marshalling Substation	A substation which connects circuits from more than

two line routes.

Medium Power Station	A power station which is:

- directly connected to NGET’s transmission system where such power station has a registered capacity of 50MW or more, but less than 100MW; or

- embedded within an user system (or part thereof) where such user system (or part thereof) is connected under normal operating conditions to NGET’s transmission system where such power station has a registered capacity of 50MW or more but less than 100MW;

The medium power station category does not exist in SPT’s transmission system and SHET’s transmission system.

| Member | A person duly appointed in accordance with Paragraph 4.6 to be a Member of the Panel. |
| --- | --- |

Minister of the Crown	 As defined in the ESO licence.

National Electricity Transmission The national electricity transmission system comprises

System	the onshore transmission system and the offshore

transmission systems.

National Electricity Transmission

System Operator Area 	 Has the meaning set out in Schedule 1 of ESO licence

| NETS SQSS or SQSS | National Electricity Transmission System Security and Quality of Supply Standard. The SQSS sets out a coordinated set of criteria and methodologies that the Licensees shall use in the planning and operation of the National Electricity Transmission System. |
| --- | --- |

NESO	 The company with registered number 11014226 as the designated ISOP and holder of the ESO licence and the Gas System Planner licence.

Network Operator	A person with a system directly connected to the

onshore transmission system to which customers and/or power stations (not forming part of that system) are connected, acting in its capacity as an operator of that system, but shall not include a person who operates an external system.

Network Operator	A person with a system directly connected to the

onshore transmission system to which customers and/or power stations (not forming part of that system) are connected, acting in its capacity as an operator of that system, but shall not include a person who operates an external system.

NGET	National Grid Electricity Transmission plc (No.

2366977) whose registered office is 1-3 Strand, London WC2N 5EH

Non-Embedded Customer	A customer, except for a Network Operator acting in its

capacity as such receiving electricity direct from the national electricity transmission system irrespective of from whom it is supplied.

Normal Infeed Loss Risk	Until 31st March 2014, this is a loss of power infeed risk

of 1000MW. From April 1st 2014, this is a loss of power infeed risk of 1320MW.

Offshore	Means wholly or partly in offshore waters, and when

used in conjunction with another term and not defined means that the associated term is to be read accordingly.

Offshore Generating Unit	Any apparatus, which produces electricity including, a

synchronous offshore generating unit and non-synchronous offshore generating unit and which is located in offshore waters.

| Offshore Grid Entry Point Capacity (OffGEP Capacity) | The cumulative registered capacity of all offshore power stations connected at a single offshore grid entry point and/or the cumulative registered capacity of all offshore power stations connected to all the offshore grid entry points of an offshore transmission system |
| --- | --- |

Offshore Platform	A platform, located in offshore waters, which contains

plant and apparatus associated with the generation and/or transmission of electricity including high voltage electrical circuits which form part of an offshore transmission system and which may include one or more offshore grid entry points

Offshore Power Park Module	A collection of one or more offshore power park strings,

located in offshore waters, registered as an offshore power park module under the provisions of the Grid Code. There is no limit to the number of offshore power park strings within the offshore power park module, so long as they either:

- connect to the same busbar which cannot be electrically split; or

- connect to a collection of directly electrically connected busbars of the same nominal voltage and are configured in accordance with the operating arrangements set out in the relevant Bilateral Agreement.

Offshore Power Park String	A collection of non-synchronous offshore generating

units, located in offshore waters that are powered by an intermittent power source joined together by cables with a single point of connection to an offshore transmission system.

Offshore Power Station	An installation, located in offshore waters, comprising

one or more offshore generating units or offshore power park modules or offshore gas turbines (even where sited separately) owned and/or controlled by the same generator, which may reasonably be considered as being managed as one offshore power station.

| Offshore Power Station Demand Group | An offshore site or group of offshore sites located on an offshore platform/s which collectively take power from the remainder of an offshore transmission system for the purpose of supplying offshore power station demand. |
| --- | --- |

Offshore Supply Point (OSP)	A point of supply from an offshore transmission system

to an offshore power station.

Offshore Transmission Circuit	Part of an offshore transmission system between two

or more circuit-breakers which includes, for example, transformers, reactors, cables, overhead lines and DC converters but excludes busbars and onshore transmission circuits.

Offshore Licensee	Means the holder of a Transmission Licence in respect

of an offshore transmission system granted under Section 6 (1) (b) of the Electricity Act 1989 (as amended by the Utilities Act 2000 and the Energy Act 2004)

| Offshore Transmission Owner (OFTO) | A Licensee in relation to whose Transmission Licence the Standard Conditions in Section E (offshore transmission owner standard conditions) have been given effect. |
| --- | --- |

Offshore Transmission System	A system consisting (wholly or mainly) of high voltage

lines of 132kV or greater owned and/or operated by an offshore Licensee and used for the transmission of electricity to or from an offshore power station to or from an interface point, or user system interface point if embedded, or to or from another offshore power station and includes equipment, plant and apparatus and meters owned or operated by an offshore Licensee in connection with the transmission of electricity. An offshore transmission system extends from the interface point or user system interface point, as the case may be, to the offshore grid entry point/s and may include plant and apparatus located onshore and offshore. For the avoidance of doubt, the offshore transmission systems, together with the onshore transmission system, form the national electricity transmission system.

Offshore Waters	Has the meaning given to “offshore waters” in Section

90(9) of the Energy Act 2004.

Onshore Generating Unit	Any apparatus which produces electricity including a

synchronous generating unit and non-synchronous generating unit but excluding an offshore generating unit.

Onshore Interface Point	An electrical point of connection between the transmission systems of two onshore transmission licencees

Onshore Power Park Module	A collection of non-synchronous generating units

(registered as a power park module under the Planning Code in the Grid Code) that are powered by an intermittent power source, joined together by a system with a single point of electrical connection to the onshore transmission system (or user system if

embedded).	The connection to the onshore
transmission system (or user system if embedded) may include a DC converter.

Onshore Power Station	An installation comprising one or more onshore

generating units or onshore power park module (even where sited separately) owned and/or controlled by the same generator, which may reasonably be considered as being managed as one onshore power station.

Onshore Transmission Circuit	Part of the onshore transmission system between two

or more circuit-breakers which include, for example, transformers, reactors, cables and overhead lines and DC converters, but excludes busbars, generation circuits and offshore transmission circuits.

Onshore Licensee  	NGET, SPT, SHET’s, and any transmission licensee appointed as a competitively appointed transmission owner and such other person who is the holder of a transmission licence in respect of an onshore transmission system granted under Section 6 (1) (b) of the Electricity Act 1989.

Onshore Transmission System	The system consisting (wholly or mainly) of high

voltage electric lines owned or operated by onshore Licensees and used for the transmission of electricity from one power station to a substation or to another power station or between substations or to or from offshore transmission systems or to or from any external interconnections and includes any plant and apparatus and meters owned or operated by onshore Licensees within Great Britain in connection with the transmission of electricity. The onshore transmission system does not include any remote transmission assets. For the avoidance of doubt, the onshore transmission system, together with the offshore transmission systems form the national electricity transmission system.

| Operational Intertripping |  | The automatic tripping of circuit breakers to remove generating units and/or demand. It does not provide additional transmission capacity and must not lead to unacceptable frequency conditions for any secured event. |
| --- | --- | --- |
| Operational Switching | Operation of plant and/or apparatus within the onshore transmission system or offshore transmission system to the instruction of the relevant control engineer. For the avoidance of doubt, operational switching includes manual actions and automatic actions including tap-changing, auto-switching schemes and automatic reactive switching schemes. |  |
| Panel | The SQSS panel established by the ISOP, NGET, SHET and SPT which shall be constituted in accordance with Appendix J. |  |

Planned Outage	An outage of one or more items of primary transmission

apparatus and/or generation plant, initiated by manually instructed action which has been subject to the recognised national electricity transmission system operator area outage planning process.

Planned Transfer Conditions	The condition arising from scaling the registered

capacities of each power station such that the total of the scaled capacities is equal to the ACS peak demand minus imports from external systems. This scaling shall follow the techniques described in Appendix C.

Plant Margin	The amount by which the total installed capacity of

power stations exceeds the net amount of the ACS peak demand minus the total imports from external systems. This is often expressed as a percentage (e.g. 20%) or as a decimal fraction (e.g. 0.2) of the net amount of the ACS peak demand minus the total imports from external systems.

Power Park Module	An onshore power park module and/or an offshore

power park module

Power Station	Means an onshore power station or an offshore power

station.

Pre-Fault Planning Voltage Limits The voltage limits for use in planning timescales for

circumstances before a fault.

Pre-Fault Rating	The specified pre-fault capability of transmission

equipment. Due allowance shall be made for specific conditions (e.g. ambient/seasonal temperature), agreed time-dependent loading cycles of equipment and any additional relevant procedures. In operational timeframes dynamic ratings may also be used where available.

Prevailing System Conditions	These are conditions on the national electricity

transmission system prevailing at any given time and will therefore normally include planned outages and unplanned outages.

Primary Transmission Equipment Any equipment installed on the national electricity transmission system to enable bulk transfer of power. This will include transmission circuits, busbars, and switchgear.

Prioritisation Category	Has the meaning given to that term by the Authority Guidance on Code Modification Prioritisation.

Prioritisation Criteria	Has the meaning given to that term by the Authority Guidance on Code Modification Prioritisation.

Registered Capacity	a) In the case of a generating unit other than that

forming part of a CCGT module or power park module, the normal full load capacity of a generating unit as declared by the generator, less the MW consumed by the generating unit through the generating unit’s unit transformer when producing the same (the resultant figure being expressed in whole MW).

- In the case of a CCGT module or offshore gas turbine or power park module, the normal full load capacity of the CCGT module or offshore gas turbine or power park module (as the case may be) as declared by the generator, being the active power declared by the generator as being deliverable by the CCGT module or offshore gas turbine or power park module at the GEP (or in the case of a CCGT module or offshore gas turbine or power park module embedded in a user system, at the user system entry point), expressed in whole MW.

- In the case of a power station, the maximum amount of active power deliverable by the power station at the GEP (or in the case of a power station embedded in a user system, at the user system entry point), as declared by the generator, expressed in whole MW. The maximum active power deliverable is the maximum amount deliverable simultaneously by the generating units and/or CCGT modules and/or offshore gas turbines and/or power park modules less the MW consumed by the generating units and/or CCGT modules and/or offshore gas turbines and/or power park modules in producing that active power.

- In the case of a DC converter at a DC converter station, supplying active power to the national electricity transmission system, or a user system, from an external system or generating unit(s), the normal full load amount of active power transferable from a DC converter at the GEP (or in the case of an embedded DC converter station at the user system entry point), as declared by the DC converter station owner, expressed in whole MW, or in MW to one decimal place.

- In the case of a DC converter station supplying active power to the national electricity transmission system, or a user system, from an external system or generating unit(s), the maximum amount of active power transferable from a DC converter station at the GEP (or in the case of an embedded DC converter station at the user system entry point), as declared by the DC converter station owner, expressed in whole MW, or in MW to one decimal place.

Restoration Contractor 	As defined in the Grid Code.

Restoration Plan	A plan produced, agreed and signed by the ISOP, network operators, restoration contractors and Licensees to restart the system in the event of a total or partial shutdown.

| Secretary | The secretary of the Panel appointed in accordance with Appendix J. |
| --- | --- |

Secured Event	A contingency which would be considered for the

purposes of assessing system security and which must not result in the remaining national electricity transmission system being in breach of the security criteria. Secured events are individually specified throughout the text of this Standard. It is recognised that more onerous unsecured events may occur and additional operational measures within the requirements of the Grid Code may be utilised to maintain overall national electricity transmission system integrity.

| Security Planned Transfer Conditions | The condition arising from scaling the registered capacity of each power station that is considered able to reliably contribute to peak demand security such that the total of the scaled capacities is equal to the ACS peak demand. Generation powered by intermittent sources (e.g. wind, wave, solar) and imports from external systems are not included in this condition. This scaling shall follow the techniques described in Appendix C. |
| --- | --- |

SHET	Scottish Hydro-Electric Transmission plc (No. SC213461) whose registered office is situated at Inveralmond HS, 200 Dunkeld Road, Perth, Perthshire PH1 3AQ.

Small Power Station	A power station which is:

Small Power Station	A power station which is:

1. directly connected to:

- NGET’s transmission system where such power station has a registered capacity of less than 50MW; or

- SPT’s transmission system where such power station has a registered capacity of less than 30MW;

- SHET’s transmission system where such power station has a registered capacity of less than 10 MW;

Or

2. embedded within a user system (or part thereof) where such user system (or part thereof) is connected under normal operating conditions to:

- NGET’s transmission system where such power station has a registered capacity of less than 50MW;

- SPT’s transmission system where such power station has a registered capacity of less than 30MW;

- SHET’s transmission system where such power station has a registered capacity of less than 10MW;

Or

3. In offshore waters, a power station connected to an offshore transmission system with a registered capacity of less than 10MW.

SPT	SP Transmission Limited (No. SC189126) whose

registered office is situated at 1 Atlantic Quay, Robertson Street, Glasgow G2 8SP.

Steady State	A condition of a power system in which all automatic

and manual corrective actions have taken place and all of the operating quantities that characterise it can be considered constant for the purpose of analysis.

Sub-Synchronous Oscillations	Power system oscillations at frequencies that are less

than the power frequency. They arise from modes of oscillation associated with interactions between certain elements on the system such as generator rotor circuits, generator shaft systems, series compensated lines, excitation system controllers, power system stabilisers, converter controllers of power park modules and converter controllers of DC interconnectors and links.

Supergrid	That part of the national electricity transmission system

operated at a nominal voltage of above 200kV.

System Instability	A.1	i) poor damping - where electromechanical

System Instability	A.1	i) poor damping - where electromechanical

oscillations of generating units are such that the resultant peak deviations in machine rotor angle and/or speed at the end of a 20 second period remain in excess of 15% of the peak deviations at the outset (i.e. the time constant of the slowest mode of oscillation exceeds 12 seconds); or

A.1	ii) pole slipping - where one or more

transmission connected synchronous generating units lose synchronism with the remainder of the system to which it is connected

For the purpose of assessing the existence of system instability, a fault outage is taken to include a solid three phase to earth fault (or faults) anywhere on the national electricity transmission system with an appropriate clearance time.

The appropriate clearance time is identified as follows:

- In NGET’s transmission system and on other circuits identified by agreement between the relevant licensees, clearance times consistent with the fault location together with the worst single failure in the main protection system should be used;

- elsewhere, clearance times should be consistent with the fault location and appropriate to the actual protection, signalling equipment, trip and interposing relays, and circuit breakers involved in clearing the fault.

Transfer Capacity	That circuit capacity from adjacent demand groups

which can be made available within the times stated in Table 3.1

Transient Time Phase	The time within which fault clearance or initial system

switching, the transient decay and recovery, auto switching schemes, generator inter-tripping, and fast, automatic responses of controls such as generator AVR and SVC take place. Load response may be assumed to have taken place. Typically 0 to 5 seconds after an initiating event.

Transmission Area	Has the meaning set out in the Transmission Licence of a transmission licensee.

Transmission Capacity	The ability of a network to transmit electricity. It does

not include the use of operational intertripping except in respect of paragraph 2.13 in Section 2, paragraph 4.10 in Section 4 and paragraphs 7.7 to 7.13 & 7.16 in Section 7.

Transmission Circuit	This is either an onshore transmission circuit or an

offshore transmission circuit.

Transmission Licence	Means a transmission licence granted or treated as

granted under Section 6(1)(b) of the Electricity Act 1989.

Transmission System		        Has the same meaning as the term “licensee’s

transmission system” in the Transmission licence of a licensee and in the ESO licence .

Where references are made in this document to NGET’s, SPT’s, or SHET’s transmission system, such reference shall be deemed to include:

⦁ a CATO’s transmission system where that CATO’s transmission system has onshore interface point(s) with only one of NGET’s, SPT’s, or SHET’s transmission systems; or

⦁ elements of a CATO’s transmission system located within NGET’s, SPT’s, or SHET’s transmission area where the CATO’s transmission system has onshore interface point(s) with more than one of NGET’s, SPT’s and/or SHETL’s transmission systems.

Unacceptable Frequency Conditions

Unacceptable Frequency Conditions

These are conditions where:

- the steady state frequency falls outside the statutory limits of 49.5Hz to 50.5Hz; or

- a transient frequency deviation on the MITS does not meet the criteria below.

Transient frequency deviations outside the limits of 49.5Hz and 50.5Hz shall:

- only occur at intervals which ought to reasonably be considered as infrequent.

-	only persist for a duration which ought to

reasonably be considered as tolerable; and

-	only deviate by a magnitude which ought to

reasonably be considered as tolerable.

The Frequency Risk and Control Report will define what is considered reasonable, infrequent and tolerable for each of these criteria for transient frequency deviations.

It is not possible to be prescriptive with regard to the type of secured event which could lead to transient frequency deviations since this will depend on the extant frequency response characteristics of the system which the ISOP adjust from time to time to meet the security and quality requirements of this Standard.

Unacceptable Overloading

Unacceptable Overloading

The overloading of any primary transmission equipment beyond its specified time-related capability. Due allowance shall be made for specific conditions (e.g. ambient/seasonal temperature), pre-fault loading, agreed time-dependent loading cycles of equipment and any additional relevant procedures. In operational timeframes dynamic ratings may also be used where

Unacceptable Sub-Synchronous Oscillations

Unacceptable Sub-Synchronous Oscillations

available.

Unacceptable Sub-Synchronous Oscillations are Sub-Synchronous Oscillations with the relevant modes of oscillation having negative or insufficient net damping. Unacceptable Sub-Synchronous Oscillations may have a significant effect on generating units including a significant reduction in the lifetime of the machine shaft system due to fatigue or the failure of some of its electrical components due to high voltages and / or currents.

Unacceptable Voltage Conditions  Voltages out with those specified in Section 6, Voltage Limits in Planning and Operating the Onshore Transmission System and/or outside the limits specified in Section 10, Voltage Limits in Planning and Operating an Offshore Transmission System, as applicable.

Unacceptably High Voltage	Steady state voltages above the maximum values

specified in Section 6, Voltage Limits In Planning and Operating the Onshore Transmission System and/or above the maximum values specified in Section 10, Voltage Limits In Planning and Operating an Offshore Transmission System, as applicable.

Unplanned Outage	An outage of one or more items of primary transmission

apparatus and/or generation plant, initiated by manually instructed action which has not been subject to the recognised national electricity transmission system operator area outage planning process.

User System	Any system owned or operated by a user of the national

electricity transmission system other than a Licensee comprising:

- generating units; and/or

- systems consisting wholly or mainly of electric circuits used for the distribution of electricity from grid supply points or offshore supply points or generating units or other entry points to the point of delivery to customers or other users.

and plant and/or apparatus connecting:

- the system described above; or

- non-embedded customers’ equipment;

to the national electricity transmission system or to the relevant other user system, as the case may be.

The user system includes any remote transmission assets operated by such user or other person and any plant and/or apparatus and meters owned or operated by the user or other person in connection with the distribution of electricity but do not include any part of the national electricity transmission system.

| National Electricity Transmission System Security and Quality of Supply Standard, Version 2.5, 01 April 2021 76 National Electricity Transmission System Security and Quality of Supply Standard, Version 2.5, 01 April 2021 76 User System Interface Point (USIP) | A point at which an offshore transmission system, which is directly connected to a user system, connects to the user system. The user system interface point is located at the first onshore substation which the offshore transmission circuits reach onshore. The default point of connection, within the first onshore substation, is taken to be the busbar clamp in the case of an air insulated substation, gas zone separator in the case of a gas insulated substation, or equivalent point on either the lower voltage (LV) busbars or the higher voltage (HV) busbars as may be determined by the relevant Licensee and distribution licensee. Normally, and unless otherwise agreed, if the offshore transmission owner owns the first onshore substation, the user system interface point would be on the HV busbars and if the first onshore substation is owned by the onshore distribution owner, the user system interface point would be on the LV busbars. |
| --- | --- |

Voltage Collapse	Where progressive, fast or slow voltage decrease or

increase develops such that it can lead to either tripping of generating units and/or loss of demand.

Voltage Step Change	The difference in voltage between that immediately

before a secured event or operational switching and that at the end of the transient time phase after the event.

Appendix A

Recommended Substation Configuration and Switching Arrangements

Part 1 – Onshore Transmission System

A.1	The recommendations set out in paragraphs A.2 to A.6 apply to the onshore

transmission system

A.2	The key factors which must be considered when planning the onshore

transmission system substation include:

A.2.1 Security and Quality of Supply - Relevant criteria are presented in Sections 2, 3 and 4.

A.2.2 Extendibility - The design should allow for the forecast need for future extensions.

A.2.3 Maintainability - The design must take account of the practicalities of maintaining the substation and associated circuits.

A.2.4 Operational Flexibility - The physical layout of individual circuits and groups of circuits must permit the required power flow control.

A.2.5 Protection Arrangements - The design must allow for adequate protection of each system element.

A.2.6 Short Circuit Limitations - In order to contain short circuit currents to acceptable levels, busbar arrangements with sectioning facilities may be required to allow the system to be split or re-connected through a fault current limiting reactor.

A.2.7 Land Area - The low availability and/or high cost of land particularly in densely populated areas may place a restriction on the size and consequent layout of the substation.

A.2.8 Cost

A.3	Accordingly the design of a substation is a function of prevailing circumstances

and future requirements as perceived in the planning time phase. This appendix is intended as a functional guidance for substation layout design and switchgear arrangements. Variations away from this guidance are permissible provided that such variations comply with the requirements of the criteria set out in the main text of this Standard.

Generation Point of Connection Substations

A.4	In accordance with the planning criteria for generation connection set out in

Section 2, generation point of connection substations should:

A.4.1 have a double busbar design (i.e. with main and reserve busbars such that generation circuits and onshore transmission circuits may be selected to either);

A.4.2 have sufficient busbar sections to permit the requirements of paragraph 2.6 to be met without splitting the substation during maintenance of busbar sections;

A.4.3 have sufficient busbar coupler and/or busbar section circuit breakers so that each section of the main and reserve busbar may be energised using either a busbar coupler or busbar section circuit breaker;

A.4.4 have generation circuits and onshore transmission circuits disposed between busbar sections such that the main busbar may be operated split for fault level control purposes; and

A.4.5 have sufficient facilities to permit the transfer of generation circuits and onshore transmission circuits from one section of the main busbar to another.

Marshalling Substations

A.5	Marshalling substations should:

A.5.1 have a double busbar design (i.e. with main and reserve busbars such that onshore transmission circuits may be selected to either);

A.5.2 have sufficient busbar sections to permit the requirements of paragraphs 2.6, 4.6 and 4.9 to be met;

A.5.3 have onshore transmission circuits disposed between busbar sections such that the main busbar may be operated split for fault level control purposes; and

A.5.4 have sufficient facilities to permit the transfer of onshore transmission circuits from one section of busbar to another.

Grid Supply Point Substations

A.6	In accordance with the planning criteria for demand connection set out in

Section 3, GSP substations configurations range from a single transformer teed into an onshore transmission circuit to a four switched mesh substation or a double busbar substation. The choice and need for the extendibility will depend on the circumstances as perceived in the planning time phase.

Part 2 – Offshore Transmission Systems

A.7 The recommendations set out in paragraphs A.7 to A.15 apply to offshore transmission systems

A.8	The key factors which must be considered when planning an offshore

transmission system substation include:

A.8.1 Security and Quality of Supply - Relevant criteria are presented in Sections 7 and 8.

A.8.2 Maintainability - The design must take account of the practicalities of maintaining the substation and associated circuits.

A.8.3 Operational Flexibility - The physical layout of individual circuits and groups of circuits must permit the required power flow control.

A.8.4 Protection Arrangements - The design must allow for adequate protection of each system element.

A.8.5 Short Circuit Limitations - In order to contain short circuit currents to acceptable levels, busbar arrangements with sectioning facilities may be required to allow the system to be split or re-connected through a fault current limiting reactor.

A.8.6 Available Area –The high cost of the offshore platform may place a restriction on the size and consequent layout of the substation.

A.8.7 Cost.

A.9	Accordingly the design of a substation is a function of prevailing circumstances

and future requirements as perceived in the planning time phase. This appendix is intended as a functional guidance for substation layout design and switchgear arrangements. Variations away from this guidance are permissible provided that such variations comply with the requirements of the criteria set out in the main text of this Standard.

Offshore Transmission System Substations Offshore GEP Substations (on an Offshore Platform)

A.10 In accordance with the planning criteria for offshore generation connection set out in Section 7, the substation should:

A.10.1 have sufficient busbar sections to permit the requirements of paragraph 7.8 to be met without splitting the substation during maintenance of busbar sections; and

A.10.2 have sufficient busbar coupler and/or busbar section circuit breakers so that each busbar section may be energised using either a busbar coupler or busbar section circuit breaker.

IP and USIP Substations

A.11 The following recommendations apply equally to substations at the:

A.11.1 	In the case of an offshore transmission system at the Onshore Interface Point (at the First Onshore Substation); and

A.11.2 	Onshore User System Interface Point (at the First Onshore Substation)

A.12 In accordance with the planning criteria for offshore generation connection set out in Section 7, the substation should in the case of an offshore power park module and multiple gas turbine connections:

A.12.1 have a double busbar design (i.e. with main and reserve busbars such that offshore generation circuits owned by the generator and offshore transmission circuits may be selected to either);

A.12.2 have sufficient busbar sections to permit the requirements of paragraph 7.13 to be met without splitting the substation during maintenance of busbar sections;

A.12.3 have sufficient busbar coupler and/or busbar section circuit breakers so that each section of the main and reserve busbar may be energised using either a busbar coupler or busbar section circuit breaker; and

A.12.4 have sufficient facilities to permit the transfer of offshore generation circuits owned by the generator and offshore transmission circuits from one section of the main busbar to another.

A.13 In the case of a single gas turbine connection and in accordance with the planning criteria for offshore generation connection set out in Section 7, the substation should have a single busbar design;

Marshalling Substations

A.14 The following recommendations apply to offshore marshalling substations, which interconnect offshore transmission circuits from two or more offshore platforms, where offshore grid entry points are located, and the first onshore substation, where the interface point or user system interface point is located.

A.15 Marshalling Substations should:

A.15.1 have a double busbar design (i.e. with main and reserve busbars such that offshore transmission circuits may be selected to either);

A.15.2 have sufficient busbar sections to permit the requirements of Section 7 to be met;

A.15.3 have transmission circuits disposed between busbar sections such that the main busbar may be operated split for fault level control purposes; and

A.15.4 have sufficient facilities to permit the transfer of offshore transmission circuits from one section of busbar to another.

Offshore Supply Point Substations

A.16 Offshore supply point substations should be designed to meet the requirements of Section 8. The actual design will depend on the circumstances as perceived in the planning time phase.

Appendix B	Circuit Complexity on the Onshore Transmission

Appendix B	Circuit Complexity on the Onshore Transmission

System

B.1	This appendix defines restrictions to be applied by the relevant onshore

Licensee when onshore transmission circuits are designed, constructed or extended. These restrictions are intended to ensure that the time required to isolate and earth circuits in preparation for maintenance work is kept to a minimum and is not disproportionate to the time required to carry out maintenance work. The restrictions also limit the potential for human error.

B.2	This appendix is divided into two parts. The first defines those restrictions that

apply to transmission circuits on the supergrid part of the MITS. The second gives guidance on those restrictions that may be applied to transmission circuits on that part of the MITS operated at a nominal voltage of 132kV.

Restrictions for Transmission Circuits on the Supergrid

B.3	The three restrictions to be applied to transmission circuits on the supergrid

part of the MITS are as follows.

B.3.1 The facilities, for the isolation and earthing of transmission circuits and Transmission Equipment, shall not be located at more than three individual sites;

B.3.2 The normal operational procedure, for the isolation and earthing of transmission circuits and Transmission Equipment, shall not require the operation of more than five circuit-breakers; and

B.3.3 No more than three transformers shall be connected together and controlled by the same circuit breaker.

B.4	A site, in this context, is defined as being where the points of isolation at one

end of a transmission circuit are within the same substation such that only one authorised person is required, at the site, to enable the efficient and effective release and restoration of the circuit.

B.5	If the design of a substation is such that two circuit-breakers of the same voltage

are used to control a circuit (e.g. in a mesh type of substation), for the purposes of the above restrictions the two circuit-breakers are to be considered as a single circuit breaker. This also applies where duplicate circuit-breakers control a circuit including those used for busbar selection.

B.6	Switch disconnectors that are not rated for fault breaking duty should not be

included in the design of new transmission circuits and substations for the purpose of reducing complexity. Where the extension of an existing transmission circuit includes an existing switch disconnector and that switch disconnector is not rated for fault

breaking duty, that switch disconnector can be considered for use in planned switching procedures only.

B.7	For the purposes of restriction in B.3.3 a transformer which includes two low

voltage windings in its construction shall be considered as single transformer.

Guidance for Transmission Circuits Operated at a Nominal Voltage of 132kV

B.8	The restrictions recommended below should be regarded as being in general

the limits of good planning. The majority of 132 kV circuits do not reach this limit nor will they be expected to do so.

B.9	Any proposals which would result in these limits being exceeded should be

fully explained and agreed with operational engineers.

B.10 Care must be observed in the application of these recommendations to “Active Circuits” to ensure that protective gear clearance times and discrimination are satisfactory and that the security of lower voltage connected generation is not unduly prejudiced.

Restriction A

B.11 The normal operating procedure or protective gear operation for making dead any 132 kV circuit shall not require the opening of more than seven circuit-breakers. These circuit-breakers shall not be located on more than four different sites.

B.11.1 The circuit-breakers to be counted include all those which connect the circuit to other parts of the system.

B.11.2 In a mesh or similar type substation, two circuit-breakers of the same voltage in the mesh controlling a circuit count as one circuit-breaker.

B.11.3 Where a circuit is controlled by two circuit-breakers which select between main and reserve busbars, these count as one circuit-breaker.

B.11.4 Switching isolators are not regarded as circuit-breakers for the purpose of this restriction.

Restriction B

B.12 Not more than three transformers shall be banked together on any one circuit at any one site.

B.12.1 A transformer with two lower voltage windings counts as one transformer.

Restriction C

B.13 No item of equipment shall have isolating facilities on more than four different sites.

B.13.1 Isolating facilities will normally be provided by means of circuit-breakers and their associated isolators.

B.13.2 Points of isolation on a circuit within an agreed reasonable walking distance to permit the efficient and effective use of one authorized person only at those points during the release and restoration of the circuit shall be regarded as being on one site.

B.13.3 Switching isolators having a “fault make, load break” capability shall be regarded as circuit-breakers for the purpose of this restriction.

B.13.4 In special circumstances a plain-break normally-open isolator may be counted as an isolating facility for the equipment on either side of it. An example of this is an isolator in the route of a circuit bridging two supergrid zones which would be closed only for emergencies of greater severity than those covered by the security standards for 132 kV planning.

Appendix C	Modelling of Security Planned Transfer

C.1	There are two techniques relevant to the determination of Security planned

transfer conditions. For circumstances in which apparent future plant margins exceed 20%, the ‘Ranking Order technique’ should be applied. Where the apparent future plant margin is 20% or less, the ‘Straight Scaling Technique’ should be applied. These techniques are described below.

C.2	Imports from external systems (e.g. in France or Ireland) shall not be scaled

under either of these two scaling techniques because they result from tranches of generation rather than single power stations.

Availability Factors

C.3	In derivation of Security planned transfer conditions, the registered capacities

of power stations are scaled by availability factors, known as AT, for classes T of power station. For the Security planned transfer condition, these factors are set as follows:

C.3.1 For stations powered by wind, wave, or tides, AT = 0. This zero factor is set for the Security planned transfer condition so that there is confidence that there is sufficient transmission capacity to meet demand securely in the absence of this class of generation.

C.3.2 For imports or exports from / to external systems, AT = 0.

A.1	C.3.3 For all other power stations, AT = 1.0
Ranking Order Technique

C.4	In some circumstances apparent future plant margins may exceed 20%. This

may arise where the ISOP has been notified of increases in future generation capacity but has not yet been formally notified of future reductions in generation capacity due to plant closures. The ranking order technique maintains the output of power stations considered more likely to operate at times of ACS peak demand at more realistic levels and treats those less likely to operate as non-contributory.

C.5	This is achieved by ranking all directly connected power stations, embedded

large power stations, and groups of embedded medium power stations and embedded small power stations aggregated based on their generation technology and their location in order of likelihood of operation at times of ACS peak demand. Those power stations considered least likely to operate at peak are progressively removed and treated as non-contributory until a plant margin of 20% or just below is achieved. The output of the remainder is then calculated using the same scaling method as used in the straight scaling technique described in paragraphs C.5 and C.6 below.

Straight Scaling Technique

C.6	In this technique, all power stations at the time of the ACS peak demand are considered contributory and their output is calculated by applying a scaling factor to their registered capacity proportional to an availability representative of the generating plant type at the time of ACS peak demand such that their aggregate output is equal to the forecast ACS peak demand minus total imports from external systems.

- C.7	Thus,

Where

and

|  | = | the output of the ith power station of generating plant type T |
| --- | --- | --- |
|  | = | an availability representative of generating plant type T at the time of ACS peak demand |
|  | = | the registered capacity of the ith power station of generating plant type T |
|  | = | total national electricity transmission system active power losses at time of ACS peak demand |
|  | = | the active power demand at the jth national electricity transmission system demand site at the time of ACS peak demand |

Appendix D	Application of the Interconnection Allowance

Appendix D	Application of the Interconnection Allowance

D.1 This appendix outlines the techniques underlying the use of the interconnection allowance under paragraphs 4.4.2 and 4.4.5.

D.2	The modification of the MITS Security planned transfer condition power flow

pattern to reflect an interconnection allowance shall apply to the national electricity transmission system divided into any two contiguous parts provided that

D.2.1 the smaller part contains more than 1500MW of demand at the time of the ACS peak demand; and

D.2.2 the boundary between the two parts lies on the boundary between SHET’s transmission system and SPT’s transmission system, or between SPT’s transmission system and NGET’s transmission system, or entirely within NGET’s transmission system.

D.3	The interconnection allowance is then applied by:-

D.3.1 summing the demand and the total active power generation output (including imports from external systems) under the Security planned transfer condition within the smaller of the two parts and expressing this sum as a percentage of twice the ACS peak demand;

D.3.2 using Figure D.1, traditionally known as the ‘Circle Diagram’, to determine the interconnection allowance (in MW) by taking the appropriate percentage of the ACS peak demand;

D.3.3 finding the total active power generation output and total demand in each part of the system when applying the interconnection allowance or half interconnection allowance (as appropriate) as described in paragraphs D.4 and D.5;

D.3.4 for the conditions described under paragraph 4.4.2, proportionally scaling all the generation and demand in both parts of the system, as described in paragraphs D.4 and D.5 below, such that the transfer between the two parts increases by: first, the full interconnection allowance when considering the single fault outages in 4.6.1; and second, half the interconnection allowance for all other secured events in paragraph 4.6;

D.3.5 for the conditions described under paragraph 4.4.5, proportionally scaling demand in both parts of the system and setting generating units with their outputs such that their totals are as described in paragraphs D.4 and D.5 below such that the transfer between the two parts increases by: first, the full interconnection allowance when considering the single fault outages in item 4.6.1; and second, half the interconnection allowance for all other secured events in paragraph 4.6.

D.4	Suppose that the two contiguous parts of the system in question are areas 1

and 2 and that area 1 exports to area 2. Let G1 and G2 be the total generation in areas 1 and 2 respectively and D1 and D2 be the total demand in areas 1 and 2 under the Security planned transfer condition. Let I be the transfer required in addition to that under the Security planned transfer condition (i.e. the value of I is equal to the interconnection allowance or half the interconnection allowance as specified in paragraphs D.3.4 and D.3.5).

D.5	The additional transfer is proportionally divided between the generation and

D.5	The additional transfer is proportionally divided between the generation and

demand in the two areas as follows:

the total demands after application of the interconnection allowance or half interconnection allowance in areas 1 and 2 are

and the total amounts of generation in areas 1 and 2 are

| where | kd |  | = | 1 |  |  | I |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 |  |  |  | D1 | +G1 I |
|  | kg |  | = | 1+ |  |  |  |
| and |  | 1 |  |  |  | D1 | +G1 |

| kd |  | = | 1+ |  | I |
| --- | --- | --- | --- | --- | --- |
|  | 2 |  |  | D2 | +G2 I |
| kg |  | = | 1 |  |  |
|  | 2 |  |  | D2 | +G2 |

3.5

3.5

2.5

2.5

0.5

0.5

1.5

1.5

4

4

3

3

2

2

0

0

1

1

Notes

- 'Demand' shall comprise all components of

Notes

- 'Demand' shall comprise all components of

ACS peak demand

- 'Generation' shall comprise

(a) the output from large power stations, medium power stations, and small power stations whether these are embedded or directly connected to the national electricity transmission system

b)imports into the national electricity transmissionsystem from external systems

ACS peak demand

- 'Generation' shall comprise

(a) the output from large power stations, medium power stations, and small power stations whether these are embedded or directly connected to the national electricity transmission system

b)imports into the national electricity transmissionsystem from external systems

Interconnection allowance as a percentage of total ACS peak demand

Interconnection allowance as a percentage of total ACS peak demand

0 2.5 5 7.5 10 12.5 15 17.5 20 22.5 25 27.5 30 32.5 35 37.5 40 42.5 45 47.5 50

Sum of demand and generation in the smaller area as a percentage of
twice the total ACS peak demand

Figure D.1 Interconnection allowance as a function of area size (the ‘circle diagram’)

Appendix E	Modelling of Economy Planned Transfer

E.1	For the determination of economy planned transfer conditions plant is

categorised in three groups:

E.1.1 non-contributory generation. This plant, such as OCGTs, does not form part of the generation background

E.1.2 directly scaled plant. The output of plant in this category is determined by a fixed scaling factor, described in E.3

E.1.3 variably scaled plant. The output of plant in this category is uniformly scaled by a variable factor that is calculated to ensure that generation and demand balance. This is described in E.5.

E.2 The ISOP will from time-to-time review, consult on, and publish the categorisation of plant.

Directly Scaled Plant

E.3	In the Economy planned transfer condition the registered capacities of certain

classes of power station are scaled by fixed factors, known as DT, for classes T of power station. These factors are set as follows:

E.3.1 For nuclear stations, and for coal-fired and gas-fired stations fitted with Carbon Capture and Storage, DT = 0.85

E.3.2 For stations powered by wind, wave, or tides, DT = 0.70. E.3.3 For pumped storage based stations, DT = 0.5

E.3.4 For interconnectors to external systems regarded as importing into GB at the time of peak demand, DT = 1.0

E.4	The ISOP will review the appropriateness of these factors and revise them where necessary, based on alignment with cost benefit analysis. The period between reviews shall be no more than five years, but may be less if required.

Variably Scaled Plant

E.5	All remaining power stations and on the system at the time of the ACS peak

demand are considered contributory and their output is calculated by applying a scaling factor to their registered capacity such that their aggregate output is equal to the forecast ACS peak demand minus the total output of directly scaled plant.

E.6 Thus,

where

and

|  | = | the output of the ith power station of generation plant type T |
| --- | --- | --- |
|  | = | the direct scaling factor for directly scaled generation of plant type T |
|  | = | the registered capacity of the kth power station of generation plant type DT in the directly scaled category |
|  | = | the registered capacity of the nth power station of generation plant type VT in the variably scaled category |
|  | = | total national electricity transmission system active power losses at time of ACS peak demand |
|  | = | the active power demand at the jth national electricity transmission system demand site at the time of ACS peak demand |

Appendix F	Application of the Boundary Allowance

F.1	This appendix outlines the techniques underlying the use of the boundary

allowance under paragraphs 4.4.4 and 4.4.5.

F.2	The modification of the MITS Economy planned transfer condition power flow

pattern to reflect a boundary allowance shall apply to the national electricity transmission system divided into any two contiguous parts, irrespective of the size or location of the parts.

F.3	The boundary allowance is applied by:-

F.3.1 summing the demand and the total active power generation output (including imports from external systems) under the Economy planned transfer condition within the smaller of the two parts;

F.3.2 using Figure F.1 to determine the boundary allowance (in MW)

F.3.3 finding the total active power generation output and total demand in each part of the system when applying the boundary allowance or half boundary allowance (as appropriate) as described in paragraphs F.4 and F.5;

F.3.4 for the conditions described under paragraph 4.4.4, proportionally scaling all the generation and demand in both parts of the system, as described in paragraphs F.4 and F.5 below, such that the transfer between the two parts increases by: first, the full boundary allowance when considering the single fault outages in 4.6.1; and second, half the boundary allowance for all other secured events in paragraph 4.6;

F.3.5 for the conditions described under paragraph 4.4.5, proportionally scaling demand in both parts of the system and setting generating units with their outputs such that their totals are as described in paragraphs

F.4 and F.5 below such that the transfer between the two parts increases by: first, the full boundary allowance when considering the single fault outages in item 4.6.1; and second, half the boundary allowance for all other secured events in paragraph 4.6.

F.4	Suppose that the two contiguous parts of the system in question are areas 1

and 2 and that area 1 exports to area 2. Let G1 and G2 be the total generation in areas 1 and 2 respectively and D1 and D2 be the total demand in areas 1 and 2 under the planned transfer condition. Let B be the transfer required in addition to that under the planned transfer condition (i.e. the value of B is equal to the boundary allowance or half the boundary allowance as specified in paragraphs F.3.4 and F.3.5).

F.5	The additional transfer is proportionally divided between the generation and

demand in the two areas as follows:

the total demands after application of the boundary allowance or half boundary allowance in areas 1 and 2 are

and the total amounts of generation in areas 1 and 2 are

Where

and

Figure F.1 Boundary allowance

Appendix G	Guidance on Economic Justification

G.1	These guidelines may be used to assist in the:

G.1.1 economic justification of investment in transmission equipment and/or purchase of services such as reactive power in addition to that required

to meet the planning criteria of Sections 2, 3, 4, 7 or 8.

G.1.2 economic justification of the rearrangement of typical planned outage patterns and appropriate re-selection of generating units, for example through balancing services, from those expected to be available under the provisions of paragraph 2.13 in Section 2, paragraph 4.10 in Section 4 and 7.19 in Section 7; and

G.1.3 evaluation of any expected additional operational costs or investments resulting from a proposed variation in connection design under the provisions of paragraphs 2.15 to 2.18 and/or paragraphs 3.12 to 3.15 and/or paragraphs 7.21 to 7.24.

G.2 Guidelines:

G.2.1 additional investment in transmission equipment and/or the purchase of services would normally be justified if the net present value of the additional investment and/or service cost is less than the net present value of the expected operational or unreliability cost that would otherwise arise.

G2.2 the assessment of expected operational costs and the potential reliability implications shall normally require simulation of the expected operation of the national electricity transmission system in accordance with the operational criteria set out in Section 5 and Section 9 of the Standard.

G.2.3 due regard should be given to the expected duration of an appropriate range of prevailing conditions and the relevant secured events under those conditions as defined in section 5 and Section 9.

G.2.4 the operational costs to be considered shall normally include those arising from:

- transmission power losses;

- frequency response;

- reserve;

- reactive power requirements; and

- system constraints,

and may also include costs arising from:

- rearrangement of transmission maintenance times; or

-	modified or additional contracts for other services.

G.2.5 all costs should take account of future uncertainties

G.2.6 the evaluation of unreliability costs expected from operation of the national electricity transmission system shall normally take account of the number and type of customers affected by supply interruptions and

use appropriate information available to facilitate a reasonable assessment of the economic consequences of such interruptions.

Appendix H	Frequency Risk and Control Report Methodology

Appendix H	Frequency Risk and Control Report Methodology

and Application

Introduction

H.1	This appendix sets out the process for production of a periodic

Frequency Risk and Control Report (FRCR), in accordance with an agreed process and which is regularly reviewed and updated in consultation with interested parties and is subject to approval by the Authority.

H.2	The FRCR is required to provide a transparent and consulted

assessment of the risk of unacceptable frequency conditions occurring, and their impact on Security of Supply inherent in the operation of the National Electricity Transmission System. It will set out which of these frequency risks the system should be secured against by the ISOP in their operation of the system to allow a balance to be struck between the consideration of risks, the benefit of avoiding these risks materialising, and the economic and efficient costs that will be incurred in ensuring the safe and secure operation of the system to do so.

H.3	The methodology underpinning the FRCR process, along with how this will be approved, is set out in Part A of this appendix. The requirements for the publication of the periodic FRCR are outlined in Part B. Obligations on parties regarding the provision of information underpinning the FRCR process are described in Part C. Together these activities make up the FRCR process.

Part A: The Frequency Risk and Control Report (FRCR) methodology

H.4	The ISOP shall initially and thereafter as required or as the Authority may direct, develop proposals for the FRCR methodology which will include the form and general expected content and structure of the FRCR. This will be carried out in consultation with interested parties. The consultation shall be of such a form and duration as to reasonably allow all interested parties to contribute.

H.5	Following any consultation pursuant to paragraph H4,  the ISOP must:

- by 1 April 2021, or such other date as directed by the Authority, submit to the SQSS Panel an initial FRCR methodology and proposed form of the initial FRCR; and

- by such other date as directed by the Authority or as the ISOP may see fit, further submit to the SQSS Panel an updated FRCR methodology.

H.7	Submissions made under paragraph H5 must include:

H.7	Submissions made under paragraph H5 must include:

H.6	The ISOP must make reasonable endeavours to ensure the FRCR methodology includes the information set out in paragraph H9. Where this has not been possible, the ISOP must explain the reasons and how it proposes to progress outstanding issues.

- detailed explanation of the consultation process undertaken in the development of the FRCR methodology;

- a summary of the views received from interested parties as part of the consultation process and an explanation of how these were taken into account in the development of the FRCR methodology; and

- copies of any formal responses submitted as part of the consultation process.

H.8	The SQSS Panel will on receipt of a submission under paragraph H5:

- recommend that the proposed FRCR methodology be used in the subsequent production of a FRCR; or

- give direction to the ISOP that the FRCR methodology requires further development.

In making its recommendation the SQSS Panel will give due regard to its expertise in the matters covered by the proposed FRCR methodology and will seek appropriate advice and guidance where required.

H.9	The FRCR methodology must be designed to facilitate the economic

assessment of the risk of unacceptable frequency conditions occurring on the National Electricity Transmission System and which of these risks will be secured. The FRCR methodology must include (but need not be limited to):

- the approach to be used to determine the circumstances for which unacceptable frequency conditions should not occur;

- the approach to be used in clearly setting out each of the risks or categories of risk that are present in the operation of the system which will be used in the assessment of unacceptable frequency conditions, including specific events and the direct and indirect consequences of these, and as will be set out in the FRCR in accordance with the methodology and the specific requirements of paragraph H17;

- how each of the risks identified in (b) will be assessed, including but not limited to:

- the approach used to assess the technical and economic impacts;

- the approach used to assess the likelihood and consequence of each such risk occurring; and

- the approach used to quantify the cost of mitigating each such risk.

(iv) the sources of information as used to perform the assessment.

- the benefits to the consumer in mitigating risks to the secure operation of the system;

- how the ISOP will engage with interested parties to share relevant information and how that information will be used to review and revise the FRCR methodology; and

- detailed of the ISOP’s proposed timetable for updating and consulting on the FRCR methodology.

Part B: The Frequency Risk and Control Report (FRCR)

H.10	The ISOP shall initially and at such other times as the ISOP may see fit or the Authority may direct, develop proposals for the FRCR in consultation with interested parties. The consultation shall be of such a form and duration as to reasonably allow all interested parties to contribute.

H.11	Following any consultation pursuant to paragraph H10, the ISOP must:

- produce an initial FRCR by 1 April 2021 or such other date as directed by the Authority and submit this to the SQSS Panel for their recommendation that this be onwards submitted to the Authority for approval. This must be based on and prepared in accordance with the draft initial methodology set out in part A.; and

- by such other date as directed by the Authority or as The ISOP may see fit, and as set out in paragraph H12, publish a revised FRCR.

H.12	Following publication of the initial FRCR, the ISOP must:

- review at least once in each financial year the FRCR prepared and published in the previous financial year and consider any improvements to better facilitate the economic and efficient operation of the National Electricity Transmission System; and

- at least annually, or at such date as directed by the Authority, publish an updated FRCR and submit this to the SQSS Panel for their recommendation that this be onwards submitted to the Authority for approval. This must be based on and prepared in accordance with the latest approved methodology set out in part A.

H.13 The ISOP must make reasonable endeavours to ensure any FRCR submitted under paragraph H11 or H12 includes the information set out in paragraph H14. Where this has not been possible, the ISOP must explain the reasons and how it proposes to progress outstanding issues.

H.14 Submissions made under paragraphs H11 or H12 must include:

- a detailed explanation of the consultation process undertaken in the development of the FRCR;

- a summary of the views received from interested parties as part of the consultation process and an explanation of how these were taken into account in the development of the FRCR; and

- copies of any formal responses submitted to the ISOP as part of its consultation process.

H.15 	Following the approval of the FRCR under H19, the ISOP must publish the FRCR on its website in such readily accessible form and manner that it considers will best facilitate engagement with stakeholders, and provide a copy of the FRCR on request, and free of charge, to any person who asks for one.

H.16	In complying with the requirements of paragraph H15,  the ISOP must have due regard to the need for excluding from the published FRCR any information that could cause security concerns or that would or might seriously and prejudicially affect the commercial interests of the owner of that information if published or might be expected to be incompatible with any legislation, rule of law or licence condition and will take due regard of any representations made by owners of such data. The ISOP must provide to the SQSS Panel and the Authority its reasons for any omission of information from the FRCR as published and where it is intended that this be different from the report as submitted for approval under H11 or H12.

H.17 	Each FRCR (including the initial FRCR) prepared in accordance with the methodology set out in Part A must:

(a) set out:

- those risks to the secure operation of the system considered under the FRCR;

- the likelihood and consequence of each such risk occurring;

- the likely cost of securing the system against such risks;

- the benefits to the consumer in mitigating such risks;

(b) include the ISOP’s assessment of continued effective operation of the system and their considered view of which risks should be secured representing the best value for money for consumers and balancing the likelihood of risks occurring and their consequence with the cost of mitigation.

H.18 The SQSS Panel will on receipt of a submission made by the ISOP under paragraph H11 or H12:

- recommend that the proposed FRCR be onwards submitted to the Authority for approval; or

- give direction to the ISOP that the FRCR requires further development.

In making its recommendation the SQSS Panel will give due regard to its expertise in the matters covered by the proposed FRCR and will seek appropriate advice and guidance where required.

H.19 The Authority will on receipt of a submission made by the  ISOP under paragraph H11:

- approve the proposed FRCR and in particular the recommendations as detailed in H17 (b) of which operational risks the  ISOP will incur costs in securing the system against to avoid unacceptable frequency conditions; or

- give direction to the ISOP that the FRCR requires further development, and the date by which the ISOP is required to submit a revised FRCR to the Authority for approval.

H.20 On approval by the Authority of the FRCR, the ISOP shall ensure that the risks set out in the FRCR to be mitigated in its operation of the system shall reasonably be secured until the subsequent approval by the Authority of any update of the FRCR.

Part C: Provision of information

H.21 Based on the FRCR methodology set out in Part A, the ISOP must provide licenced electricity operators if reasonably requested to do so:

- with information and analysis to support them in their decision-making on, for example, operation of their plant and equipment;

- with updated information and analysis to support submissions made to the Authority by the ISOP and in such form and within such timescales as reasonably requested; and

- In complying with the requirements of this paragraph, the ISOP must have due regard to the need to exclude from disclosure any information which would or might seriously and prejudicially affect the commercial interests of the owner of that information if disclosed or might be expected to be incompatible with any relevant legislation, code or licence condition. he ISOP must provide to the Authority its reasons for any nondisclosure of information.

H.22 The Authority may direct the ISOP to submit additional information on any submissions made under this appendix within such timeframe as the Authority may require in order to carry out any of its functions in relation to the assessment of submissions.

- Appendix I 		System Restoration Requirements

I.1	These key requirements apply to onshore transmission systems. In the case of offshore transmission systems, the requirements of this Appendix I would only be applied to those offshore transmission systems who had concluded design contracts for their assets on or after 05 February 2024.

- I.1.1	Each transmission system shall be designed to facilitate participation in a restoration plan as appropriate including but not limited to the assessment of reactive gain and the ability for generation to energise sections of the transmission system.

- I.1.2	In addition to the requirements of I1.1, each transmission system shall be designed to permit power stations to be subsequently synchronised to the transmission system and operated within their normal operational capability limits.

- I.1.3	The no load gain between adjacent substations shall be designed to prevent system collapse during restoration.

- Appendix J Governance Framework

J.1	Interpretations

J.1.1 Except as otherwise provided herein and unless the context otherwise admits, words and expressions used herein shall have the same meaning as defined in the SQSS.

J.1.2 Words importing the singular only also include the plural and vice versa where the context requires.

J.1.3 Headings and titles shall not be taken into consideration in the interpretation or construction of the words and expressions used in the SQSS

J.2	Introduction

J.2.1	The Electricity Act 1989 requires licensees to develop and maintain an efficient, co-ordinated and economical system of electricity transmission.

J.2.2	The transmission licences place an obligation upon the licensees to plan, develop and operate their systems in accordance with, amongst other things, the SQSS. In addition, the ESO licence places an obligation on the ISOP to coordinate and direct the flow of electricity onto and over the National Electricity Transmission System, in accordance with the SQSS, together with the STC, the grid code or such other standard of planning and operation as the authority may approve from time to time, and with which the licensee may be required to comply (following consultation, where appropriate, with any authorised electricity operator liable to be materially affected thereby).

J.2.3	In order to facilitate these requirements, the SQSS may need, from time to time, to be

revised to reflect changes in both the GB Electricity Supply Industry and technological advances.

J.2.4	The panel is the co-ordinator, not a decision making body. The purpose of the panel is to

consider developments to the SQSS and recommend SQSS changes to the authority.

J.2.5	The governance framework sets out:

J.2.5.1 	arrangements for the establishment and composition of the Panel, to  include a Chairperson and;

J.2.5.2	the procedure for proposing Modifications to the SQSS.

J.2.6	The governance framework governs the industry led process for reviewing, and

proposing modifications to, the SQSS. The governance framework is not intended to reflect upon the powers and decisions of the authority in relation to the SQSS.

J.3	SQSS Objectives

J.3.1	The panel shall endeavour at all times to perform its functions to ensure efficient discharge by each of the licensees of the obligations imposed upon it under the Electricity Act, and by the ISOP of the obligations imposed upon it by the Energy Act, and their associated licences, specifically focusing on the following objectives:

- facilitate the planning, development and maintenance of an efficient, coordinated and economical system of electricity transmission, and the operation of that system in an efficient, economic and coordinated manner;

- ensure an appropriate level of security and quality of supply and safe operation of the National Electricity Transmission System;

- facilitate effective competition in the generation and supply of electricity, and (so far as consistent therewith) facilitating such competition in the distribution of electricity; and

- facilitate licensees to comply with any relevant obligations under assimilated law.

J.4	Establishment and Composition

J.4.1	Establishment

J.4.1.1 NESO (as the ISOP), NGET, SPT and SHET shall establish the panel which shall be constituted in accordance with the further provisions of this Section 4.

J.4.1.2 Subject as expressly provided in this governance framework, the members may regulate the conduct of and adjourn and convene panel meetings as they deem fit.

J.4.2	Functions of the Panel

J.4.2.1 The panel shall consider all reasonable requests to modify the SQSS. Such requests may be made by any of the members, the authority or any relevant interested person. SQSS modification proposals shall be raised via the secretary.

J.4.2.2 The functions of the panel shall be to:

J.4.2.2.1 keep the SQSS and its working under review;

J.4.2.2.2	evaluate and administrate modifications to the SQSS in accordance with procedures set out in the governance framework;

J.4.2.2.3 keep the governance framework and its working under review;

J.4.2.2.4 publish recommendations to modify the SQSS and the reasons for the recommendations;

J.4.2.2.5 recommend to the authority any modifications of the SQSS; and

J.4.2.2.6 the panel shall endeavor at all times to perform its functions:

- in an efficient, economical and expeditious manner, taking account of the Prioritisation Criteria and the Prioritisation Category of a particular modification to the SQSS; and

- with a view to ensuring the SQSS facilitates achievement of its objectives.

J.4.3	Chairperson

J.4.3.1 There shall be a Chairperson of the panel who shall be appointed every second year, by the agreement of all members, from 01 April 2012 or as otherwise agreed by the members and who shall, taking into account the functions set out in subparagraph J.4.3.2, carry out such activities as may be agreed between the members from time to time.

J.4.3.2 The functions of the Chairperson include:

J.4.3.2.1 to ensure that meetings are conducted in a professional, proper, impartial and efficient manner;

J.4.3.2.2 to ensure that each member, any person invited to speak or any representative of the authority have been given a reasonable opportunity to speak on any matter contained in the agenda for the meeting.

J.4.3.3 In the event that the Chairperson is not present within fifteen minutes of the scheduled start of any meeting and has not nominated another person to take the position of Chairperson, those members present shall appoint one of their number to act as Chairperson.

J.4.4	Secretary

J.4.4.1 The panel shall be assisted by a Secretary who shall be a person appointed by the ISOP. The ISOP may remove and reappoint the Secretary by giving notice to the Panel.

J.4.4.2 The Secretary shall carry out such activities as are specified in this governance framework and as are otherwise agreed between the members from time to time.

J.4.5 Authority

J.4.5.1 A representative of the authority shall be entitled to attend panel meetings as an observer and may speak at any meeting. The authority shall from time to time notify the Secretary of the identity of the observer. For the avoidance of doubt the authority representative shall not be considered a member of the panel.

J.4.6	Membership

J.4.6.1 The panel shall consist of:-

- a Chairperson;

- a Secretary appointed by the ISOP;

- a person appointed by the authority; and

- the following members

- two persons representing the ISOP;

- two persons representing NGET;

- two persons representing SHET;

- two persons representing SPT;

- two persons representing offshore transmission owners;

- a person representing generators; and

- a person representing network operators.

J.4.6.2 ISOP members

J.4.6.2.1	The ISOP is entitled to nominate two members to attend panel meetings and may appoint, remove and reappoint their members by giving notice to the Secretary.

J.4.6.3 NGET members

J.4.6.3.1	NGET is entitled to nominate two members to attend panel meetings and may appoint, remove and reappoint their members by giving notice to the Secretary.

J.4.6.4 SHET members

J.4.6.4.1	SHET is entitled to nominate two members to attend panel meetings and may appoint, remove and reappoint their members by giving notice to the Secretary.

J.4.6.5 SPT members

J.4.6.5.1SPT is entitled to nominate two members to attend panel meetings and may appoint, remove and reappoint their members by giving notice to the Secretary.

J.4.6.6 Offshore transmission owner members

J.4.6.6.1	Offshore transmission owners may appoint not more than two members and not more than two Alternate members every second year from 01 April 2012 in accordance with Annex 1. Any person shall be eligible for reappointment on expiry of their term.

J.4.6.6.2	Offshore transmission owner members shall have the duty to impartially represent the views of the offshore transmission owners that they represent.

J.4.6.7 Generator member

J.4.6.7.1	The panel will agree on an appropriate representative body within the electricity industry to represent the interests of generators.

J.4.6.7.2	The agreed representative body is entitled to nominate a member to attend panel meetings. The agreed representative body may appoint, remove and reappoint their member by giving notice to the Secretary.

J.4.6.8 Network operator member

J.4.6.8.1	The panel will agree on an appropriate representative body within the electricity industry to represent the interests of network operators.

J.4.6.8.2	The agreed representative body is entitled to nominate a member to attend panel meetings. The agreed representative body may appoint, remove and reappoint their member by giving notice to the Secretary.

For the avoidance of doubt the generator and network operator representative bodies, the ISOP, NGET, SHET and SPT are not required to identify Alternate members as members are appointed, removed and reappointed by giving notice to the Secretary.

J.4.7	Meeting Frequency

J.4.7.1	All meetings shall be called by the Secretary giving notice to Members at least 15 business days before that date of the next meeting or such other shorter period as all the members may agree. The notice shall set out the date, time and place of the meeting.

J.4.7.2 The panel shall hold a minimum of 4 meetings per calendar year at regular intervals as agreed by the members. Attendance at such meetings may be in person, by teleconference or video conference or in any alternative manner as all the members may agree and such members will be counted as present for the purposes of the quorum.

J.4.8	Meeting Administration

J.4.8.1 The Secretary will make available to the panel, not less than 10 business days before the date of the meeting or such other shorter period as the members may agree, an agenda of the matters for consideration at the meeting and any supporting papers for discussion.

J.4.8.2 An omission to send panel documents to a person entitled to receive them under sub-paragraph J.4.9.2 shall not prevent a panel meeting from proceeding unless otherwise directed by the authority.

J.4.8.3 As soon as is practicable after each panel meeting, the Secretary shall prepare and send to the members and the authority the minutes of such panel meeting, which shall be approved (or amended and approved) by the panel at the next panel meeting after they were so sent and, when approved, the panel Secretary shall publish the approved minutes (excluding any matter which it was agreed at such panel meeting was not appropriate for such publication) on the ISOP website.

J.4.9 	Quorum

J.4.9.1 Subject to sub-paragraph J.4.9.3, no business shall be transacted at any panel meeting unless a quorum (as defined in sub-paragraph J.4.9.2) is present.

J.4.9.2 A quorum shall be constituted where there is at least one member representing each of the ISOP, NGET, SHET, SPT and the OFTOs, unless the Secretary and the panel has been notified in writing by a member representing the ISOP, NGET, SHET, SPT or the OFTOs that the matters to be discussed at such panel meeting do not materially affect it and in which case that member (with the consent of the other members forming the quorum) may waive their right to attend.

J.4.9.3 Where a quorum is not present, the Secretary shall seek to adjourn the panel meeting to a later date unless it is the third consecutive panel meeting that has been required to be adjourned as a consequence of the failure to attend by a particular member, in which case, the panel meeting shall nonetheless proceed and subsequent ratification of decisions taken at the panel meeting by such non-attending member shall not be required unless the lack of attendance by such member (on any of the three occasions) was as a consequence of an omission to send such member the details of the panel meeting required pursuant to subparagraph J.4.9.2.

J.4.10 Attendance by Other Persons

J.4.10.1 A member may, with the agreement of the other members, invite any person other than a person already entitled to attend under Paragraph J.4.6 to attend any part of a panel meeting and to speak at such meeting, where that person so attends.

J.4.11 Removal from Office

J.4.11.1 A person shall cease to hold office as a member or an Alternate member:

(a)	in the case of offshore transmission owner members only, upon expiry of their term of office unless re-appointed;

(b)	if they:

- resign by notice delivered to the Secretary;

- become bankrupt or make any arrangement or composition with their creditors generally;

- are or may be suffering from a mental disorder and either are admitted to hospital in pursuance of an application under the Mental Health Act 1983 or the Mental Health (Scotland) Act 1960 or an order is made by a court having jurisdiction in matters concerning mental disorder for their detention or for the appointment of a receiver, curator bonis or other person with respect to their property or affairs;

- become prohibited by law from being a director of a company under the Companies Act 1985;

- die; or

- are convicted on an indictable offence; or

- if the panel resolves (and the authority does not veto such resolution by notice in writing to the Secretary within 15 business days) that they should cease to hold office on grounds of their serious misconduct.

J.4.11.2 A panel resolution under Paragraph J.4.11.1 (c) shall, notwithstanding any other Paragraph, require the vote in favour of at least all members less one (other than the member or Alternate member who is the subject of such resolution) and for these purposes an abstention shall count as a vote cast in favour of the resolution. A copy of any such resolution shall forthwith be sent to the authority by the Secretary.

J.4.11.3 A person shall not qualify for appointment as a member or Alternate member if at the time of the proposed appointment they would be required by the above Paragraph to cease to hold that office.

J.4.11.4 The Secretary shall give prompt notice by electronic means to all members and the authority of the appointment or re-appointment of any member or Alternate member or of any member or Alternate member ceasing to hold office.

J.5	Modification of the SQSS

J.5.1	General

J.5.1.1 Each member shall keep under review whether any possible change to the SQSS would better facilitate achievement of the SQSS objectives and shall, in accordance with J.5 and to the extent that such matter is not covered by a Modification Proposal, raise a Modification Proposal which, in the member’s opinion, would do so.

J.5.1.2 The members shall endeavor at all times to act pursuant to this J.5:

- in an efficient, economical and expeditious manner taking account of the Prioritisation Criteria and the Prioritisation Category of a particular modification proposal; and

- with a view to ensuring that the SQSS facilitates achievement of the SQSS objectives.

J.5.1.3 The SQSS Modification process flow chart is shown in Annex 2. Paragraph J.5.2 presents a more detailed account of the modification process.

J.5.2	The SQSS Modification Process

J.5.2.1 Modification Proposal

J.5.2.1.1 A Modification Proposal may be made by any of the following:

- a member;

- the authority; or

- relevant interested person

referred to in J.5 as the ‘Proposer’.

J.5.2.1.2 A Modification Proposal made pursuant to sub-paragraph J.5.2.1.1 shall be submitted to the Secretary in the form of Annex 3 which may be amended by the panel from time to time.

J.5.2.1.2A A Modification Proposal made pursuant to sub-paragraph J.5.2.1.1 shall also contain an assessment by the Proposer of the Modification Proposal against the Prioritisation Criteria.

J.5.2.1.3 If a Modification Proposal fails to contain any information required under sub-paragraph J.5.2.1.2, the Secretary shall notify the Proposer, who may submit a revised request in compliance with this sub-paragraph J.5.2.1.2.

J.5.2.1.4  Upon receipt of a Modification Proposal made pursuant to and in compliance with sub-paragraph J.5.2.1.2, the Secretary shall as soon as reasonably practicable:

- make a copy of the Modification Proposal available to the members, the authority and any relevant interested person, such as by publishing it on the licensee’s website;  subject to the provisions of Paragraph J.4.8, put the request on the agenda for the next panel meeting; and

- add the new Modification Proposal to the SQSS Modification Register (“Modification Register”) as further provided for and defined in Paragraph J.5.2.7.

J.5.2.1.5  It shall be a condition to the right to raise an SQSS Modification Proposal under this Paragraph J.5.2.1 that the Proposer:

- grants a non-exclusive royalty-free licence to all Parties who request the same covering all present and future rights, Intellectual Property Rights and moral rights it may have in such request (as regards use or application in Great Britain and its offshore waters); and

- warrants that, to the best of its knowledge, information and belief, no other person has asserted to the Proposer that such person has any Intellectual Property Rights or moral rights or rights of confidence in such proposal inconsistent with the Parties' rights to make, publish or use such request, and, in making a request, a shall be deemed to have granted the licence and given the warranty contained in sub-paragraphs (a) and (b) above respectively.

J.5.2.1.6 The Proposer may withdraw its Modification Proposal on notice to the Secretary at any time, in which case, the Secretary shall promptly notify the members and the authority and then, 5 business days after issue of such notice by the Secretary, shall:

- revise the Modification Register; and

- remove the Modification Proposal from the agenda of the next panel meeting (as relevant);

J.5.2.2 Review of Modification Proposals at Panel Meetings

J.5.2.2.1 The panel shall consider a Modification Proposal (if compliant with subparagraph J.5.2.1.2 and not withdrawn under sub-paragraph J.5.2.1.6) at the next panel meeting and at such meeting shall use all reasonable endeavours to decide (as and where relevant) whether:

- the members require additional information in order to assess whether the request would better facilitate achievement of the SQSS Objectives; or

- pursuant to sub-paragraph J.5.2.2.5, to amalgamate the request with any other Proposed Modification; and

- having assessed the Modification Proposal against the Prioritisation Criteria, as compared with other Modification Proposals, taking into account the Proposer’s opinion provided pursuant to paragraph J.5.2.1.2A, the Modification Proposal should be accorded a relevant Prioritisation Category.

J.5.2.2.2     Where, pursuant to sub-paragraph J.5.2.2.1 (a) above, the panel decides not to take the Modification Proposal further, the Secretary shall notify the Proposer explaining why the proposal has been rejected. The Secretary shall also amend the Modification Register as appropriate.

J.5.2.2.3   Where, pursuant to sub-paragraph J.5.2.2.1 (a) above, the panel decides that additional information is required or the panel cannot reach a decision on such matters, the panel shall refer the Modification Proposal to a Workgroup to carryout such analysis as set out under sub-paragraph J.5.2.3.

J.5.2.2.4   Where, pursuant to sub-paragraph J.5.2.2.1 (a) above, the panel decides that additional information is not required, the panel shall proceed directly to Industry Consultation under sub-paragraphs J.5.2.4.

J.5.2.2.5    The panel may decide to amalgamate a Modification Proposal with one or more other Modification Proposal(s) where the subject matter is sufficiently proximate to justify amalgamation on the grounds of efficiency and/or where such Modification Proposal(s) are logically dependent on each other.

J.5.2.2.6	Where Modification Proposals are amalgamated pursuant to sub-

paragraph J.5.2.2.5:

- such Modification Proposals shall be treated as a single Modification Proposal;

- references in J.5 to a Modification Proposal shall include and apply to a group of two or more Modification Proposals so amalgamated;

- the Proposers of each such amalgamated Modification Proposal shall cooperate in deciding which of them shall constitute the Proposer of such amalgamated Modification Proposals, failing which agreement, the Modification Proposals shall continue separately as before; and

- the Panel shall determine the amalgamated Modification Proposal to have a single Prioritisation Category. When determining a Prioritisation Category for an amalgamated Modification Proposal, the Panel shall consider the Prioritisation Categories, and the relevant assessments undertaken in determining these Prioritisation Categories, accorded to the original Modification Proposals that have been amalgamated.

J.5.2.3 Evaluation and Assessment by a Workgroup

J.5.2.3.1   Following referral of a Modification Proposal, pursuant to sub-paragraph J.5.2.2.3, to a Workgroup, the panel shall invite representations or commission such studies, convene industry workshops and other evaluation as it deems appropriate in order that the panel is provided with sufficient information such that it can assess whether the Modification Proposal would better facilitate achievement of the SQSS Objectives.

J.5.2.3.2   The panel shall use its reasonable endeavours in order to ensure that evaluation and assessment by a Workgroup takes no longer than 6 months from its referral under sub-paragraph J.5.2.2.3 up to the submission of the Workgroup Report to the panel under sub-paragraph J.5.2.3.13 unless otherwise agreed by the panel.

J.5.2.3.3   A Workgroup shall comprise at least 5 persons (who may be panel members) “Workgroup Quorum” or any such number of persons agreed by the panel.

J.5.2.3.4  In addition to the Workgroup Quorum the panel shall appoint a Workgroup Chairperson who will ensure that meetings are conducted in a professional, proper, impartial and efficient manner.

J.5.2.3.5   The Workgroup shall be assisted by a Secretary who shall be appointed by the panel. As soon as is practicable after each Workgroup meeting, the Secretary shall prepare and send to the Workgroup members the minutes of such Workgroup meeting, which shall be approved (or amended and approved) by the Workgroup at the next Workgroup meeting after they were so sent and, when approved, the Secretary shall publish the approved minutes (excluding any matter which it was agreed at such Workgroup meeting was not appropriate for such publication) on the ISOP website.

J.5.2.3.6  A representative of the authority may attend any meeting of a Workgroup as an observer and may speak at any such meeting.

J.5.2.3.7   The panel shall determine the terms of reference of each Workgroup and may change those terms of reference from time to time as it sees fit.

J.5.2.3.8   The terms of reference for a Workgroup must include provision in respect of the following matters:

- detail the Workgroup’s responsibilities for assisting the panel in the evaluation of the Modification Proposal and consider whether it better facilitates achievement of the SQSS Objectives and to provide additional information to the panel;

- detail the Modification Proposal;

- detail the work to be undertaken by the Workgroup to assist the panel in the evaluation of the Modification Proposal;

- specify any matters which the Workgroup should address in its report;

- the timetable for the work to be done by the Workgroup;

- specify if the Workgroup is to comment upon any legal text.

J.5.2.3.9    Unless otherwise determined by the panel the Workgroup shall develop and adopt its own internal working procedures for the conduct of its business.

J.5.2.3.10 A Workgroup Report will be submitted to the panel responding to the matters detailed in the terms of reference and in accordance with the timetable set out in the terms of reference and will indicate the issues and views which arose in the Workgroup discussions and any recommendations made.

J.5.2.3.11 If a Workgroup is unable to reach agreement on any such matter, the Workgroup Report must reflect the views of the members of the Workgroup.

J.5.2.3.12 The Workgroup Report will be circulated in draft form to the Workgroup members for a period of not less than 5 business days for comment. Any unresolved comments made shall be reflected in the final Workgroup Report.

J.5.2.3.13 The final Workgroup Report shall be submitted to the panel. Upon receipt of the Workgroup Report, the Secretary shall as soon as reasonably practicable:

- send a copy of the Workgroup Report to the members and the authority; and

- subject to the provisions of Paragraph J.4.8.1, put the Workgroup Report on the agenda for the next panel meeting;

J.5.2.3.14 The Workgroup Chairperson or another person (nominated by the Workgroup Chairperson) shall be present at the panel meeting at which that Workgroup Report is to be discussed and may be invited to present the findings and/or answer the questions of panel members.

J.5.2.3.15 Following receipt of any representations, study, Workgroup Report or other evaluation pursuant to sub-paragraph J.5.2.3.1, the panel shall consider whether the information provided is sufficient to form a view as to whether the Modification Proposal better facilitates achievement of the SQSS Objectives and may invite such further representations, studies, and other evaluation including sending matters back to the Workgroup as it deems appropriate until the panel considers that the information provided is sufficient.

J.5.2.4 Industry Consultation

J.5.2.4.1 Following completion of the steps set out in sub-paragraphs J.5.2.3.1 to J.5.2.3.15 above (where relevant), the Secretary shall prepare a consultation document ("Consultation Document") setting out:

- the Modification Proposal;

- the views and recommendations of the panel as to whether the changes proposed in the Modification Proposal(s) should be made, including the analysis of whether (and, if so, to what extent) the Modification Proposal(s) would better facilitate achievement of the SQSS Objectives and the views and rationale in respect thereof;

- an analysis and impact assessment (“Assessment”) which shall identify the likely effect of the Modification Proposal(s) on the assets and systems of panel members), including a description of any works necessary to implement the change and an estimate of the development, capital and operating costs associated with implementing the changes to the SQSS;

- the proposed implementation date of the Modification Proposal(s) as agreed by the panel, failing which, as shall be proposed by the Proposer and, in the later case, accompanied by the written representations of the other members giving their own opinion as to what the implementation date should be; and

- any proposed text to modify the SQSS;

- (to the extent that such matters are not included pursuant to subparagraph (c)), an analysis of:

- the impact of the Modification Proposal(s) on the core industry documents;

- the changes which would be required to give effect to the Modification Proposal(s) in relation to the core industry documents;

- the mechanism and likely timescale for making the changes referred to in sub-paragraph (ii);

- the changes or developments which would be required to central computer systems and, if practicable, processes used in connection with the operation of arrangements established under the core industry documents;

- the mechanism and likely timescale for making the changes referred to in sub-paragraph (iv); or

- an estimate of the costs associated with making and delivering the changes referred to in sub-paragraphs (ii) and (iv), such costs being expected to relate to: for (ii), the costs of implementing Modifications to the Industry Framework Document(s), and for (iv), the costs of changes to computer systems and possibly processes which are established for the operation of the core industry documents, and

- details of the analysis carried out, pursuant to paragraph J.5.2.2.1 (c), by the Panel to determine the Prioritisation Category of the Modification Proposal, and the Prioritisation Category that has been determined, where this determination has been carried out.

together with a summary of representations of the panel in relation to such matters,

J.5.2.4.2	Pursuant to sub-paragraph J.5.2.4.1, the Secretary shall:

(a)	circulate the Consultation Document to each of the members

and such persons or bodies as have responsibility for progressing changes to the core industry documents and publish it on the ISOP website or otherwise in such manner as may be deemed appropriate by the members to bring it to the attention of other persons who may have a relevant interest in the Modification Proposal;

(b) 	invite representations in relation to the Consultation Document within 20 business days or such other period as the panel shall determine; and

- on receipt of representations pursuant to sub-paragraph (b), prepare a summary of such representations.

J.5.2.5 The Modification Report

J.5.2.5.1	Pursuant to sub-paragraph J.5.2.4.2, the panel shall consider the

representations made in response to the Consultation Document and shall instruct the Secretary to prepare a report as in sub-paragraph J.5.2.4.1 incorporating comments from the Consultation Document respondents and recommendations in light of those comments. This report shall form the “Modification Report”

J.5.2.5.2	If members agree that Modification to the SQSS is not required, the panel shall instruct the Secretary to prepare the Modification Report and send it to the authority. The Secretary shall also update the Modification Register and publish the Modification Report on the ISOP website.

J.5.2.5.3	If members agree that Modification to the SQSS is required, the Panel shall instruct the Secretary to prepare the Modification Report and send it to the authority. Each licensee member will individually send a licence change request to the authority based on the Modification Report. The Secretary shall also update the Modification Register and publish the Modification Report on the ISOP website.

J.5.2.5.4 	If not all members agree that Modification to the SQSS is needed, the Secretary shall record the range of recommendations which shall be incorporated into the Modification Report. The panel shall instruct the Secretary or Workgroup Chairperson to prepare the Modification Report for subsequent submission to the authority. Those licensee members that recommend Modification to the SQSS may send licence change requests to the authority. The Secretary shall also update the Modification Register and publish the Modification Report on the ISOP website.

J.5.2.5.5 None of the facts, opinions or statements contained in the Modification Report may be relied upon by any other person.

J.5.2.5.6 The Modification Report shall contain details of the analysis carried out, pursuant to paragraph J.5.2.2.1 (c), by the Panel to determine the Prioritisation Category of the Modification Proposal, and the Prioritisation Category that has been determined, where this determination has been carried out.

J.5.2.6 Further versions of SQSS

J.5.2.6.1 If the authority directs a change to the SQSS the licensee shall

provide a revised version of the SQSS in accordance with the terms of such notice, update the Modification Register and publish the revised SQSS on the ISOP website.

No change shall be made to the SQSS without prior consent of the authority.

J.5.2.6.2 A Modification to the SQSS shall take effect from the date and time as specified in the direction referred to in sub-paragraph J.5.2.6.1.

J.5.2.6.3 The relevant members shall be responsible for implementing any changes to their relevant computer systems and processes as necessary to effect the Approved Modification in accordance with this sub-paragraph J.5.2.6.

J.5.2.6.4 Following implementation of licence changes by the authority in relation to Approved Modifications, each relevant member shall:

- use its reasonable endeavours to progress changes made to the core industry documents (to the extent that it is a party to them) in order to give full and timely effect to a Modification to the SQSS by the implementation date;

- do what is required to those of its systems and processes which support the operation of the SQSS as may be necessary in order to give full and timely effect to a Modification to the SQSS by the implementation date; and

- keep the Panel informed of any matter that may affect the ability for the implementation date to be met.

J.5.2.6.5 	Without prejudice to the obligations of the members under this subparagraph J.5.2.6, the implementation date may be extended or shortened with the prior approval of, or at the direction of, the authority.

J.5.2.6.6  Any relevant member shall apply to the authority for an extension of the implementation date if it becomes aware of any circumstances that are likely to cause a delay in the implementation of an Approved Modification.

J.5.2.6.7 A Modification made pursuant to and in accordance with this Paragraph J.5.2 shall not be impaired or invalidated in any way by any inadvertent failure to comply with or give effect to this sub-paragraph J.5.2.6.

J.5.2.7 The Modification Register

J.5.2.7.1  The Secretary shall establish and maintain a register (the "Modification Register") which shall record, in such form as the panel may determine, the matters set out in sub-paragraph J.5.2.8.3.

J.5.2.7.2 The purpose of the Modification Register shall be to assist the panel in the operation of the Modification process under this Governance Framework and to enable the members and other interested third parties to be reasonably informed of the progress of Modification Proposals and Approved Modifications from time to time.

J.5.2.7.3 The Modification Register shall record:

- details of each Modification Proposal (including the name of the Proposer, the date raised and a brief description of the Modification Proposal);

- the current status and progress of each Modification Proposal and the anticipated date for reporting to the Authority in respect thereof;

- the current status and progress of each Approved Modification to the SQSS;

- such other matters as the Panel may consider appropriate from time to time in order to achieve the purposes set out in subparagraph J.5.2.7.2;

(e) 	the Prioritisation Category attached to the Modification Proposal, and the reasons for the Panel’s determinations where they have been made in regard to the Prioritisation Category of the Modification Proposal; and

(f) 	where the Prioritisation Category of a Modification Proposal has been changed, details of and the reasons for its change.

J.5.2.7.4 The Modification Register shall, in addition to those matters set out in subparagraphs J.5.2.7.3, also include details of:

- each Modification Proposal which has been withdrawn pursuant to sub-paragraph J.5.2.1.6 or rejected by the panel; and

- each Modification to the SQSS which has been implemented pursuant to sub-paragraph J.5.2.7,

for a period of 6 months after such withdrawal, rejection or implementation, or such longer period as the panel may determine.

J.5.2.7.5 The Secretary shall publish the Modification Register (as updated from time to time and indicating the revisions since the previous issue) on the ISOP website with such frequency as the panel may agree, in order to bring it to the attention of interested third parties.

J.5.3	Review of Prioritisation Category of Modification Proposals

J.5.3.1 	The Panel shall review the Prioritisation Category of Modification Proposals on a bi-annual basis and adjust the relevant modification timetable for each Modification Proposal accordingly.

Appendix J, Annex 1 - Offshore Transmission Owner Election Process

J.A1.1 General

J.A1.1.1 Introduction

J.A1.1.1.1 This Annex 1 sets out the basis for election of offshore transmission owner members and offshore transmission owner Alternate members which will apply except to the extent that the conditions in J.A1.1.1.5 are met.

J.A1.1.1.2 This Annex 1 shall apply:

- in relation to each year (the “Election Year”) in which the term of office of offshore transmission owner members and offshore transmission owner Alternate members expires, for the purposes of electing offshore transmission owner members and offshore transmission owner Alternate members to hold office with effect from 01 April in that year;

- subject to and in accordance with Paragraph J.A1.4, upon a offshore transmission owner member and/or offshore transmission owner Alternate member ceasing to hold office before the expiry of their term of office.

J.A1.1.1.3	For the purposes of an election under Paragraph J.A1.1.1.2(a) references to offshore transmission owner are to persons who are an offshore transmission owner as at 01 January in the Election Year.

J.A1.1.1.4 The Secretary shall administer each election of offshore transmission owner members and offshore transmission owner Alternate members pursuant to this Annex

J.A1.1.1.5 Where the following conditions (a) and (b) in this Paragraph J.A1.1.1.5 are met, the offshore transmission owner member(s) and/or offshore transmission owner Alternate member(s) will be those notified to the Secretary as set out below:

(a)	each Offshore Transmission Owner Member as at 01 January in the relevant Election Year, has confirmed in writing to the Secretary that the offshore transmission owner member(s) and/or offshore transmission owner Alternate member(s) will be elected in accordance with a process other than that set out in Annex 1 ("Alternative OFTO Election Process"); and

(b)	each offshore transmission owner member as at 01 January

in the relevant Election Year, has notified the Secretary in writing by 25 January of the relevant Election Year of the identity of the offshore transmission owner member(s) and/or offshore transmission owner Alternate member(s) elected through the Alternative OFTO Election Process, and each notification identifies the same individual(s).

Upon receipt of such notifications in accordance with the above, the provisions of this Annex 1, with exception of Paragraph J.A1.1.1.4, shall not apply until the following Election Year.

J.A1.1.2 Election timetable

J.A1.1.2.1	The Secretary shall not later than 01 February in the Election Year

prepare and circulate to all offshore transmission owners (by publication on the ISOP Website and, where relevant details are supplied, by electronic mail), with a copy to the authority, an invitation to nominate candidates who must be willing to be either an offshore transmission owner member or an Alternate member and a timetable for the election (the “Election Timetable”), setting out:

- the date by which nominations of candidates are to be received, which shall not be less than three (3) weeks after the timetable is circulated;

- the date by which the Secretary shall circulate a list of candidates and voting papers;

- the date by which voting papers are to be submitted, which shall not be less than three (3) weeks after the date for circulating voting papers;

- the date by which the results of the election will be made known, which shall not be later than 18 March in the Election Year.

J.A1.1.2.2 If for any reason it is not practicable to establish an Election Timetable in accordance with Paragraph J.A1.2.1.1 or to proceed on the basis of an Election Timetable which has been established, the Secretary may establish a different timetable, or revise the Election Timetable, by notice to all offshore transmission owners, the panel and the authority, provided that such timetable or revised timetable shall provide for the election to be completed before 01 April in the Election Year.

J.A1.1.2.3 A nomination or voting paper received by the Secretary later than the respective required date under the Election Timetable (subject to any revision under Paragraph A1.1.2.2) shall be disregarded in the election.

J.A1.2.	CANDIDATES

J.A1.2.1 Nominations

J.A1.2.1.1	Nominations for candidates shall be made in accordance with the

Election Timetable.

J.A1.2.1.2 Subject to Paragraph J.A1.1.1.3, each offshore transmission owner may nominate one candidate for election by giving notice to the Secretary.

J.A1.2.2 List of candidates

J.A1.2.2.1 The Secretary shall draw up a list of the nominated candidates and circulate the list to all offshore transmission owners by the date specified in the Election Timetable.

J.A1.2.2.2 The list shall specify the offshore transmission owner by whom each candidate was nominated and any affiliations which the candidate may wish to have drawn to the attention of offshore transmission owners.

J.A1.2.2.3 Except where Paragraphs J.A1.4.3 or J.A1.4.4 apply, if two (2) or fewer candidates are nominated no further steps in the election shall take place and such candidate(s) shall be treated as elected as offshore transmission owner members and Paragraph J.A1.3.2.4 shall apply in relation to such candidate(s).

J.A1.2.2.4 Where Paragraph J.A1.4.3 applies, if only one (1) candidate is nominated, no further steps in the election shall take place and such candidate shall be treated as elected as a member and Paragraph J.A1.3.2.4 shall apply in relation to such candidate.

J.A1.2.2.5 Where Paragraph J.A1.4.4 applies, if two (2) or fewer candidates are nominated, no further steps in the election shall take place and such candidate(s) shall be treated as elected as Alternate members and Paragraph J.A1.3.2.4 shall apply in relation to such candidate(s).

J.A1.3	VOTING

J.A1.3.1 Voting papers

J.A1.3.1.1 Voting papers shall be submitted in accordance with the Election Timetable.

J.A1.3.1.2 Each offshore transmission owner may submit one voting paper. A1.3.2 Preference votes and voting rounds

J.A1.3.2.1   Each offshore transmission owner submitting a voting paper shall vote by indicating on the voting paper a first, second and third preference ("Preference Votes") among the candidates.

J.A1.3.2.2   A voting paper need not indicate a second, or a third, preference, but the same candidate may not receive more than one Preference Vote in a voting paper.

J.A1.3.2.3  Candidates shall be elected in three voting rounds (together where necessary with a further round under Paragraph J.A1.3.6) in accordance with the further provisions of this Paragraph J.A1.3.

J.A1.3.2.4  The Secretary shall determine which candidates are elected and announce (to the authority and all offshore transmission owners) the results of the election in accordance with the Election Timetable.

J.A1.3.2.5	The Secretary shall not disclose the Preference Votes cast by offshore transmission owners or received by candidates; but an offshore transmission owner may request that the authority scrutinise the conduct of the election, provided that such offshore transmission owner shall bear the costs incurred by the authority in doing so unless the authority recommends that the election results should be annulled.

J.A1.3.2.6 Further references to voting papers in this Paragraph J.A1.3 do not include voting papers which are invalid or are to be disregarded (i.e. voting papers not made or submitted in accordance with this Annex 1).

J.A1.3.3 First voting round

J.A1.3.3.1	In the first voting round:

- the number of first Preference Votes allocated under all voting papers to each candidate shall be determined.

- the first round qualifying total shall be: ( T / N ) + 1

Where

T is the total number of first Preference Votes in all voting papers;

N is the number of offshore transmission owners’ members

and/or Alternate members to be elected.

J.A1.3.3.2		If the number of first Preference Votes allocated to any candidate is equal to or greater than the first round qualifying total, that candidate shall be elected.

J.A1.3.4 Second voting round

J.A1.3.4.1	In the second voting round:

- the remaining candidates are those which were not elected in the first voting round;

- the remaining voting papers are voting papers other than those under which the first Preference Votes were for candidates elected in the first voting round;

- the number of first and second Preference Votes allocated under all remaining voting papers to each remaining candidate shall be determined;

- the second round qualifying total shall be ( T' / N' ) + 1

Where

T' is the total number of first Preference Votes and second Preference Votes allocated under all remaining voting papers;

N' is the number of members and/or Alternate members remaining to be elected after the first voting round.

J.A1.3.4.2	If the number of first and second Preference Votes allocated to any remaining candidate is equal to or greater than the second round qualifying total, that candidate shall be elected.

J.A1.3.5 Third voting round

J.A1.3.5.1	In the third voting round:

(a) the remaining candidates are those which were not elected in the first or second voting rounds;

- the remaining voting papers are voting papers other than those under which the first or second Preference Votes were for candidates elected in the first or second voting rounds;

- the number of first, second and third Preference Votes allocated under all remaining voting papers to each remaining candidate shall be determined;

- the third round qualifying total shall be ( T" / N" ) + 1

Where

T" is the total number of first Preference Votes, second Preference Votes and third Preference Votes allocated under all remaining voting papers;

N" is the number of members remaining to be elected after the first and second voting rounds.

J.A1.3.5.2	If the number of first, second and third Preference Votes allocated

to any remaining candidate is equal to or greater than the third round qualifying total, that candidate shall be elected.

J.A1.3.6	Further provisions

J.A1.3.6.1	If after any voting round the number of candidates achieving the

required Preference Votes threshold exceeds the number of persons remaining to be elected, the following tie-break provisions shall apply between the tied candidates. In addition, if after the third voting round any member(s) or Alternate member(s) remain to be elected the following tie-break provisions shall apply between the remaining candidates:

- the tied or remaining candidates (as applicable) shall be ranked in order of the number of first Preference Votes allocated to them, and the candidate(s) with the greatest number of such votes shall be elected;

- in the event of a tie between two or more candidates within Paragraph (a), the candidate(s) (among those tied) with the greatest number of second Preference Votes shall be elected;

- in the event of a tie between two or more candidates within Paragraph (b), the Secretary shall select the candidate(s) (among those tied) to be elected by drawing lots.

J.A1.3.7 Members and Alternate Members

J.A1.3.7.1   Except where Paragraphs J.A1.4.3 or J.A1.4.4 apply, the two (2) candidates receiving the greatest number of votes shall be elected as offshore transmission owners’ members and the next two (2) shall be elected as offshore transmission owners’ Alternate members.

J.A1.3.7.2   Where Paragraph J.A1.4.3 applies the number of candidate(s) up to and including the number of Member Interim Vacancies receiving the greatest number of votes pursuant to the Interim panel and Alternate Election Process shall be elected as offshore transmission owners’ member(s) and the remaining candidates up to and including the number of Alternate member Interim Vacancies receiving the greatest number of votes shall be elected as Alternate member(s).

J.A1.3.7.3 	Where Paragraph J.A1.4.4 applies the two (2) candidates receiving the greatest number of votes pursuant to the Alternate Election Process shall be elected as Alternate members.

J.A1.4	VACANCIES

J.A1.4.1 General

J.A1.4.1.1	If a member ceases to hold office pursuant to Paragraph J.4.11.1 (b) (i) then Paragraph J.A1.4.2 shall apply.

J.A1.4.1.2	If a member ceases to hold office pursuant to Paragraph J.4.11.1 (a), J.4.11.1 (b) (ii) to (vi) (inclusive) or J.4.11.1 (c) then Paragraph J.A1.4.3 shall apply.

J.A1.4.1.3 If an Alternate member ceases to hold office pursuant to Paragraph J.4.11 (the “Resigning” Alternate member) then Paragraph J.A1.4.4 shall apply.

J.A1.4.1.4 The provisions of Paragraph J.A1.2.1.2 shall apply, mutatis mutandis, to any replacement member or any replacement Alternate member under this Paragraph J.A1.4.

J.A1.4.2 Replacement of a member who ceases to hold office pursuant to Paragraph J.4.11.1 (b) (i)

J.A1.4.2.1	Where this Paragraph J.A1.4.2 applies, and in accordance with the duties set out in Paragraph J.4.2, such member may appoint a replacement member (subject to Paragraph J.A1.4.2.2) for the remainder of the term of office of such member and shall notify the Secretary of a replacement member at the same time as they  resign. If such member does not appoint a replacement at the time of notifying the Secretary of their resignation then such member will be replaced in accordance with Paragraph J.A1.4.3 and this Paragraph J.A1.4.2.1 shall no longer apply.

J.A1.4.2.2 A member shall only appoint an Alternate member to be their replacement pursuant to Paragraph J.A1.4.2.1 and such Alternate member chosen to be a member shall then become a Resigning Alternate member and be replaced in accordance with Paragraph J.A1.4.4.

J.A1.4.3	Replacement of a member who ceases to hold office pursuant to Paragraph J.4.11.1 (a), J.4.11.1 (b) (ii) to (vi) or J.4.11.1 (c)

J.A1.4.3.1   Subject to Paragraph J.A1.4.3.2, such member shall, where one or more Alternate member(s) hold office, be replaced by the Alternate member who previously received the highest number of cumulative Preference Votes but if there were a tie-break in relation to such Preference Votes then the tie-break provisions set out in Paragraph J.A1.3.6.1 shall apply, in either circumstance such Alternate member selected to be a member shall then become a Resigning Alternate member and be replaced in accordance with Paragraph J.A1.4.4.

J.A1.4.3.2   If there are no Alternate members in office upon a member ceasing to hold office then:

- Where there are not less than six (6) months remaining until the next full election further members shall be elected in accordance with Paragraphs J.A1.2, J.A1.3 and subject to the following Paragraphs J.A1.4.3.3 to J.A1.4.3.5 (inclusive) (the “Interim Panel and Alternate Election Process”).

- Where there are less than six (6) months remaining until the next full election no further members or Alternate members shall be elected pursuant to this Paragraph J.A1.4.3 and the positions shall remain vacant until the next full election.

J.A1.4.3.3   Where this Paragraph J.A1.4.3.3 applies the Secretary shall indicate in the invitation referred to at Paragraph J.A1.1.2.1 the number of vacancies for both member(s) (“member Interim Vacancies”) and Alternate member(s) (“Alternate member Interim Vacancies”) for which the Interim panel and Alternate Election Process is being held.

J.A1.4.3.4  Any member(s) or Alternate member(s) elected pursuant to the Interim panel and Alternate Election Process shall cease to hold office at the next full election.

J.A1.4.3.5    The timetable for the Interim panel and Alternate Election Process shall be expedited and the Secretary shall prepare a timetable accordingly.

J.A1.4.4	Replacement of a Resigning Alternate Member

J.A1.4.4.1	Subject to Paragraph J.A1.4.4.2 a Resigning Alternate member shall not be replaced.

J.A1.4.4.2	If there are no Alternate members remaining in office following the

resignation of an Alternate member or their appointment as a member in accordance with J.A1.4.2 or J.A1.4.3 then:

- Where there are not less than six (6) months remaining until the next full election further Alternate members shall be elected in accordance with Paragraphs J.A1.2, J.A1.3 and subject to the following paragraphs J.A1.4.4.3 to J.A1.4.4.5 (inclusive) (the “Alternate Election Process”).

- Where there are less than six (6) months remaining until the next full election no further Alternate members shall be elected and the positions shall remain vacant until the next full election.

J.A1.4.4.3    Where this Paragraph A1.4.4.3 applies, a reference in Paragraphs J.A1.2 and J.A1.3 to an offshore transmission owners’ member shall not apply except in the case of Paragraph J.A1.3.5.1 (d) where the reference to “members” shall be read and construed as a reference to “Alternate members”.

J.A1.4.4.4    Any Alternate member(s) elected pursuant to the Alternate Election Process shall cease to hold office at the next full election.

J.A1.4.4.5    The timetable for the Alternate Election Process shall be expedited and the Secretary shall prepare a timetable accordingly.

Appendix J, Annex 2 - SQSS Modification Process Flow Chart

Appendix J, Annex 3 - Modification Proposal Form

A copy of the Modification Proposal Form can be found electronically on the ISOP website at

Modification Proposal Form