## Slide 1: Grid Code Development Forum
05 August 2026

## Slide 2: Agenda
1 | Introduction, meeting objectives and review of previous actions - Claire Newton, NESO | 
2 | Code Administrator Update – NESO (Code Administrator) | 
3 | Alternate Reactive Power Capability – Tanmay Kadam, NESO | 
4 | Compliance Clarifications and Corrections Modifications – Tanmay Kadam/Amanda Rooney, NESO | 
5 | AOB and Meeting Close - Claire Newton, NESO | 

## Slide 3: GCDF – Objectives and Expectations
Objective
Develop ideas, understand impacts to industry and modification content discussion, in relation to Grid Code related issues.
Anyone can bring an agenda item (not just NESO!)
Expectations
Explain acronyms and context of the update or change
Be respectful of each other’s opinions and polite when providing feedback and asking questions
Contribute to the discussion
Language and Conduct to be consistent with the values of equality and diversity
Keep to agreed scope
  The Forum will be recorded and made available on the GCDF webpage along with summary notes.

## Slide 4: Code Administrator Update
NESO (Code Administrator)

## Slide 5: Alternate Reactive Power Capability due to Network Restrictions Tanmay Kadam – Eng. Compliance

## Slide 6: Current Grid Code Requirements
ECC.A.7.2.1
  The Company requires that the continuously acting automatic voltage control system for the Onshore Power Park Module, Onshore HVDC Converter or OTSDUW Plant and Apparatus shall meet the following functional performance specification.
  If a Network Operator has confirmed to The Company that its network to which an Embedded Onshore Power Park Module or Onshore HVDC Converter or OTSDUW Plant and Apparatus is connected is restricted such that the full reactive range under the steady state voltage control requirements (ECC.A.7.2.2) cannot be utilised, The Company may specify alternative limits to the steady state voltage control range that reflect these restrictions.
  Where the Network Operator subsequently notifies The Company that such restriction has been removed, The Company may propose a Modification to the Bilateral Agreement (in accordance with the CUSC contract) to remove the alternative limits such that the continuously acting automatic voltage control system meets the following functional performance specification. All other requirements of the voltage control system will remain as in this Appendix.

## Slide 7: Case – 1: DNO Restriction in place before NESO Compliance
A Distribution Network Operator (DNO) may put a restriction on the Embedded Generator’s reactive power capability
This restriction may be time bound and may occur due to any ongoing network reinforcement works or operability challenge from the DNO (example: low fault level)
In such case, the Generator shall inform NESO of the relevant restriction at the earliest possible opportunity and agree on the alternative reactive power capability
  These restrictions shall then be incorporated into the NESO Bilateral Agreement with the User
Where the restricted reactive capability is smaller than the required GC minimum (0.95pf)
  User shall still be required to demonstrate that the installed Plant will be capable of providing the GC minimum reactive power using the ‘voltage control and reactive capability’ simulation studies*
  Additionally, the User shall be required to submit simulations demonstrating compliance with respect to the restricted reactive capability
  The onsite testing shall be completed with respect to the restricted capability (in co-ordination with the DNO)
When the DNO lifts the restriction, the corresponding NESO Bilateral Agreement shall then be amended, and the User will be required to demonstrate compliance with unrestricted capability as per Grid Code
*Network restrictions or conditions can change over time, and the User is required to ensure their Plant and Apparatus is designed and capable of providing the Grid Code minimum required capability for future proofing the asset.

## Slide 8: Case – 2: DNO Restriction in place after NESO Compliance
A Network Operator may put a restriction on the Embedded Generator’s reactive power capability when the Site has achieved NESO compliance (post FON)
The User (which may also include the Network Operator) shall notify NESO of such operational restrictions as per OC7 procedures. This may be treated as an operational issue and NESO Control Room shall liaise with the relevant Network Operator prior to issuing any instructions to the Embedded Generator
It is not required for the Generator to re-demonstrate the full Grid Code compliance in such cases as it already achieved the FON.
The Generator may be asked to re-submit the models incorporating the relevant restriction as per PC.A.9.7.5 that puts obligation on User to ensure the submitted models continue to demonstrate true and accurate representation of their Plant

## Slide 9: Case – 3: No Restriction in place, but Low Network Fault Levels (applicable for both Embedded/Directly Connected)
There may be instances where there is no restriction in place by the Network Operator or TO however the site fault level is very low which may cause issues for the User in achieving the compliance (e.g. voltage control simulations)
Where the User is unable to demonstrate the GC min. reactive capability using the min. fault level, NESO may suggest alternative methods to demonstrate compliance.
For example, it has been brought to NESO’s attention that some Users may not be able to demonstrate ECP.A.3.4 (v) where the fault level is very low.
  Users shall demonstrate the capability based on actual system fault level (showing the limitation in achieving required reactive capability without triggering LVRT/HVRT)
  In such cases, the Users are required to follow NESO recommended approaches to demonstrate compliance (e.g. using slightly higher fault levels (that are within the TO specified range) for the purposes of this simulation)
Where the DNO has any concerns over onsite testing performance and impact on DNO’s network (say during reactive capability testing as per ECP.A.6), NESO can agree on alternative testing procedure in coordination with the relevant DNO

## Slide 10: Thank you
For any questions, please reach out: tanmay.kadam@neso.energy

## Slide 11: Compliance Clarifications and Corrections Modifications
Amanda Rooney, NESO

## Slide 12: New Modification- Housekeeping and small but Material Changes
We're here to discuss:
  A large number of small changes

## Slide 13: Thank You

## Slide 14
AOB:
AOB1: Technical Requirements for Demand Connections (An update on progress of the demand expert group)